## Worksheet
Title | Abstract | Publication Number | Publication Date | Application Number | Filing Date | Priority | Patent Family | Applicant(s) | Inventor(s) | International Patent Classification (IPC) | Cooperative Patent Classification (CPC) | Cited Documents | Citing Documents | Claims | Description | Tags | Comments | Reviews | Rankings
[ZH CN108566071B]: 模块化电源系统 [EN US11101740B2]: Modular power supply system [PT BR112019012080A2]: sistema de fornecimento de energia modular [DE EP3557753A4]: MODULARES ENERGIESYSTEM [FR EP3557753A4]: SYSTÈME D'ALIMENTATION MODULAIRE | [ZH CN108566071B]: 一种模块化电源系统包括：一个主控制器，被配置为输出主控制信号；N个本地控制器，其中每一个所述本地控制器被配置为接收所述主控制信号，以输出至少一个本地控制信号；以及N个功率单元，与所述N个本地控制器一一对应，其中每一个所述功率单元包括第一端和第二端，每一个所述功率单元的所述第二端连接到相邻的一个所述功率单元的所述第一端，每一个所述功率单元被配置为包括M个功率变换器，其中每一个所述功率变换器包括第三端和第四端，每一个所述功率变换器的所述第四端连接到相邻的一个所述功率变换器的所述第三端，每一个所述功率变换器被配置为根据对应的所述本地控制器输出的所述本地控制信号运行，其中N和M均为大于1的自然数。 [EN US11101740B2]: A modular power supply system includes: a main controller, configured to output a main control signal; N local controllers, wherein each of the local controllers is configured to receive the main control signal to output at least one local control signal; and N power units, in one-to-one correspondence with the N local controllers, wherein each of the power units includes a first end and a second end, and the second end of each of the power units is connected to the first end of an adjacent one of the power units, each of the power units is configured to include M power converters, wherein each of the power converters includes a third end and a fourth end, the fourth end of each of the power converters is connected to the third end of an adjacent one of the power converters. [PT BR112019012080A2]: a presente invenção refere-se a um sistema de fornecimento de energia modular, incluindo: um controlador principal (90), configurado para emitir um sinal de controle principal; em que cada um dos controladores locais (91) recebe o sinal de controle principal para emitir pelo menos um sinal de controle local; n fornecimentos de energia auxiliares (93), em correspondência um-para-um com os n controladores locais (91), em que cada um dos fornecimentos de energia auxiliares (93) fornece energia ao controlador local correspondente (91); e n unidades de potência (70), em correspondência um-para-um com os n controladores locais (91), em que cada uma das unidades de potência (70) inclui uma primeira extremidade e uma segunda extremidade, a segunda extremidade de cada uma das unidades de potência (70) estão ligadas à primeira extremidade de uma unidade adjacente das unidades de potência (70), cada uma das unidades de potência (70) inclui m conversores de potência (701), cada um dos conversores de potência (701) opera de acordo com o sinal de controle local. | EP3557753A4 | 2019-10-23 2020-09-16 | EP17881738A | 2017-12-15 2017-12-15 | CN201611170857A, 2016-12-16 CN201611191912A, 2016-12-21 CN201710106946A, 2017-02-27 CN201711322794A, 2017-12-12 CN2017116353W, 2017-12-15 CN201611170857A, 2016-12-16 CN201611191912A, 2016-12-21 CN201710106946A, 2017-02-27 CN201711322794A, 2017-12-12 CN2017116353W, 2017-12-15 | CN108233747B: 2020-12-04 CN108566071B: 2021-04-20 CN108566072A: 2018-09-21 CN108566101B: 2020-09-22 TWI661632B: 2019-06-01 TWI661633B: 2019-06-01 TWI661634B: 2019-06-01 TWI675542B: 2019-10-21 AU2017376697B2: 2021-04-29 AU2017376698B2: 2021-04-29 AU2017376699B2: 2021-05-06 US2019294187A1: 2019-09-26 BR112019011177A2: 2019-10-08 EP3557751A4: 2020-09-09 EP3557752A4: 2020-09-16 EP3557753A4: 2020-09-16 US10924030B2: 2021-02-16 BR112019012073A2: 2019-11-12 BR112019012080A2: 2019-11-12 US11101740B2: 2021-08-24 US2020044555A1: 2020-02-06 | DELTA ELECTRONIC ENTERPRISE MAN SHANGHAI CO LTD 台达电子企业管理(上海)有限公司 DELTA ELECTRONICS SHANGHAI CO LTD DELTA ELECTRONICS SHANGHAI CO DELTA ELECTRONICS (SHANGHAI) CO LTD | YING JIANPING WANG MING HUANG XIAOBO LIU JUN HU ZHIMING YING JIAN-PING HUANG XIAO-BO HU ZHI-MING JIANPING YING JUN LIU MING WANG XIAOBO HUANG ZHIMING HU | H02M7/493: I H02M7/487: I H02M1/00: I H02M1/32: I H02M1/08: I H02M7/483: I H02M7/00: I H02M3/00: I H02J3/18: I H02M7/48: I H02M7/49: I G05F1/10: I H02M7/219: I H02M7/521: I H02M1/096: I G06F1/26: I H02M3/335: I H02M7/797: I H02M1/36: I H02M3/155: I H02M7/5387: I | H02M1/00: I H02M1/08: I H02M1/32: I H02M3/00: I H02M7/00: I H02M7/483: I H02M7/487: A H02M7/493: I H02M1/0067: A H02M1/007: A H02M1/325: A H02M7/4835: A G05F1/10: I H02M1/096: I H02M7/49: I H02M1/0006: A H02M1/0095: I H02M7/4837: I | CN103280952A CN103546024A CN105453405A EP2595302A1 US2015340890A1 CN105406705A CN102593859A CN103314517A CN201864877U CN102545675A CN203562783U CN103856091A CN106505896A CN101917126A CN104410101A TW201218604A TW201633691A CN105391313A TW201306470A CN102148579A TW265484B TW201528666A CN202616988U CN204967648U WO2012028640A2 US2012032512A1 FR3015146A1 DE102012213055A1 EP2905889A1 CN203775065U CN105071403A CN104272589A CN204858577U CN105429476A CN105490285A CN101719727A WO2018050256A1 EP2945273A1 US2016190846A1 US7705705B2 US8686746B2 US2005237010A1 US2009268496A1 US2013148390A1 US2013229838A1 US2014015322A1 US2016072395A1 US2016277071A1 US2017029242A1 US2017033703A1 US2017187234A1 CN101158701A CN101795072A CN101262178A CN102611345A CN102684543A CN102967748A CN203522498U CN103311932A CN103580050A CN105356770A CN103762596A CN106160463A CN206332626U WO2009027520A2 WO2014037406A1 US2015180352A1 CN103326393A CN204044223U | CN109830968A CN109830968 109830968 CN110718953A CN110718953 110718953 US10978964B2 US10978964 10978964 CN111600387A CN111600387 111600387 US10727664B2 US10727664 10727664 | [ZH CN108566071B]: 1 .一种模块化电源系统，被配置为包括： 一个主控制器，被配置为输出主控制信号； N个本地控制器，其中每一个所述本地控制器被配置为接收所述主控制信号，以输出至 少一个本地控制信号；以及 N个功率单元，与所述N个本地控制器一一对应，其中每一个所述功率单元包括第一端 和第二端，每一个所述功率单元的所述第二端连接到相邻的一个所述功率单元的所述第一 端，每一个所述功率单元被配置为包括M个功率变换器，其中每一个所述功率变换器包括第 三端和第四端，每一个所述功率变换器的所述第四端连接到相邻的一个所述功率变换器的 所述第三端，且第一个所述功率变换器的所述第三端为所述功率单元的所述第一端，第M个 所述功率变换器的所述第四端为所述功率单元的所述第二端，每一个所述功率变换器被配 置为根据对应的所述本地控制器输出的所述本地控制信号运行， 其中N和M均为大于1的自然数，用于控制所述M个功率变换器中至少2个功率变换器中 的功率半导体开关导通和断开的所述本地控制信号为同一个本地控制信号，其中所述至少 2个功率变换器具有相同的拓扑结构。 2 .如权利要求1所述的模块化电源系统，被配置为还包括： N个辅助电源，与所述N个本地控制器一一对应，其中每一个所述辅助电源被配置为给 对应的所述本地控制器提供电源。 3 .如权利要求1所述的模块化电源系统，其中所述功率变换器为AC/DC变换器、DC/AC变 换器和DC/DC变换器中的任何一种。 4 .如权利要求1所述的模块化电源系统，其中所述M个功率变换器的直流母线电压为全 部相同，部分相同，或全部不相同。 5 .如权利要求1所述的模块化电源系统，其中所述M个功率变换器的拓扑结构为全部相 同，或部分相同。 6 .如权利要求5所述的模块化电源系统，其中每一个所述功率单元中的所述M个功率变 换器的拓扑结构全部为全桥变换器、半桥变换器、中性点可控三电平变换器、二极管钳位三 电平变换器、飞跨电容三电平变换器、全桥谐振变换器和半桥谐振变换器中的一种。 7 .如权利要求5所述的模块化电源系统，其中每一个所述功率单元中的所述M个功率变 换器的拓扑结构为全桥变换器、半桥变换器、中性点可控三电平变换器、二极管钳位三电平 变换器、飞跨电容三电平变换器、全桥谐振变换器和半桥谐振变换器中的两种或两种以上 的组合。 8 .如权利要求6所述的模块化电源系统，其中每一个所述功率变换器被配置为包括： 至少一个所述功率半导体开关，其中每一个所述本地控制信号被配置为控制对应的所 述功率半导体开关的导通和断开。 9 .如权利要求7所述的模块化电源系统，其中每一个所述功率变换器被配置为包括： 至少一个所述功率半导体开关，其中每一个所述本地控制信号被配置为控制对应的所 述功率半导体开关的导通和断开。 10 .如权利要求8或9所述的模块化电源系统，其中每一个所述功率单元还包括： M个驱动电路，与所述M个功率变换器一一对应，其中每一个所述驱动电路被配置为连 接于对应的所述功率变换器的所述功率半导体开关，接收对应的所述本地控制器输出的本 地控制信号，以输出至少一个驱动信号来驱动对应的所述M个功率变换器中的所述功率半 导体开关的导通和断开。 11 .如权利要求8或9所述的模块化电源系统，其中每一个所述功率单元还包括： 多个驱动电路，其中所述多个驱动电路的数量等于所述功率单元中所述至少一个功率 半导体开关的数量，每一个所述驱动电路被配置为连接于对应的所述功率变换器的所述功 率半导体开关，接收对应的所述本地控制器输出的本地控制信号，以输出驱动信号来驱动 对应的所述功率半导体开关的导通和断开。 12 .如权利要求10所述的模块化电源系统，其中每一个所述驱动电路与对应的所述本 地控制器直接电连接，或者通过磁隔离器件连接，或者通过光隔离器件连接。 13 .如权利要求1所述的模块化电源系统，其中每一个所述本地控制器与所述主控制器 通过磁隔离器件连接，或者通过光隔离器件连接。 14 .如权利要求11所述的模块化电源系统，其中每一个所述驱动电路与对应的所述本 地控制器直接电连接，或者通过磁隔离器件连接，或者通过光隔离器件连接。 15 .如权利要求10所述的模块化电源系统，其中各所述驱动电路为彼此相同或彼此不 相同。 16 .如权利要求11所述的模块化电源系统，其中各所述驱动电路为彼此相同或彼此不 相同。 17 .如权利要求10所述的模块化电源系统，其中每一个所述驱动电路包括磁隔离器件， 所述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲;或者每一个所述驱动电路 包括磁隔离器件，所述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲以及功率 脉冲;或者每一个所述驱动电路包括磁隔离器件，一部分所述驱动电路的所述磁隔离器件 传输所述本地控制信号中包含的驱动逻辑脉冲，另一部分所述驱动电路的所述磁隔离器件 传输所述本地控制信号中包含的所述驱动逻辑脉冲以及功率脉冲。 18 .如权利要求11所述的模块化电源系统，其中每一个所述驱动电路包括磁隔离器件， 所述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲;或者每一个所述驱动电路 包括磁隔离器件，所述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲以及功率 脉冲;或者每一个所述驱动电路包括磁隔离器件，一部分所述驱动电路的所述磁隔离器件 传输所述本地控制信号中包含的驱动逻辑脉冲，另一部分所述驱动电路的所述磁隔离器件 传输所述本地控制信号中包含的所述驱动逻辑脉冲以及功率脉冲。 19 .如权利要求5所述的模块化电源系统，其中所述同一个本地控制信号的数量与所述 至少2个功率变换器中的所述至少一个功率半导体开关的数量相同，且每一个所述相同的 本地控制信号被配置为控制对应的所述功率半导体开关导通和断开。 20 .如权利要求1所述的模块化电源系统，其中每一个所述功率变换器的所述第三端和 所述第四端之间并联有开关，当所述功率变换器正常工作时，所述开关断开，当所述功率变 换器发生故障时，所述开关导通。 21 .如权利要求20所述的模块化电源系统，其中所述开关是半控型器件、全控型器件或 机械开关。 22 .如权利要求20所述的模块化电源系统，当任一所述功率变换器发生故障时，所述本 地控制器会接收到反映对应的所述功率变换器故障类型的故障信号，并输出至少一个保护 信号。 23 .如权利要求22所述的模块化电源系统，其中所述本地控制器输出所述保护信号以 控制对应的所述功率变换器的开关导通，并且所述本地控制器停止输出控制对应的所述功 率变换器运行的所述本地控制信号。 24 .如权利要求22所述的模块化电源系统，其中所述至少一个保护信号的数量为M，所 述本地控制器输出每一个所述保护信号以控制对应的所述功率变换器的所述开关导通，并 且所述本地控制器停止输出控制所述M个功率变换器运行的所述至少一个本地控制信号。 25 .如权利要求22所述的模块化电源系统，其中所述至少一个保护信号的数量为1，所 述本地控制器输出所述保护信号以控制所述M个功率变换器的所述开关导通，并且所述本 地控制器停止输出控制所述M个功率变换器运行的所述至少一个本地控制信号。 26 .如权利要求1所述的模块化电源系统，其中所述功率单元的所述第一端和所述第二 端之间并联有开关，当所述功率单元正常工作时，所述开关断开，当所述功率单元发生故障 时，所述开关导通。 27 .如权利要求26所述的模块化电源系统，其中，当任一所述功率变换器发生故障时， 所述本地控制器会接收到反映对应的所述功率变换器故障类型的故障信号，并输出一保护 信号以控制所述开关导通，并且所述本地控制器停止输出控制所述M个功率变换器运行的 所述至少一个本地控制信号。 [EN US11101740B2]: 1. A modular power supply system, configured to comprise: a main controller, configured to output a main control signal;N local controllers, wherein each of the local controllers is configured to receive the main control signal to output at least one local control signal; andN power units, in one-to-one correspondence with the N local controllers, wherein each one of the power units comprises a first end and a second end, and the second end of the said one power units is connected to the first end of an adjacent one of the power units, the said one power unit is further configured to comprise M power converters, wherein each one of the power converters comprises a third end and a fourth end, the fourth end of the said one power converter is connected to the third end of an adjacent one of the power converters, and the third end of a first one of the power converters is connected to the first end of the said one power unit, the fourth end of an M-th one of the power converters is connected to the second end of the said one power unit, each of the power converters is configured to operate according to the local control signal output by a corresponding local controller, and the first end of a first one of the power units is open and the second end of a N-th one of the power units is open,wherein both N and M are natural numbers greater than one,wherein the said one power unit further comprises: M drive circuits, in one-to-one correspondence with the M power converters, wherein each one of the drive circuits is configured to be connected to at least one power semiconductor switch of the corresponding power converter, and receive the at least one local control signal output by the corresponding local controller, to output at lease one driving signal to control turn-on and turn-off of the power semiconductor switch in the corresponding M power converters; or the said one power unit further comprises: a plurality of drive circuits, wherein a number of the plurality of drive circuits is equal to a number of the power semiconductor switches in the power unit, each one of the drive circuits is configured to be connected to the power semiconductor switch of the corresponding power converter, to receive a local control signal output by the corresponding local controller to output a driving signal to control turn-on and turn-off of the corresponding power semiconductor switch, andwherein each of the drive circuits comprises a magnetic isolation device, the magnetic isolation device of a portion of the drive circuits transmits drive logic pulses contained in the local control signal, and the magnetic isolation device of another portion of the drive circuits transmits the drive logic pulses and power pulses contained in the local control signal. 2. The modular power supply system of claim 1, further comprising: N auxiliary power supplies, in one-to-one correspondence with the N local controllers, wherein each of the auxiliary power supplies is configured to provide power to a corresponding local controller. 3. The modular power supply system of claim 1, wherein the power converter is any one of an AC/DC converter, a DC/AC converter and a DC/DC converter. 4. The modular power supply system of claim 1, wherein the topology of all of the M power converters in each of the power units is full-bridge converters. 5. The modular power supply system of claim 1, wherein the topologies of the M power converters in each of the power units ae a combination of two or mom kinds of full-bridge converters, half-bridge converters, neutral point clamped three-level converters, diode clamping three-level converters, flying capacitor three-level converters, full-bridge resonant converters and half-bridge resonant converters. 6. The modular power supply system of claim 5, wherein each of the power converters is configured to comprise: at least one power semiconductor switch, wherein each of the local control signals is configured to control turn-on and turn-off of a corresponding power semiconductor switch. 7. The modular power supply system of claim 1, wherein each of the local controllers is connected to the main controller by a magnetic isolation device or an optical isolation device. 8. The modular power supply system of claim 1, wherein a number of the at least one local control signal is identical to a number of the at least one power semiconductor switch in the power converter, and each of the local control signals is configured to control the corresponding power semiconductor switch to be turned on or off. 9. The modular power supply system of claim 1, wherein a bypass switch is connected in parallel between the third end and the fourth end of each of the power converters, the bypass switch is turned off when the power converter operates normally, and the bypass switch is turned on when the power converter fails. 10. The modular power supply system of claim 9, wherein, when any one of the power converter fails, the local controller receives a fault signal reflecting a fault type of the corresponding power converter, and outputs at least one protection signal. 11. The modular power supply system of claim 10, wherein the local controller outputs the protection signal to control the bypass switch of the corresponding power converter to be turned on, and the local controller stops outputting the local control signal that controls operation of the corresponding power converter. 12. The modular power supply system of claim 10, wherein a number of the at least one protection signal is M, the local controller outputs each of the protection signals to control the bypass switches of the corresponding power converters to be turned on, and the local controller stops outputting the at least one local control signal that controls operation of the M power converters. 13. The modular power supply system of claim 10, wherein a number of the at least one protection signal is one, the local controller outputs the protection signal to control the bypass switches of the M power converters to be turned on, and the local controller stops outputting the at least one local control signal that controls operation of the M power converters. 14. The modular power supply system of claim 1, wherein a bypass switch is connected in parallel between the first end and the second end of the power unit, the bypass switch is turned off when the power unit operates normally, and the bypass switch is turned on when the power unit fails. 15. The modular power supply system of claim 14, wherein, when any one of the power converters fails, the local controller receives a fault signal reflecting a failure type of the corresponding power converter, and outputs a protection signal to control the bypass switch to be turned on, and the local controller stops outputting the at least one local control signal that controls operation of the M power converters. | [ZH CN108566071B]: 模块化电源系统 技术领域 [0001]本发明涉及电力电子技术领域，特别涉及一种模块化电源系统。 背景技术 [0002]目前，在一些较高电压等级（如10kV以上）应用场合，如静止无功发生器（Static Var Generator，SVG）、中压变频器（Medium Variable-frequency Drive，MVD）以及轻型高 压直流输电系统（High Voltage Direct Current Transmission Light，HVDC-Light）等， 由于系统电压等级较高，受半导体器件的耐压等级和成本所限，通常都采用功率单元级联 的电路拓扑结构。 [0003]传统的功率单元级联的拓扑结构需要给每一个功率单元即功率变换器配备一套 光纤、辅助电源、本地控制器。这种功率单元级联的拓扑结构随着电压等级的提高，需要级 联的功率单元的数量也随之增加，导致光纤、辅助电源及本地控制器的数量也随之增加，使 得这种拓扑结构的设计复杂，成本高，同时也会降低其可靠性。 [0004]图1是现有技术中一个三相SVG系统的结构示意图。图2是现有技术中一个更具体 的三相SVG系统的示意图。图1和图2中的SVG系统包括三相电路，每一相电路中的功率单元 级联连接。 [0005]如图1中所示，该SVG系统的每一相电路都由多个功率单元1级联而成。这里的术语 “级联”在本领域中是公知常识，即每一个功率单元包括第一端「和第二端T2,相邻两个功率 单元的其中一个的第二端T2与另一个的第一端T1连接。每一相电路的第1个功率单元的第一 端「经滤波器L分别连接到三相电网的UA、UB和UC三相线路上，每一相电路的最后一个功率 单元的第二端相互连接。 [0006]如图2所述，该SVG系统的每一相电路都由8个功率单元P1至P8级联而成。每一个功 率单元包括如图1中所示的第一端和第二端，其中相邻两个功率单元的其中一个的第二端 与另一个的第一端连接。例如，功率单元P1的第二端与功率单元P2的第一端连接，功率单元 P2的第二端与功率单元P3的第一端连接，依次类推，功率单元P7的第二端与功率单元P8的第 一端连接。三相电路中三个功率单元P3q第一端经过滤波电路（由电感L、电阻R和电容C组 成）分别连接于三相电网G的UA、UB和UC相，其中三相电网G的UA、UB和UC相连接负载R10ad。三相 电路中三个功率单元P8的第二端相互连接。每一个功率单元中包括四个功率开关器件2。每 一个功率开关器件2由一个功率半导体开关S与一个反向并联的体二极管或外接二极管D构 成。功率半导体开关S的集电极与二极管D的阴极连接，功率半导体开关S的发射极与二极管 D的阳极连接。由于功率半导体开关S与一个反向并联的体二极管或外接二极管D二者通常 作为一个整体使用，所以为了描述简洁的目的，以下描述中不再单独提及反向并联的体二 极管或外接二极管D。 [0007]图1中所示的功率单元1可以是全桥（H桥）电路，也可以是其它的电路拓扑结构，如 半桥电路、整流-逆变电路等。图3是现有技术中的一个H桥电路（拓扑）的示意图。例如，以功 率单元为H桥电路为例,H桥电路如图3中所示，包括功率半导体开关51至54和直流母线电容 CB。功率半导体开关51的第一端连接于直流母线电容CB的正极端和功率半导体开关S3的第 一端。功率半导体开关S1的第二端连接于功率半导体开关S4的第一端。功率半导体开关邑的 第二端连接于直流母线电容CB的负极端和功率半导体开关52的第二端。功率半导体开关S3 的第二端连接功率半导体开关务的第一端。功率半导体开关SI的第二端作为H桥电路的第一 输出端，也即功率单元1的第一端「，功率半导体开关S3的第二端作为H桥电路的第二输出 端，也即功率单元1的第二端T2。 [0008]图4是现有技术中一个单相SVG的示意图。如图4中所示，该单相SVG包括充电部分 3、功率部分4和控制部分5。该单相SVG也包括多个功率单元40，每一个功率单元40包括如图 1中所示的第一端和第二端，相邻两个功率单元40其中一个的第一端与另一个的第二端连 接。图4是应用于25kV单相SVG的传统级联式方案。该SVG由多个功率单元级联后形成一相， 经滤波器和接触器接入电网。该SVG的每一个功率单元40通常采用一个H桥电路。H桥电路的 拓扑结构如图3中所示，这里不再赘述。该SVG系统的每一个功率单元40还包括直流母线电 容CB，其连接关系如图4中所示，其中充电部分3用以对直流母线电容CB进行预充电，控制部 分5用以控制功率部分4的运行。 [0009] 从图4可以看出，在传统的级联式拓扑结构中，除了包括一个主控制器50之外，每 一个功率单元40即作为功率变换器，例如H桥电路，都需要单独配备一套本地控制器51、驱 动电路52、辅助电源53及光纤54,其连接关系如图4中所示，主控制器50输出主控制信号至 本地主控制器51，本地主控制器51根据主控制信号产生对应的功率单元的本地控制信号至 驱动电路52,驱动电路52根据本地控制信号输出驱动信号来驱动对应的功率单元运行。例 如25kV单相SVG，通常可以采用以下两种方案来实现。第一种方案:H桥电路中的功率开关器 件均采用常用的1700V绝缘栅双极型晶体管(Insulated Gate Bipolar Translator， IGBT)，那么单个功率单元40的直流母线电压为1000V，考虑冗余，共需要55级功率单元级 联，因此一共需要55套本地控制板51、55套光纤54及55个辅助电源53。如此多的本地控制器 51、光纤54、辅助电源53将导致SVG的结构设计极其复杂，成本也相当高昂，同时降低了其可 靠性。 [0010] 第二种方案：H桥电路中的功率开关器件选用高压IGBT，例如3300V IGBT甚至 6500V IGBT，将单个功率单元40的电压等级提高。为减少功率单元40的级联数量，减少本地 控制器51、光纤54、辅助电源53的数量，通常可以采用第二种方案。在第二种方案中，若选用 3300V IGBT，每个功率单元40的电压等级相比1700V IGBT方案提高一倍，级联数量可由55 级减少为28级，本地控制器51、光纤54及辅助电源53的数量及成本也可减少一半。但受限于 当前的半导体工艺发展水平，3300V IGBT的成本依然居高不下，同样的电流规格下，其成本 远远超过1700V IGBT成本的2倍。因此第二种方案的成本将远远超过第一种方案。如果选用 6500V IGBT，成本的压力则更高。 [0011]因此，目前不管是采用低压IGBT的功率单元级联方案，或是采用高压IGBT的功率 单元级联方案，均有其显著的缺点。 [0012] 图5是现有技术中一个HVDC-Light系统的示意图。如图5中所示，该HVDC-Light包 括三相电路，每一相电路包括上半桥臂和下半桥臂，每一相电路的上半桥臂和下半桥臂均 包括多个级联的功率单元40和电感L，每一个功率单元40也包括如图1中所示的第一端和第 二端，相邻两个功率单元40其中一个的第一端与另一个的第二端连接，每个上桥臂的电感L 与相应下桥臂的电感L相连，并且两个电感L之间的连接点分别连接到电网，其连接关系如 图5中所示。该HVDC-Light的每一个功率单元40采用了一个半桥变换器。该HVDC-Light的每 一个功率单元40还包括直流母线电容，该HVDC-Light的每一个功率单元40还需要连接驱动 电路52,功率单元40根据驱动电路52输出的驱动信号进行运行。除了主控制器50之外，每一 个功率单元40也都需要配备一套本地控制器51、光纤54及辅助电源53,其连接关系如图5中 所示。 [0013]由于HVDC-Light的直流电压高达上百千伏，需要级联的功率单元40的数量极其庞 大，所以上述提到的问题更加显著，即现有技术中HVDC-Light整体结构复杂、成本高且可靠 性低。 [0014]另外，功率半导体开关的驱动方式也需要进一步考虑和改进。 [0015]另外，针对功率变换器和功率单元的故障的措施也需要进一步考虑和改进。 发明内容 [0016]本发明的目的在于提供一种模块化电源系统，以简化电力电子系统的结构，降低 成本，并提高可靠性。 [0017]根据本发明的一个方面，提供一种模块化电源系统，被配置为包括：一个主控制 器，被配置为输出主控制信号；N个本地控制器，其中每一个所述本地控制器被配置为接收 所述主控制信号，以输出至少一个本地控制信号；以及N个功率单元，与所述N个本地控制器 一一对应，其中每一个所述功率单元包括第一端和第二端，每一个所述功率单元的所述第 二端连接到相邻的一个所述功率单元的所述第一端，每一个所述功率单元被配置为包括M 个功率变换器，其中每一个所述功率变换器包括第三端和第四端，每一个所述功率变换器 的所述第四端连接到相邻的一个所述功率变换器的所述第三端，且第一个所述功率变换器 的所述第三端为所述功率单元的所述第一端，第M个所述功率变换器的所述第四端为所述 功率单元的所述第二端，每一个所述功率变换器被配置为根据对应的所述本地控制器输出 的所述本地控制信号运行，其中N和M均为大于1的自然数。 [0018] 在本发明的一些示例性实施例中，所述的模块化电源系统被配置为还包括:N个辅 助电源，与所述N个本地控制器一一对应，其中每一个所述辅助电源被配置为给对应的所述 本地控制器提供电源。 [0019] 在本发明的一些示例性实施例中，其中所述功率变换器为AC/DC变换器、DC/AC变 换器和DC/DC变换器中的任何一种。 [0020] 在本发明的一些示例性实施例中，其中所述M个功率变换器的直流母线电压为全 部相同，部分相同，或全部不相同。 [0021]在本发明的一些示例性实施例中，其中所述M个功率变换器的拓扑结构为全部相 同，或部分相同。 [0022] 在本发明的一些示例性实施例中，其中每一个所述功率单元中的所述M个功率变 换器的拓扑结构全部为全桥变换器、半桥变换器、中性点可控三电平变换器、二极管钳位三 电平变换器、飞跨电容三电平变换器、全桥谐振变换器和半桥谐振变换器中的一种。 [0023] 在本发明的一些示例性实施例中，其中每一个所述功率单元中的所述M个功率变 换器的拓扑结构为全桥变换器、半桥变换器、中性点可控三电平变换器、二极管钳位三电平 变换器、飞跨电容三电平变换器、全桥谐振变换器和半桥谐振变换器中的两种或两种以上 的组合。 [0024] 在本发明的一些示例性实施例中，其中每一个所述功率变换器被配置为包括:至 少一个功率半导体开关，其中每一个所述本地控制信号被配置为控制对应的所述功率半导 体开关的导通和断开。 [0025] 在本发明的一些示例性实施例中，其中每一个所述功率单元还包括:M个驱动电 路，与所述M个功率变换器一一对应，其中每一个所述驱动电路被配置为连接于对应的所述 功率变换器的所述功率半导体开关，接收对应的所述本地控制器输出的本地控制信号，以 输出至少一个驱动信号来驱动对应的所述M个功率变换器中的所述功率半导体开关的导通 和断开。 [0026] 在本发明的一些示例性实施例中，其中每一个所述功率单元还包括:多个驱动电 路，其中所述多个驱动电路的数量等于所述功率单元中所述至少一个功率半导体开关的数 量，每一个所述驱动电路被配置为电连接于对应的所述功率变换器的所述功率半导体开 关，接收对应的所述本地控制器输出的本地控制信号，以输出驱动信号来驱动对应的所述 功率半导体开关的导通和断开。 [0027] 在本发明的一些示例性实施例中，其中每一个所述驱动电路与对应的所述本地控 制器直接电连接，或者通过磁隔离器件连接，或者通过光隔离器件连接。 [0028] 在本发明的一些示例性实施例中，其中每一个所述本地控制器与所述主控制器通 过磁隔离器件连接，或者通过光隔离器件连接。 [0029]在本发明的一些示例性实施例中，其中各所述驱动电路为彼此相同或彼此不相 同。 [0030] 在本发明的一些示例性实施例中，其中每一个所述驱动电路包括磁隔离器件，所 述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲;或者每一个所述驱动电路包 括磁隔离器件，所述磁隔离器件传输所述本地控制信号中包含的驱动逻辑脉冲以及功率脉 冲;或者每一个所述驱动电路包括磁隔离器件，一部分所述驱动电路的所述磁隔离器件传 输所述本地控制信号中包含的驱动逻辑脉冲，另一部分所述驱动电路的所述磁隔离器件传 输所述本地控制信号中包含的所述驱动逻辑脉冲以及功率脉冲。 [0031] 在本发明的一些示例性实施例中，其中所述至少一个本地控制信号的数量与所述 功率变换器中的所述至少一个功率半导体开关的数量相同，且每一个所述本地控制信号被 配置为控制对应的所述功率半导体开关导通和断开。 [0032]在本发明的一些示例性实施例中，其中每一个所述功率变换器的所述第三端和所 述第四端之间并联有开关，当所述功率变换器正常工作时，所述开关断开，当所述功率变换 器发生故障时，所述开关导通。 [0033] 在本发明的一些示例性实施例中，其中所述开关是半控型器件、全控型器件或机 械开关。 [0034] 在本发明的一些示例性实施例中，当任一所述功率变换器发生故障时，所述本地 控制器会接收到反映对应的所述功率变换器故障类型的故障信号，并输出至少一个保护信 号。 [0035]在本发明的一些示例性实施例中，其中所述本地控制器输出所述保护信号以控制 对应的所述功率变换器的开关导通，并且所述本地控制器停止输出控制对应的所述功率变 换器运行的所述本地控制信号。 [0036]在本发明的一些示例性实施例中，其中所述至少一个保护信号的数量为M，所述本 地控制器输出每一个所述保护信号以控制对应的所述功率变换器的所述开关导通，并且所 述本地控制器停止输出控制所述M个功率变换器运行的所述至少一个本地控制信号。 [0037]在本发明的一些示例性实施例中，其中所述至少一个保护信号的数量为1，所述本 地控制器输出所述保护信号以控制所述M个功率变换器的所述开关导通，并且所述本地控 制器停止输出控制所述M个功率变换器运行的所述至少一个本地控制信号。 [0038]在本发明的一些示例性实施例中，其中所述功率单元的所述第一端和所述第二端 之间并联有开关，当所述功率单元正常工作时，所述开关断开，当所述功率单元发生故障 时，所述开关导通。 [0039] 在本发明的一些示例性实施例中，其中，当任一所述功率变换器发生故障时，所述 本地控制器会接收到反映对应的所述功率变换器故障类型的故障信号，并输出一保护信号 以控制所述开关导通，并且所述本地控制器停止输出控制所述M个功率变换器运行的所述 至少一个本地控制信号。 [0040] 本发明通过将多个功率变换器组成一个功率单元，利用一套本地控制器、光纤控 制多个功率变换器的方法，可大大减少本地控制器、光纤的数量，简化结构设计，降低成本, 提高可靠性。 [0041]本发明通过让功率单元中功率变换器在发生故障时被旁路，同时停止输出控制功 率变换器运行的本地控制信号，提高模块化电源系统的安全性和可靠性。 [0042] 本发明适用于所有AC/DC、DC/AC、DC/DC功率变换器连接的拓扑结构，应用广泛。 附图说明 [0043] 通过参照附图详细描述其示例实施例，本发明的上述和其它目标、特征及优点将 变得更加明显。 [0044]图1是现有技术中一个三相SVG系统的结构示意图； [0045]图2是现有技术中一个更具体的三相SVG系统的示意图； [0046]图3是现有技术中的一个H桥电路（拓扑）的示意图； [0047]图4是现有技术中一个单相SVG的示意图； [0048]图5是现有技术中一个HVDC-Light系统的示意图； [0049]图6是本发明一个实施例的模块化电源系统的方框图； [0050]图7是本发明另一个实施例的模块化电源系统的方框图； [0051]图8是本发明另一个实施例的模块化电源系统的方框图； [0052]图9是本发明另一个实施例的模块化电源系统的方框图； [0053]图10是本发明另一个实施例的模块化电源系统的方框图； [0054]图11是本发明另一个实施例的模块化电源系统的方框图； [0055]图12是本发明另一个实施例的模块化电源系统的方框图； [0056]图13是本发明另一个实施例的模块化电源系统的方框图； [0057]图14是本发明另一个实施例的模块化电源系统的方框图； [0058]图15是本发明另一个实施例的模块化电源系统的方框图； [0059]图16是说明本发明本地控制器与驱动电路之间连接方式的示意图； [0060]图17是本发明另一个实施例的模块化电源系统的方框图； [0061]图18是说明本发明驱动电路的驱动方式的示意图； [0062]图19是说明本发明驱动电路的另一种驱动方式的示意图； [0063]图20是本发明一个实施例的驱动电路的电路图； [0064]图21是本发明一个实施例的驱动电路的时序图； [0065]图22是本发明另一个实施例的模块化电源系统的方框图； [0066]图23是本发明另一个实施例的模块化电源系统的方框图； [0067]图24是本发明另一个实施例的模块化电源系统的方框图； [0068]图25是本发明另一个实施例的模块化电源系统的方框图；以及 [0069]图26是本发明另一个实施例的模块化电源系统的方框图。 具体实施例 [0070] 现在将参考附图更全面地描述示例实施例。然而，示例实施例能够以多种形式实 施，且不应被理解为限于在此阐述的范例;相反，提供这些实施例使得本发明将更加全面和 完整，并将示例实施例的构思全面地传达给本领域的技术人员。附图仅为本发明的示意性 图解，并非一定是按比例绘制。图中相同的附图标记表示相同或类似的部分，因而将省略对 它们的重复描述。 [0071]此外，所描述的特征、结构或特性可以以任何合适的方式结合在一个或更多实施 例中。在下面的描述中，提供许多具体细节从而给出对本发明的实施例的充分理解。然而， 本领域技术人员将意识到，可以实践本发明的技术方案而省略所述特定细节中的一个或更 多，或者可以采用其它的方法、组元、装置、步骤等。在其它情况下，不详细示出或描述公知 结构、方法、装置、实现或者操作以避免喧宾夺主而使得本发明的各方面变得模糊。 [0072]图6是本发明一个实施例的模块化电源系统的方框图。如图6中所示，本发明的电 力电子变换器被配置为包括:一个主控制器90、N个本地控制器91和N个功率单元70，其中N 为大于1的自然数。 [0073]主控制器90被配置为输出主控制信号。主控制信号例如是设置来控制该模块化电 源系统的整体运行状态的一个或多个参数。 [0074] 每一个本地控制器91被配置为接收前述的主控制信号，以输出至少一个本地控制 信号。本地控制信号例如是设置来控制对应的功率单元70的整体运行状态的一个或多个参 数，或者本地控制信号用来控制对应的功率单元70中部分功率变换器的运行状态。 [0075] 本发明的电力电子变换器可以被配置为还包括N个辅助电源93，N个辅助电源93与 N个本地控制器91一一对应，其中每一个辅助电源93被配置为给对应的本地控制器91提供 电源。 [0076] N个功率单元70与N个本地控制器91——对应，每一个功率单元70包括第一端X/口 第二端X2,每一个功率单元70的第二端X2连接到相邻的一个功率单元70的第一端看，也就是 说，相邻两个功率单元70的其中一个的第二端X2与另一个的第一端看连接。 [0077] 每一个功率单元70被配置为包括M个功率变换器701，其中每一个功率变换器701 包括第三端X3和第四端X4,每一个功率变换器的第四端X4连接到相邻的一个功率变换器701 的第三端X3。也就是说，相邻两个功率变换器701的其中一个的第四端X4与另一个的第三端 X3连接。M为大于1的自然数。这样，第1个功率变换器701的第三端X3即为该功率单元70的第 一端X1，第M个功率变换器701的第四端X4为该功率单元70的第二端X2。每一个功率变换器 701被配置为根据对应的本地控制器91输出的本地控制信号运行。 [0078] 作为本发明的一个实施例，主控制器90与每一个本地控制器91之间可以通过光隔 离器件，例如光纤94传输前述的主控制信号。在其他实施例中，主控制器90与每一个本地控 制器91之间可以通过磁隔离器件，例如隔离变压器，进行连接，主控制器90与每一个本地控 制器91之间的连接方式不仅限于上述连接方式。 [0079] 本发明的电力电子装置可以应用于SVG、MVD、HVDC-Light以及风力发电系统等领 域。 [0080]如图6中所示，本发明提出将M个功率变换器701合成为一个功率单元70，一个功率 单元70配置一套本地控制器91、光纤94及辅助电源93,即一套本地控制器91、光纤94及辅助 电源93控制M个功率变换器701。而在传统的方案中，每个功率单元40即功率变换器均需要 配置一套本地控制器51、光纤54及辅助电源53。相比于传统方案，本发明提出的模块化电源 系统所需要配置的本地控制器91、光纤94及辅助电源93的数量将降为传统方案的1/M。本发 明使得模块化电源系统的结构设计大大简化，成本也显著降低，同时可靠性得到极大提高。 [0081] 本发明不限制各个功率变换器701的直流母线电压。本发明的模块化电源系统中 的M个功率变换器701的直流母线电压可以为全部相同，部分相同，或全部不相同。基于图6, 图7是本发明另一个实施例的模块化电源系统的方框图。如图7中所示，功率单元70内M个功 率变换器701的直流母线电压可以分别为VrV2…和VM,其中VrV2…和VM可以全部相同，即汇 = V2=…= VM,也可以部分相同匕=%，匕中旷皿或者全部不相同，即匕中外力…中ν犷 [0082]本发明也不限制各个功率变换器701中所用的拓扑结构。本发明的模块化电源系 统中的M个功率变换器701可以为交流/直流(AC/DC)变换器、直流/交流(DC/AC)变换器和直 流/直流(DC/DC)变换器中的任何一种，因此图7中用功率变换器701代表所有适用的AC/DC、 DC/AC和DC/DC拓扑结构中的任何一种。本发明不限制M个功率变换器701中所用的拓扑结构 还体现在M个功率变换器的拓扑结构可以为全部相同，或部分相同。例如，本发明的模块化 电源系统中的每一个功率单元70中的M个功率变换器701的拓扑结构可以全部为全桥变换 器、半桥变换器、中性点可控三电平变换器、二极管钳位三电平变换器、飞跨电容三电平变 换器、全桥谐振变换器和半桥谐振变换器中的一种。或者例如，本发明的模块化电源系统中 的每一个功率单元70中的M个功率变换器701的拓扑结构可以为全桥变换器、半桥变换器、 中性点可控三电平变换器、二极管钳位三电平变换器、飞跨电容三电平变换器、全桥谐振变 换器和半桥谐振变换器中的两种或两种以上的组合。 [0083] 本发明的模块化电源系统中的每一个功率单元70中的M个功率变换器701中每一 个功率变换器701可以被配置为包括:至少一个功率半导体开关，其中每一个本地控制信号 被配置为控制对应的功率半导体开关的导通和断开。 [0084]如图6和图7中所示，本实施例的模块化电源系统中的每一个功率单元70可以包 括:M个驱动电路702,与M个功率变换器701——对应，其中每一个驱动电路702被配置为连 接于对应的功率变换器701中的功率半导体开关，接收并根据对应的本地控制器91输出的 至少一个本地控制信号，以输出至少一个驱动信号来驱动对应的M个功率变换器701中的功 率半导体开关的导通和断开。 [0085] 在其它实施例中，模块化电源系统中的每一个功率单元可以包括:多个驱动电路， 多个驱动电路的数量等于这个功率单元中功率半导体开关的数量，每一个驱动电路被配置 为连接于对应的功率半导体开关，接收并根据对应的本地控制信号以输出一个驱动信号来 驱动对应的功率半导体开关的导通和断开。 [0086]图8是本发明另一个实施例的模块化电源系统的方框图。如图8中所示，本实施例 的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用全桥变换 器，例如H桥电路。每一个H桥电路701包括4个功率半导体开关和直流母线电容，4个功率半 导体开关构成2个桥臂，为了便于说明，将4个功率半导体开关分别定义为一个桥臂的上功 率半导体开关、下功率半导体开关、另一个桥臂的上功率半导体开关和下功率半导体开关， 其中一个桥臂的上功率半导体开关的一端连接另一个桥臂的上功率半导体开关的一端和 直流母线电容的一端，一个桥臂的下功率半导体开关的另一端连接另一个桥臂的下功率半 导体开关的另一端和直流母线电容的另一端，一个桥臂的上功率半导体开关与下功率半导 体开关连接于第三端X3,另一个桥臂的上功率半导体开关与下功率半导体开关连接于第四 端X4。以其中第M个功率变换器70为例，功率变换器701包括两个桥臂和直流母线电容，一个 桥臂的上功率半导体开关禺第勺一端连接另一个桥臂的上功率半导体开关QM3的一端和直流 母线电容CB的一端，一个桥臂的下功率半导体开关QM2的另一端连接另一个桥臂的下功率半 导体开关QM4的另一端和直流母线电容CB的另一端，一个桥臂的上功率半导体开关QM1与下功 率半导体开关QM2的连接点为第三端X3,另一个桥臂的上功率半导体开关QM3与下功率半导体 开关QM4的连接点为第四端X4。 [0087] 在本实施例中，每一个功率单元70中的第1个H桥电路701的第三端X3为该功率单 元70的第一端乂]，第1个H桥电路701的第四端X4连接第二个H桥电路701的第三端X3,以此类 推，第M-1个H桥电路701的第四端X4连接第M个H桥电路701的第三端X3,第M个功率变换器的 第四端X4为该功率单元70的第二端X2。 [0088] 每一个功率单元70所对应的本地控制器91输出至少一个本地控制信号用以控制 对应的H桥电路701中功率半导体开关的导通和断开。在本实施例中，每一个H桥电路701需 要4个本地控制信号，分别控制对应的功率半导体开关导通和断开，每一个功率单元70需要 4 X M个本地控制信号，即，本地控制器需要输出4 X M个本地控制信号，用以控制对应的功率 半导体开关的导通和断开，即，功率半导体开关q11yM4均需要一个对应的本地控制信号。 [0089] 如图8所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个H桥电 路701 一 一对应，每一个驱动电路702接收对应的本地控制信号，并输出至少一驱动信号来 分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动电路702接收对应的 4个本地控制信号，并输出4个驱动信号来分别驱动对应的功率半导体开关的导通和断开， 以第1个H桥电路701所对应的驱动电路702为例，该驱动电路输出4个驱动信号分别驱动功 率半导体开关Q11yl4的导通和断开。 [0090] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于4 XM,每一个驱动电路连接于对应的一个功率半导体开关，并且接收一个对应的本地控制信 号以输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个H桥电路701 所对应的4个驱动电路为例,4个驱动电路分别连接功率半导体开关q11yl4并且每一个驱动 电路输出一个驱动信号来驱动对应的功率半导体开关QM「QM4的导通和断开。 [0091]图9是本发明另一个实施例的模块化电源系统的方框图。如图9中所示，本实施例 的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用半桥变换 器。每一个半桥变换器701包括2个功率半导体开关和直流母线电容，其连接关系如图9中所 示。一个功率半导体的一端连接直流母线电容的一端，其另一端连接另一个功率半导体开 关的一端，另一个功率半导体开关的另一端连接直流母线电容CB的另一端。2个功率半导体 开关相互连接的连接点为第三端X3,另一个功率半导体开关的另一端为第四端X4。以第1个 功率变换器70为例，功率变换器701包括两个功率半导体开关Q^'Q^和直流母线电容CB。功 率半导体开关Qu的一端连接于直流母线电容CB的一端，功率半导体开关Q1的另一端连接于 功率半导体开关q12的一端，功率半导体开关q12的另一端连接于直流母线电容CB的另一端， 功率半导体开关Qu与功率半导体开关Q12的连接点为第1个功率变换器701的第三端X3,功率 半导体开关Q12的另一端为第1个功率变换器701的第四端X4。 [0092]在本实施例中，每一个功率单元70中第1个半桥变换器的第三端X3为功率单元70 的第一端％，第1个半桥变换器的第四端X4连接第二个半桥变换器的第三端X3,依次类推，第 M-1个半桥变换器的第四端X4连接第M个半桥变换器的第三端X3,第M个半桥变换器的第四端 X4为功率单元70的第二端X2。 [0093] 在本实施例中，每一个功率单元70对应的本地控制器可以输出2XM个本地控制信 号，用以控制半桥变换器701中的功率半导体开关Q11MM2的导通和断开，即，功率半导体开 关q11yM2均需要一个本地控制信号。 [0094] 如图9所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个半桥变 换器701 一 一对应，每一个驱动电路702接收对应的本地控制信号，并输出至少一驱动信号 来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动电路702接收对应 的2个本地控制信号，并输出2个驱动信号来分别驱动对应的功率半导体开关的导通和断 开，以第1个半桥变换器701所对应的驱动电路702为例，该驱动电路输出2个驱动信号分别 驱动功率半导体开关Q11yl2的导通和断开。 [0095] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于2 XM,每一个驱动电路连接于对应的一个功率半导体开关，并且接收一个对应的本地控制信 号以输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个半桥变换器 701所对应的2个驱动电路为例，2个驱动电路分别连接功率半导体开关Q^Q^并且每一个 驱动电路输出一个驱动信号来驱动对应的功率半导体开关q11yl2的导通和断开。 [0096]图10是本发明另一个实施例的模块化电源系统的方框图。如图10中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用中性点 可控三电平变换器。每一个中性点可控三电平变换器701包括8个功率半导体开关和2个直 流母线电容，其连接关系如图10中所示。以第1个功率变换器701为例加以说明，功率半导体 开关Qu的一端连接于直流母线电容”的一端和功率半导体开关Q15的一端，直流母线电容“ 的另一端连接于直流母线电容C2的一端，功率半导体开关5]的另一端连接于功率半导体开 关Q12的一端，功率半导体开关Qu与功率半导体开关Q12的连接点为第1个功率变换器701的 第三端X3,功率半导体开关Q12的另一端连接于直流母线电容C2的另一端和功率半导体开关 Q16的另一端，功率半导体开关Q15的另一端连接于功率半导体开关Q16的一端，功率半导体开 关55与功率半导体开关Q16的连接点为第1个功率变换器701的第四端X4,功率半导体开关 Q13的一端连接于直流母线电容”的另一端，功率半导体开关q13的另一端连接于功率半导体 开关Q14的一端，功率半导体开关Q14的另一端连接于功率半导体开关Qu的另一端，功率半导 体开关Q17的一端连接于直流母线电容^的另一端，功率半导体开关Q17的另一端连接于功率 半导体开关Q18的一端，功率半导体开关Q18的另一端连接于功率半导体开关Q15的另一端。 [0097] 在本实施例中，每一个功率单元70中第1个中性点可控三电平变换器的第三端X3 为功率单元70的第一端％，第1个中性点可控三电平变换器的第四端X4连接第二个中性点可 控三电平变换器的第三端X3,依次类推，第M-1个中性点可控三电平变换器的第四端X4连接 第M个中性点可控三电平变换器的第三端X3,第M个中性点可控三电平变换器的第四端X4为 功率单元70的第二端X2。 [0098] 在本实施例中，每一个功率单元对应的本地控制器可以输出8XM个本地控制信 号，用以控制中性点可控三电平变换器701中功率半导体开关Q11MM8的的导通和断开，即， 功率半导体开关q11yM8均需要一个本地控制信号。 [0099] 如图10所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个中性 点可控三电平变换器701 一 一对应，每一个驱动电路702接收对应的本地控制信号，并输出 至少一驱动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动 电路702接收对应的8个本地控制信号，并输出8个驱动信号来分别驱动对应的功率半导体 开关的导通和断开，以第1个中性点可控三电平变换器701所对应的驱动电路702为例，该驱 动电路输出8个驱动信号分别驱动功率半导体开关q11yl8的导通和断开。 [0100] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于8 XM，每一个驱动电路连接对应的一个功率半导体开关，并且接收一个对应的本地控制信号 以输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个中性点可控三 电平变换器701所对应的8个驱动电路为例，8个驱动电路分别连接功率半导体开关Q^Q^ 并每一个驱动电路输出一个驱动信号来驱动对应的功率半导体开关q11yl8的导通和断开。 [0101]图11是本发明另一个实施例的模块化电源系统的方框图。如图11中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用二极管 钳位三电平变换器。每一个二极管钳位三电平变换器701包括8个功率半导体开关、4个钳位 二极管和2个直流母线电容，其连接关系如图11中所示。以第1个功率变换器701为例，功率 半导体开关Qu的一端连接于直流母线电容”的一端和功率半导体开关Q15的一端，功率半导 体开关Qu的另一端连接于功率半导体开关Q12的一端和钳位二极管D1的阴极，功率半导体开 关Q12的另一端连接于功率半导体开关Q13的一端，功率半导体开关Q13的另一端连接于功率 半导体开关Q14的一端和钳位二极管D2的阳极，直流母线电容”的另一端连接于直流母线电 容C2的一端，功率半导体开关Q14的另一端连接于直流母线电容C2的另一端，钳位二极管口第勺 阳极连接于钳位二极管D2的阴极和直流母线电容”的另一端，功率半导体开关q12与功率半 导体开关Q13的连接点为第1个功率变换器701的第三端X3,功率半导体开关55的另一端连接 于功率半导体开关Q16的一端和钳位二极管d3的阴极，功率半导体开关Q16的另一端连接于功 率半导体开关Q17的一端，功率半导体开关Q17的另一端连接于功率半导体开关Q18的一端和 钳位二极管d4的阳极，功率半导体开关q18的另一端连接于直流母线电容分的另一端，钳位 二极管D3的阳极连接于钳位二极管d4的阴极和直流母线电容4的另一端，功率半导体开关 Q16与功率半导体开关Q17的连接点为第1个功率变换器701的第四端x4。 [0102]在本实施例中，每一个功率单元70中第1个二极管钳位三电平变换器的第三端X3 为功率单元70的第一端％，第1个二极管钳位三电平变换器的第四端X4连接第二个二极管钳 位三电平变换器的第三端X3,依次类推，第M-1个二极管钳位三电平变换器的第四端X4连接 第M个二极管钳位三电平变换器的第三端X3,第M个二极管钳位三电平变换器的第四端X4为 功率单元70的第二端X2。 [0103] 在本实施例中，每一个功率单元对应的本地控制器可以输出8XM个本地控制信 号，用以控制中性点可控三电平变换器701中功率半导体开关Q11MM8的的导通和断开，即， 功率半导体开关q11yM8均需要一个本地控制信号。 [0104] 如图11所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个二极 管钳位三电平变换器701 一 一对应，每一个驱动电路702接收对应的本地控制信号，并输出 至少一驱动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动 电路702接收对应的8个本地控制信号，并输出8个驱动信号来分别驱动对应的功率半导体 开关的导通和断开，以第1个二极管钳位三电平变换器701所对应的驱动电路702为例，该驱 动电路输出8个驱动信号分别驱动功率半导体开关q11yl8的导通和断开。 [0105] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于8 XM，每一个驱动电路连接对应的一个功率半导体开关，并且接收一个对应的本地控制信号 以输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个二极管钳位三 电平变换器701所对应的8个驱动电路为例，8个驱动电路分别连接功率半导体开关Q^Q^ 并且每一个驱动电路输出一个驱动信号来驱动对应的功率半导体开关Q^-Q^的导通和断 开。 [0106]图12是本发明另一个实施例的模块化电源系统的方框图。如图12中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701拓扑结构均采用飞跨电容 三电平变换器。每一个飞跨电容三电平变换器701包括8个功率半导体开关、2个直流母线电 容和2个飞跨电容，其连接关系如图12中所示。以第1个功率变换器701为例，功率半导体开 关QI]的一端连接于直流母线电容L的一端和功率半导体开关Q15的一端，功率半导体开关 Qu的另一端连接于功率半导体开关Q12的一端和飞跨电容C3的一端，功率半导体开关Q12的 另一端连接于功率半导体开关Q13的一端，功率半导体开关Q13的另一端连接于功率半导体 开关Q14的一端和飞跨电容C3的另一端，直流母线电容”的另一端连接于直流母线电容分的 一端，功率半导体开关q14的另一端连接于直流母线电容C2的另一端，功率半导体开关q12与 功率半导体开关Q13的连接点为第1个功率变换器701的第三端X3,功率半导体开关55的另一 端连接于功率半导体开关Q16的一端和飞跨电容C4的一端，功率半导体开关Q16的另一端连接 于功率半导体开关q17的一端，功率半导体开关q17的另一端连接于功率半导体开关q18的一 端和飞跨电容C4的另一端，功率半导体开关Q18的另一端连接于直流母线电容C2的另一端， 功率半导体开关Q16与功率半导体开关Q17的连接点为第1个功率变换器701的第四端X4。 [0107]在本实施例中，每一个功率单元70中第1个飞跨电容三电平变换器的第三端X3为 功率单元70的第一端％，第1个飞跨电容三电平变换器的第四端X4连接第二个飞跨电容三电 平变换器的第三端X3,依次类推，第M-1个飞跨电容三电平变换器的第四端X4连接第M个飞跨 电容三电平变换器的第三端X3，第M个飞跨电容三电平变换器的第四端X4为功率单元70的第 二端X2。 [0108] 在本实施例中，每一个功率单元对应的本地控制器可以输出8XM个本地控制信 号，用以控制中性点可控三电平变换器701中功率半导体开关Q11MM8的的导通和断开，即， 功率半导体开关q11yM8均需要一个本地控制信号。 [0109] 如图12所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个飞跨 电容三电平变换器701一一对应，每一个驱动电路702接收对应的本地控制信号，并输出至 少一驱动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动电 路702接收对应的8个本地控制信号，并输出8个驱动信号来分别驱动对应的功率半导体开 关的导通和断开，以第1个飞跨电容三电平变换器701所对应的驱动电路702为例，该驱动电 路输出8个驱动信号分别驱动功率半导体开关q11yl8的导通和断开。 [0110] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于8 XM，每个驱动电路接收一个对应的本地控制信号并输出一个驱动信号来驱动对应的功率 半导体开关的导通和断开，以第1个飞跨电容三电平变换器701所对应的8个驱动电路为例， 8个驱动电路分别连接功率半导体开关q11yl8并且每一个驱动电路输出一个驱动信号来驱 动对应的功率半导体开关q11yl8的导通和断开。 [0111]图8-图12的模块化电源系统中的M个功率变换器701可以为交流/直流(AC/DC)变 换器或者直流/交流(DC/AC)变换器，但是不以此为限，还可以是其它拓扑结构的变换器。 [0112]图13是本发明另一个实施例的模块化电源系统的方框图。如图13中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用全桥谐 振变换器。每一个全桥谐振变换器701包括全桥电路、谐振电路、变压器和整流桥，其连接关 系如图13中所示。以第1个全桥LLC谐振变换器701为例，全桥电路包括4个功率半导体开关 和一个直流母线电容，功率半导体开关Qu的一端连接于直流母线电容CB’的一端和功率半 导体开关53的一端，功率半导体开关Qu的另一端连接于功率半导体开关Q12的一端，功率半 导体开关Q12的另一端连接于直流母线电容CB’的另一端和功率半导体开关Q14的另一端，功 率半导体开关Qu与功率半导体开关Q12的连接点连接于电容C’和电感L’构成的谐振电路的 一端，谐振电路的另一端连接于变压器T’的原边线圈的一端，变压器T’的原边线圈的另一 端连接于功率半导体开关Q13与功率半导体开关Q14的连接点，直流母线电容CB’的前述一端 为第1个功率变换器的第三端X3,直流母线电容CB’的另一端为第1个功率变换器的第四端 X4,整流桥包括4个整流二极管，整流二极管D：的一端连接于整流二极管D3’ 一端，整流二极 管D：的另一端连接于整流二极管D2’ 一端，整流二极管D3’的另一端连接于整流二极管D4’ 一端，整流二极管D2’的另一端连接于整流二极管D4’另一端，整流二极管D；的前述一端为 变换器的第五端X5,整流二极管D2’的另一端为变换器的第六端X6,变压器T’的输出端分别 连接于整流二极管D：与整流二极管D2’的连接点以及整流二极管D3’与整流二极管D4’的连 接点，其中变压器T’可以是中间抽头变压器，具有两个副边线圈，两个副边线圈并联连接， 变压器T’也可以具有单个副边线圈。 [0113]在实施例中，每一个功率单元70中第1个全桥谐振变换器的第三端X3为功率单元 70的第一端乂]，第1个全桥谐振变换器的第四端X4连接第二个全桥谐振变换器的第三端X3, 依次类推，第M-1个全桥谐振变换器的第四端X4连接第M个全桥谐振变换器的第三端X3，第M 个全桥谐振变换器的第四端X4为功率单元70的第二端X2。每一个功率单元70中所有的全桥 谐振变换器器的第五端X5连在一起，而第六端X6连在一起。 [0114] 在本实施例中，每一个功率单元对应的本地控制器可以输出4XM个本地控制信 号，用以控制全桥谐振变换器701中功率半导体开关Q11MM4的的导通和断开，即，功率半导 体开关q11yM4均需要一个本地控制信号。 [0115] 如图13所示，每一个功率单元70还包括M个驱动电路702，驱动电路702与M个全桥 谐振变换器701 一 —对应，每一个驱动电路702接收对应的本地控制信号，并输出至少一驱 动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动电路702接 收对应的4个本地控制信号，并输出4个驱动信号来分别驱动对应的功率半导体开关的导通 和断开，以第1个全桥谐振变换器701所对应的驱动电路702为例，该驱动电路输出4个驱动 信号分别驱动功率半导体开关q11yl4的导通和断开。 [0116] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于4 XM，每一个驱动电路连接对应的一个功率半导体开关，并且接收一个对应的本地控制信号 以输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个全桥谐振变换 器701所对应的4个驱动电路为例，4个驱动电路分别连接功率半导体开关Qu-Q^并且每一 个驱动电路输出一个驱动信号来驱动对应的功率半导体开关q11yl4的导通和断开。 [0117]图14是本发明另一个实施例的模块化电源系统的方框图。如图14中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构均采用半桥谐 振变换器。每一个半桥谐振变换器701包括半桥电路、谐振电路、变压器和整流桥，其连接关 系如图14中所示。以第1个半桥谐振变换器701为例，半桥电路包括2个功率半导体开关和一 个直流母线电容，功率半导体开关Qu的一端连接于直流母线电容CB'的一端，功率半导体开 关5]的另一端连接于功率半导体开关Q12的一端，功率半导体开关Q12的另一端连接于直流 母线电容CB’的另一端，功率半导体开关5]与功率半导体开关Q12的连接点连接于电容C,和 电感L,构成的谐振电路的一端，谐振电路的另一端连接于变压器T,的原边线圈的一端，变 压器T’的原边线圈的另一端连接于功率半导体开关Q12的另一端，直流母线电容CB'的一端 为第1个功率变换器的第三端X3,直流母线电容CB'的另一端为第1个功率变换器的第四端 X4,整流桥包括4个整流二极管，整流二极管D：的一端连接于整流二极管D3, 一端，整流二极 管D：的另一端连接于整流二极管D2, 一端，整流二极管D3’的另一端连接于整流二极管D4, 一端，整流二极管D2’的另一端连接于整流二极管D4,另一端，整流二极管D；的一端为变换 器的第五端X5,整流二极管D2’的另一端为变换器的第六端X6,变压器T,的输出端分别连接 于整流二极管D；与整流二极管D2’的连接点以及整流二极管D3,与整流二极管D4’的连接 点，其中变压器T,可以是中间抽头变压器，具有两个副边线圈，两个副边线圈并联连接，变 压器T’也可以具有单个副边线圈。 [0118]在本实施例中，每一个功率单元70中第1个半桥谐振变换器的第三端X3为功率单 元70的第一端乂]，第1个半桥谐振变换器的第四端X4连接第二个半桥谐振变换器的第三端 X3，依次类推，第M-1个半桥谐振变换器的第四端X4连接第M个半桥谐振变换器的第三端X3， 第M个半桥谐振变换器的第四端X4为功率单元70的第二端X2。每一个功率单元70中所有的半 桥谐振变换器器的第五端X5连在一起，而第六端X6连在一起。 [0119] 在本实施例中，每一个功率单元对应的本地控制器可以输出2XM个本地控制信 号，用以控制半桥谐振变换器701中功率半导体开关Q11MM2的的导通和断开，即，功率半导 体开关q11yM2均需要一个本地控制信号。 [0120] 如图14所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个半桥 谐振变换器701 一 一对应，每一个驱动电路702接收对应的本地控制信号，并输出至少一驱 动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，每一个驱动电路702接 收对应的2个本地控制信号，并输出2个驱动信号来分别驱动对应的功率半导体开关的导通 和断开，以第1个半桥谐振变换器701所对应的驱动电路702为例，该驱动电路输出2个驱动 信号分别驱动功率半导体开关q11yl2的导通和断开。 [0121] 在其它实施例中，每一个功率单元70还包括多个驱动电路，驱动电路的数量等于2 XM，每一个驱动电路连接对应的一个功率半导体开关，并且接收一个对应的本地控制信号 并输出一个驱动信号来驱动对应的功率半导体开关的导通和断开，以第1个半桥谐振变换 器701所对应的2个驱动电路为例，2个驱动电路分别连接功率半导体开关QuR班且每一 个驱动电路输出一个驱动信号来驱动对应的功率半导体开关q11yl2的导通和断开。 [0122]图13和图14的模块化电源系统中的M个功率变换器701可以为直流/直流(DC/DC) 变换器，但是不以此为限，还可以是其它拓扑结构的变换器。 [0123]图15是本发明另一个实施例的模块化电源系统的方框图。如图15中所示，本实施 例的模块化电源系统中每一个功率单元70的M个功率变换器701的拓扑结构同时采用全桥 变换器和半桥变换器的组合。每一个全桥变换器的功率转换器7011’包括4个功率半导体开 关，每一个半桥变换器7012'包括2个功率半导体开关，其连接关系如图15中所示。在本实施 例中，全桥变换器的具体连接关系如图8所述，半桥变换器的具体连接关系如图9所示，在此 不再赘述。类似的，相邻两个功率变换器701的其中一个的第四端X4与另一个的第三端X3连 接，其中M为大于1的自然数。这样，第1个功率变换器701的第三端X3即为该功率单元70的第 一端X1，第1个功率变换器701的第四端X4连接第2个功率变换器701的第三端乂3，依次类推， 第M-1个功率变换器701的第四端X4连接第M个功率变换器701的第三端X3,第M个功率变换器 701的第四端X4为该功率单元70的第二端X2。 [0124] 本实施例中，每一个功率单元70对应的本地控制器所输出的本地控制信号的数量 等于功率单元70中功率半导体开关的数量，这些本地控制信号分别控制全桥变换器和半桥 变换器701中的功率半导体开关的导通和断开，即，每一个功率半导体开关均需要一个本地 控制信号。 [0125] 如图15所示，每一个功率单元70还包括M个驱动电路702,驱动电路702与M个功率 变换器7011'和7012' 一一对应，每一个驱动电路702接收对应的本地控制信号，并输出至少 一驱动信号来分别驱动对应的功率半导体开关的导通和断开，具体而言，功率变换器7011' 对应的驱动电路702接收对应的4个本地控制信号，并输出4个驱动信号来分别驱动对应的 功率半导体开关的导通和断开，功率变换器7012'对应的驱动电路702接收对应的2个本地 控制信号，并输出2个驱动信号来分别驱动对应的功率半导体开关的导通和断开。 [0126] 在其它实施例中，每一个功率单元70还包括多个驱动电路，功率单元中驱动电路 的数量等于其对应的功率单元中功率半导体开关的数量，每一个驱动电路连接对应的一个 功率半导体开关，并且接收一个对应的本地控制信号以输出一个驱动信号来驱动对应的功 率半导体开关的导通和断开，以功率变换器7011'所对应的4个驱动电路为例，4个驱动电路 分别连接对应的功率半导体开关并且每一个驱动电路输出一个驱动信号来驱动对应的功 率半导体开关的导通和断开，以及以功率变换器7012'所对应的2个驱动电路为例，2个驱动 电路分别连接对应的功率半导体开关并且每一个驱动电路输出一个驱动信号来驱动对应 的功率半导体开关的导通和断开。 [0127]尽管图15仅仅示出了本实施例的模块化电源系统中每一个功率单元70的M个功率 变换器701的拓扑结构同时采用全桥变换器和半桥变换器的组合。然而本发明不限于此，如 前所述，本发明的模块化电源系统中的每一个功率单元70中的M个功率变换器701的拓扑结 构可以为全桥变换器、半桥变换器、中性点可控三电平变换器、二极管钳位三电平变换器、 飞跨电容三电平变换器、全桥LLC谐振变换器和半桥LLC谐振变换器中的两种或两种以上的 组合。 [0128] 本发明的模块化电源系统中的每一个功率单元70中的M个功率变换器701中每一 个功率变换器701可以被配置为包括:至少一个功率半导体开关，例如前述的功率半导体开 关q11yl4、q11yl2,Qu-q18 VMi-qM4、qM1-qM2或qM1-qM8,其中每一个前述的本地控制信号被配置 为控制对应的功率半导体开关的导通和断开。 [0129] 本发明模块化电源系统中的每一个驱动电路702与对应的本地控制器91可以直接 电连接，或者通过磁隔离器件连接，或者通过光隔离器件连接。 [0130]图16是说明本发明本地控制器与驱动电路之间连接方式的示意图。如图16中所 示，作为一个实施例，驱动电路72 (702)与对应的本地控制器91通过磁隔离器件T连接，传输 本地控制信号。采用磁隔离器件具有高可靠性、高性能、低功耗等优点。 [0131] 作为一个实施例，驱动电路72 (702)与对应的本地控制器91也可以通过光隔离器 件连接。采用光隔离器件具有信号单向传输、输入端与输出端完全实现了电气隔离、输出信 号对输入端无影响、抗干扰能力强、工作稳定、无触点、使用寿命长、传输效率高等优点。 [0132]作为一个实施例，驱动电路72 (702)与对应的本地控制器91直接电连接。 [0133]本发明的模块化电源系统中的各驱动电路72 (702)可以为彼此相同或彼此不相 同。 [0134]如图6-图15中所示，本实施例的模块化电源系统中的各驱动电路702为彼此相同。 [0135]图17是本发明另一个实施例的模块化电源系统的方框图。如图17中所示，本实施 例的模块化电源系统中的一个功率单元中包括5个H桥电路的功率变换器701。其中4个功率 变换器701的驱动电路721不同于中间的功率变换器701的驱动电路722。 [0136]图18是说明本发明驱动电路的驱动方式的示意图。如图18中所示，驱动电路722包 括原边电路7221、副边电路7222以及磁隔离器件「，原边电路7221接收本地控制器91输出 的本地控制信号，其中本地控制信号中只包含驱动成分，该本地控制信号是一个弱信号。原 边电路7221将本地控制信号调制成为高低电平的窄脉冲信号，其中该高低电平的窄脉冲信 号包括驱动逻辑脉冲，该窄脉冲信号经由磁隔离器件(例如，高频隔离变压器)T/传输副边 电路7222,副边电路7222将高低压窄脉冲信号还原成PWM信号并经过放大处理以输出驱动 信号来驱动功率半导体开关Q的导通和断开。功率单元70还包括电源电路7223,用以给原边 电路7221和副边电路7222提供电源。电源电路7223接收的电源可以来自于辅助源93,或者 其他外部电源，电源电路7223将接收到的电源转换为给原边电路7221供电的电压汇以及给 副边7222供电的电压V2,且电压V^DV2之间是相互隔离的。在其它实施例中，电源电路7223 还包括原边电源电路（未示出）、隔离变压器（未示出）以及副边电源电路（未示出），原边电 源电路将接收到的电源转换为原边电源给原边电路7221提供直流电Vj同时原边电源电路 将接收到的电源转换为功率脉冲即电源脉冲通过隔离变压器传输给副边电源电路，再由副 边电源电路将功率脉冲转换为副边电源给副边电路7222提供直流电V2。 [0137]为简化驱动电路722,节省成本，提高驱动电路72的可靠性，本发明中各功率变换 器的驱动方式可采用“简易驱动”。 [0138]图19是说明本发明驱动电路的另一种驱动方式的示意图。如图19中所示，本实施 例的模块化电源系统中每一个驱动电路721包括原边电路7211、副边电路7212和磁隔离器 件（例如，隔离变压器）T2。原边电路7211接收本地控制信号，其中本地控制信号包括驱动成 分和功率成分，该本地控制信号是一个强信号，原边电路7211将本地控制信号调制成为正 负窄脉冲信号YMN，经由磁隔离器件T2传输给副边电路7212,副边电路7212将窄脉冲信号YMN 解调成驱动信号以驱动功率半导体开关Q的导通和断开，其中该正负窄脉冲信号丫MN包括驱 动逻辑脉冲以及功率脉冲，功率半导体开关Q例如包括栅极G、集电极C和发射极E，驱动信号 被输出至功率半导体开关的栅极G。图19所述的驱动方式为“简易驱动”，这种“简易驱动”省 去了大量的电源电路，使得驱动电路721的器件减少了很多，整个驱动电路721的结构得到 简化，功耗得以减小，可靠性得到了提高。 [0139]图20是本发明一个实施例的驱动电路的电路图。图20基于图19并且为图19中驱动 电路的副边电路的具体化。图21是本发明一个实施例的驱动电路的时序图。如图20中所示， 本发明的驱动电路主要包括磁隔离器件T2和一个双向稳压管W,其它电阻Ru'R^'R^'R'R^、 R22、R23、栅极电容CGE、二极管Du、％、稳压管WrW2和开关管明和电为辅助元件，其连接关系如 图20中所示。 [0140] 结合图20和图21,本地控制器91发出的本地控制信号PWM经原边电路调制后形成 正负脉冲信号YMN,如图21中YNM所示。该正负脉冲信号YNM经磁隔离器件（例如，隔离变压器） T2传输至副边电路，触发开关管贴和电动作后向IGBT栅极电容CGE充放电，形成驱动功率半导 体开关所需的驱动信号VGE,VGE的波形图基本与本地控制信号PWM相近，如图21所示。为了减 小磁隔离器件即隔离变压器T2的磁芯，且使磁芯不饱和，正负脉冲信号YNM的刷新脉冲的宽 度可能只有几Ps。以功率半导体开关Q的栅极-发射级电压VGE为正进行说明，几us的正脉冲 一次给栅极电容CGE充的电，就可以使得驱动信号VGE达到功率半导体开关的栅极开通电压， 例如+15V。然而要维持功率半导体开通导通，其需要的正脉冲可能有几十us到上百us甚至 更长，因此，如果没有刷新脉冲，栅极电容CGE会缓慢放电导致驱动信号VGE逐渐降低，达不到 功率半导体开关正常导通所需的栅极开通电压，因此需要刷新脉冲每隔一段时间对栅极电 容CGE充电以维持驱动信号VGE在正常的栅极开通电压。至于刷新脉冲的时间间隔，主要由栅 极电容CGE的放电时间常数确定，原则是在下一个刷新脉冲来之前，VGE不至于下降太多，例 如下一个刷新脉冲到来之前驱动信号VGE不能低于14V。 [0141]图20的驱动电路接收的本地控制信号包括驱动逻辑脉冲以及功率脉冲，因而该驱 动电路就不需要外接电源，也不需要对本地控制信号进行放大处理，相对于图18的驱动电 路省去了大量的电源电路，使得驱动电路721的器件减少了很多，整个驱动电路721的结构 得到简化，功耗得以减小，可靠性得到了提高。 [0142] 在本发明的上述实施例中，如图6-图15所示，每一个驱动电路702可以采用图19所 描述的驱动电路，磁隔离器件Tj传输的本地控制信号中包含驱动逻辑脉冲以及功率脉冲。 [0143] 在本发明的上述实施例中，如图6-图15所示，每一个驱动电路702可以采用图18所 描述的驱动电路，磁隔离器件T/传输本地控制信号中包含的驱动逻辑脉冲。 [0144] 在本发明的上述实施例中，如图6-图15所示，一部分驱动电路702可以采用图19所 描述的驱动电路，磁隔离器件传输本地控制信号中包含的驱动逻辑脉冲以及功率脉冲；以 及另一部分驱动电路702采用图18所描述的驱动电路，磁隔离器件传输本地控制信号中包 含的驱动逻辑脉冲。 [0145] 在本发明的上述实施例中，如图17所示，驱动电路721可以采用图19所描述的驱动 电路，磁隔离器件传输本地控制信号中包含的驱动逻辑脉冲以及功率脉冲；以及驱动电路 722采用图18所描述的驱动电路，磁隔离器件传输本地控制信号中包含的驱动逻辑脉冲。 [0146] 在本发明的上述实施例中，如图17所示，驱动电路722可以采用图19所描述的驱动 电路，磁隔离器件传输本地控制信号中包含的驱动逻辑脉冲以及功率脉冲；以及驱动电路 721采用图18所描述的驱动电路，磁隔离器件传输本地控制信号中包含的驱动逻辑脉冲。 [0147]图22是本发明另一个实施例的模块化电源系统的方框图。如图22中所示，本实施 例的模块化电源系统中的每一个功率变换器701每一个功率变换器的第三端X3和第四端X4 之间并联有开关K12，例如，K12是常开开关，当该功率变换器正常工作时，开关K12断开，当该 功率变换器401发生故障时，开关K12导通。 [0148]作为一个实施例，开关K12是半控型器件，例如晶闸管，或者全控型器件，例如IGBT， 或者机械开关。 [0149]如图22中所示，当任一功率变换器701发生故障时，故障检测电路（图22中未示出） 检测到功率变换器701的各类故障，并根据故障类型输出对应的故障信号至本地控制器91， 本地控制器91会接收到反映对应的功率变换器701的故障类型的故障信号，并输出对应的 保护信号以控制对应的功率变换器701的开关K12导通，并且本地控制器91停止输出控制对 应的功率变换器701运行的本地控制信号。 [0150]如图22中所示，各功率变换器701中的开关K12根据该功率变换器701自己反馈的故 障信号来控制。在功率单元70的运行过程中，当本地控制器91接收到任一个功率变换器701 反馈的故障信号后，根据该故障信号控制对应的功率变换器中的开关K12闭合，同时停止输 出控制该故障的功率变换器701运行的本地控制信号，即该故障的功率变换器701被旁路 掉。以一个功率变换器发生故障为例说明，如果第1个功率变换器701发生故障，本地控制器 91会接收到反映第1个功率变换器的故障类型的故障信号，并输出保护信号S同以控制第1个 功率变换器701的开关K12导通，并且本地控制器91停止输出控制第1个功率变换器701运行 的本地控制信号。以2个功率变换器发生故障为例说明，如果第1个功率变换器701和第M个 功率变换器均发生故障，本地控制器91会接收到反映第1个功率变换器和第M个功率变换器 的故障类型的故障信号，并输出保护信号SF/KFM以分别控制第1个功率变换器701和第M个 功率变换器701的开关K12导通，并且本地控制器91停止输出控制第1个功率变换器701和第M 个功率变换器701运行的本地控制信号。 [0151]图23是本发明另一个实施例的模块化电源系统的方框图。如图23中所示，本实施 例的模块化电源系统中的保护信号的数量为M，与前述M个功率变换器701一—对应，本实施 例的模块化电源系统的本地控制信号根据每一个保护信号5“至5两以分别控制对应的功率 变换器701的开关K12导通，并且本地控制器91停止输出控制功率单元70中每一个功率变换 器701运行的本地控制信号。 [0152]如图23中所示，在功率单元70的运行过程中，当本地控制器91接收到任一个功率 变换器701反馈的故障信号后，本地控制器91根据故障信号输出保护信号SF1，…，SFM以控制 所有功率变换器701中的K12闭合，同时停止输出本地控制信号，即该功率单元70整体被旁 路。 [0153]图24是本发明另一个实施例的模块化电源系统的方框图。如图24中所示，本实施 例的模块化电源系统中的保护信号SF的数量为1，本地控制器91输出保护信号SF以控制所有 M个功率变换器的开关K12导通，并且本地控制器91停止输出本地控制信号以控制功率单元 70中每一个功率变换器701的运行。 [0154]如图24中所示，功率单元70内所有功率变换器的开关K12由本地控制器91输出的保 护信号SF控制。在功率单元70的运行过程中，当本地控制器91接收到任一个功率变换器701 反馈的故障信号后，本地控制器91根据故障信号输出一个保护信号SF以控制所有功率变换 器701中的开关K12闭合，同时停止输出本地控制信号，即该功率单元70整体被旁路。 [0155]图25是本发明另一个实施例的模块化电源系统的方框图。如图25中所示，本实施 例的模块化电源系统中的功率单元70的第一端X/口第二端X2之间并联有第三开关K3,当功 率单元70正常工作时，第三开关K3断开，当功率单元70发生故障时，第三开关K3导通。 [0156]如图25中所示，当任一所述功率变换器701发生故障时，本地控制器91会接收到反 映对应的功率变换器701的故障类型的故障信号，并输出一保护信号SF’以控制开关K3导通, 并且本地控制器91停止输出控制功率单元70中每一个功率变换器701运行的本地控制信 号。 [0157]如图25中所示，在功率单元70的输出端并联常开开关K3，K3受控于本地控制器91。 在功率单元70运行过程中，当本地控制器91接收到任一个功率变换器701反馈的故障信号 后，本地控制器91根据故障信号输出保护信号SF’以控制开关K3闭合，同时停止输出该功率 单元70内所有本地控制信号，即该功率单元70整体被旁路。 [0158]图26是本发明另一个实施例的模块化电源系统的方框图。如图26中所示，本实施 例的模块化电源系统中的功率单元70由5个级联的H桥电路的功率变换器组成。在功率单元 70的输出端并联常开开关K3，K3受控于本地控制器91。在功率单元70运行过程中，任一H桥电 路的功率变换器发生故障并向本地控制器91反馈故障信号后，本地控制器91根据故障信号 输出保护信号SF’以控制开关K3闭合，同时停止输出控制该功率单元70运行的所有本地控制 信号，即该功率单元70整体被旁路。 [0159] 本发明通过将多个功率变换器组成一个功率单元，利用一套本地控制器、光纤控 制多个功率变换器的方法，可大大减少本地控制器、光纤的数量，简化结构设计，降低成本, 提高可靠性。 [0160] 本发明适用于所有AC/DC、DC/AC、DC/DC功率变换器连接的拓扑结构，应用广泛。 [0161]以上具体地示出和描述了本发明的示例性实施例。应可理解的是，本发明不限于 这里描述的详细结构、设置方式或实现方法;相反，本发明意图涵盖包含在所附权利要求的 精神和范围内的各种修改和等效设置。最后应说明的是：以上各实施例仅用以说明本发明 的技术方案，而非对其限制;尽管参照前述各实施例对本发明进行了详细的说明，本领域的 普通技术人员应当理解:其依然可以对前述各实施例所记载的技术方案进行修改，或者对 其中部分或者全部技术特征进行等同替换;而这些修改或者替换，并不使相应技术方案的 本质脱离本发明各实施例技术方案的范围。 CN 108566071 Β [EN US11101740B2]: CROSS-REFERENCE TO RELATED APPLICATIONS This application is a continuation application of International Application No. PCT/CN2017/116354, filed on Dec. 15, 2017, which is based upon and claims priority to Chinese Patent Application No. 201611170857.3, filed on Dec. 16, 2016, Chinese Patent Application No. 201611191912.7, filed on Dec. 21, 2016, Chinese Patent Application No. 201710106946.X, filed on Feb. 27, 2017, Chinese Patent Application No. 201711322795.8, filed on Dec. 12, 2017, the entire content of all of which is incorporated herein by reference. TECHNICAL FIELD The present disclosure relates to the field of power electronics, and particularly to a modular power supply system. BACKGROUND Currently, in some applications of high voltage level (such as above 10 kV), such as Static Var Generator (SVG), Medium Variable-frequency Drive (MVD), and High Voltage Direct Current Transmission Light (HVDC-Light), etc., the systems are of high voltage level, and limited by the withstanding voltage level and cost of semiconductor devices, so the systems often adopt a circuit topology of cascaded power units. The traditional topology of cascaded power units needs to equip a set of optical fiber, auxiliary power supply and local controller for each power unit, i.e., power converter. In such topology of cascaded power units, the number of power units that need to be cascaded increases with the increase of the voltage level, resulting in an increase in the number of optical fibers, auxiliary power supplies and local controllers. Therefore, the design of such a topology is complex, the cost is expensive, and its reliability is low. FIG. 1 is a schematic structural view of a three-phase SVG system in the prior art. FIG. 2 is a schematic diagram of a more specific three-phase SVG system in the prior art. Each of the SVG systems in FIGS. 1 and 2 includes a three-phase circuit, and power units in each phase of circuit are connected in cascade. As shown in FIG. 1, each phase of circuit of the SVG system is formed by cascading a plurality of power units 1. The term “cascade” as used herein is well-known in the art. That is, each power unit includes a first end T1 and a second end T2. A second end T2 of one of adjacent two power units is connected to a first end T1 of the other one of the adjacent two power units. The first end T1 of the first power unit of each phase of circuit is connected to a corresponding phase of three-phase lines UA, UB and UC of the three-phase grid via a filter inductor L, and the second ends of the last power units of the three phase of circuit are mutually connected. As shown in FIG. 2, each phase of circuit of the SVG system is formed by cascading eight power units P1 to P8. Each power unit includes a first end and a second end as shown in FIG. 1, wherein a second end of one of adjacent two power units is connected to the first end of the other one of adjacent two power units. For example, the second end of the power unit P1 is connected to the first end of the power unit P2, the second end of the power unit P2 is connected to the first end of the power unit P3, and so on, and the second end of the power unit P7 is connected to the first end of the power unit P8. Each of the first ends of the three power units P1 in the three-phase circuit is connected to a corresponding phase of phases UA, UB and UC of the three-phase grid G by a filter circuit (composed of an inductor L, a resistor R and a capacitor C), wherein the phases UA, UB and UC of the three-phase grid G are connected to a load Rload. The second ends of the three power units P8 in the three-phase circuit are connected to each other. Each power unit includes four power switch devices 2. Each power switch device 2 consists of a power semiconductor switch S and an anti-parallel body diode D or external diode D. A collector of the power semiconductor switch S is connected to a cathode of the diode D, and an emitter of the power semiconductor switch S is connected to an anode of the diode D. Since the power semiconductor switch S and the anti-parallel body diode D or the anti-parallel external diode D are generally used as a whole, for the sake of brevity, the anti-parallel body diode D or the anti-parallel external diode D will not be separately mentioned in the following description. The power unit 1 shown in FIG. 1 may be a full-bridge (H-bridge) circuit, or may be other circuit topologies, such as a half-bridge circuit, a rectifier-inverter circuit, and the like. FIG. 3 is a schematic diagram of an H-bridge circuit (topolog
[ZH CN110690723B]: 海上风电系统中储能型模块化多电平变换器的控制方法 [EN CN110690723B]: Control method of energy storage type modular multilevel converter in offshore wind power system | [ZH CN110690723B]: 本发明提供了一种海上风电系统中储能型模块化多电平变换器的控制方法，在正常工作模式下，通过对储能型模块化多电平变换器进行合理的控制，可以实现对风电场进行虚拟惯量补偿，产生和同容量的同步发电机相同的虚拟惯量，平滑风电功率波动，实现无直流断路器海上风电场设计，且故障发生阶段一定时间内交流风机侧仍可以把发出的电能存储在储能电池组中，减少风电机组内卸荷电阻的配置需求，降低风电机组成本和体积重量。 [EN CN110690723B]: The invention provides a control method of an energy storage modular multilevel converter in an offshore wind power system. In a normal working mode, by rationally controlling the energy storage modular multilevel converter, virtual inertia compensation can be performed on wind farm, virtual inertia having the same capacity as a synchronous generator is generated, the wind power fluctuation is smoothened, and the design of an offshore wind farm without a DC circuit breaker is achieved. An AC wind-driven generator side can still store the transmitted electric energy in an energy storage batterypack within certain time during a fault phase, thereby reducing the configuration requirements of an unloading resistor in a wind-driven generator set, and reducing the cost and the volume weight ofthe wind-driven generator set. | CN110690723B | 2020-01-14 2021-03-19 | CN201911051029A | 2019-10-31 2019-10-31 | CN201911051029A, 2019-10-31 CN201911051029A, 2019-10-31 | CN110690723B: 2021-03-19 | UNIV SHANGHAI JIAOTONG GLOBAL ENERGY INTERCONNECTION RES INST CO LTD 上海交通大学 全球能源互联网研究院有限公司 | LI RUI HAN XIAO CAI XU | H02J3/32: I H02J3/24: I H02J3/38: I | H02J3/24: I H02J3/32: I Y02E10/76: A Y02E70/30: A | CN103647310A CN104538982A CN104953873A CN106712062A CN106877713A CN107039991A CN107154741A |  | [ZH CN110690723B]: 1 .一种海上风电系统中储能型模块化多电平变换器的控制方法，其特征在于，包括如 下工作模式： 「正常工作模式： 储能型模块化多电平变换器对海上风电系统进行虚拟惯量补偿，产生和同容量的同步 发电机相同的虚拟惯量，以平滑风电功率波动； 当海上风电系统发出的功率高于上限值时，储能型模块化多电平变换器中的电池模块 吸收海上风电系统的功率； 当海上风电系统发出的功率低于下限值时，储能型模块化多电平变换器中的电池模块 向直流母线发出功率； 一直流短路故障工作模式： 当直流侧发生短路故障时，储能型模块化多电平变换器中的电池模块吸收海上风电系 统的功率； 其中： 所述正常工作模式和直流短路故障工作模式之间的切换步骤，包括： 「判断海上风电系统的直流侧是否发生短路故障； 若直流侧发生短路故障，储能型模块化多电平变换器切换到直流短路故障工作模式， 储能型模块化多电平变换器中电池模块充电； 若直流侧未发生短路故障，进入以下判断； 「判断海上风电系统发出的功率是否大于上限值； 若海上风电系统发出的功率大于上限值，储能型模块化多电平变换器切换到正常工作 模式，储能型模块化多电平变换器中电池模块充电； 若海上风电系统发出的功率不大于上限值，进入以下判断； 「判断海上风电系统发出的功率是否小于下限值； 若海上风电系统发出的功率小于下限值，储能型模块化多电平变换器切换到正常工作 模式，储能型模块化多电平变换器中电池模块放电； 若海上风电系统发出的功率不小于下限值，储能型模块化多电平变换器切换到正常工 作模式，控制储能型模块化多电平变换器中每个电池模块的荷电状态维持在一定值； 控制储能型模块化多电平变换器中每个电池模块的荷电状态维持在一定值的方法为： 将储能型模块化多电平变换器中每个类全桥储能子模块电池的荷电状态与所有类全 桥储能子模块电池的平均荷电状态相减，得到的结果作为荷电状态控制信号； 获取电池充电电流给定值和实际值的差，将所述荷电状态控制信号乘上比例系数，再 与所述电池充电电流给定值和实际值的差叠加，该叠加结果作为PI控制器的输入，PI控制 器的输出作为调制信号修正值； 将所述调制信号修正值叠加到类全桥储能子模块与电池相连半桥的调制信号的基准 值上，使每个类全桥储能子模块电池的荷电状态趋于一致，其中，所述调制信号基准值为电 池电压与电容平均电压的比值。 2 .根据权利要求1所述的海上风电系统中储能型模块化多电平变换器的控制方法，其 特征在于，所述海上风电系统，包括储能型模块化多电平变换器、变压器、风机变流器以及 风电集电系统；其中，所述风机变流器连接风电集电系统后经变压器与储能型模块化多电 平变换器相连，由储能型模块化多电平变换器进行交流与直流之间的电力变换后通过海底 直流电缆进行电能传输。 3 .根据权利要求2所述的海上风电系统中储能型模块化多电平变换器的控制方法，其 特征在于，所述储能型模块化多电平变换器包括三个相单元，其中：每个相单元均包括上桥 臂、下桥臂、上桥臂电感和下桥臂电感;所述上桥臂的正极端作为相单元的直流出线正极 端;所述上桥臂的负极端与所述上桥臂电感的一端相连;所述上桥臂电感的另一端与所述 下桥臂电感的一端相连后作为相单元的交流出线端，连接到交流电网；所述下桥臂电感的 另一端与所述下桥臂的正极端相连;所述下桥臂的负极端作为相单元的直流出线负极端； 三个相单元中的所述上桥臂和所述下桥臂均由半桥子模块和类全桥储能子模块混合 串联而成。 4 .根据权利要求3所述的海上风电系统中储能型模块化多电平变换器的控制方法，其 特征在于，所述的半桥子模块，包括:第一直流电容器、第一可控开关器件、第二可控开关器 件、第一续流二极管和第二续流二极管;其中： 所述第一可控开关器件和所述第二可控开关器件的集电极分别与所述第一续流二极 管和所述第二续流二极管的阴极相连;所述第一可控开关器件和所述第二可控开关器件的 发射极分别与所述第一续流二极管和所述第二续流二极管的阳极相连;所述第一可控开关 器件的集电极与所述第一直流电容器的阳极相连;所述第二可控开关器件的发射极与所述 第一直流电容器的阴极相连;所述第一可控器件和第二可控器件的栅极均与控制电路相 连。 5 .根据权利要求3所述的海上风电系统中储能型模块化多电平变换器的控制方法，其 特征在于，所述类全桥储能子模块包括:第二直流电容器、电池、电池电感、第三可控开关器 件、第四可控开关器件、第五可控开关器件、第六可控开关器件、第七可控开关器件、第八可 控开关器件、第三续流二极管、第四续流二极管、第五续流二极管和第六续流二极管;其中： 所述第三可控开关器件、所述第四可控开关器件、所述第五可控开关器件和所述第六 可控开关器件的集电极分别与所述第三续流二极管、所述第四续流二极管、所述第五续流 二极管和所述第六续流二极管的阴极相连;所述第三可控开关器件、所述第四可控开关器 件、所述第五可控开关器件和所述第六可控开关器件的发射极分别与所述第三续流二极 管、所述第四续流二极管、所述第五续流二极管和所述第六续流二极管的阳极相连;所述第 三可控开关器件的集电极与所述第二直流电容器的阳极相连;所述第四可控开关器件的发 射极与所述第二直流电容器和所述电池的阴极相连;所述第三可控开关器件的发射极作为 类全桥储能子模块的正极端，并与所述第七可控开关器件的一端相连；所述第四可控开关 器件的发射极与所述第八可控开关器件的一端相连并作为类全桥储能子模块的负极端;所 述第七可控开关器件和所述第八可控开关器件的另一端与所述电池电感的一端相连;所述 电池电感的另一端与所述电池的阳极相连;所述第三可控开关器件、所述第四可控开关器 件、所述第五可控开关器件、所述第六可控开关器件、所述第七可控开关器件和所述第八可 控开关器件的栅极均与控制电路相连。 6 .根据权利要求5所述的海上风电系统中储能型模块化多电平变换器的控制方法，其 特征在于，正常工作模式下，海上风电系统的直流侧未发生短路故障，所述储能型模块化多 电平变换器中类全桥储能子模块的第八可控开关器件导通，第七可控开关器件关断；在直 流短路故障工作模式下，海上风电系统的直流侧发生短路故障，所述储能型模块化多电平 变换器中类全桥储能子模块的第七可控开关器件导通，第八可控开关器件关断。 [EN CN110690723B]: 1 . A control method of an energy storage type modular multilevel converter in an offshore wind power system, which is characterized by including the following working modes: "Normal operating mode: The energy storage type modular multilevel converter performs an operation on the offshore wind power system The virtual inertia compensation generates the same virtual inertia as the synchronous generator of the same capacity to smooth wind power fluctuations; when the power generated by the offshore wind power system is higher than the upper limit, the battery in the energy storage type modular multilevel converter The module absorbs the power of the offshore wind power system; when the power emitted by the offshore wind power system is lower than the lower limit, the battery module in the energy storage type modular multilevel converter sends power to the DC bus; a DC short-circuit fault working mode: When When a short-circuit fault occurs on the DC side, the battery module in the energy storage type modular multilevel converter absorbs the power of the offshore wind power system; wherein: the switching steps between the normal operating mode and the DC short-circuit fault operating mode include: " Determine whether a short-circuit fault occurs on the DC side of the offshore wind power system; if a short-circuit fault occurs on the DC side, the energy storage modular multilevel converter switches to the DC short-circuit fault working mode. The battery module in the energy storage modular multilevel converter Charging; If there is no short-circuit fault on the DC side, enter the following judgment; "Judging whether the power generated by the offshore wind power system is greater than the upper limit; if the power generated by the offshore wind power system is greater than the upper limit, the energy storage type modular multilevel converter Switch to normal working mode, and charge the battery module in the energy storage type modular multi-level converter; If the power generated by the offshore wind power system is not greater than the upper limit, the following judgment is entered: "Judge whether the power generated by the offshore wind power system is less than the lower limit; if the power generated by the offshore wind power system is less than the lower limit, the energy storage type modular multi-electricity The level converter switches to the normal working mode, and the battery modules in the energy storage modular multilevel converter are discharged; if the power generated by the offshore wind power system is not less than the lower limit, the energy storage modular multilevel converter switches to normal Working mode, control the state of charge of each battery module in the energy storage modular multi-level converter to maintain a certain value; control the state of charge of each battery module in the energy storage modular multi-level converter to maintain The method for a certain value is: Subtract the state of charge of each full-bridge energy storage sub-module battery in the energy storage type modular multilevel converter from the average state of charge of all the full-bridge energy storage sub-module batteries, The obtained result is used as the state-of-charge control signal; the difference between the given value and the actual value of the battery charging current is obtained, and the state-of-charge control signal is multiplied by the proportional coefficient, and then the difference between the given value and the actual value of the battery charging current Difference superposition, the superposition result is used as the input of the PI controller, and the output of the PI controller is used as the modulated signal correction value; the modulated signal correction value is superimposed on the reference of the modulation signal of the half-bridge connected to the battery-like full-bridge energy storage submodule In terms of value, the state of charge of each full-bridge energy storage sub-module battery tends to be consistent, wherein the modulation signal reference value is the ratio of the battery voltage to the average voltage of the capacitor. 2 The control method of an energy storage type modular multilevel converter in an offshore wind power system according to claim 1, wherein the offshore wind power system comprises an energy storage type modular multilevel converter, a transformer, A wind turbine converter and a wind power collection system; wherein the wind turbine converter is connected to the wind power collection system through a transformer and an energy storage type modular multi-electricity system. The flat converter is connected, and the power conversion between AC and DC is performed by the energy storage type modular multilevel converter, and then the electric energy is transmitted through the submarine DC cable. 3 The control method of an energy storage type modular multilevel converter in an offshore wind power system according to claim 2, wherein the energy storage type modular multilevel converter includes three phase units, wherein: Each phase unit includes an upper bridge arm, a lower bridge arm, an upper bridge arm inductance, and a lower bridge arm inductance; the positive terminal of the upper bridge arm is used as the positive terminal of the DC outlet of the phase unit; the negative terminal of the upper bridge arm is connected to the One end of the upper bridge arm inductance is connected; the other end of the upper bridge arm inductance is connected to one end of the lower bridge arm inductance and then serves as the AC outlet end of the phase unit, which is connected to the AC power grid; The other end is connected to the positive terminal of the lower bridge arm; the negative terminal of the lower bridge arm serves as the negative terminal of the DC outlet of the phase unit; the upper bridge arm and the lower bridge arm of the three phase units are all connected by half The bridge sub-module and the full-bridge-like energy storage sub-module are mixed in series. 4 The control method of an energy storage type modular multilevel converter in an offshore wind power system according to claim 3, wherein the half-bridge sub-module includes: a first DC capacitor, a first controllable switch A device, a second controllable switching device, a first freewheeling diode, and a second freewheeling diode; wherein: the collectors of the first controllable switching device and the second controllable switching device are respectively connected to the first continuous The current diode is connected to the cathode of the second freewheeling diode; the emitters of the first controllable switching device and the second controllable switching device are respectively connected to the first freewheeling diode and the second freewheeling diode The anode of the diode is connected; the collector of the first controllable switching device is connected to the anode of the first DC capacitor; the emitter of the second controllable switching device is connected to the cathode of the first DC capacitor; so The gates of the first controllable device and the second controllable device are both connected to the control circuit. 5 The control method of an energy storage type modular multilevel converter in an offshore wind power system according to claim 3, wherein the full-bridge-like energy storage sub-module includes: a second DC capacitor, a battery, and a battery inductor , The third controllable switching device, the fourth controllable switching device, the fifth controllable switching device, the sixth controllable switching device, the seventh controllable switching device, the eighth controllable switching device, the third freewheeling diode, the first Four freewheeling diodes, fifth freewheeling diodes, and sixth freewheeling diodes; wherein: the third controllable switching device, the fourth controllable switching device, the fifth controllable switching device, and the sixth The collectors of the controllable switching device are respectively connected to the cathodes of the third freewheeling diode, the fourth freewheeling diode, the fifth freewheeling diode, and the sixth freewheeling diode; the third controllable The emitters of the switching device, the fourth controllable switching device, the fifth controllable switching device, and the sixth controllable switching device are respectively connected to the third freewheeling diode, the fourth freewheeling diode, The fifth freewheeling diode is connected to the anode of the sixth freewheeling diode; the collector of the third controllable switching device is connected to the anode of the second DC capacitor; the fourth controllable switching device is connected to the anode of the second DC capacitor. The emitter is connected to the second DC capacitor and the cathode of the battery; the emitter of the third controllable switching device serves as the positive terminal of the full-bridge-like energy storage submodule and is connected to the seventh controllable switching device Connected to one end; the fourth controllable switch The emitter of the device is connected to one end of the eighth controllable switching device and serves as the negative terminal of the full-bridge-like energy storage submodule; the other end of the seventh controllable switching device and the eighth controllable switching device are connected to One end of the battery inductor is connected; the other end of the battery inductor is connected to the anode of the battery; the third controllable switching device, the fourth controllable switching device, the fifth controllable switching device, The gates of the sixth controllable switching device, the seventh controllable switching device and the eighth controllable switching device are all connected to a control circuit. 6 The control method of an energy storage type modular multilevel converter in an offshore wind power system according to claim 5, characterized in that, in the normal operating mode, no short-circuit fault occurs on the DC side of the offshore wind power system, and the energy storage The eighth controllable switching device of the full-bridge energy storage sub-module in the type modular multilevel converter is turned on, and the seventh controllable switching device is turned off; In the current short-circuit fault working mode, a short-circuit fault occurs on the DC side of the offshore wind power system, the seventh controllable switching device of the full-bridge-like energy storage submodule in the energy storage type modular multilevel converter is turned on, and the eighth The switching device is turned off. | [ZH CN110690723B]: 海上风电系统中储能型模块化多电平变换器的控制方法 技术领域 [0001]本发明涉及电气自动化设备技术领域，具体地，涉及一种海上风电系统中储能型 模块化多电平变换器的控制方法。 背景技术 [0002]随着大规模、远距离海上风电的发展，将海上风电输送到陆上存在电网稳定、电能 质量以及故障保护技术等方面的技术挑战。由于风电机组不能像传统同步发电机一样对电 力系统的频率波动做出响应，用风能取代传统能源会减少电力系统的惯量和频率稳定性。 然而，风电场只要接入储能功率占风电场额定容量5%的储能设备，就能产生和同容量的同 步发电机相同的虚拟惯量。 [0003]在现有的技术中，用于解决风电场并网问题的储能设备通常是作为一个单独设备 接入风电场汇集母线，增加了发电损耗和系统成本。 [0004] 此外，变换器的运行必须考虑到系统的故障情况。在直流输电中，直流侧传输线路 短路故障是最严重的故障类型。常规的基于半桥子模块的模块化多电平变换器不具备阻断 直流故障电流的能力。基于全桥子模块的模块化多电平变换器虽然具备阻断直流故障电流 的能力，但在故障发生时系统的所有子模块必须进入闭锁状态。 [0005] 一方面，应用于海上直流输电的拓扑需要具有故障穿越的能力，另一方面，面向海 上风电的应用，系统又需要一定的储能以增加系统惯性。这就需要能同时把储能与故障穿 越集成到同一个变换器中，且在合理的控制方法下才能实现上述功能。 [0006]目前没有发现同本发明类似技术的说明或报道，也尚未收集到国内外类似的资 料。 发明内容 [0007]针对现有技术中存在的上述不足，本发明的目的是提供一种海上风电系统及其储 能型模块化多电平变换器控制方法，该系统基于储能型模块化多电平变换器，通过对储能 型模块化多电平变换器的工作状态切换进行控制，可以在变换器不停机的同时有效隔离故 障，在故障清除后再切换到正常工作模式。 [0008]本发明是通过以下技术方案实现的。 [0009] 一种海上风电系统中储能型模块化多电平变换器的控制方法，包括如下工作模 式： [0010] -正常工作模式： [0011]储能型模块化多电平变换器对海上风电系统进行虚拟惯量补偿，产生和同容量的 同步发电机相同的虚拟惯量，以平滑风电功率波动； [0012]当海上风电系统发出的功率高于上限值时，储能型模块化多电平变换器中的电池 模块吸收海上风电系统的功率； [0013]当海上风电系统发出的功率低于下限值时，储能型模块化多电平变换器中的电池 模块向直流母线发出功率； [0014] -直流短路故障工作模式： [0015]当直流侧发生短路故障时，储能型模块化多电平变换器中的电池模块吸收海上风 电系统的功率； [0016]其中： [0017]所述正常工作模式和直流短路故障工作模式之间的切换步骤，包括： [0018] -判断海上风电系统的直流侧是否发生短路故障； [0019]若直流侧发生短路故障，储能型模块化多电平变换器切换到直流短路故障工作模 式，储能型模块化多电平变换器中电池模块充电； [0020] 若直流侧未发生短路故障，进入以下判断； [0021] -判断海上风电系统发出的功率是否大于上限值； [0022]若海上风电系统发出的功率大于上限值，储能型模块化多电平变换器切换到正常 工作模式，储能型模块化多电平变换器中电池模块充电； [0023] 若海上风电系统发出的功率不大于上限值，进入以下判断； [0024] -判断海上风电系统发出的功率是否小于下限值； [0025]若海上风电系统发出的功率小于下限值，储能型模块化多电平变换器切换到正常 工作模式，储能型模块化多电平变换器中电池模块放电； [0026]若海上风电系统发出的功率不小于下限值，储能型模块化多电平变换器切换到正 常工作模式，控制储能型模块化多电平变换器中每个电池模块的荷电状态维持在一定值。 [0027]优选地，控制储能型模块化多电平变换器中每个电池模块的荷电状态维持在一定 值的方法为： [0028]将储能型模块化多电平变换器中每个类全桥储能子模块电池的荷电状态与所有 类全桥储能子模块电池的平均荷电状态相减，得到的结果作为荷电状态控制信号； [0029]获取电池充电电流给定值和实际值的差，将所述荷电状态控制信号乘上比例系 数，再与所述电池充电电流给定值和实际值的差叠加，该叠加结果作为PI控制器的输入，PI 控制器的输出作为调制信号修正值； [0030]将所述调制信号修正值叠加到类全桥储能子模块与电池相连半桥的调制信号的 基准值上，使每个类全桥储能子模块电池的荷电状态趋于一致，其中，所述调制信号基准值 为电池电压与电容平均电压的比值。 [0031] 优选地，所述海上风电系统，包括储能型模块化多电平变换器、变压器、风机变流 器以及风电集电系统;其中，所述风机变流器连接风电集电系统后经变压器与储能型模块 化多电平变换器相连，由储能型模块化多电平变换器进行交流与直流之间的电力变换后通 过海底直流电缆进行电能传输。 [0032]优选地，所述储能型模块化多电平变换器包括三个相单元，其中：每个相单元均包 括上桥臂、下桥臂、上桥臂电感和下桥臂电感;所述上桥臂的正极端作为相单元的直流出线 正极端;所述上桥臂的负极端与所述上桥臂电感的一端相连;所述上桥臂电感的另一端与 所述下桥臂电感的一端相连后作为相单元的交流出线端，连接到交流电网；所述下桥臂电 感的另一端与所述下桥臂的正极端相连;所述下桥臂的负极端作为相单元的直流出线负极 端； [0033]三个相单元中的所述上桥臂和所述下桥臂均由半桥子模块和类全桥储能子模块 混合串联而成。 [0034] 优选地，所述的半桥子模块，包括:第一直流电容器、第一可控开关器件、第二可控 开关器件、第一续流二极管和第二续流二极管;其中： [0035] 所述第一可控开关器件和所述第二可控开关器件的集电极分别与所述第一续流 二极管和所述第二续流二极管的阴极相连;所述第一可控开关器件和所述第二可控开关器 件的发射极分别与所述第一续流二极管和所述第二续流二极管的阳极相连;所述第一可控 开关器件的集电极与所述第一直流电容器的阳极相连;所述第二可控开关器件的发射极与 所述第一直流电容器的阴极相连;所述第一可控器件和第二可控器件的栅极均与控制电路 相连。 [0036] 优选地，所述类全桥储能子模块包括:第二直流电容器、电池、电池电感、第三可控 开关器件、第四可控开关器件、第五可控开关器件、第六可控开关器件、第七可控开关器件、 第八可控开关器件、第三续流二极管、第四续流二极管、第五续流二极管和第六续流二极 管;其中： [0037] 所述第三可控开关器件、所述第四可控开关器件、所述第五可控开关器件和所述 第六可控开关器件的集电极分别与所述第三续流二极管、所述第四续流二极管、所述第五 续流二极管和所述第六续流二极管的阴极相连;所述第三可控开关器件、所述第四可控开 关器件、所述第五可控开关器件和所述第六可控开关器件的发射极分别与所述第三续流二 极管、所述第四续流二极管、所述第五续流二极管和所述第六续流二极管的阳极相连;所述 第三可控开关器件的集电极与所述第二直流电容器的阳极相连;所述第四可控开关器件的 发射极与所述第二直流电容器和所述电池的阴极相连;所述第三可控开关器件的发射极作 为类全桥储能子模块的正极端，并与所述第七可控开关器件的一端相连;所述第四可控开 关器件的发射极与所述第八可控开关器件的一端相连并作为类全桥储能子模块的负极端; 所述第七可控开关器件和所述第八可控开关器件的另一端与所述电池电感的一端相连;所 述电池电感的另一端与所述电池的阳极相连;所述第三可控开关器件、所述第四可控开关 器件、所述第五可控开关器件、所述第六可控开关器件、所述第七可控开关器件和所述第八 可控开关器件的栅极均与控制电路相连。 [0038] 优选地，正常工作模式下，海上风电系统的直流侧未发生短路故障，所述储能型模 块化多电平变换器中类全桥储能子模块的第八可控开关器件导通，第七可控开关器件关 断;在直流短路故障工作模式下，海上风电系统的直流侧发生短路故障，所述储能型模块化 多电平变换器中类全桥储能子模块的第七可控开关器件导通，第八可控开关器件关断。 [0039]与现有技术相比，本发明具有如下有益效果： [0040]本发明提供了一种海上风电系统及其储能型模块化多电平变换器控制方法，将储 能电池（即类全桥储能子模块中电池，以下相同）集成在变换器中，减少了发电损耗和系统 成本，同时还保持了直流侧故障穿越能力，可以实现无直流断路器海上风电场设计，解决目 前高压直流断路器技术不成熟的矛盾;且故障发生阶段一定时间内交流风机侧仍可以把发 出的电能存储在储能电池组中，通过配合风电机组变桨控制，可以减少风电机组内卸荷电 阻的配置需求，降低风电机组成本和体积重量。 附图说明 [0041] 通过阅读参照以下附图对非限制性实施例所作的详细描述，本发明的其它特征、 目的和优点将会变得更明显： [0042]图1为本发明一实施例中提供的海上风电系统中储能型模块化多电平变换器工作 状态切换步骤框图； [0043]图2为本发明一实施例中提供的一种基于储能型模块化多电平变换器的海上风电 系统结构示意图； [0044]图3为本发明一实施例中提供的海上风电系统中的储能型模块化多电平变换器电 路拓扑图； [0045]图4为本发明一实施例中提供的储能型模块化多电平变换器中的半桥子模块电路 图； [0046]图5为本发明一实施例中提供的储能型模块化多电平变换器中的类全桥储能子模 块电路图。 具体实施方式 [0047]下面结合具体的实施例对本发明进行详细的说明。以下实施例将有助于本领域的 技术人员进一步理解本发明，但不以任何形式限制本发明。应当指出的是，对本领域的普通 技术人员来说，在不脱离本发明构思的前提下，还可以做出若干变形和改进，这都属于本发 明的保护范围。 [0048]本发明实施例提供了一种上述海上风电系统中储能型模块化多电平变换器的控 制方法，在正常工作模式下，通过对储能型模块化多电平变换器进行合理的控制，实现对风 电场进行虚拟惯量补偿，产生和同容量的同步发电机相同的虚拟惯量。当风电场发出的功 率高于上限值时，储能电池吸收风电场的功率，当风电场发出的功率低于下限值时，储能电 池向直流母线发出功率，以平滑风电功率波动。当直流侧发生短路故障时，储能型模块化多 电平变换器切换到直流短路故障工作模式，储能电池吸收风电场的功率，可以在变换器不 停机的同时有效隔离故障，在故障清除后再切换到正常工作模式。 [0049]具体包括如下工作状态切换步骤： [0050] -判断海上风电系统直流侧是否发生短路故障； [0051]若直流侧发生短路故障，储能型模块化多电平变换器切换到直流短路故障工作模 式，电池充电； [0052] 若直流侧未发生短路故障，进入以下判断； [0053] -判断海上风电系统发出的功率是否大于上限值； [0054]若海上风电系统发出的功率大于上限值，储能型模块化多电平变换器切换到正常 工作模式，电池充电； [0055] 若海上风电系统发出的功率不大于上限值，进入以下判断； [0056] -判断海上风电系统发出的功率是否小于下限值； [0057]若海上风电系统发出的功率小于下限值，储能型模块化多电平变换器切换到正常 工作模式，电池放电； [0058]若海上风电系统发出的功率不小于下限值，储能型模块化多电平变换器切换到正 常工作模式，控制每个电池模块的荷电状态维持在一定值。 [0059]进一步地，所述基于储能型模块化多电平变换器的海上风电系统，将储能型模块 化多电平变换器安装在海上，风机变流器连接风电集电系统后经变压器与储能型模块化多 电平变换器相连，由储能型模块化多电平变换器进行交流-直流电力变换后通过海底直流 电缆将电能传输到陆上。 [0060]进一步地，所述储能型模块化多电平变换器包括三个相单元，每个相单元均包括 上桥臂、下桥臂、上桥臂电感、下桥臂电感;所述上桥臂的正极端作为相单元的直流出线正 极端;所述上桥臂的负极端与所述上桥臂电感的一端相连;所述上桥臂电感的另一端与所 述下桥臂电感的一端相连，作为相单元的交流出线端，连接到交流电网;所述下桥臂电感的 另一端与所述下桥臂的正极端相连;所述下桥臂的负极端作为相单元的直流出线负极端; 三个相单元中的所述上桥臂、所述下桥臂均由半桥子模块和类全桥储能子模块混合串联而 成。 [0061] 进一步地，所述的半桥子模块，包括:第一直流电容器、第一可控开关器件、第二可 控开关器件、第一续流二极管、第二续流二极管;其中： [0062] 所述第一可控开关器件、所述第二可控开关器件的集电极分别与所述第一续流二 极管、所述第二续流二极管的阴极相连;所述第一可控开关器件、所述第二可控开关器件的 发射极分别与所述第一续流二极管、所述第二续流二极管的阳极相连;所述第一可控开关 器件的集电极与所述第一直流电容器的阳极相连;所述第二可控开关器件的发射极与所述 第一直流电容器的阴极相连;所述第一可控器件，第二可控器件的栅极均与控制电路相连。 [0063] 进一步地，所述类全桥储能子模块包括:第二直流电容器、电池、电池电感、第三可 控开关器件、第四可控开关器件、第五可控开关器件、第六可控开关器件、第七可控开关器 件、第八可控开关器件、第三续流二极管、第四续流二极管、第五续流二极管、第六续流二极 管;其中： [0064] 所述第三可控开关器件、所述第四可控开关器件、所述第五可控开关器件、所述第 六可控开关器件的集电极分别与所述第三续流二极管、所述第四续流二极管、所述第五续 流二极管、所述第六续流二极管的阴极相连;所述第三可控开关器件、所述第四可控开关器 件、所述第五可控开关器件、所述第六可控开关器件的发射极分别与所述第三续流二极管、 所述第四续流二极管、所述第五续流二极管、所述第六续流二极管的阳极相连;所述第三可 控开关器件的集电极与所述第二直流电容器的阳极相连;所述第四可控开关器件的发射极 与所述第二直流电容器、所述电池的阴极相连;所述第三可控开关器件的发射极作为类全 桥储能子模块的正极端，并与所述第七可控开关器件的一端相连；所述第四可控开关器件 的发射极与所述第八可控开关器件的一端相连并作为类全桥储能子模块的负极端;所述第 七可控开关器件、所述第八可控开关器件的另一端与所述电池电感的一端相连;所述电池 电感的另一端与所述电池的阳极相连;所述第三可控开关器件、所述第四可控开关器件、所 述第五可控开关器件、所述第六可控开关器件、所述第七可控开关器件、所述第八可控开关 器件的栅极均与控制电路相连。 [0065] 进一步地，所述正常工作模式，直流母线（直流侧）未发生短路故障，所述第八可控 开关器件导通，所述第七可控开关器件关断。所述直流短路故障工作模式，直流母线（直流 侧）发生短路故障，所述第七可控开关器件导通，所述第八可控开关器件关断。 [0066] 进一步地，控制储能型模块化多电平变换器中每个电池模块的荷电状态维持在一 定值的方法为:根据储能型模块化多电平变换器中每个类全桥储能子模块电池的荷电状态 与所有类全桥储能子模块电池的平均荷电状态相减，产生荷电状态控制信号，乘上比例系 数后再与电池充电电流给定值和实际值的差叠加作为PI控制器的输入,ΡΙ控制器的输出作 为调制信号修正值，叠加到类全桥储能子模块与电池相连半桥的调制信号的基准值上，其 中调制信号基准值为电池电压与电容平均电压的比值,使每个类全桥储能子模块电池的荷 电状态维持在一定值。 [0067] 在本发明实施例中，ΡΙ控制器是实现整个控制方法的控制方案的一部分，控制电 路是用于实现控制方案的硬件电路。 [0068]下面结合附图，对本发明实施例所提供的技术方案进一步详细描述。 [0069]如图1所示，为本发明一优选实施例中提供的海上风电系统中的储能型模块化多 电平变换器工作状态切换步骤框图；包括如下工作状态切换步骤： [0070] S1：判断直流侧是否发生短路故障； [0071]若直流侧发生短路故障,储能型模块化多电平变换器切换到直流短路故障工作模 式，电池充电； [0072] 若直流侧未发生短路故障，进入以下判断； [0073] S2：判断风电场发出的功率Ρ是否大于上限值Pmax； [0074]若风电场发出的功率P大于上限值Pmax，储能型模块化多电平变换器切换到正常工 作模式，电池充电，每个电池模组充电电流给定值/设定为； [0075] [0076] [0077] [0078] [00791 其中,Nf为每个桥臂类全桥储能子模块个数,Vbat为电池模组电压。 若风电场发出的功率P不大于上限值Pmax，进入以下判断； S3:判断风电场发出的功率P是否小于下限值Pmin； 若风电场发出的功率P小于下限值Pmi/储能型模块化多电平变换器切换到正常工 作模式，电池放电，每个电池模组充电电流给定值设定为； [0080] bat [0081]若风电场发出的功率P不小于下限值Ρ疝η，储能型模块化多电平变换器切换到正常 工作模式，控制每个电池模块的荷电状态维持在一定值SOC。； [0082]如图2所示，为本发明一优选实施例中提供的一种基于储能型模块化多电平变换 器的海上风电系统（即海上风电场侧）方案;将储能型模块化多电平变换器安装在海上，风 机变流器连接风电集电系统后经变压器与储能型模块化多电平变换器相连，由储能型模块 化多电平变换器进行交流-直流电力变换后通过海底直流电缆将电能传输到陆上。在正常 工作模式下，通过对储能型模块化多电平变换器进行合理的控制，可以实现对风电场进行 虚拟惯量补偿，产生和同容量的同步发电机相同的虚拟惯量。当风电场发出的功率高于上 限值时，储能电池吸收风电场的功率。当风电场发出的功率低于下限值时，储能电池向直流 母线发出功率，以平滑风电功率波动。当直流侧发生短路故障时，储能型模块化多电平变换 器切换到直流短路故障工作模式，可以在变换器不停机的同时有效隔离故障，在故障清除 后再切换到正常工作模式。 [0083]如图3所示，为本发明一实施例中提供的应用于海上风电的储能型模块化多电平 变换器电路拓扑图;所述混合储能型模块化多电平变换器包括三个相单元，每个相单元x (x = a,b,c)均包括上桥臂、下桥臂、上桥臂电感Lxp、下桥臂电感Lxn ；所述上桥臂的正极端作为 相单元的直流出线正极端;所述上桥臂的负极端与所述上桥臂电感Lxp的一端相连;所述上 桥臂电感Lxp的另一端与所述下桥臂电感Lxn的一端相连，作为相单元的交流出线端Vx，连接 到电网;所述下桥臂电感的另一端与所述下桥臂的正极端相连;所述下桥臂Lxn的负极端作 为相单元的直流出线负极端;三个相单元中的所述上桥臂、所述下桥臂均由半桥子模块和 类全桥储能子模块混合串联而成。子模块xy i(x = a,b,c,y = p,n,i = 1,2 N；其中p代表 上，n代表下)代表x相y桥臂的第i个子模块，ix指x相交流侧电流，ixy指x相y桥臂的电流，Vxy 指x相y桥臂所有子模块输出的电压和，1d指直流侧电流，Vdc指直流侧电压。 [0084]如图4所示,为一优选实施例的半桥子模块电路图；所述的半桥子模块，包括：第一 直流电容器C1,第一可控开关器件S1、第二可控开关器件S2,以及第一续流二极管D1、第二 续流二极管D2；其中： [0085] 所述第一可控开关器件S1的集电极、所述第二可控开关器件S2的集电极分别与所 述第一续流二极管D1的阴极、所述第二续流二极管D2的阴极相连;所述第一可控开关器件 S1的发射极、所述第二可控开关器件S2的发射极分别与所述第一续流二极管D1的阳极、所 述第二续流二极管D2的阳极相连;所述第一可控开关器件S1的集电极还与所述第一直流电 容器C1的阳极相连;所述第二可控开关器件S1的发射极还与所述第一直流电容器C1的阴极 相连;所述第一可控开关器件S1的栅极、第二可控开关器件S2的栅极均与控制电路相连。 [0086]如图5所示，为本发明一实施例中提供的类全桥储能子模块电路图；所述的类全桥 储能子模块，包括:第二直流电容器C2、电池、电池电感L、第三可控开关器件S3、第四可控开 关器件S4、第五可控开关器件S5、第六可控开关器件S6、第七可控开关器件T1、第八可控开 关器件T2、第三续流二极管D3、第四续流二极管D4、第五续流二极管D5、第六续流二极管D6； 其中： [0087]所述第三可控开关器件S3的集电极、所述第四可控开关器件S4的集电极、所述第 五可控开关器件S5的集电极、所述第六可控开关器件S6的集电极分别与所述第三续流二极 管D3的阴极、所述第四续流二极管D4的阴极、所述第五续流二极管D5的阴极、所述第六续流 二极管D6的阴极相连;所述第三可控开关器件S3的发射极、所述第四可控开关器件S4的发 射极、所述第五可控开关器件S5的发射极、所述第六可控开关器件S6的发射极分别与所述 第三续流二极管D3的阳极、所述第四续流二极管D4的阳极、所述第五续流二极管D5的阳极、 所述第六续流二极管D6的阳极相连;所述第三可控开关器件S3的集电极与所述第二直流电 容器C2的阳极相连;所述第四可控开关器件S4的发射极与所述第二直流电容器C2的阴极、 所述电池的阴极相连;所述第三可控开关器件S3的发射极作为类全桥储能子模块的正极 端，并与所述第七可控开关器件T1的一端相连；所述第四可控开关器件S4的发射极与所述 第八可控开关器件T2的一端相连并作为类全桥储能子模块的负极端;所述第七可控开关器 件T1、所述第八可控开关器件T2的另一端与所述电池电感L的一端相连;所述电池电感L的 另一端与所述电池的阳极相连;所述第三可控开关器件S3的栅极、所述第四可控开关器件 S4的栅极、所述第五可控开关器件S5的栅极、所述第六可控开关器件S6的栅极、所述第七可 控开关器件T1的栅极、所述第八可控开关器件T2的栅极均与控制电路相连； [0088] 在正常工作模式下，直流母线未发生短路故障，所述第八可控开关器件T2导通，所 述第七可控开关器件T1关断。在直流短路故障工作模式下，直流母线发生短路故障，所述第 七可控开关器件T1导通，所述第八可控开关器件T2关断。 [0089]本发明上述实施例提供的海上风电系统及其储能型模块化多电平变换器控制方 法，所述模块化多电平变换器包括三个相单元，每个相单元包括上桥臂，下桥臂，上桥臂电 感，下桥臂电感，上、下桥臂均由半桥子模块和类全桥储能子模块混合串联而成。将储能型 模块化多电平变换器安装在海上，风机变流器连接风电集电系统后经变压器与储能型模块 化多电平变换器相连，由储能型模块化多电平变换器进行交流-直流电力变换后通过海底 直流电缆将电能传输到陆上。在正常工作模式下，通过对储能型模块化多电平变换器进行 合理的控制，可以实现对风电场进行虚拟惯量补偿，产生和同容量的同步发电机相同的虚 拟惯量，平滑风电功率波动。上述方法将储能电池集成在变换器中，减少了发电损耗和系统 成本，同时还保持了直流侧故障穿越能力，可以实现无直流断路器海上风电场设计，且故障 发生阶段一定时间内交流风机侧仍可以把发出的电能存储在储能电池组中，通过配合风电 机组变桨控制，可以减少风电机组内卸荷电阻的配置需求，降低风电机组成本和体积重量。 [0090]以上对本发明的具体实施例进行了描述。需要理解的是，本发明并不局限于上述 特定实施方式，本领域技术人员可以在权利要求的范围内做出各种变形或修改，这并不影 响本发明的实质内容。 CN 110690723 Β [EN CN110690723B]: Control method of energy storage type modular multilevel converter in offshore wind power system Technical field [0001] The present invention relates to the technical field of electrical automation equipment, and in particular, to a control method of an energy storage type modular multilevel converter in an offshore wind power system. Background technique [0002] With the development of large-scale, long-distance offshore wind power, there are technical challenges in terms of grid stability, power quality, and fault protection technology to transport offshore wind power to land. Since wind turbines cannot respond to the frequency fluctuations of the power system like traditional synchronous generators, replacing traditional energy with wind energy will reduce the inertia and frequency stability of the power system. However, a wind farm can generate the same virtual inertia as a synchronous generator of the same capacity as long as it is connected to an energy storage device whose energy storage power accounts for 5% of the wind farm's rated capacity. [0003] In the existing technology, the energy storage device used to solve the problem of wind farm grid connection is usually connected to the wind farm collection bus as a separate device, which increases power generation loss and system cost. [0004] In addition, the operation of the converter must take into account the failure of the system. In DC transmission, the short-circuit fault of the transmission line on the DC side is the most serious type of fault. Conventional modular multilevel converters based on half-bridge sub-modules do not have the ability to block DC fault currents. Although the modular multi-level converter based on the full-bridge sub-module has the ability to block the DC fault current, all sub-modules of the system must enter the locked state when a fault occurs. [0005] On the one hand, the topology applied to offshore direct current transmission needs to have the capability of fault ride-through. On the other hand, for offshore wind power applications, the system needs a certain amount of energy storage to increase the system inertia. This requires that energy storage and fault ride-through can be integrated into the same converter at the same time, and the above functions can be realized under a reasonable control method. [0006] At present, there is no description or report of a technology similar to the present invention, and similar information at home and abroad has not been collected. Summary of the invention [0007] In view of the above-mentioned shortcomings in the prior art, the purpose of the present invention is to provide an offshore wind power system and its energy storage type modular multilevel converter control method, which is based on the energy storage type modular multilevel converter. The converter, by controlling the switching of the working state of the energy storage type modular multilevel converter, can effectively isolate the fault while the converter is not shutting down, and then switch to the normal working mode after the fault is cleared. [0008] The present invention is achieved through the following technical solutions. [0009] A control method of an energy storage type modular multilevel converter in an offshore wind power system includes the following working modes: [0010]-Normal working mode: [0011] The energy storage type modular multilevel converter performs virtual inertia compensation for the offshore wind power system, and generates the same virtual inertia as a synchronous generator of the same capacity to smooth wind power fluctuations; [0012] When the power emitted by the offshore wind power system is higher than the upper limit, the battery module in the energy storage type modular multilevel converter absorbs the power of the offshore wind power system; [0013] When the power emitted by the offshore wind power system is lower than the lower limit, the battery in the energy storage type modular multilevel converter The module sends power to the DC bus; [0014]-DC short-circuit fault working mode: [0015] When a short-circuit fault occurs on the DC side, the battery module in the energy storage type modular multilevel converter absorbs the power of the offshore wind power system; [0016] where: [0017] The switching step between the normal operating mode and the DC short-circuit fault operating mode includes: [0018]-Determine whether a short-circuit fault occurs on the DC side of the offshore wind power system; [0019] If a short-circuit fault occurs on the DC side, the energy storage type modular multilevel converter switches to the DC short-circuit fault operation mode, and the battery module in the energy storage type modular multilevel converter is charged; [0020] If there is no short-circuit fault on the DC side, enter the following judgment; [0021]-Determine whether the power emitted by the offshore wind power system is greater than the upper limit; [0022] If the power emitted by the offshore wind power system is greater than the upper limit, the energy storage type modular multilevel converter is switched to the normal operating mode, and the battery module in the energy storage type modular multilevel converter is charged; [0023] If the power emitted by the offshore wind power system is not greater than the upper limit, enter the following judgment; [0024]-Determine whether the power emitted by the offshore wind power system is less than the lower limit; [0025] If the power emitted by the offshore wind power system is less than the lower limit, the energy storage type modular multilevel converter is switched to the normal operating mode, and the battery module in the energy storage type modular multilevel converter is discharged; [0026] If the power emitted by the offshore wind power system is not less than the lower limit, the energy storage modular multilevel converter switches to the normal working mode to control the charge of each battery module in the energy storage modular multilevel converter The electrical state is maintained at a certain value. [0027] Preferably, the method for controlling the state of charge of each battery module in the energy storage type modular multilevel converter to maintain a certain value is: [0028] The state of charge of each full-bridge energy storage sub-module battery in the energy storage type modular multilevel converter is subtracted from the average state of charge of all the full-bridge energy storage sub-module batteries, and the result is obtained As a state-of-charge control signal; [0029] Obtain the difference between the given value and the actual value of the battery charging current, multiply the state-of-charge control signal by the proportional coefficient, and then superimpose it with the difference between the given value and the actual value of the battery charging current, and the superposition result is taken as The input of the PI controller, and the output of the PI controller as the modulating signal correction value; [0030] The modulation signal correction value is superimposed on the reference value of the modulation signal of the half-bridge connected to the battery-like full-bridge energy storage sub-module, so that the state of charge of each battery-like full-bridge energy storage sub-module tends to be consistent , Wherein the reference value of the modulation signal is the ratio of the battery voltage to the average voltage of the capacitor. [0031] Preferably, the offshore wind power system includes an energy storage type modular multilevel converter, a transformer, a wind turbine converter, and a wind power collection system; wherein the wind turbine converter is connected to the wind power collection system. The energy storage type modular multilevel converter is connected via a transformer, and the energy storage type modular multilevel converter performs power conversion between AC and DC and then transmits electric energy through a submarine DC cable. [0032] Preferably, the energy storage type modular multilevel converter includes three phase units, wherein: each phase unit includes an upper bridge arm, a lower bridge arm, an upper bridge arm inductance and a lower bridge arm inductance; The positive terminal of the upper bridge arm serves as the positive terminal of the DC outlet of the phase unit; the negative terminal of the upper bridge arm is connected to one end of the upper bridge arm inductance; the other end of the upper bridge arm inductance is connected to the lower bridge. One end of the arm inductance is connected as the AC outlet end of the phase unit and connected to the AC power grid; the other end of the lower bridge arm inductance is connected to the positive terminal of the lower bridge arm; the negative end of the lower bridge arm is used as the phase unit The negative terminal of the DC outlet; [0033] The upper bridge arm and the lower bridge arm in the three phase units are all formed by a mixed series connection of a half-bridge sub-module and a full-bridge-like energy storage sub-module. [0034] Preferably, the half-bridge sub-module includes: a first DC capacitor, a first controllable switching device, a second controllable switching device, a first freewheeling diode and a second freewheeling diode; wherein: [0035] The collectors of the first controllable switching device and the second controllable switching device are respectively connected to the cathodes of the first freewheeling diode and the second freewheeling diode; the first controllable The emitters of the switching device and the second controllable switching device are respectively connected to the anodes of the first freewheeling diode and the second freewheeling diode; the collector of the first controllable switching device is connected to the first freewheeling diode. The anode of a DC capacitor is connected; the emitter of the second controllable switching device is connected to the cathode of the first DC capacitor; the gates of the first controllable device and the second controllable device are both connected to the control circuit . [0036] Preferably, the full-bridge-like energy storage sub-module includes: a second DC capacitor, a battery, a battery inductor, a third controllable switching device, a fourth controllable switching device, a fifth controllable switching device, and a sixth The controllable switching device, the seventh controllable switching device, the eighth controllable switching device, the third freewheeling diode, the fourth freewheeling diode, the fifth freewheeling diode and the sixth freewheeling diode; where: [0037] The collectors of the third controllable switching device, the fourth controllable switching device, the fifth controllable switching device and the sixth controllable switching device are respectively connected to the third freewheeling diode , The fourth freewheeling diode, the fifth freewheeling diode and the cathode of the sixth freewheeling diode are connected; the third controllable switching device, the fourth controllable switching device, the fifth The emitters of the controllable switching device and the sixth controllable switching device are respectively connected to the third freewheeling diode, the fourth freewheeling diode, the fifth freewheeling diode and the sixth freewheeling diode. The anode is connected; the collector of the third controllable switching device is connected to the anode of the second DC capacitor; the emitter of the fourth controllable switching device is connected to the second DC capacitor and the cathode of the battery The emitter of the third controllable switching device is used as the positive terminal of the full-bridge-like energy storage submodule and is connected to one end of the seventh controllable switching device; the emitter of the fourth controllable switching device is connected to One end of the eighth controllable switching device is connected and used as the negative terminal of the full-bridge-like energy storage submodule; The other ends of the seventh controllable switching device and the eighth controllable switching device are connected to one end of the battery inductance; the other end of the battery inductance is connected to the anode of the battery; the third controllable Gates of switching device, said fourth controllable switching device, said fifth controllable switching device, said sixth controllable switching device, said seventh controllable switching device, and said eighth controllable switching device Both are connected to the control circuit. [0038] Preferably, in the normal operating mode, no short-circuit fault occurs on the DC side of the offshore wind power system, and the eighth controllable switching device of the full-bridge-like energy storage submodule in the energy storage type modular multilevel converter is conductive On, the seventh controllable switching device is turned off; in the DC short-circuit fault operation mode, a short-circuit fault occurs on the DC side of the offshore wind power system, and the energy storage type modular multi-level converter has a full-bridge energy storage sub-module The seventh controllable switching device is turned on, and the eighth controllable switching device is turned off. [0039] Compared with the prior art, the present invention has the following beneficial effects: [0040] The present invention provides an offshore wind power system and its energy storage type modular multilevel converter control method, which integrates an energy storage battery (that is, the battery in a full-bridge energy storage sub-module, the same below) in the converter In this way, the power loss and system cost are reduced, while the DC side fault ride-through capability is maintained. The design of offshore wind farms without DC circuit breakers can be realized, and the contradiction of the current immature high-voltage DC circuit breaker technology can be solved; and the fault occurs within a certain period of time. The AC fan side can still store the generated electrical energy in the energy storage battery pack. By cooperating with the pitch control of the wind turbine, the configuration requirements for unloading resistors in the wind turbine can be reduced, and the wind turbine composition and volume weight can be reduced. Description of the drawings [0041] By reading the detailed description of the non-limiting embodiments with reference to the following drawings, other features, objectives and advantages of the present invention will become more apparent: [0042] FIG. 1 is a block diagram of the operating state switching steps of an energy storage type modular multilevel converter in an offshore wind power system provided in an embodiment of the present invention; [0043] FIG. 2 is a schematic structural diagram of an offshore wind power system based on an energy storage type modular multilevel converter provided in an embodiment of the present invention; [0044] FIG. 3 is a circuit topology diagram of an energy storage type modular multilevel converter in an offshore wind power system provided in an embodiment of the present invention; [0045] FIG. 4 is a circuit diagram of a half-bridge sub-module in an energy storage type modular multilevel converter provided in an embodiment of the present invention; [0046] FIG. 5 is a circuit diagram of a full-bridge-like energy storage submodule in an energy storage type modular multilevel converter provided in an embodiment of the present invention. detailed description [0047] The present invention will be described in detail below in conjunction with specific embodiments. The following examples will help those skilled in the art to further understand the present invention, but do not limit the present invention in any form. It should be pointed out that for those of ordinary skill in the art, without departing from the concept of the present invention, several modifications and improvements can be made, which all fall within the protection scope of the present invention. [0048] The embodiment of the present invention provides a method for controlling the energy storage type modular multilevel converter in the above-mentioned offshore wind power system. In the normal working mode, the energy storage type modular multilevel converter is reasonably controlled. It realizes the virtual inertia compensation for the wind farm and generates the same virtual inertia as the synchronous generator of the same capacity. When the power generated by the wind farm is higher than the upper limit, the energy storage battery absorbs the power of the wind farm. When the power generated by the wind farm is lower than the lower limit, the energy storage battery sends power to the DC bus to smooth wind power fluctuations. When a short-circuit fault occurs on the DC side, the energy storage modular multilevel converter switches to the DC short-circuit fault working mode. The energy storage battery absorbs the power of the wind farm, which can effectively isolate the fault while the converter is not shutting down, and clear the fault. Then switch to normal working mode. [0049] It specifically includes the following working state switching steps: [0050]-Determine whether a short-circuit fault occurs on the DC side of the offshore wind power system; [0051] If a short-circuit fault occurs on the DC side, the energy storage type modular multilevel converter switches to the DC short-circuit fault working mode, and the battery is charged; [0052] If there is no short-circuit fault on the DC side, enter the following judgment; [0053]-Determine whether the power generated by the offshore wind power system is greater than the upper limit; [0054] If the power generated by the offshore wind power system is greater than the upper limit, the energy storage modular multilevel converter switches to the normal working mode, and the battery is charged; [0055] If the power emitted by the offshore wind power system is not greater than the upper limit, enter the following judgment; [0056]-Determine whether the power emitted by the offshore wind power system is less than the lower limit; [0057] If the power emitted by the offshore wind power system is less than the lower limit, the energy storage modular multilevel converter switches to the normal operating mode, and the battery is discharged; [0058] If the power emitted by the offshore wind power system is not less than the lower limit, the energy storage type modular multilevel converter switches to positive Normal working mode, controlling the state of charge of each battery module to maintain a certain value. [0059] Further, in the offshore wind power system based on the energy storage type modular multilevel converter, the energy storage type modular multilevel converter is installed at sea, and the wind turbine converter is connected to the wind power collection system through The transformer is connected to the energy storage type modular multilevel converter, and the energy storage type modular multilevel converter performs AC-DC power conversion and then transmits the electric energy to the land through a submarine DC cable. [0060] Further, the energy storage type modular multilevel converter includes three phase units, each of which includes an upper bridge arm, a lower bridge arm, an upper bridge arm inductance, and a lower bridge arm inductance; The positive terminal of the upper bridge arm serves as the positive terminal of the DC outlet of the phase unit; the negative terminal of the upper bridge arm is connected to one end of the upper bridge arm inductance; the other end of the upper bridge arm inductance is connected to the lower bridge arm inductance. The other end of the lower bridge arm is connected to the positive terminal of the lower bridge arm as the AC outlet end of the phase unit, which is connected to the AC power grid; the other end of the lower bridge arm is connected to the positive terminal of the lower bridge arm; the negative terminal of the lower bridge arm is used as the DC of the phase unit The negative terminal of the outlet line; the upper bridge arm and the lower bridge arm in the three phase units are formed by a mixed series connection of a half-bridge sub-module and a full-bridge-like energy storage sub-module. [0061] Further, the half-bridge sub-module includes: a first DC capacitor, a first controllable switching device, a second controllable switching device, a first freewheeling diode, and a second freewheeling diode; wherein: [0062] The collectors of the first controllable switching device and the second controllable switching device are respectively connected to the cathodes of the first freewheeling diode and the second freewheeling diode; the first controllable The emitters of the switching device and the second controllable switching device are respectively connected to the anodes of the first freewheeling diode and the second freewheeling diode; the collector of the first controllable switching device is connected to the first freewheeling diode. The anode of a DC capacitor is connected; the emitter of the second controllable switching device is connected to the cathode of the first DC capacitor; the gates of the first controllable device and the second controllable device are connected to the control circuit . [0063] Further, the full-bridge-like energy storage submodule includes: a second DC capacitor, a battery, a battery inductor, a third controllable switching device, a fourth controllable switching device, a fifth controllable switching device, and a sixth The controllable switching device, the seventh controllable switching device, the eighth controllable switching device, the third freewheeling diode, the fourth freewheeling diode, the fifth freewheeling diode, and the sixth freewheeling diode; among them: [0064] The collectors of the third controllable switching device, the fourth controllable switching device, the fifth controllable switching device, and the sixth controllable switching device are respectively connected to the third freewheeling diode , The cathodes of the fourth freewheeling diode, the fifth freewheeling diode, and the sixth freewheeling diode are connected; the t
[KO KR101711948B1]: ＭＭＣ 컨버터의 서브모듈용 전원제어장치 [EN EP3242387B1]: POWER CONTROL APPARATUS FOR SUB-MODULE OF MMC CONVERTER [FR EP3242387B1]: APPAREIL DE COMMANDE D'ALIMENTATION POUR SOUS-MODULE DE CONVERTISSEUR MMC [DE EP3242387B1]: LEISTUNGSREGELUNGSVORRICHTUNG FÜR EIN UNTERMODUL EINES MMC-WANDLERS [PT BR112017013961A2]: aparelho de controle de potência para submódulo de conversor mmc | [KO KR101711948B1]: 본 발명은 HVDC 시스템 및 STATCOM과 연계되는 MMC 컨버터의 서브모듈(sub-module)에 전원공급을 제어하도록 하는 서브모듈용 전원제어장치에 관한 것이다.본 발명에 따른 전원제어장치는, MMC 컨버터의 P-N 모선의 입력전압을 상대적으로 낮은 저전압으로 변환하여 출력하는 하프브릿지회로부; 상기 하프브릿지회로부에서 출력된 저전압의 출력전압(1차측)을 2차측으로 전달하는 트랜스포머; 상기 트랜스포머의 2차측 출력전압을 변환하는 DC/DC 컨버터; 상기 트랜스포머의 2차측 출력전압의 크기에 대응하는 기준신호를 출력하는 포토커플러; 상기 포토커플러의 기준신호에 따라 상기 하프브릿지 회로부 내의 상기 스위치에 대한 스위칭을 제어하는 PWM 제어부; 및 상기 PWM 제어부로 초기 기동전압을 공급하는 기동회로부; 를 포함하고, 상기 PWM 제어부는 초기에 상기 기동회로부로부터 공급된 기동전압에 의해 기동되어 상기 포토커플러로부터 수신된 상기 기준신호에 따라 상기 스위치의 스위칭을 제어하고 상기 스위칭에 따라 상기 트랜스포머의 2차측에 출력되는 출력전압을 동작전압으로 입력받아 동작한다. [EN EP3242387B1]: The present invention relates to a power control apparatus for sub-modules in a Modular Multilevel Converter (MMC), which controls the supply of power to sub-modules in an MMC connected to an HVDC system and to a STATCOM. The power control apparatus includes a half-bridge circuit unit for switching multiple switches, converting an input voltage across P and N buses of the MMC into a relatively low voltage, and outputting the low voltage; a transformer for transferring the low output voltage (primary side), output through switching of the switches in the half-bridge circuit unit via switching of the switches, to a secondary side of the transformer; a DC/DC converter for converting an output voltage on the secondary side of the transformer; a photocoupler for outputting a reference signal corresponding to a magnitude of the secondary side output voltage of the transformer; a Pulse Width Modulation (PWM) control unit for controlling switching of the switches in the half-bridge circuit unit in response to the reference signal output from the photocoupler; and a starting circuit unit for supplying an initial starting voltage to the PWM control unit, wherein the PWM control unit is started in response to the starting voltage initially supplied from the starting circuit unit, and is configured to control switching of the switches in response to the reference voltage received from the photocoupler, and to receive the secondary side output voltage of the transformer as an operating voltage depending on the switching, thus being operated. [FR WO2016108552A1]: La présente invention concerne un appareil de commande d'alimentation pour sous-module, qui commande l'alimentation d'un sous-module d'un convertisseur MMC connecté à un système HVDC et un STATCOM. L'appareil de commande d'alimentation de la présente invention comprend : une unité de circuit en demi-pont pour convertir une tension d'entrée d'une barre omnibus P-N d'un convertisseur MMC et la délivrer en sortie sous la forme d'une basse tension qui est relativement basse ; un transformateur pour transférer à un côté secondaire la tension de sortie (côté primaire) de la basse tension délivrée par l'unité de circuit en demi-pont ; un convertisseur continu/continu pour convertir la tension de sortie au niveau du côté secondaire du transformateur ; un photocoupleur pour délivrer un signal de référence correspondant à l'amplitude de la tension de sortie au niveau du côté secondaire du transformateur ; une unité de commande PWM pour commander la commutation d'un commutateur à l'intérieur de l'unité de circuit en demi-pont en fonction du signal de référence du photocoupleur ; et une unité de circuit de démarrage pour fournir une tension de démarrage initiale à l'unité de commande PWM. L'unité de commande PWM est initialement démarrée par une tension de démarrage fournie par l'unité de circuit de démarrage, commande la commutation du commutateur en fonction de la tension de référence reçue en provenance du photocoupleur, et est faite fonctionner par réception, à titre de tension de fonctionnement, d'une entrée de la tension de sortie délivrée au côté secondaire du transformateur conformément à la commutation. [PT BR112017013961A2]: a presente invenção diz respeito a um aparelho de controle de potência para submódulos em um conversor multinível modular (mmc), que controla o fornecimento de energia para os submódulos em um mmc conectado a um sistema hvdc e a um statcom. o aparelho de controle de potência inclui uma unidade de circuito em meia ponte para comutação de múltiplos comutadores; um transformador para transferir a baixa tensão de saída (lado primário); um conversor dc/dc para converter uma tensão de saída no lado secundário do transformador; um fotoacoplador para emitir um sinal de referência correspondente a uma magnitude da tensão de saída do lado secundário do transformador; uma unidade de controle modulação por largura de pulso (pwm) e unidade de circuito de partida para fornecer uma tensão de partida inicial para a unidade de controle pwm, em que a unidade de controle pwm é iniciada em resposta à tensão de partida inicialmente fornecida pela unidade de circuito de partida e é configurada para controlar a comutação dos comutadores e para receber a tensão de saída do lado secundário do transformador. | EP3242387B1 | 2017-11-08 2018-05-30 2021-09-22 | EP15875646A | 2015-12-28 2015-12-28 2015-12-28 | KR20140192745A, 2014-12-29 KR2015014360W, 2015-12-28 KR20140192745A, 2014-12-29 KR2015014360W, 2015-12-28 KR20140192745A, 2014-12-29 KR2015014360W, 2015-12-28 | WO2016108552A1: 2016-07-07 KR101711948B1: 2017-03-03 EP3242387B1: 2021-09-22 US9917522B2: 2018-03-13 BR112017013961A2: 2018-02-20 | HYOSUNG CORP 주식회사 효성 HYOSUNG HEAVY IND CORP | KIM JUNE SUNG JUNG HONG JU PARK JUNG SOO LEE DOO YOUNG CHOI JONG YUN KIM JUNE-SUNG JUNG HONG-JU PARK JUNG-SOO LEE DOO-YOUNG CHOI JONG-YUN DOO YOUNG LEE HONG JU JUNG JONG YUN CHOI JUNE SUNG KIM JUNG SOO PARK | H02M7/19: I H02J1/00: I H02M7/483: I H02M1/08: I H02M3/335: I H02M7/49: I H02J1/10: I H02M3/24: I H02M5/42: I H02M7/44: I H02M7/68: I | H02M7/49: I H02M1/0006: A H02M7/4835: A G05F1/46: I H02J1/00: I H02M3/00: I H02M7/19: I H02M1/08: I H02M3/33523: I H02M3/3353: I | WO2014091801A1 US2012212981A1 JP2011114920A JP2013255422A KR20140087450A EP2765696A1 JP2014180110A JPH0777513B2 US8885363B2 DE19744548A1 US2007041227A1 US2010290257A1 US2013208519A1 US5638263A US6246592B1 US8305775B2 US8385086B2 US2011157920A1 US2012250360A1 US2013279211A1 | CN106655850A CN106655850 106655850 US10673353B2 US10673353 10673353 CN108306318A CN108306318 108306318 KR20200016431A KR20200016431 1020200016431 KR10-2020-0016431A KR1020200016431A KR20180075340A KR20180075340 1020180075340 KR1020180075340A KR10-2018-0075340A KR20200084121A KR20200084121 1020200084121 KR10-2020-0084121A KR1020200084121A KR20190080628A KR20190080628 1020190080628 KR1020190080628A KR10-2019-0080628A CN108365625A CN108365625 108365625 | [KO KR101711948B1]: 1개 이상의 상모듈(phase module)을 포함하는 모듈러 멀티레벨 컨버터(MMC)에서 상기 상모듈을 구성하는 다수의 서브모듈(submodule)의 동작을 위한 전원공급을 제어하기 위한 MMC 컨버터의 서브모듈용 전원제어장치에 있어서, 다수의 스위치를 스위칭하여 MMC 컨버터의 P-N 모선의 입력전압을 상대적으로 낮은 저전압으로 변환하여 출력하는 하프브릿지 회로부; 상기 하프브릿지 회로부의 상기 스위치의 스위칭을 통해 출력되는 저전압의 출력전압(1차측)을 2차측으로 전달하는 트랜스포머; 상기 트랜스포머의 2차측 출력전압을 변환하는 DC/DC 컨버터; 상기 트랜스포머의 2차측 출력전압의 크기에 대응하는 기준신호를 출력하는 포토커플러; 상기 포토커플러의 기준신호에 따라 상기 하프브릿지 회로부 내의 상기 스위치에 대한 스위칭을 제어하는 PWM 제어부; 및 상기 PWM 제어부로 초기 기동전압을 공급하는 기동회로부; 를 포함하고, 상기 기동회로부는 상기 입력전압에 의한 전류를 도통 및 차단하는 B접점 스위치와, 상기 B접점 스위치에 직렬로 연결되어 전류의 크기를 제한하는 저항와, 상기 저항에 직렬로 연결되어 기설정된 전압보다 큰 전압이 걸리면 상기 전류를 도통시키는 전압강하 다이오드와, 상기 전압강하 다이오드에 직렬로 연결되어 상기 PWM 제어부로 일정한 전압이 인가되도록 하는 제너다이오드를 포함하며, 상기 B접점 스위치는 초기에 단락상태를 유지하고 상기 트랜스포머의 2차측에 출력되는 전압에 의해 개방되고, 상기 전압강하 다이오드는 상기 P-N 모선의 입력전압이 기설정된 PWM 제어부의 기동전압보다 작으면 전류를 차단하고 크면 전류를 상기 PWM 제어부로 도통시키며, 상기 PWM 제어부는 상기 기동회로부로부터 공급된 기동전압에 의해 기동되어 상기 포토커플러로부터 수신된 상기 기준신호에 따라 상기 스위치의 스위칭을 제어하고 상기 스위칭에 따라 상기 트랜스포머의 2차측에 출력되는 출력전압을 동작전압으로 입력받아 동작하는 MMC 컨버터의 서브모듈용 전원제어장치. 제1항에 있어서, 상기 입력전압은 0V부터 기설정된 최대전압(Vmax)까지 증가함을 특징으로 하는 MMC 컨버터의 서브모듈용 전원제어장치. 제2항에 있어서, 상기 기동회로부는 초기에 상기 입력전압이 증가하여 상기 PWM 제어부의 기설정된 기동전압에 도달하면 상기 PWM 제어부로 상기 기동전압을 제공하고 상기 트랜스포머의 2차측 출력전압이 기설정된 전압으로 정상 출력되면 상기 2차측 출력전압을 제공받아 상기 PWM제어부로의 전원공급을 차단하는 MMC 컨버터의 서브모듈용 전원제어장치. 삭제 제1항에 있어서, 상기 B접점 스위치는 상기 입력전압이 상기 기설정된 기동전압에 도달하기 전까지는 단락(short) 상태를 유지하고, 상기 트랜스포머의 2차측 출력전압이 인가되면 개방(open) 상태로 전환되는 MMC 컨버터의 서브모듈용 전원제어장치.. 삭제 제1항에 있어서, 상기 PWM제어부는 상기 2차측 출력전압 및 출력전류를 이용하여 상기 스위치의 스위칭 듀티비(duty ratio)를 연산하고 상기 연산된 스위칭 듀티비에 따라 상기 스위치의 스위칭 펄스폭을 가변하는 MMC 컨버터의 서브모듈용 전원제어장치. [EN EP3242387B1]: A power control apparatus (100) arranged to supply power to sub-modules (10) of a Modular Multilevel Converter, MMC the power control apparatus comprising: a half-bridge circuit unit (110), comprising multiple switches (113, 114) and capacitors (111, 112) connected to form the half-bridge circuit unit (110), the half-bridge circuit unit being connected to the P and N buses of the MMC and arranged to convert a voltage across these P and N buses into a relatively lower voltage and to output the lower voltage;a transformer (120) arranged to transfer the lower voltage, which is output from the half bridge circuit unit (110), from a primary side to a secondary side of the transformer, and to output an output voltage;a DC/DC converter (130) arranged to receive a voltage corresponding to the output voltage which is output from the secondary side of the transformer, to convert the received voltage into a voltage required for the operation of the sub-module, and to output a converted voltage to the sub-module;a photocoupler (140) arranged to output a reference signal corresponding to a magnitude of the secondary side output voltage of the transformer;a Pulse Width Modulation (PWM) control unit (150) arranged to control switching of the switches (113, 114) of the half-bridge circuit unit (110) in response to the reference signal output from the photocoupler (140); anda starting circuit unit (160) arranged to supply an initial starting voltage to the PWM control unit,wherein the PWM control unit (150) is arranged to start in response to the starting voltage initially supplied from the starting circuit unit (160), and is configured to receive the voltage corresponding to the output voltage which is output from the secondary side of the transformer as an operating voltage. The power control apparatus (100) of claim 1, wherein the input voltage increases from 0 V to a preset maximum voltage (Vmax). The power control apparatus (100) of claim 2, wherein the starting circuit unit (160) is configured to, when the input voltage initially increases and reaches a preset starting voltage of the PWM control unit (150), supply the starting voltage to the PWM control unit (150), and when the secondary side output voltage of the transformer (120) is normally output as a preset voltage, receive the secondary side output voltage and block a supply of power to the PWM control unit (150). The power control apparatus (100) of claim 3, wherein the starting circuit unit (160) comprises: a B contact switch (161) configured to allow current corresponding to the input voltage to flow therethrough or to block the flow of the current;a resistor (162) connected in series with the B contact switch (161) and configured to limit a magnitude of the current;a voltage-drop diode (163) connected in series with the resistor (162) and configured to, when a voltage higher than the preset voltage is induced, allow the current to flow through the voltage-drop diode (163); anda Zener diode (164) connected in series with the voltage-drop diode (163) and configured to apply a constant voltage to the PWM control unit (150). The power control apparatus (100) of claim 4, wherein the B contact switch (161) is maintained in a shorted state until the input voltage reaches the preset starting voltage, and is switched to an opened state when the secondary side output voltage of the transformer (120) is applied. The power control apparatus (100) of claim 1, further comprising a current-limiting circuit for preventing current equal to or higher than a preset reference current from being applied to the half-bridge circuit unit (110). The power control apparatus (100) of claim 1, wherein the PWM control unit (150) calculates a switching duty ratio of the switches using the secondary side output voltage and an output current and varies a width of a switching pulse for the switches (113, 114) depending on the calculated switching duty ratio. [DE EP3242387B1]: Leistungsregelungsvorrichtung (100), die eingerichtet ist, um Untermodulen (10) eines modularen Mehrstufenumrichters, MMC, Leistung zuzuführen, wobei die Leistungssteuerungsvorrichtung aufweist: eine Halbbrückenschaltungseinheit (110), aufweisend mehrere Schalter (113, 114) und Kondensatoren (111, 112), die verbunden sind, um die Halbbrückenschaltungseinheit (110) auszubilden, wobei die Halbbrückenschaltungseinheit mit den P- und N-Bussen des MMC verbunden ist und eingerichtet ist, um eine Spannung über diesen P- und N-Bussen in eine relativ niedrigere Spannung umzuwandeln und die niedrigere Spannung auszugeben,einen Transformator (120), der eingerichtet ist, um die niedrigere Spannung, die von der Halbbrückenschaltungseinheit (110) ausgegeben wird, von einer Primärseite zu einer Sekundärseite des Transformators zu übertragen und eine Ausgangsspannung auszugeben,einen DC/DC-Wandler (130), der eingerichtet ist, um eine Spannung zu empfangen, die der Ausgangsspannung entspricht, die von der Sekundärseite des Transformators ausgegeben wird, die empfangene Spannung in eine Spannung umzuwandeln, die für den Betrieb des Untermoduls erforderlich ist, und eine umgewandelte Spannung an das Untermodul auszugeben,einen Optokoppler (140), der eingerichtet ist, um ein Referenzsignal auszugeben, das einer Größe der Sekundärseiten-Ausgangsspannung des Transformators entspricht,eine Pulsweitenmodulations- (PWM) -Steuereinheit (150), die eingerichtet ist, um ein Schalten der Schalter (113, 114) der Halbbrückenschaltungseinheit (110) als Reaktion auf das von dem Optokoppler (140) ausgegebene Referenzsignal zu steuern, undeine Startschaltungseinheit (160), die eingerichtet ist, eine Anfangsstartspannung an die PWM-Steuereinheit zuzuführen,wobei die PWM-Steuereinheit (150) eingerichtet ist, um als Reaktion auf die anfänglich von der Startschaltungseinheit (160) zugeführte Startspannung zu starten, und konfiguriert ist, um die Spannung, die der Ausgangsspannung entspricht, die von der Sekundärseite des Transformators ausgegeben wird, als eine Betriebsspannung zu empfangen. Leistungsregelungsvorrichtung (100) gemäß Anspruch 1, wobei die Eingangsspannung von 0 V auf eine voreingestellte Maximalspannung (Vmax) ansteigt. Leistungsregelungsvorrichtung (100) gemäß Anspruch 2, wobei die Startschaltungseinheit (160) konfiguriert ist, um, wenn die Eingangsspannung anfänglich ansteigt und eine voreingestellte Startspannung der PWM-Steuereinheit (150) erreicht, die Startspannung an die PWM-Steuereinheit (150) zuzuführen, und wenn die Sekundärseiten-Ausgangsspannung des Transformators (120) normal als eine voreingestellte Spannung ausgegeben wird, die Sekundärseiten-Ausgangsspannung zu empfangen und eine Stromversorgung der PWM-Steuereinheit (150) zu blockieren. Leistungsregelungsvorrichtung (100) gemäß Anspruch 3, wobei die Startschaltungseinheit (160) aufweist: einen B-Kontaktschalter (161), der konfiguriert ist, um zu ermöglichen, dass der Eingangsspannung entsprechender Strom durch diesen hindurchfließt, oder um den Stromfluss zu blockieren,einen Widerstand (162), der in Reihe mit dem B-Kontaktschalter (161) geschaltet und konfiguriert ist, um eine Größe des Stroms zu begrenzen, undeine Spannungsabfalldiode (163), die mit dem Widerstand (162) in Reihe geschaltet und konfiguriert ist, um, wenn eine höhere Spannung als die voreingestellte Spannung induziert wird, zu ermöglichen, dass der Strom durch die Spannungsabfalldiode (163) fließt, undeine Zenerdiode (164), die mit der Spannungsabfalldiode (163) in Reihe geschaltet und konfiguriert ist, um eine konstante Spannung an die PWM-Steuereinheit (150) anzulegen. Leistungsregelungsvorrichtung (100) gemäß Anspruch 4, wobei der B-Kontaktschalter (161) in einem Kurzschlusszustand gehalten wird, bis die Eingangsspannung die voreingestellte Startspannung erreicht, und in einen offenen Zustand geschaltet wird, wenn die Sekundärseiten-Ausgangsspannung des Transformators (120) angelegt wird. Leistungsregelungsvorrichtung (100) gemäß Anspruch 1, ferner aufweisend eine Strombegrenzungsschaltung, um zu verhindern, dass Strom, der größer oder gleich einem voreingestellten Referenzstrom ist, an die Halbbrückenschaltungseinheit (110) angelegt wird. Leistungsregelungsvorrichtung (100) gemäß Anspruch 1, wobei die PWM-Steuereinheit (150) ein Schalttastverhältnis der Schalter mittels der Sekundärseiten-Ausgangsspannung und eines Ausgangsstroms berechnet und eine Weite eines Schaltimpulses für die Schalter (113, 114) in Abhängigkeit von dem berechneten Schalttastverhältnis variiert. [FR EP3242387B1]: Appareil de commande électrique (100) conçu pour alimenter des sous-modules (10) d'un Convertisseur Multiniveau Modulaire, MMC, l'appareil de commande électrique comprenant : une unité de circuit en demi-pont (110), comprenant de multiples commutateurs (113, 114) et des condensateurs (111, 112) connectés pour former l'unité de circuit en demi-pont (110), l'unité de circuit en demi-pont étant connectée aux bus P et N du MMC et étant conçue pour convertir une tension à travers ces bus P et N en une tension relativement inférieure et émettre la tension inférieure ;un transformateur (120) conçu pour transférer la tension inférieure, qui est émise depuis l'unité de circuit en demi-pont (110), d'un côté primaire à un côté secondaire du transformateur, et pour émettre une tension de sortie ;un convertisseur CC/CC (130) conçu pour recevoir une tension correspondant à la tension de sortie qui est émise depuis le côté secondaire du transformateur, pour convertir la tension reçue en une tension requise pour le fonctionnement du sous-module, et pour émettre une tension convertie dans le sous-module ;un photocoupleur (140) agencé pour émettre un signal de référence correspondant à une amplitude de la tension de sortie du côté secondaire du transformateur ;une unité de commande de Modulation de Largeur d'Impulsion (PWM) (150) conçue pour commander la commutation des commutateurs (113, 114) de l'unité de circuit en demi-pont (110) en réponse à la sortie du signal de référence provenant du photocoupleur (140) ; etune unité de circuit de démarrage (160) conçue pour fournir une tension de démarrage initiale à l'unité de commande PWM,dans lequel l'unité de commande PWM (150) est conçue pour démarrer en réponse à la tension de démarrage initialement fournie par l'unité de circuit de démarrage (160), et est configurée pour recevoir la tension correspondant à la tension de sortie qui est émise depuis le côté secondaire du transformateur comme une tension de fonctionnement. Appareil de commande électrique (100) selon la revendication 1, dans lequel la tension d'entrée augmente de 0 V à une tension maximale préétablie (Vmax). Appareil de commande électrique (100) selon la revendication 2, dans lequel l'unité de circuit de démarrage (160) est configurée, lorsque la tension d'entrée augmente initialement et atteint une tension de démarrage préétablie de l'unité de commande PWM (150), pour fournir la tension de démarrage à l'unité de commande PWM (150) et quand la tension de sortie du côté secondaire du transformateur (120) est normalement émise comme une tension préétablie, recevoir la tension de sortie du côté secondaire et bloquer une alimentation électrique à l'unité de commande PWM (150). Appareil de commande électrique (100) selon la revendication 3, dans lequel l'unité de circuit de démarrage (160) comprend : un commutateur de contact B (161) configuré pour permettre au courant correspondant à la tension d'entrée de s'écouler à travers lui ou pour bloquer le flux du courant ;une résistance (162) raccordée en série avec le commutateur de contact B (161) et configurée pour limiter une amplitude du courant ;une diode à chute de tension (163) branchée en série à la résistance (162) et configurée, lorsqu'une tension supérieure à la tension préétablie est induite, pour permettre au courant de s'écouler à travers la diode à chute de tension (163) ; etune diode Zener (164) branchée en série à la diode à chute de tension (163) et configurée pour appliquer une tension constante à l'unité de commande PWM (150) . Appareil de commande électrique (100) selon la revendication 4, dans lequel le commutateur de contact B (161) est maintenu dans un état de court-circuit jusqu'à ce que la tension d'entrée atteigne la tension de démarrage préétablie, et est commuté vers un état ouvert quand la tension de sortie du côté secondaire du transformateur (120) est appliquée. Appareil de commande électrique (100) selon la revendication 1, comprenant en outre un circuit limiteur de courant pour empêcher un courant égal ou supérieur à un courant de référence préétabli d'être appliqué à l'unité de circuit en demi-pont (110). Appareil de commande électrique (100) selon la revendication 1, dans lequel l'unité de commande PWM (150) calcule un rapport cyclique de commutation des commutateurs en utilisant la tension de sortie du côté secondaire et un courant de sortie et varie une largeur d'une impulsion de commutation pour les commutateurs (113, 114) en fonction du rapport cyclique de commutation calculé. | [KO KR101711948B1]: ＭＭＣ 컨버터의 서브모듈용 전원제어장치{POWER CONTROL DEVICE FOR SUB-MODULE OF MMC CONVERTER} 본 발명은 전원제어장치에 관한 것으로서, 특히 고전전 직류송전(HVDC)시스템 및 정지형 동기보상기(STATCOM)과 연계된 모듈러 멀티레벨 컨버터(MMC:Modular Multilevel Converter)의 서브모듈(sub-module)에 안정적인 전원공급을 제어하도록 하는 MMC 컨버터의 서브모듈용 전원제어장치에 관한 것이다. 일반적으로, 초고압 직류송전(HVDC:High Voltage Direct Current) 시스템에서는 발전소에서 생산되는 교류전력을 직류로 변환시켜 송전하고 수전단에서 교류로 재변환하여 부하에 전력을 공급하도록 한다. 이러한 HVDC 시스템은 전압승압을 통하여 효율적이고 경제적인 전력전송이 가능하고 이종계통 연계, 장거리 고효율 송전 등의 장점을 갖는다. 또한, 정지형 동기 보상기(STATCOM:Static Synchronous Compensator)은 FACTS(Flexible AC Transmission System) 기기 중 하나의 부류로 전력계통에 연결되어 전력전송 용량을 증대시키고 기존 설비의 이용률을 극대화하기 위해 사용되는 전력전자 기반의 보상기기를 말한다. 이러한 STATCOM 시스템은 전압형 전력반도체를 사용하여 계통을 병렬로 보상함으로써 전압을 일정하게 유지시켜 계통을 안정화시키는 장점을 갖는다. HVDC 또는 STATCOM 시스템에는 MMC 컨버터가 연계될 수 있다. 이러한 MMC 컨버터에는 다수의 서브모듈(sub-module)이 직렬로 연결된다. MMC 컨버터에서 서브모듈은 매우 중요한 구성요소 중 하나이다. 따라서 다양한 환경에서도 서브모듈이 정상적으로 동작하도록 하기 위해 서브모듈에 안정적인 전원을 공급하는 것이 요구된다. 또한, MMC 컨버터에서 서브모듈은 전압을 변환하고 전력전송을 위한 전류의 통로가 된다. 이러한 서브모듈의 동작시 발생하는 손실은 서브모듈의 효율적인 동작에 악영향을 미치므로 이를 최소화하기 위한 노력이 계속되고 있다. 도 1에는 MMC 컨버터의 등가회로도이고, 도 2는 종래의 MMC 컨버터의 서브모듈용 전원제어장치의 회로도이다. 주지된 바와 같이 MMC 컨버터는 1개 이상의 상모듈(phase module)(1)로 구성되고 각 상모듈(1)은 다수의 서브모듈(10)이 직렬로 연결된다. 또한, 각 상모듈(1)은 직류전압측을 정(+) 및 부(-)의 직류전압 모선 P 및 N에 각각 접속시킨다. 이들 직류전압 P-N 모선의 사이에는 고전압의 직류전압이 존재한다. 각각의 서브모듈(10)은 두 개의 접속단자(X1,X2)가 형성된다. 종래에 MMC 컨버터의 서브모듈용 전원제어장치(20)는 서브모듈의 동작에 필요한 전원을 공급하기 위해 P-N 모선의 고전압(약 2~3㎸)을 저전압(약 300~400V)로 변환하도록 한다. 이때, HVDC 시스템의 특성상 고신뢰성을 유지하기 위해 저항(R)과 제너다이오드(Z)의 결합을 사용한다. 예컨대, P-N 모선 사이에 직렬로 연결된 다수의 저항(R1~R3) 중 특정 저항(R1,R2)을 활용하여 전류를 제한시키고 제너다이오드(Z)를 이용하여 저전압으로 변환하도록 한다. 하지만, 이러한 종래의 전원제어장치(20)는 전류제한을 위한 저항(R1,R2)에 발열로 인한 손실이 발생하는 문제점이 있고 이러한 발열은 소자의 신뢰성에 매우 밀접한 관련이 있어 전원제어장치 전체의 동작에 악영향을 미칠 수 있다. 이에, 발열을 방지하기 위한 방열판을 별도로 취부해야 하는 번거로움이 있다. 또한, HVDC 시스템과 연계되는 MMC 컨버터의 서브모듈은 입력전압이 매우 넓은 범위(0~3㎸)의 전압을 수용하게 되며, 이를 조합하여 MMC 컨버터를 구동시켜야 하므로 일반적으로 800V 이하에서 서브모듈의 전원이 모두 정상적으로 공급되어야 한다. 이러한 사유로 800V 영역에서 제어전원의 출력을 정상적으로 이루어지도록 전류제한 저항(R1,R2)을 선정하고 입력전압을 3㎸까지 올리게 되면 저항(R1,R2)에 큰 전류가 흐르게 되며, 이로 인해 손실이 증가되고 발열을 일으키는 원인이 된다. 이와 동시에 증가된 대부분의 전류가 제너다이오드(Z)로 유입되어 제어다이오드(Z)의 높은 발열을 유발하여 신뢰성에 매우 큰 영향을 미치게 된다. 그 이유는 일반적으로 R3의 선로저항값보다 제너다이오드(Z)의 저항값이 상대적으로 적기 때문이다. 전류제한용 저항(R1,R2)의 경우 방열판을 이용하여 방열이 원활히 이루어질 수 있지만, 제너다이오드(Z)의 경우는 방열판 등을 취부하는 것이 부피확장 등의 이유로 어려움이 발생하는 문제점이 있다. 따라서 해당 기술분야에서는 HVDC 시스템과 연계되는 MMC 컨버터의 서브모듈에서 추가적인 소자의 설치 없이 전류제한 저항에 손실을 최소화하도록 하면서 안정적인 전원제어가 가능하도록 하는 전원제어장치의 기술개발이 요구되고 있다. 본 발명은 HVDC 및 STATCOM과 연계되는 MMC 컨버터에서 고전압을 저전압으로 변환하여 MMC 컨버터의 서브모듈에 공급할 때 내부의 소자에 발열을 방지하고 손실을 최소화하도록 하는 MMC 컨버터의 서브모듈용 전원제어장치를 제공하는데 그 목적이 있다. 본 발명에 따른 MMC 컨버터의 서브모듈용 전원제어장치는, 1개 이상의 상모듈(phase module)을 포함하는 모듈러 멀티레벨 컨버터(MMC)에서 상기 상모듈을 구성하는 다수의 서브모듈(submodule)의 동작을 위한 전원공급을 제어하기 위한 MMC 컨버터의 서브모듈용 전원제어장치에 있어서, 다수의 스위치를 스위칭하여 MMC 컨버터의 P-N 모선의 입력전압을 상대적으로 낮은 저전압으로 변환하여 출력하는 하프브릿지 회로부; 상기 하프브릿지 회로부의 상기 스위치의 스위칭을 통해 출력되는 저전압의 출력전압(1차측)을 2차측으로 전달하는 트랜스포머; 상기 트랜스포머의 2차측 출력전압을 변환하는 DC/DC 컨버터; 상기 트랜스포머의 2차측 출력전압의 크기에 대응하는 기준신호를 출력하는 포토커플러; 상기 포토커플러의 기준신호에 따라 상기 하프브릿지 회로부 내의 상기 스위치에 대한 스위칭을 제어하는 PWM 제어부; 및 상기 PWM 제어부로 초기 기동전압을 공급하는 기동회로부; 를 포함하고, 상기 기동회로부는 상기 입력전압에 의한 전류를 도통 및 차단하는 B접점 스위치와, 상기 B접점 스위치에 직렬로 연결되어 전류의 크기를 제한하는 저항와, 상기 저항에 직렬로 연결되어 기설정된 전압보다 큰 전압이 걸리면 상기 전류를 도통시키는 전압강하 다이오드와, 상기 전압강하 다이오드에 직렬로 연결되어 상기 PWM 제어부로 일정한 전압이 인가되도록 하는 제너다이오드를 포함하며, 상기 B접점 스위치는 초기에 단락상태를 유지하고 상기 트랜스포머의 2차측에 출력되는 전압에 의해 개방되고, 상기 전압강하 다이오드는 상기 P-N 모선의 입력전압이 기설정된 PWM 제어부의 기동전압보다 작으면 전류를 차단하고 크면 전류를 상기 PWM 제어부로 도통시키며, 상기 PWM 제어부는 상기 기동회로부로부터 공급된 기동전압에 의해 기동되어 상기 포토커플러로부터 수신된 상기 기준신호에 따라 상기 스위치의 스위칭을 제어하고 상기 스위칭에 따라 상기 트랜스포머의 2차측에 출력되는 출력전압을 동작전압으로 입력받아 동작한다. 본 발명에서, 상기 입력전압은 0V부터 기설정된 최대전압(Vmax)까지 증가한다. 본 발명에서, 상기 기동회로부는 초기에 상기 입력전압이 증가하여 상기 PWM 제어부의 기설정된 기동전압에 도달하면 상기 PWM 제어부로 상기 기동전압을 제공하고 상기 트랜스포머의 2차측 출력전압이 기설정된 전압으로 정상 출력되면 상기 2차측 출력전압을 제공받아 상기 PWM제어부로의 전원공급을 차단한다. 삭제 본 발명에서, 상기 B접점 스위치는 상기 입력전압이 상기 기설정된 기동전압에 도달하기 전까지는 단락(short) 상태를 유지하고, 상기 트랜스포머의 2차측 출력전압이 인가되면 개방(open) 상태로 전환된다. 삭제 본 발명에서, 상기 PWM제어부는 상기 2차측 출력전압 및 출력전류를 이용하여 상기 스위치의 스위칭 듀티비(duty ratio)를 연산하고 상기 연산된 스위칭 듀티비에 따라 상기 스위치의 스위칭 펄스폭을 가변한다. 본 발명에 의하면 MMC 컨버터의 서브모듈용 전원제어장치 내부의 각종 소자에서 발생하는 손실을 최소화할 수 있고, 발열을 방지하므로 방열판 등과 같은 별도의 장치를 취부할 필요가 없다. 또한, 본 발명에 의하면 종래의 전원제어장치가 800V에서 제어전원을 출력할 수 있는데 반해, 500~700V에서도 제어전원을 출력할 수 있다. 또한, 본 발명에 의하면 분압저항과 제너다이오드를 이용한 종래의 전원제어장치보다 훨씬 높은 효율을 유지할 수 있다. 도 1은 일반적인 MMC 컨버터의 등가회로도, 도 2는 종래의 MMC 컨버터의 서브모듈용 전원제어장치의 회로도, 도 3은 본 발명의 실시 예에 따른 MMC 컨버터의 서브모듈용 전원제어장치의 구성도, 도 4 내지 도 7은 본 발명의 실시 예에 따른 전원제어장치(100)의 동작에 따른 전류흐름의 예시도. 이하, 본 발명의 일부 실시 예들을 예시적인 도면을 통해 상세히 설명한다. 각 도면의 구성요소들에 참조부호를 부가함에 있어서, 동일한 구성요소들에 대해서는 비록 다른 도면상에 표시되더라도 가능한 한 동일한 부호를 가지도록 하고 있음에 유의해야 한다. 또한, 본 발명의 실시 예를 설명함에 있어, 관련된 공지 구성 또는 기능에 대한 구체적인 설명이 본 발명의 실시 예에 대한 이해를 방해한다고 판단되는 경우에는 그 상세한 설명은 생략한다. 또한, 본 발명의 실시 예의 구성요소를 설명하는 데 있어서, 제 1, 제 2, A, B, (a), (b) 등의 용어를 사용할 수 있다. 이러한 용어는 그 구성요소를 다른 구성 요소와 구별하기 위한 것일 뿐, 그 용어에 의해 해당 구성요소의 본질이나 차례 또는 순서 등이 한정되지 않는다. 어떤 구성요소가 다른 구성요소에 "연결", "결합" 또는 "접속"된다고 기재된 경우, 그 구성요소는 그 다른 구성요소에 직접적으로 연결되거나 접속될 수 있지만, 각 구성요소 사이에 또 다른 구성요소가 "연결", "결합" 또는 "접속"될 수도 있다고 이해되어야 할 것이다. 도 3은 본 발명의 실시 예에 따른 MMC 컨버터의 서브모듈용 전원제어장치의 회로도이다. 도 3을 참조하면, 본 발명의 실시 예에 따른 MMC 컨버터의 서브모듈용 전원제어장치(100)는 1개 이상의 상모듈(phase module)을 포함하는 MMC 컨버터에 적용된다. 구체적으로, MMC 컨버터의 상모듈을 구성하는 다수의 서브모듈에 전원을 공급한다. 이를 위하여 본 발명의 전원제어장치(100)는 각 상모듈이 접속된 정(+) 및 부(-)의 P 모선과 N 모선 사이에 걸리는 고전압을 입력받아 서브모듈의 동작에 필요한 저전압으로 변환하여 공급하도록 한다. 이러한 MMC 컨버터는 HVDC 시스템 및 STATCOM에 연계된다. 본 발명의 실시 예에 따른 전원제어장치(100)는 하프브릿지회로부(110), 트랜스포머(120), DC/DC컨버터(130), 포토커플러(140), PWM제어부(150) 및 기동회로부(160)를 포함하여 구성된다. 하프브릿지회로부(110)는 MMC 컨버터의 P-N 모선의 입력전압을 공급받아 상대적으로 낮은 1/2의 전압크기에서 스위칭할 수 있다. 하프브릿지회로부(110)는 P-N 모선 간에 연결된 제1커패시터(111)와, 제1커패시터(111)에 직렬로 연결된 제2커패시터(112)를 포함하고 상기 제1 및 제2 커패시터(111,112)의 직렬연결에 병렬로 연결된 제1스위치(113) 및 제2스위치(114)의 직렬연결을 포함한다. 상기 제1,2커패시터(111,112)의 중성점과 제1,2스위치(113,114)의 중성점은 트랜스포머(120)의 1차측에 각각 연결되며 제1,2스위치(113,114)의 스위칭에 따라 각 중성점에서의 전압이 1차측으로 입력된다. 이들 제1,2스위치(113,114)의 스위칭은 후술하는 PWM제어부(150)에 의해 제어된다. 본 발명의 하프브릿지회로부(110)는 바람직하게는 P-N 모선의 입력전압을 제공받아 그 입력전압의 1/2로 변환하여 출력한다. 트랜스포머(120)는 하프브릿지회로부(110)로부터 출력된 1차측 전압을 2차측으로 전달한다. 이러한 2차측 출력전압은 트랜스포머(120)의 내부 권선비에 의해 결정된다. 바람직하게는 1차측 전압보다 더 낮은 저전압으로 출력된다. DC/DC컨버터(130)는 트랜스포머(120)의 2차측 출력전압을 서브모듈에 필요한 전압으로 변환한다. 이로써 서브모듈에 공급되는 전압은 P-N 모선의 고전압의 입력전압을 하프브릿지회로부(110)에서 저전압으로 변환한 후 트랜스포머(120)를 통해 더 낮은 저전압으로 변환되는 것이다. 포토커플러(140)는 트랜스포머(120)의 2차측에서 출력되는 전압을 검출한다. 이러한 포토커플러(140)는 트랜스포머(120)의 1차측과 2차측이 전기적으로 절연되어 있으므로 트랜스포머(120)의 2차측의 출력전압에 의한 전류가 발광부로 공급되어 빛을 발광하고 이에 대하여 수광부에서는 발광부로부터의 빛을 수광하여 2차측 전압에 대응하는 기준신호를 출력한다. 이와 같이 포토커플러(140)는 2차측 출력전압에 대응하는 기준신호를 후술하는 PWM제어부(150)로 제공한다. 이로써, PWM제어부(150)는 해당 기준신호를 이용하여 하프브릿지 회로부(110)를 동작시킨다. PWM제어부(150)는 하프브릿지 회로부(110)의 스위치(113,114)의 스위칭을 제어한다. 이때, PWM제어부(150)는 포토커플러(140)로부터 제공된 2차측 출력전압에 대응하는 기준신호를 이용하여 다수의 스위치(113,114)에 대한 온(on)/오프(off)의 듀티비(duty ratio)를 연산하고 그 연산된 스위칭 듀티비에 따라 스위치(113,114)의 스위칭 펄스폭을 가변하도록 한다. 특히, 본 실시 예에서 PWM제어부(150)는 초기에 후술하는 기동회로부(160)로부터 공급된 기동전압에 의해 기동되고, 이에 따라 PWM제어부(150)는 하프브릿지 회로부(110)의 제1 및 제2 스위치(113,114)의 스위칭을 제어한다. 이러한 스위칭에 따라 하프브릿지 회로부(110)를 통해 입력전압의 1/2만큼의 전압이 트랜스포머(120)의 1차측으로 공급되며 2차측에 상대적으로 낮은 저전압이 출력된다. 이때, 이러한 트랜스포머(120)의 2차측에서 출력되는 저전압을 동작전압으로 공급받는다. 이와 같이, PWM제어부(150)는 초기에 기동할 때는 기동회로부(160)로부터 기동전압을 공급받고, 기동된 이후에 트랜스포머(120)의 2차측에 전압이 입력되면 그 입력된 2차측 출력전압을 동작전원으로 사용하는 것이다. 이때, PWM제어부(150)는 트랜스포머(120)의 2차측 출력전압을 동작전원으로 사용하기 위해서는 바람직하게는 2차측 출력전압이 기설정된 전압으로 정상 출력되어야 한다. 즉, 동작전원으로 사용하기 위해서는 일정한 크기 이상의 전압이 필요한데 2차측 출력전압이 그 설정된 전압 크기 이상으로 정상적으로 출력되는 경우에 그 2차측 출력전압을 PWM제어부(150)의 동작전원으로 사용하는 것이다. 기동회로부(160)는 PWM제어부(150)에 초기 기동전압을 제공한다. 특히, 본 실시 예에서 기동회로부(160)는 입력전압이 OV부터 증가하여 PWM제어부(150)의 기동전압에 도달하기 전까지는 PWM제어부(150)로 기동전압을 공급하지 않으며, 입력전압이 더 증가하여 기동전압에 도달하면 PWM제어부(150)로 기동전압을 공급하여 PWM제어부(150)가 기동하도록 한다. 이러한 PWM제어부(150)의 기동은 본 발명에 따른 전원제어장치(100)의 기동에 해당된다. 이러한 기동회로부(160)는 B접점 스위치(161), 저항(162), 전압강하 다이오드(163) 및 제너다이오드(164)를 포함하여 구성된다. B접점 스위치(131)는 MMC 컨버터의 P-N 모선의 입력전압에 의해 발생한 전류의 흐름을 제어한다. 즉, B접점 스위치(131)는 초기상태가 닫힌(close)된 상태이므로 선로는 단락(short)이 형성되어 전류를 도통시킨다. 이후 트랜스포머(120)의 2차측 출력전압이 인가되면 개방(open)된 상태가 되어 전류흐름을 차단한다. 저항(162)는 B접점 스위치(161)에 직렬로 연결되어 B접점 스위치(161)를 통해 흐르는 전류의 크기를 제한한다. 전압강하 다이오드(163)은 저항(162)에 직렬로 연결되어 기설정된 전압보다 큰 전압이 걸리면 전류를 도통시킨다. 즉, 전압강하 다이오드(163)는 입력전압이 기설정된 PWM제어부(150)의 기동전압보다 작은 경우에는 전류를 차단하고 기동전압보다 큰 경우에만 전류를 도통시킨다. 이러한 전압강하 다이오드(163)는 예컨대 과도전압억제(TVS:Transient Voltage Suppressor) 다이오드를 포함할 수 있다. 제너다이오드(164)는 전압강하 다이오드(163)에 직렬로 연결되며 전압강하 다이오드(163)를 통해 흐르는 전류에 의해 발생된 클램핑 전압을 PWM제어부(150)로 공급한다. 이러한 제너다이오드(164)는 PWM제어부(150)에 일정한 전압이 인가되도록 하기 위한 것이다. 이와 같이, 본 발명에 따른 기동회로부(160)는 초기에 B접점 스위치(161)가 닫힌(close) 상태이므로 선로는 단락(short)이 형성되어 전류를 도통시킨다. 이때, P-N 모선의 입력전압은 0V부터 기설정된 최대전압(Vmax)까지 증가하게 되는데 0V부터 증가하여 PWM제어부(150)의 기동전압에 도달하기 전까지는 B접점 스위치(161)를 통해 흐르는 전류는 전압강하 다이오드(163)에 의해 차단된다. 즉, 상기한 바와 같이, 전압강하 다이오드(163)는 입력전압이 기동전압 이상인 경우에만 전류를 도통시킨다. 이후에, 입력전압이 계속 증가하여 PWM제어부(150)의 기동전압에 도달하게 되면 전압강하 다이오드(163)가 전류를 도통시켜 제너다이오드(164)의 양단에 클램핑 전압이 인가되고, 이러한 클램핑 전압은 PWM제어부(150)로 인가된다. 이와 같이 인가되는 전압이 바로 PWM제어부(150)의 기동전압이 되는 것이다. 이하에서, 도 4 내지 도 7을 참조하며 본 발명의 실시 예에 따른 MMC 컨버터의 서브모듈용 전원제어장치의 동작을 상세하게 설명한다. 도 4 내지 도 7은 본 발명의 실시 예에 따른 전원제어장치(100)의 동작에 따른 전류흐름의 예시도이다. 도 4의 일례에 도시된 바와 같이, P-N 모선의 입력전압이 0V부터 증가하기 시작한다. 초기에 기동회로부(160)의 B접점 스위치(161)는 단락(shot)된 상태이므로 이러한 입력전압에 의한 전류가 B접점 스위치(161)를 통해 저항(162)를 거쳐 전압강하 다이오드(163)으로 흐르게 된다. 하지만, 전압강하 다이오드(163)는 기설정되 전압 이상이 걸리는 경우에만 전류가 도통하므로, 본 실시 예에서는 전원제어장치(100)의 기동, 즉 PWM제어부(150)의 기동을 위한 기동전압 이상에서만 전류가 도통하는 것으로 설정합으로써 입력전압이 기동전압보다 낮은 저전압 영역에서는 전압강하 다이오드(163)가 전류를 도통하지 않는다. 이로써 도 5에서는 제너다이오드(164)로 전류가 흐르지 않으므로 제너다이오드(164)의 양단의 전압은 0(zero) 전압이 되어 PWM제어부(150)로는 아무런 전압이 인가되지 않는다. 이 경우에는 전원제어장치(100)가 기동하지 않는다. 즉, 입력전압이 0V부터 증가하여 기설정된 기동전압압에 도달하기 전에는 PWM제어부(150)가 기동하지 않으므로 전원제어장치(100)가 기동하지 않는 것이다. 따라서, PWM제어부(150)에 0(zero)전압이 인가되어 하프브릿지회로부(110)의 스위치도 동작시키지 않으므로 트랜스포머(120)의 2차측에도 전압이 출력되지 않는다. 도 5의 일례를 참조하면, 입력전압이 계속 증가하여 PWM제어부(150)을 기동하기 위한 기동전압에 도달하게 되면 전압강하 다이오드(163)은 전류를 도통시키므로 B접점 스위치(161) 및 저항(162)를 통과한 전류는 제너다이오드(164)로 인가되고 제너다이오드(164)의 클램핑 전압이 PWM제어부(1150)에 기동전압으로 인가된다. 이와 같이 PWM제어부(150)에 기동전압이 인가되면 PWM제어부(150)는 하프브릿지 회로부(110)의 스위치(113,114)를 스위칭한다. 도 6의 일례에서는 하프브릿지 회로부(110)의 스위치(113,114)가 동작하면 전류는 전류가 트랜스포머(120)로 흐르게 된다. 이로써 트랜스포머(120)의 1차측에는 하프브릿지 회로부(110)의 출력전압이 인가되고 이는 다시 트랜스포머(120)의 2차측으로 전달된다. 트랜스포머(120)의 2차측에는 권선비에 의해 변환된 전압이 출력된다. 이러한 2차측 출력전압은 DC/DC컨버터(130), PWM제어부(150) 및 기동회로부(160)로 각각 제공된다. 이때, PWM제어부(150)로 공급된 2차측 출력전압은 PWM제어부(150)의 동작전원으로 사용되며, 기동회로부(160)로 공급된 2차측 출력전압에 의해 B접점 스위치(161)가 동작하여 개방(open)으로 전환된다. 도 7의 일례에서는 B접점 스위치(161)가 개방(open)된 상태에서의 전류흐름을 도시한다. B접점 스위치(161)가 개방된 상태에서는 전류가 B접점 스위치(161)에서 차단되기 때문에 PWM제어부(180)로는 더 이상 전압이 인가되지 않으며, 트랜스포머(120)의 2차측 출력전압만이 PWM제어부(150)에 동작전압으로 공급된다. 이에 따라 PWM제어부(150)는 이러한 동작전압을 이용하여 전원제어장치(100)를 동작시키도록 한다. 따라서, 기동회로부(160)는 PWM제어부(150)로 기동전압을 공급하여 PWM제어부(150)를 기동시킨 후 트랜스포머(120)의 2차측에 전압이 출력되면 기동회로부(160)는 동작을 정지한다. 이때, PWM제어부(150)는 기동회로부(160)로부터 더 이상 전압을 공급지 않고 트랜스포머(120)의 2차측 출력전압을 인가받아 동작전원으로 사용하는 것이다. 이상에서 설명한 바와 같이, 본 발명에 따른 MMC 컨버터의 서브모듈용 전원공급장치(100)에서는 입력전압이 PWM제어부(150)를 기동시키기 위한 기동전압 이상인 경우에만 PWM제어부(150)를 기동시키도록 하고 PWM제어부(150)가 기동하여 트랜스포머(120)의 2차측에 정상적인 전압이 출력되는 경우에는 그 2차측 출력전압을 이용하여 PWM제어부(150)의 동작전원으로 사용하도록 한다. 이로써, 종래기술에서 문제점으로 제기된 저항과 제너다이오드에서의 발열 및 손실을 크게 줄일 수 있게 된다. 이상에서, 본 발명의 실시 예를 구성하는 모든 구성 요소들이 하나로 결합하거나 결합하여 동작하는 것으로 설명되었다고 해서, 본 발명이 반드시 이러한 실시 예에 한정되는 것은 아니다. 즉, 본 발명의 목적 범위 안에서라면, 그 모든 구성 요소들이 하나 이상으로 선택적으로 결합하여 동작할 수도 있다. 또한, 이상에서 기재된 "포함하다", "구성하다" 또는 "가지다" 등의 용어는, 특별히 반대되는 기재가 없는 한, 해당 구성 요소가 내재할 수 있음을 의미하는 것이므로, 다른 구성 요소를 제외하는 것이 아니라 다른 구성 요소를 더 포함할 수 있는 것으로 해석되어야 한다. 기술적이거나 과학적인 용어를 포함한 모든 용어들은, 다르게 정의되지 않는 한, 본 발명이 속하는 기술 분야에서 통상의 지식을 가진 자에 의해 일반적으로 이해되는 것과 동일한 의미가 있다. 사전에 정의된 용어와 같이 일반적으로 사용되는 용어들은 관련 기술의 문맥상의 의미와 일치하는 것으로 해석되어야 하며, 본 발명에서 명백하게 정의하지 않는 한, 이상적이거나 과도하게 형식적인 의미로 해석되지 않는다. 이상의 설명은 본 발명의 기술 사상을 예시적으로 설명한 것에 불과한 것으로서, 본 발명이 속하는 기술 분야에서 통상의 지식을 가진 자라면 본 발명의 본질적인 특성에서 벗어나지 않는 범위에서 다양한 수정 및 변형이 가능할 것이다. 따라서, 본 발명에 개시된 실시 예들은 본 발명의 기술 사상을 한정하기 위한 것이 아니라 설명하기 위한 것이고, 이러한 실시 예에 의하여 본 발명의 기술 사상의 범위가 한정되는 것은 아니다. 본 발명의 보호 범위는 아래의 청구범위에 의하여 해석되어야 하며, 그와 동등한 범위 내에 있는 모든 기술 사상은 본 발명의 권리범위에 포함되는 것으로 해석되어야 할 것이다. 110 : 하프브릿지 회로부 120 : 트랜스포머 130 : DC/DC컨버터 140 : 포토커플러 150 : PWM제어부 160 : 기동회로부 161 : B접점 스위치 162 : 저항 163 : 전압강하 다이오드 164 : 제너다이오드 [EN EP3242387B1]: Technical Field The present invention generally relates to a power control apparatus and, more particularly, to a power control apparatus for sub-module of a Modular Multilevel Converter (MMC), which controls the stable supply of power to sub-modules in an MMC connected to a High Voltage Direct Current (HVDC) system and to a Static Synchronous Compensator (STATCOM). Background Art Generally, in High Voltage Direct Current (HVDC) systems, Alternating Current (AC) power produced in a power plant is converted into DC power and the DC power is transmitted, and a power receiving stage re-converts the DC power into AC power and supplies the AC power to a load. Such an HVDC system is advantageous in that power may be efficiently and economically transmitted via voltage boosting, and in that connections between heterogeneous systems and long-distance high-efficiency power transmission are possible. Further, a Static Synchronous Compensator (STATCOM) is a kind of Flexible AC Transmission System (FACTS) device, and denotes an electric power electronics-based compensator, which is connected to a power system and is used to increase power transmission capacity and to maximize the usage of existing facilities. Such a STATCOM system is advantageous in that power systems are compensated in parallel using a voltage-type power semiconductor device, thus stabilizing the systems by maintaining voltage at a constant value. An MMC may be connected to an HVDC or STATCOM system. In such an MMC, multiple sub-modules are connected in series. In the MMC, a sub-module is one of the most important components. Therefore, in order for sub-modules to operate normally in various environments, there is a need to stably supply power to the sub-modules. Further, in the MMC, sub-modules become a current path through which voltage is converted and power is transmitted. Since loss occurring during the operation of sub-modules negatively influences the efficient operation of the sub-modules, efforts to minimize such loss have been continuously made. FIG. 1 is an equivalent circuit diagram of an MMC, and FIG. 2 is a circuit diagram of a conventional power control apparatus for MMC sub-modules. As is well-known to those skilled in the art, an MMC is composed of one or more phase modules 1, and individual sub-modules 10 are connected in series in each phase module 1. Further, DC voltage terminals of each of the phase modules 1 are connected to positive (+) and negative (-) DC voltage buses P and N, respectively. A high DC voltage is present between the DC voltage P and N buses. In each sub-module 10, two connection terminals X1 and X2 are formed. A conventional power control apparatus 20 for MMC sub-modules converts a high voltage (about 2 to 3 kV) on the P and N buses into a low voltage (about 300 to 400 V) so as to supply the power required to operate the sub-modules. Here, in order to maintain high reliability depending on the characteristics of the HVDC system, the coupling of resistors R and a Zener diode Z is used. For example, current is limited using specific resistors R1 and R2, among multiple resistors R1 to R3 connected in series between the P and N buses, and the high voltage is converted into the low voltage using the Zener diode Z. However, the conventional power control apparatus 20 is problematic in that loss occurs due to heat generated in the resistors R1 and R2 for current limiting, and such heat generation may negatively influence the overall operation of the power control apparatus because it is closely related to the reliability of elements. Thus, there is inconvenience in that a heat dissipation plate for preventing heat generation must be separately attached. Further, the sub-modules of the MMC connected to the HVDC system accommodate voltages falling within a very wide range (0 to 3 kV), and must drive the MMC by combining the voltages, and thus the power of the sub-modules must be normally supplied at a voltage of 800 V or less. For this reason, if current-limiting resistors R1 and R2 are selected so that the control power is normally output in a range of 800 V, and the input voltage is increased up to 3 kV, high current flows through the resistors R1 and R2, thus increasing loss and resulting in heat generation. At the same time, most of the increased current flows into the Zener diode Z, so that high heat is generated in the Zener diode Z, thus greatly deteriorating the reliability of the apparatus. The reason for this is that the resistance of the Zener diode Z is lower than the line resistance of the resistor R3. In the case of the current-limiting resistors R1 and R2, heat dissipation may be smoothly performed using a heat dissipation plate, but, in the case of the Zener diode Z, a problem arises in that it is difficult to attach a heat dissipation plate or the like, for the reason of increased volume or the like. Therefore, in the field of this art, there is required the development of technology for a power control apparatus, which enables power control to be stably performed while minimizing the loss of current-limiting resistors without requiring the installation of additional elements in the sub-modules of an MMC connected to an HVDC system. Prior art power supply solutions for the sub-modules of Modular Multilevel Converters are exemplarily known from WO 2014/091801 A1, JP 2011 114920 A, KR 2014 0087450 A and US 2013/208519 A1. Disclosure Technical Problem An object of the present invention is to provide a power control apparatus for sub-module of an MMC converter, which prevents the generation of heat in internal elements and minimizes loss in the elements when the MMC, connected to an HVDC and to a STATCOM, converts a high voltage into a low voltage and supplies the low voltage to the sub-modules in the MMC converter. Technical Solution A power control apparatus for sub-modules in a Modular Multilevel Converter (MMC) according to the present invention includes a half-bridge circuit unit for switching multiple switches, converting an input voltage across P and N buses of the MMC into a relatively low voltage, and outputting the low voltage; a transformer for transferring the low output voltage (primary side), output through switching of the switches in the half-bridge circuit unit via switching of the switches, to a secondary side of the transformer; a DC/DC converter for converting an output voltage on the secondary side of the transformer; a photocoupler for outputting a reference signal corresponding to a magnitude of the secondary side output voltage of the transformer; a Pulse Width Modulation (PWM) control unit for controlling switching of the switches in the half-bridge circuit unit in response to the reference signal output from the photocoupler; and a starting circuit unit for supplying an initial starting voltage to the PWM control unit, wherein the PWM control unit is started in response to the starting voltage initially supplied from the starting circuit unit, and is configured to control switching of the switches in response to the reference voltage received from the photocoupler, and to receive the secondary side output voltage of the transformer as an operating voltage depending on the switching, thus being operated. In the present invention, the input voltage may increase from 0 V to a preset maximum voltage (Vmax). In the present invention, the starting circuit unit may be configured to, when the input voltage initially increases and reaches a preset starting voltage of the PWM control unit, supply the starting voltage to the PWM control unit, and when the secondary side output voltage of the transformer is normally output as a preset voltage, receive the secondary side output voltage and block a supply of power to the PWM control unit. In the present invention, the starting circuit unit may include a B contact switch configured to allow current corresponding to the input voltage to flow therethrough or to block the flow of the current; a resistor connected in series with the B contact switch and configured to limit a magnitude of the current; a voltage-drop diode connected in series with the resistor and configured to, when a voltage higher than the preset voltage is induced, allow the current to flow through the voltage-drop diode; and a Zener diode connected in series with the voltage-drop diode and configured to apply a constant voltage to the PWM control unit. In the present invention, the B contact switch may be maintained in a shorted state until the input voltage reaches the preset starting voltage, and is switched to an opened state when the secondary side output voltage of the transformer is applied. In the present invention, the power control apparatus may further include a current-limiting circuit for preventing current equal to or higher than a preset reference current from being applied to the half-bridge circuit unit. In the present invention, the PWM control unit may calculate a switching duty ratio of the switches using the secondary side output voltage and an output current and varies a width of a switching pulse for the switches depending on the calculated switching duty ratio. Advantageous Effects According to the present invention, loss occurring in various types of internal elements in the power control apparatus for sub-modules in an MMC may be minimized, and the generation of heat may be prevented, and thus there is no need to attach an additional device such as a heat dissipation plate. Further, according to the present invention, control power may be output even at 500 to 700 V, compared to the conventional power control apparatus which can output control power at 800 V. Furthermore, according to the present invention, efficiency much higher than that of the conventional power control apparatus which use voltage-dividing resistors and a Zener diode may be maintained. Description of Drawings FIG. 1 is an equivalent circuit diagram of a typical MMC; FIG. 2 is a circuit diagram showing a conventional power control apparatus for sub-module of an MMC converter; FIG. 3 is a circuit diagram showing a power control apparatus for sub-modules in an MMC converter according to a first embodiment of the present invention; and FIGS. 4 to 7 are diagrams illustrating current flow depending on the operation of a power control apparatus 100 according to an embodiment of the present invention. Best Mode Embodiments of the present invention are described with reference to the accompanying drawings in order to describe the present invention in detail so that those having ordinary knowledge in the technical field to which the present invention pertains can easily practice the present invention. It should be noted that the same reference numerals are used to designate the same or similar elements throughout the drawings. In the following description of the present invention, detailed descriptions of known functions and configurations which are deemed to make the gist of the present invention obscure will be omitted. Further, terms such as "first", "second", "A", "B", "(a)", and "(b)" may be used to describe the components of the present invention. These terms are merely used to distinguish relevant components from other components, and the substance, sequence or order of the relevant components is not limited by the terms. It should be understood that a representation indicating that a first component is "linked", "coupled", or "connected" to a second component includes not only the case where the first component is directly coupled or connected to the second component but also cases where a third component is "linked", "coupled" or "connected" between the first and second components. FIG. 3 is a circuit diagram showing a power control apparatus for sub-modules in an MMC converter according to an embodiment of the present invention. Referring to FIG. 3, a power control apparatus 100 for MMC sub-modules according to the embodiment of the present invention is applied to an MMC having one or more phase modules. More specifically, power is supplied to multiple sub-modules constituting each phase module in the MMC. For this, the power control apparatus 100 according to the present invention receives a high voltage across positive (+) P and negative (-) N buses, to which each phase module is connected, converts the high voltage into a low voltage required for the operation of the sub-modules, and supplies the low voltage. Such an MMC is connected both to an HVDC system and to a STATCOM. The power control apparatus 100 according to the embodiment of the present invention includes a half-bridge circuit unit 110, a transformer 120, a DC/DC converter 130, a photocoupler 140, a Pulse Width Modulation (PWM) control unit 150, and a starting circuit unit 160. The half-bridge circuit unit 110 may receive an input voltage across the P and N buses of the MMC and perform switching at a voltage magnitude of 1/2 of the input voltage. The half-bridge circuit unit 110 includes a first capacitor 111a connected between the P and N buses and a second capacitor 112 connected in series with the first capacitor 111, and series-connected first and second switches 113 and 114 connected in parallel with the series-connected first and second capacitors 111 and 112. The junction of the first and second capacitors 111 and 112 and the junction of the first and second switches 113 and 114 are individually connected to the primary side of the transformer 120, and voltages at respective junctions are input to the primary side depending on the switching of the first and second switches 113 and 114. The switching of the first and second switches 113 and 114 is controlled by the PWM control unit 150, which will be described later. Preferably, the half-bridge circuit unit 110 of the present invention receives the input voltage across the P-N buses, converts the input voltage into a voltage corresponding to 1/2 of the input voltage, and outputs the resulting voltage. The transformer 120 transfers the primary side voltage, output from the half-bridge circuit unit 110, to the secondary side thereof. Such an output voltage on the secondary side is determined according to the internal turns ratio of the transformer 120. Preferably, the secondary side output voltage is output as a low voltage, which is much lower than the primary side voltage. The DC/DC converter 130 converts the secondary side output voltage of the transformer 120 into the voltage required for the sub-modules. In this way, the voltage supplied to the sub-modules is obtained by converting the input voltage that is a high voltage across the P and N buses into a low voltage using the half-bridge circuit unit 110, and converting the low voltage into a voltage that is even lower than the low voltage through the transformer 120. The photocoupler 140 detects the output voltage on the secondary side of the transformer 120. In the photocoupler 140, the primary side and the secondary side of the transformer 120 are electrically isolated from each other, and thus current corresponding to the secondary side output voltage of the transformer 120 is supplied to a light-emitting unit, so that light is emitted. A light-receiving unit receives the light emitted from the light-emitting unit, and then outputs a reference signal corresponding to the secondary side voltage. In this way, the photocoupler 140 provides the reference signal corresponding to the secondary side output voltage to the PWM control unit 150, which will be described later. By means of this, the PWM control unit 150 operates the half-bridge circuit unit 110 using the corresponding reference signal. The PWM control unit 150 controls the switching of the switches 113 and 114 in the half-bridge circuit unit 110. Here, the PWM control unit 150 calculates the ON/OFF switching duty ratio of the switches 113 and 114 using the reference signal corresponding to the secondary side output voltage supplied from the photocoupler 140, and varies the width of the switching pulse for the switches 113 and 114 depending on the calculated switching duty ratio. In particular, in the present embodiment, the PWM control unit 150 is started in response to a starting voltage initially supplied from the starting circuit unit 160, which will be described later, and thus the PWM control unit 150 controls the switching of the first and second switches 113 and 114 of the half-bridge circuit unit 110. By this switching, a voltage corresponding to 1/2 of the input voltage is supplied to the primary side of the transformer 120 through the half-bridge circuit unit 110, and a relatively low voltage is output from the secondary side. In this case, the low voltage output from the secondary side of the transformer 120 is supplied as an operating voltage. In this way, during initial startup, the PWM control unit 150 receives a starting voltage from the starting circuit unit 160, and uses the output voltage on the secondary side, to which the voltage is input, as operating power when the voltage is input to the secondary side of the transformer 120 after startup. Here, in order for the PWM control unit 150 to use the secondary side output voltage of the transformer 120 as the operating power, it is preferable for the secondary side output voltage to normally be output as a preset voltage. That is, in order to be used as the operating power, a voltage having a predetermined magnitude or more is required. When the secondary side output voltage is normally output as the voltage having the preset magnitude or more, the secondary side output voltage is used as the operating power for the PWM control unit 150. The starting circuit unit 160 supplies an initial starting voltage to the PWM control unit 150. In particular, in the present embodiment, the starting circuit unit 160 does not supply the starting voltage to the PWM control unit 150 until the input voltage reaches the starting voltage of the PWM control unit 150 after increasing from O V, and then supplies the starting voltage to the PWM control unit 150 when the input voltage further increases and reaches the starting voltage, with the result that the PWM control unit 150 starts to be operated. The startup of the PWM control unit 150 corresponds to the startup of the power control apparatus 100 according to the present invention. Such a starting circuit unit 160 includes a B contact switch 161, a resistor 162, a voltage-drop diode 163, and a Zener diode 164. The B contact switch 131 controls the flow of current generated by the input voltage across the P and N buses of the MMC. That is, since the B contact switch 131 is initially in a closed state, a line is shorted, and then current flows through the B contact switch. Thereafter, when the secondary side output voltage of the transformer 120 is applied, the B contact switch is opened, thus blocking the flow of current. The resistor 162 is connected in series with the B contact switch 161, and limits the magnitude of current flowing through the B contact switch 161. The voltage-drop diode 163 is connected in series with the resistor 162 and is configured to, when a voltage higher than a preset voltage is induced, allow the current to flow through the voltage-drop diode 163. That is, the voltage-drop diode 163 blocks the current when the input voltage is lower than the preset starting voltage of the PWM control unit 150, and allows the current to flow therethrough only when the input voltage is higher than the starting voltage. Such a voltage-drop diode 163 may include, for example, a Transient Voltage Suppressor (TVS) diode. The Zener diode 164 is connected in series with the voltage-drop diode 163, and supplies a clamping voltage, generated using the current flowing through the voltage-drop diode 163, to t
[EN US10811962B2]: Multi-level switching power converter, and controller circuit and control method thereof | [EN US10811962B2]: A multi-level switching power converter includes a multi-level power stage circuit which converts an input power to an output power. The power stage circuit includes an inductor, a conversion capacitor and plural power switches. The controller circuit controls the multi-level power stage circuit and includes: a feedback pulse generator circuit which generates a trigger pulse; a first timer circuit and a second timer circuit which determine a first time period and a second time period respectively according to the trigger pulse; and an adjusting circuit which adjusts the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage. | US2020161967A1 | 2020-10-20 2020-05-21 | US201916680599A | 2019-11-12 2019-11-12 | US201916680599A, 2019-11-12 CN201811381770A, 2018-11-20 US201916653940A, 2019-10-15 US201916680599A, 2019-11-12 CN201811381770A, 2018-11-20 US201916653940A, 2019-10-15 | US10811962B2: 2020-10-20 | RICHTEK TECHNOLOGY CORP | CHUANG YUNG-CHUN HUANG TSUNG-WEI | H02M3/158: I H02M1/00: N H02M3/07: I H02M1/14: I | H02M3/158: I H02M1/0025: A H02M1/0095: A H02M7/4833: I H02M7/4837: I H02M3/07: I | US2004095081A1 US2004095108A1 US2004095112A1 US2004095116A1 US2004095164A1 US2004095264A1 US2020161959A1 | US10944321B2 US10944321 10944321 | [EN US10811962B2]: 1. A multi-level switching power converter, comprising: a multi-level power stage circuit, configured to operably convert an input power to an output power by multi-level power conversion; and a controller circuit, configured to operably control the multi-level power stage circuit; wherein the multi-level power stage circuit includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; wherein the controller circuit includes: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 2. The multi-level switching power converter of claim 1, wherein the controller circuit further includes another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. 3. The multi-level switching power converter of claim 1, wherein the timer circuit includes: a current source, configured to operably provide a predetermined current;a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current;a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; anda timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage;wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. 4. The multi-level switching power converter of claim 3, wherein the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period;(2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or(3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. 5. The multi-level switching power converter of claim 4, wherein the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or(2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage;wherein the adjusting output signal corresponds to the first adjusting signal. 6. The multi-level switching power converter of claim 1, wherein the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power stage circuit operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node;(2) a second state: the inductor being electrically connected between the third node and the first node;(3) a third state: the inductor and the conversion capacitor being electrically connected in series between the third node and the first node, wherein the terminal of the conversion capacitor is electrically connected to the third node, and the other terminal of the conversion capacitor is electrically connected to the switching node; or(4) a fourth state: the inductor being electrically connected between the second node and the first node;wherein the first pulse modulation signal controls the power stage circuit to operate in the first state in the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the third state in the second time period; orthe first pulse modulation signal controls the power stage circuit to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the second state outside the second time period. 7. The multi-level switching power converter of claim 1, wherein: when the multi-level power stage circuit operates as the buck power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an input voltage of the input power; when the multi-level power stage circuit operates as the boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power; or when the multi-level power stage circuit operates as the inverting buck-boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the input power and the proportion voltage level, wherein the level of the reference voltage is ½ of a difference between the input voltage and the output voltage. 8. The multi-level switching power converter of claim 1, wherein the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; anda modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. 9. A controller circuit for use in controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, the multi-level power converter including: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; the controller circuit comprising: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 10. The controller circuit of claim 9, further comprising another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. 11. The controller circuit of claim 9, wherein the timer circuit includes: a current source, configured to operably provide a predetermined current;a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current;a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; anda timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage;wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. 12. The controller circuit of claim 11, wherein the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period;(2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or(3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. 13. The controller circuit of claim 12, wherein the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or(2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage;wherein the adjusting output signal corresponds to the first adjusting signal. 14. The controller circuit of claim 9, wherein the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power converter operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node;(2) a second state: the inductor being electrically connected between the third node and the first node;(3) a third state: the inductor and the conversion capacitor being electrically connected in series between the third node and the first node, wherein the terminal of the conversion capacitor is electrically connected to the third node, and the other terminal of the conversion capacitor is electrically connected to the switching node; or(4) a fourth state: the inductor being electrically connected between the second node and the first node;wherein the first pulse modulation signal controls the power converter to operate in the first state in the first time period, and the second pulse modulation signal controls the power converter to operate in the third state in the second time period; orthe first pulse modulation signal controls the power converter to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power converter to operate in the second state outside the second time period. 15. The controller circuit of claim 9, wherein: when the multi-level power stage circuit operates as the buck power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an input voltage of the input power; when the multi-level power stage circuit operates as the boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power; or when the multi-level power stage circuit operates as the inverting buck-boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the input power and the proportion voltage level, wherein the level of the reference voltage is ½ of a difference between the input voltage and the output voltage. 16. The controller circuit of claim 9, wherein the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; anda modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. 17. A control method for controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, wherein the multi-level power converter includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; the control method comprising: generating a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; generating at least a first phase pulse and a second phase pulse according to the trigger pulse; determining a first time period and generating a first pulse modulation signal according to the first phase pulse and the first time period; determining a second time period and generating a second pulse modulation signal according to the second phase pulse and the second time period; and performing one of the followings: adjusting the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or adjusting the first time period according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 18. The control method of claim 17, further comprising one of the followings: (1) adjusting the second time period according to the difference between the voltage across the conversion capacitor and the reference voltage such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) adjusting the second time period according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. | [EN US10811962B2]: CROSS REFERENCE The present invention is a continuation-in-part application of U.S. Ser. No. 16/653,940, filed on Oct. 15, 2019, and the present invention claims priority to CN 201811381770.X, filed on Nov. 20, 2018. BACKGROUND OF THE INVENTION Field of Invention The present invention relates to a multi-level switching power converter. Particularly it relates to a multi-level switching power converter which can perform self-balance and self-calibration. The present invention also relates to a controller circuit and a control method for use in the multi-level switching power converter. Description of Related Art Relevant prior art documents are “A 50 MHz 5V 3 W 90% Efficiency 3-Level Buck Converter with Real-Time Calibration, Xun Liu et. al, 2016 Symposium on VLSI Circuits Digest of Technical Papers”, “Analysis and Design Considerations of Integrated 3-Level Buck Converters, Xun Liu et. al., IEEE TRANSACTIONS ON CIRCUITS AND SYSTEMS Vol. 63, No. 5, May 2016”, “A 2 MHz 12-100 V 90% Efficiency Self-Balancing ZVS Reconfigurable Three-Level DC-DC Regulator With Constant-Frequency Adaptive-On-Time V2 Control and Nanosecond-Scale ZVS Turn-On Delay” and “Constant ON-Time 3-Level Buck Converter for Low Power Applications, Brian M. Cassidy et. al, IEEE, 2015”, which propose different approaches from the present invention. FIG. 1 shows a prior art 3-level switching power converter (3-level switching power converter 1) which employs the power switches (N1˜N4), the conversion capacitor CF and the inductor L to convert the input power VIN to the output power VOUT by 3-level power conversion. More specifically, the switching node LX is switched among 3 levels of voltages (i.e. the input voltage VVI, the ground level and a proportion voltage level such as VVI/2) to achieve the 3-level power conversion. The prior art circuit in FIG. 1 has a drawback that the proportion voltage level may shift due to non-ideality or mismatch among circuits to cause extra power loss or un-stability of the switching frequency. FIG. 2 shows operating waveforms of the prior art multi-level switching power converter corresponding to FIG. 1. Ideally, the high level of the voltage of the switching node VLX is supposed to be equal to ½ of the input voltage, i.e. VVI/2, and the average of the voltage VCF across the conversion capacitor CF is also supposed to be equal to VVI/2. However, due to the aforementioned non-ideality, as shown in FIG. 2, the actual high level of the voltage of the switching node VLX is higher than VVI/2 during D1 period, and is lower than VVI/2 during D3 period. On the other hand, the average of the voltage VCF across the conversion capacitor CF is also shifted from the expected VVI/2, to be lower than VVI/2 as shown in FIG. 2. As described earlier, this issue causes extra power loss or un-stability of the switching frequency. Compared to the prior art in FIG. 1, the present invention is advantageous in that a self-calibration can be performed to keep the level of the voltage of the switching node VLX and the average of the voltage VCF across the conversion capacitor CF at expected levels, whereby the power loss can be reduced and the switching frequency can be kept stable. SUMMARY OF THE INVENTION From one perspective, the present invention provides a multi-level switching power converter, comprising: a multi-level power stage circuit, configured to operably convert an input power to an output power by multi-level power conversion; and a controller circuit, configured to operably control the multi-level power stage circuit; wherein the multi-level power stage circuit includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; wherein the controller circuit includes: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. In one embodiment, the controller circuit further includes another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or (2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage; wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. In one embodiment, the timer circuit includes: a current source, configured to operably provide a predetermined current; a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current; a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; and a timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage; wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. In one embodiment, the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period; (2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or (3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. In one embodiment, the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or (2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage; wherein the adjusting output signal corresponds to the first adjusting signal. In one embodiment, the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power stage circuit operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node; (2) a second state: the inductor being electrically connected between the third node and the first node; (3) a third state: the inductor and the conversion capacitor being electrically connected in series between the third node and the first node, wherein the terminal of the conversion capacitor is electrically connected to the third node, and the other terminal of the conversion capacitor is electrically connected to the switching node; or (4) a fourth state: the inductor being electrically connected between the second node and the first node; wherein the first pulse modulation signal controls the power stage circuit to operate in the first state in the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the third state in the second time period; or the first pulse modulation signal controls the power stage circuit to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the second state outside the second time period. In one embodiment, when the multi-level power stage circuit operates as the buck power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein a level of the reference voltage is ½ of an input voltage of the input power; or when the multi-level power stage circuit operates as the boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power; or when the multi-level power stage circuit operates as the inverting buck-boost power stage circuit, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the input power and the proportion voltage level, wherein the level of the reference voltage is ½ of a difference between the input voltage and the output voltage. In one embodiment, the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; and a modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. From another perspective, the present invention provides a controller circuit for use in controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, the multi-level power converter including: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; the controller circuit comprising: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. From another perspective, the present invention provides a control method for controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, wherein the multi-level power converter includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a second node, and a third node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node, the second node and the third node are configured as one of the followings: (1) the first node is coupled to the output power, the second node is coupled to the input power, and the third node is coupled to ground level, whereby the multi-level power stage circuit operates as a buck power stage circuit; (2) the first node is coupled to the input power, the second node is coupled to the output power, and the third node is coupled to the ground level, whereby the multi-level power stage circuit operates as a boost power stage circuit; or, (3) the first node is coupled to the ground level, the second node is coupled to the input power, and the third node is coupled to the output power, whereby the multi-level power stage circuit operates as an inverting buck-boost power stage circuit; the control method comprising: generating a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; generating at least a first phase pulse and a second phase pulse according to the trigger pulse; determining a first time period and generating a first pulse modulation signal according to the first phase pulse and the first time period; determining a second time period and generating a second pulse modulation signal according to the second phase pulse and the second time period; and performing one of the followings: adjusting the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or adjusting the first time period according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. In one embodiment, the control method further comprises one of the followings: (1) adjusting the second time period according to the difference between the voltage across the conversion capacitor and the reference voltage such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or (2) adjusting the second time period according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage; wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. The objectives, technical details, features, and effects of the present invention will be better understood with regard to the detailed description of the embodiments below. BRIEF DESCRIPTION OF THE DRAWINGS FIG. 1 shows a schematic diagram of a prior art multi-level switching power converter. FIG. 2 shows operating waveforms of a prior art multi-level switching power converter. FIGS. 3A-3D show schematic diagrams of various embodiments of the multi-level switching power converter according to the present invention. FIGS. 4A-4B show operating waveforms corresponding to the embodiment shown in FIG. 3A. FIG. 5 shows schematic diagrams of four coupling states corresponding to the embodiment shown in 3A. FIGS. 6A-6B show schematic diagrams of two specific embodiments of the multi-level switching power converter according to the present invention. FIGS. 6C-6E show schematic diagrams of other specific embodiments of the multi-level switching power converter according to the present invention. FIG. 7 shows a schematic diagram of a specific embodiment of the feedback pulse generator circuit of the multi-level switching power converter according to the present invention. FIG. 8 shows operating waveforms of the multi-level switching power converter according to the present invention. FIG. 9 shows operating waveforms of the multi-level switching power converter according to the present invention. FIG. 10A shows a schematic diagram of a specific embodiment of the timer circuit of the multi-level switching power converter according to the present invention. FIG. 10B shows a schematic diagram of a specific embodiment of the timer logic circuit of the multi-level switching power converter according to the present invention. FIGS. 11A-11C show schematic diagrams of several specific embodiments of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIGS. 11D-11F show schematic diagrams of several specific embodiments of the timer capacitor circuit of the multi-level switching power converter according to the present invention. FIG. 11G shows a schematic diagram of another specific embodiment of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIGS. 12A-12B show schematic diagrams of several specific embodiments of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIG. 12C shows a schematic diagram of another specific embodiment of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. DESCRIPTION OF THE PREFERRED EMBODIMENTS The drawings as referred to throughout the description of the present invention are for illustration only, to show the interrelations between the circuits and the signal waveforms, but not drawn according to actual scale. FIGS. 3A-3C show schematic diagrams of three embodiments of the multi-level switching power converter (multi-level switching power converter 3A-3C) according to the present invention. As shown in FIGS. 3A-3C, each of the multi-level switching power converter (multi-level switching power converter 3A-3C) comprises a multi-level power stage circuit 200 and a controller circuit 100. The multi-level power stage circuit 200 is configured to operably convert an input power VIN to an output power VOUT by multi-level power conversion. The controller circuit 100 is configured to operably control the multi-level power stage circuit 200. Still referring to FIGS. 3A-3C, the multi-level power stage circuit 200 includes an inductor L, at least one conversion capacitor (e.g. CF) and plural power switches (e.g. N1˜N4). The inductor L is coupled between a switching node LX and a first node ND1. The conversion capacitor CF is configured to operably generate at least one proportion voltage level by capacitive voltage division (“Capacitive voltage division” will be explained in detail later). The plural power switches (N1˜N4) are coupled to the inductor L and the conversion capacitor CF, and are configured to operably control the coupling arrangement of the inductor L and the conversion capacitor CF, such that the switching node LX is switched among the at least one proportion voltage level, a second node ND2, and a third node ND3, to achieve the multi-level power conversion, wherein the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. In one embodiment, as shown in FIG. 3A, the first node ND1 is coupled to the output power VOUT, the second node ND2 is coupled to the input power VIN, and the third node ND3 is coupled to the ground level. In this case, the multi-level switching power converter 3A is configured to be a buck (step-down) multi-level switching power converter, and the multi-level power stage circuit 200 is configured to be a buck power stage circuit. In another embodiment, as shown in FIG. 3B, the first node ND1 is coupled to the input power VIN, the second node ND2 is coupled to the output power VOUT, and the third node ND3 is coupled to the ground level. In this case, the multi-level switching power converter 3B is configured to be a boost (step-up) multi-level switching power converter, and the multi-level power stage circuit 200 is configured to be a boost power stage circuit. In another embodiment, as shown in FIG. 3C, the first node ND1 is coupled to the ground level, the second node ND2 is coupled to the input power VIN, and the third node ND3 is coupled to the output power VOUT. In this case, the multi-level switching power converter 3B is configured to be an inverting buck-boost multi-level switching power converter, and the multi-level power stage circuit 200 is configured to be an inverting buck-boost power stage circuit. Note that when the multi-level power stage circuit 200 is configured to be an inverting buck-boost power stage circuit, the output voltage VVO and the input voltage VVI have opposite signs (+/−), and the ratio of the absolute value of the output voltage VVO over the absolute value of the input voltage VVI can be larger than, equal to, or smaller than 1. The input capacitor CIN and the output capacitor COUT are coupled to the input power VIN and the output power VOUT respectively. The term “multi-level” used in the terms “multi-level switching power converter” and “multi-level power stage circuit” indicates that the switching node LX is switched among multiple levels, such as the aforementioned at least one proportion voltage level, the second node ND2 and the third node ND3, so as to convert the input power VIN to the output power VOUT, whereby the multi-level power conversion is achieved. More specifically, the multi-level switching power converters 3A-3C shown in FIGS. 3A-3C are 3-level switching power converters (corresponding to buck, boost, and inverting buck-boost types respectively). Hereinafter for simplicity, the multi-level switching power converter of the present invention will be illustrated and explained using a buck type power converter (more specifically a 3-level buck type switching power converter) as an example, unless noted. FIGS. 4A-4B show operating waveforms corresponding to the embodiment shown in FIG. 3A. As shown in FIG. 4A, in this embodiment, the input power has an input voltage VVI and the output power VOUT has an output voltage VVO. When the duty ratio of the input voltage to the output voltage (i.e. VVO/VVI) is less than 50%, the voltage VLX on the switching node LX is switched between the ground level (corresponding to the third node ND3) and the target value of the proportion voltage level (VVI/2). As shown in FIG. 4B, in this embodiment, when the duty ratio of the input voltage to the output voltage (i.e. VVO/VVI) is larger than 50%, the voltage VLX on the switching node LX is switched between the input voltage VVI and the target value of the proportion voltage level (VVI/2). In this embodiment, the level of the proportion voltage level is ½ of the input voltage VVI, i.e. VVI/2. As shown in FIG. 3B, when the first node ND1 is coupled to the input power VIN and the second node ND2 is coupled to the output power VOUT, the switching node LX is switched between the output power VOUT and the proportion voltage level, or the switching node LX is switched between the ground level (corresponding to the third node ND3) and the proportion voltage level. In this embodiment, the proportion voltage level is ½ of the output voltage VVO of the output power VOUT, i.e. VVO/2. As shown in FIG. 3C, when the first node ND1 is coupled to the ground level and the second node ND2 is coupled to the input power VIN, the switching node LX is switched between the output power VOUT and the proportion voltage level, or the switching node LX is switched between the input power VIN and the proportion voltage level. In this embodiment, the proportion voltage level is ½ of a difference between the input voltage VVI and the output voltage VVO, i.e. (VVI-VVO)/2. FIG. 5 shows schematic diagrams of four coupling states corresponding to the embodiment shown in 3A. Referring to FIGS. 3A and 5, the aforementioned “capacitive voltage division” means that the conversion capacitor CF is controlled to be coupled between the second node ND2 and the switching node LX (e.g. the first state as shown in FIG. 5), or to be coupled between the switching node LX and the ground voltage level (e.g. the third state as shown in FIG. 5), in a time-shared manner, thereby generating the at least one proportion voltage level (e.g. VVI/2) by the “capacitive voltage division”. In other words, the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. In the embodiments shown in FIGS. 3A, 4A and 4B, the target level of the voltage VCF across the conversion capacitor CF is VVI/2. In these embodiments, the proportion voltage level also is VVI/2. From another perspective, the multi-level switching power conversion achieved by the “capacitive voltage division” is characterized in that: during some of the time periods, the plural power switches control the inductor L and the conversion capacitor CF to be electrically connected in series between the first node ND1 and the second node ND2 (e.g. the first state shown in FIG. 5), while during other time periods, the plural power switches control the inductor L and the conversion capacitor CF to be electrically connected in series between the first node ND1 and the ground level (e.g. the third state shown in FIG. 5), such that the switching node LX is switched among the at least one proportion voltage level (e.g. VVI/2), the ground level (corresponding to the third node ND3), and the second node ND2, so that the multi-level power conversion is achieved, wherein the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. Note that, in a boost type multi-level switching power converter (e.g. FIG. 3B), the “capacitive voltage divisi
[EN US10958190B2]: Multi-level voltage sourced converter [FR WO2018201225A1]: CONVERTISSEUR À SOURCE DE TENSION À PLUSIEURS NIVEAUX | [EN US10958190B2]: A voltage sourced converter for converting power from DC to AC features a chain of power electronic modules in between which each AC connection of the converter is made so as to form a series string or arm of the modules on at least one side of that connection to the chain which are controlled so as to produce at this connection an AC voltage waveform. [FR WO2018201225A1]: La présente invention concerne un convertisseur à source de tension permettant de convertir le courant CC en CA qui comprend une chaîne de modules électroniques de courant entre lesquels chaque connexion CA du convertisseur est réalisée de manière à former une chaîne ou un bras en série des modules sur au moins un côté de cette connexion à la chaîne qui sont commandés de manière à produire au niveau de cette connexion une forme d'onde de tension CA. | WO2018201225A1 | 2018-11-08 | CA2018050384W | 2018-03-28 | US201762501948P, 2017-05-05 | WO2018201225A1: 2018-11-08 US10958190B2: 2021-03-23 | TRANSGRID SOLUTIONS INC | MOHADDES KHORASSANI MOJTABA | H02M7/44: I H02J3/36: I H02M1/12: I H02M7/483: I H02M7/5387: I | H02M7/483: I H02M7/05: A H02M7/4835: A H02M7/53871: I | US2013070495A1 US6519169B1 US2010309698A1 US2015229234A1 US2013704950A1 |  | [EN US10958190B2]: 1. A voltage sourced converter comprising: a plurality of AC terminals and a DC terminal between which electrical power is transferred; a plurality of power electronic modules each including at least one capacitive element arranged to maintain a predetermined voltage and electronic switches operatively connecting the at least one capacitive element to terminals of the respective module such that current can be guided through or to bypass the at least one capacitive element; the modules being connected in a single chain between two connections defining the DC terminal such that DC current passing through the DC terminal passes through the chain of the modules; the AC terminals being connected to the chain at prescribed locations between the modules in the chain so that on at least one side of each connection is formed an arm of the modules; a plurality of DC-blocking capacitive elements each connected between a respective one of the AC terminals and the corresponding respective connection at the chain such that the DC current passing through the chain is prevented from propagating out of the AC terminals beyond the converter; a controller for controlling the modules so as to (i) form an AC voltage waveform at each AC terminal, (ii) maintain the predetermined voltage of each of the at least one capacitive element of the respective module, and (iii) maintain a total voltage of all the modules of the chain substantially equal to a voltage at the DC terminal;each arm including a prescribed number of the modules which is related to the sum of the magnitude of a peak AC voltage which can appear across the respective arm and a DC voltage drop across the respective arm. 2. The voltage sourced converter according to claim 1 including an AC path across the two connections of the DC terminal for reducing propagation of the AC current to the DC terminal. 3. The voltage sourced converter according to claim 2 wherein the AC path is formed by at least one fundamental frequency filter. 4. The voltage sourced converter according to claim 3 wherein there is provided a fundamental frequency filter for each phase defined by the respective AC terminal, the fundamental frequency filter being connected in a manner forming a closed loop with the respective AC terminal and the arms on either side of the connection thereof. 5. The voltage sourced converter according to claim 1 wherein there is provided a capacitive element connected between a respective one of the AC terminals and the corresponding respective connection at the chain so as to block propagation of the DC current to the respective one of the AC terminals. 6. The voltage sourced converter according to claim 5 wherein between each AC terminal and the corresponding respective connection at the chain is a respective one of the DC-blocking capacitive elements. 7. The voltage sourced converter according to claim 1 including a plurality of reactors each connected in series with the respective arm. 8. The voltage sourced converter according to claim 1 wherein there is an arm of the modules on either side of said each connection of a respective one of the AC terminals to the chain. 9. The voltage sourced converter according to claim 1 including: another single chain of power electronic modules connected between the two connections of the DC terminal such that DC current passing through the DC terminal passes through said another chain of the modules,wherein each power electronic module of said another chain includes at least one capacitive element arranged to maintain a predetermined voltage and electronic switches operatively connecting said at least one capacitive element to terminals of the respective module such that current can be guided through or to bypass said at least one capacitive element;the AC terminals being connected to said another chain at prescribed locations between the modules thereof so that on at least one side of each connection is formed an arm of the modules including a prescribed number of the modules such that the modules of said another chain additionally provide AC current to the AC terminals;a plurality of DC-blocking capacitive elements each connected between a respective one of the AC terminals and the corresponding respective connection at said another chain such that the DC current passing through said another chain is prevented from propagating out of the AC terminals beyond the converter;and the modules of both chains being controllable by the controller such that there is substantially no AC current passing through to the DC terminal. 10. The voltage sourced converter according to claim 1 wherein the module is of the type selected from the group consisting of half bridge, full bridge, and semi-full bridge. 11. The voltage sourced converter according to claim 1 wherein there are three AC terminals each for one phase of an AC system to which the voltage sourced converter is connected. | [EN US10958190B2]: This application is a national phase filing of PCT/CA2018/050384 and claims the benefit under 35 U.S.C. 119(e) of U.S. Provisional Application Ser. No. 62/501,948 filed May 5, 2017. FIELD OF THE INVENTION The present invention relates generally to voltage sourced converters, and more particularly to modular multi-level voltage sourced converters. BACKGROUND Electrical power is normally transmitted from one location to another using alternating current (AC). In some cases it is economically or technically beneficial to convert the alternating current to direct current (DC) and transmit power in DC form. At the receiving end power is again converted from DC back to AC. There are also many other industrial applications where electrical power is required to be converted from AC to DC or from DC to AC. In all these cases conversion is generally done by electronic converters that use high power semiconductor devices such as thyristors, diodes, insulated gate bipolar transistors (IGBT), gate turn off thyristors (GTO) and similar electronic devices. To date the most commonly used converters are the Line Commutated Converters (LCC) and the Voltage Sourced Converters (VSC). Generally speaking, voltage sourced converters are power electronic circuits usable for converting electrical power between AC and DC and which in some applications are used for generating or absorbing reactive power. A VSC can be built in various designs, the most commonly used design today is the Modular Multilevel Converter (MMC) configuration. As shown in FIG. 1, a typical, well-known configuration 1 of MMC includes two arms for each of its phases A, B, and C of the converter, an upper arm 3 and a lower arm 4. Thus, a three phase converter has six arms of modules. Each arm includes a number of modules connected in series. In series with each arm a reactor may be connected. Each module includes at least one capacitive element, each typically a capacitor, and two or more electronic switches to allow the capacitor to be inserted into the circuit (either in forward or reverse direction), bypassed or blocked. A number of possible module configurations are available, today the most commonly used configurations are the Half Bridge (HB) and Full Bridge (FB) configurations. A module can use various power electronic devices for switching currents. Today the most commonly used devices are IGBT, IEGT (injection-enhanced gate transistor), IGCT (integrated gate-commutated thyristor) and diodes. The IGBT and diode switches can be made out of a single IGBT or diode component or a number of IGBT or diodes connected in series or parallel to create an IGBT or diode valve. During the normal operation of the converter, modules are switched on or bypassed in a controlled manner to cause the desired AC and DC currents flow through the converter terminals. A converter made with MMC technology for high voltage applications normally requires a large number of modules which takes up a considerable amount of space. SUMMARY OF THE INVENTION It is one object of the invention to provide a topology for a modular multi-level voltage sourced converter. According to an aspect of the invention there is provided a voltage sourced converter comprising: a plurality of AC terminals and a DC terminal between which electrical power is transferred; a plurality of power electronic modules each including at least one capacitive element arranged to maintain a predetermined voltage and electronic switches operatively connecting the at least one capacitive element to terminals of the respective module such that current can be guided through or to bypass the at least one capacitive element; the modules being connected in a chain between two connections defining the DC terminal such that DC current passing through the DC terminal passes through the chain of the modules; the AC terminals being connected to the chain at prescribed locations between the modules in the chain so that on at least one side of each connection is formed an arm of the modules; a plurality of DC-blocking capacitive elements each connected between a respective one of the AC terminals and the corresponding respective connection at the chain such that the DC current passing through the chain is prevented from propagating out of the AC terminals beyond the converter; a controller for controlling the modules so as to (i) form an AC voltage waveform at each AC terminal, (ii) maintain the predetermined voltage of each of the at least one capacitive element of the respective module, and (iii) maintain a total voltage of all the modules which are operated to have current passed through the at least one capacitive element thereof substantially equal to a voltage at the DC terminal; each arm including a prescribed number of the modules which is related to the sum of the magnitude of a peak AC voltage which can appear across the respective arm and a DC voltage drop across the respective arm. This arrangement of modules in a MMC type of converter can employ fewer modules than the conventional arrangement for the same number of AC terminals or phases (i.e., when there are more than one) and therefore can be more economical. In some arrangements there are no modules between a respective one of the connections nearest one of the two connections of the DC terminal. Alternatively, in other arrangements there is an arm of the modules on either side of said each connection of a respective one of the AC terminals to the chain. In one arrangement the voltage sourced converter includes an AC path across the two connections of the DC terminal for reducing propagation of the AC current to the DC terminal. In some arrangements flow of AC current into the DC system is allowed and therefore an AC path may not be used. The AC path may be formed by at least one fundamental frequency filter. In one arrangement there is provided a fundamental frequency filter for each phase defined by the respective AC terminal, the fundamental frequency filter being connected in a manner forming a closed loop with the respective AC terminal and the arms on either side of the connection thereof. In one arrangement there is provided another chain of the power electronic modules connected between the two connections of the DC terminal such that DC current passing through the DC terminal passes through the another chain of the modules, the AC terminals being connected to the another chain at prescribed locations between the modules thereof so that on at least one side of each connection is formed an arm of the modules including a prescribed number of the modules such that the modules of the another chain additionally provide AC current to the AC terminals, and the modules of all chains being controllable by the controller such that there is substantially no AC current passing through to the DC terminal. Thus in this arrangement the additional chain of modules forms an AC path so that there is substantially no AC current passing through to the DC terminal, and this additional chain may augment the AC power output of the converter at the same AC terminals to which the first chain of modules is connected. In other arrangements such additional chains of modules may be connected to different AC terminals defining different phases from those of the first chain. As such, the total DC current passing through the DC terminal is divided between each chain of modules such that only a portion of this total DC current flowing into the voltage sourced converter flows through each chain of modules. In some arrangements the prescribed number of the modules is proportional to the sum of the DC voltage drop across the arm and the magnitude of the peak AC voltage across the arm. For instance, in an arrangement where each module is rated for 2 kV and the peak AC voltage across the arm is 50 kV and the DC voltage across the arm is 100 kV, the prescribed number of the modules in each arm is 75. However, in other arrangements certain other considerations may have to be taken into account such that the number of modules in each arm may no longer be proportional to the sum of the DC voltage and the magnitude of the peak AC voltage across the arm, for example the need for redundant modules to achieve desired converter reliability level or the need for additional modules to increase the arm switching or lightning impulse voltage withstand levels. The respective module may be of the type selected from the group consisting of half bridge, full bridge, and semi-full bridge. There are other types of modules known to the person skilled in the art and new types of modules which may be developed in the future that may be suitable in the voltage sourced converter of the present invention. Typically there are three AC terminals each for one phase of an AC system to which the voltage sourced converter is connected. Most applications of such a voltage sourced converter are for three phase systems. Typically there is provided a capacitive element connected between a respective one of the AC terminals and the corresponding respective connection at the chain so as to block propagation of the DC current to the respective one of the AC terminals. In one arrangement between each AC terminal and the corresponding respective connection at the chain is a respective one of the DC-blocking capacitive elements. In another arrangement there is a DC-blocking capacitive element connected between each AC terminal and the corresponding respective connection at the chain except for one AC terminal which is connected directly to the respective connection at the chain. In such an arrangement there remains at least one DC-blocking capacitive element in each closed path along which DC current may flow out of the converter which acts to block the DC current flowing out from all AC terminals of the converter. There may be provided a plurality of reactors each connected in series with the respective arm. The arrangement of voltage sourced converter described hereinabove is suited for use in High Voltage Direct Current (HVDC) or Medium Voltage Direct Current (MVDC) or in reactive power compensation applications. BRIEF DESCRIPTION OF THE DRAWINGS Arrangements of the invention will now be described in conjunction with the accompanying drawings in which: FIG. 1 is a schematic diagram of a typical, well-known arrangement or topology of modular multilevel converter having three phases. FIG. 2 is a schematic diagram of a conventional half-bridge module with IGBT and diode switches that is usable in a voltage sourced converter. FIG. 3 is a schematic diagram of a conventional full-bridge module usable in a voltage sourced converter. FIG. 4 is a schematic diagram of a conventional semi-full bridge module usable in a voltage sourced converter. FIG. 5 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with three phases and series capacitors at all three AC connections and one fundamental frequency filter at DC terminals. FIG. 6 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with one AC terminal lacking an arm of modules between it and a nearest connection of the DC terminal. FIG. 7 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with series capacitors at all but one of the AC connections. FIG. 8 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with capacitors in series with transformer windings at a neutral connection side of the transformer windings. FIG. 9 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with three fundamental frequency filters one for each phase. FIG. 10 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with series capacitors on only two phases and having three FF filters used. FIG. 11 is a schematic diagram of voltage sourced converter according to an arrangement of the present invention, with two chains of modules and no fundamental frequency filter. In the drawings like characters of reference indicate corresponding parts in the different figures. DETAILED DESCRIPTION In FIGS. 5-11 is shown a voltage sourced converter (VSC) 10, which is generally of the modular multilevel converter (MMC) type or configuration, for converting electrical power from DC to AC and vice versa. As understood in the art, in such converters power is able to flow in either direction, from the DC side to the AC side, or vice versa. Generally speaking, the VSC 10 employs power electronic modules 12 which are shown more clearly in FIGS. 2-4, each arranged to maintain a stable predetermined voltage, acting as “blocks” that are selectively toggled between an off, or bypass, state and an on state at appropriate times so as to superpose to form an AC voltage waveform. Each power electronic module 12 includes at least one capacitive element 13, typically a capacitor, and electronic switches 15 for example IGBTs that are operatively connected to the capacitive element(s) of the module so as to be able to guide current through the module so as to provide one of a predetermined number of voltage values across terminals 17, 18 of the module. More specifically, the electronic switches 15 operatively connect the capacitive element(s) to the terminal connections 17, 18 of the module whereat the module is connected to a larger circuit, and may be operated so as to guide current around, that is bypassing, the capacitive element(s) such that the voltage across the module terminals is effectively zero, or they may be operated so as to guide current through the capacitive element(s) such that the magnitude of the predetermined module voltage sustained by the capacitive element(s) is effectively produced across the module terminals. In some arrangements the module is arranged so that the module current may be guided in forward and reverse directions such that two polarities of the predetermined module voltage can be produced at the module terminals 17, 18. As such, the modules 12 may be for example of the half bridge, full bridge, and semi-full bridge type, though these are just examples and other suitable types of modules may be usable with a MMC style of VSC. The modules are not described in further detail as their construction is known in the art and they are not the focus of the present disclosure. The VSC 10 has a DC terminal 21 with two connections 21A and 21B and a plurality of AC terminals 23, which are interconnected by a configuration of the power electronic modules 12 that will be described in further detail shortly. The modules 12 are controlled by a controller 25 (schematically shown) according to a control scheme generally known in the art so as to produce AC voltage waveforms at the AC terminals, to maintain the predetermined voltage of each capacitive element 13 of the respective module 12, and to maintain a total voltage of all the modules connected between the connections 21A and 21B of the DC terminal that are operated so that current is passed through their capacitive element(s) 13, i.e. those modules which are not bypassed and thus used to contribute to the AC voltage waveform, substantially equal to the DC terminal voltage. Each AC terminal defines a phase of the VSC. Presently, three phase converters are considered to be most common, and therefore the voltage sourced converter of the present invention is described hereinafter in relation to three phases as indicated at 23A through 23C. However, it will be appreciated that there may be a different number of AC terminals 23, that is one or a plurality of phases each having their own separate connection within the VSC. As previously mentioned, the DC terminal and the AC terminals are interconnected by a configuration of the modules 12 in which they are connected in a chain 28 between the two DC terminal connections 21A, 21B such that the DC current passing through the DC terminal passes through the chain 28. The AC terminals 23A-23C are connected respectively at 31A-31C to the chain 28 at prescribed locations so that on at least one side of each connection 31A through 31C is formed an arm 34 of the modules. In the arrangement of FIG. 5 there is an arm on either side of the respective connection of one AC terminal 23. In comparison thereto, another arrangement like that shown in FIG. 6 omits that lowermost arm of the modules between nodes 31C and 21B such that AC terminal 23C is now connected to DC terminal connection 21B either directly or through a capacitive element like a capacitor. Similarly in another arrangement which is not shown that uppermost arm between nodes 31A and 21A may be omitted and node 23A connected to 21A directly or through a capacitive element. Referring back to the illustrated arrangement of FIG. 5, there are k modules forming an upper arm of a first one of the AC terminals that is between nodes 31A and 21A. A lower arm of modules between nodes 31C and 21B comprises j modules. Furthermore, there are n modules between the first connection 31A corresponding to the first AC terminal or phase 23A and the second connection 31B corresponding to a second AC terminal or phase 23B. This string of modules is affected by the phase-to-phase voltage between 23A and 23B. The upper arm and the lower arm together are affected by the phase-to-phase voltage between nodes 23A and 23C. Therefore, generally speaking, the total number of modules in these two arms k+j is equal to n, that number of modules in each of the middle arms. Each arm 34 of modules 12 includes a prescribed number of modules, whether k or j or n, that is related to the sum of the magnitude of the peak AC voltage which can appear across that arm of modules and a DC voltage drop thereacross. More specifically, this prescribed number may be proportional to the sum of the magnitude of this peak AC voltage and this DC voltage drop as in the example where each module is rated for 2 kV and (the magnitude of) the peak AC voltage across an arm is 50 kV and the DC voltage across the arm is 100 kV, the prescribed number of the modules in that arm is 75. However, in a final design which is implemented the number of modules in the respective arm may be different from this initial calculation to account for other factors such as variations in AC system voltage, the need to operate at higher AC voltages to respond to dynamic events, the need for redundant modules to achieve desired converter reliability level and the possible need to increase the arm switching or lightning impulse voltage withstand levels. Furthermore, due to such factors and possibly others known in the art the number of modules in the arm between 31A and 31B may not be exactly equal to the sum of the modules in the upper arm between nodes 21A and 31A and the lower arm between node 31C and 21B. In the illustrated arrangements of FIG. 5 the two middle arms, that is a first middle arm between nodes 31A and 31B and a second middle arm between nodes 31B and 31C, will likely include the same number of the modules, although they may be different due to factors such as the impulse withstand level requirements. There is some flexibility in the number of modules in the upper arm between nodes 21A and 31A and the lower arm between nodes 31C and 21B. Depending on the DC voltage selected for the nodes 31A, 31B and 31C the number of modules in these two arms can be different. In some arrangements the number of modules in the lower arm (or upper arm) may be reduced to zero (i.e. the lower or upper arm is omitted) and node 31C (or 31A) is directly connected to the node 21B (or 21A). As mentioned before other factors such as required impulse withstand level may also affect the number of modules in each arm. In a conventional MMC converter such as that illustrated in FIG. 1 designed to operate with peak AC voltage less than or equal to half DC voltage, for each phase a total of at least 2N modules each with appropriate voltage rating are used between the DC connections 6A and 6B in order to be able to handle the voltage Vdc at the DC terminal of the converter. N is equal to Vdc divided by the nominal (rated) voltage of a single module. Therefore a total of at least 6N modules are used for a three phase converter. For comparison, for a converter with the topology of the present invention, as illustrated for example in FIG. 5, designed to operate with peak phase-to-phase AC voltage less than or equal to half the DC voltage across the corresponding arm, will comprise 2N modules in the entire chain between the DC terminal connections 21A and 21B. Each module is assumed to have a voltage rating equal to said conventional three phase MMC converter. Therefore, one-third of the total number of modules used in the conventional topology of FIG. 1 are now used in the VSC 10 making it much more economical. Of course, this VSC 10 is consequently able to transfer less electrical power than the corresponding conventional MMC having an equivalent number of power electronic modules for one phase in series between the DC terminal connections, but this is sufficiently suitable for applications such as where the required converter power rating is considerably lower than what a conventional converter with similar modules can provide. Typically a capacitive element 35 such as a capacitor is connected between a respective one of the AC terminals 23 and the corresponding respective connection 31 at the chain 28 so as to block propagation of the DC current to the respective one of the AC terminals and out beyond the converter, and is for this reason referred to herein as a DC-blocking capacitive element for convenience of reference. In some arrangements there is a capacitive element 35 connected between each AC terminal and the corresponding respective connection at the chain, as for example shown in FIGS. 5, 9 and 11. In other arrangements not all such paths between the AC connection to the chain 28 and the terminal 23 include such a capacitive element, as for example shown in FIGS. 7 and 10. In these arrangements the propagation of DC current out of the AC terminal is still blocked because each closed path along which DC current can flow out of the converter at an AC terminal, whether to ground or back to the converter as for example along 31A to 23A through a transformer winding and back along 23C to 31C, includes at least one capacitive element at a location therealong; however, in such arrangements the number of series capacitors is reduced which may reduce the cost and the space required by the VSC. At the AC terminals 23 may be connected an AC load for example a three-phase motor or an AC power system 37 (schematically shown), typically facilitated by a transformer 38 so as to provide the appropriate voltage ratio between the VSC and the load or power system 37. Alternatively to inserting the capacitive element between the respective AC terminal 23 and its corresponding connection 31 to the module chain, a capacitive element may be inserted in a manner which effectively places the element along this same path but outside of the VSC. That is, as shown in FIG. 8 a capacitive element 35 (capacitor) can be connected in series with each of the transformer windings but on the end of the winding not connected to the converter. In the example shown in FIG. 8 the transformer windings and capacitors are connected in a Y arrangement. The neutral point of the Y arrangement may be left open or connected to ground directly or through an impedance 39. Generally the series combination of transformer winding and the capacitor can be connected either in Delta or Y. Such an arrangement placing the DC-blocking capacitive elements on the neutral connection side of the transformer may reduce cost of the VSC. The voltage sourced converter of the illustrated arrangements includes an AC path 41 across the two connections 21A, 21B of the DC terminal for reducing propagation of the AC current to the DC terminal by providing a closed loop within the VSC around which AC current can circulate. The AC path 41 may be formed by a fundamental frequency (FF) filter 42 which provides a low impedance path for the AC currents having the same frequency as that of the AC terminals, which in other words is the fundamental frequency. In FIGS. 5-8 is shown an AC path comprising a single FF filter 42 connected in parallel with the chain 28 of modules. In FIGS. 9 and 10 is shown another arrangement of the AC path in which there is provided a fundamental frequency filter 42 for each phase defined by the respective AC terminal 23. Each fundamental frequency filter is connected in a manner forming a closed loop 43 with the respective AC terminal 23 and the anus 34 on either side of the connection 31 thereof. In a further arrangement of the VSC as shown in FIG. 11 there is provided another chain 46 of power electronic modules 12 which like those forming the first chain 28 are operatively controlled by the controller 25 and connected between the two connections 21A, 21B of the DC terminal. As such, a portion of the DC current which passes through the DC terminal 21 passes through this second chain 46 of modules, and another portion of the DC current passes through the first chain 28 of modules. In the arrangement of FIG. 11 the AC terminals 23A-23C are connected to the second chain 46 at prescribed locations 48A through 48C between the modules 12 so that on either side of each connection 48A, 48B, and 48C is formed an arm 34 of the modules comprising a prescribed number of the modules 12. Similar, if not the same, considerations are made in determining how many modules are used in one arm, and typically the prescribed number of the modules in the additional chain is related to the sum of the magnitude of the peak AC voltage and the DC voltages across the arm. In the two chain arrangement which is illustrated in FIG. 11 there is a separate capacitive element 35 in each path between the respective chain and the respective AC terminal 23 as there are two such paths therebetween, one for each chain. In another arrangement of this type of two chain configuration any one of the DC-blocking capacitive elements may be omitted, and the remaining DC-blocking elements still serve to block propagation of DC current into and out of the AC terminals. The modules 12 of the second chain 46 provide additional AC current to the AC terminals 23 so that more power can be transferred between the AC and DC sides versus the VSC configuration which has only a single chain 28 of modules. The modules of both chains 28 and 46 are controlled by the controller 25 such that the AC current leaving the chain 28 enters the chain 46 hence there is substantially no AC current passing through to the DC terminal 21 thereby substituting for the FF filter of the other arrangements. In the arrangement shown in FIG. 11 the AC terminals of the two chains 28 and 46 are connected to the same nodes 23. In other arrangements (not shown) they may be separated and connected to separate transformers, loads or AC systems. It will be appreciated that in some arrangements, which are not shown, flow of AC current into the DC system is allowed and therefore an AC path may not be used. As previously mentioned the power electronic modules 12 can be half bridge, full bridge, semi-full bridge or any other kind usable in a MMC converter. Each module 12 may include one or more capacitors 13 and a number of electronic switches 15 that allow or stop the flow of current through the module terminals 17, 18 and the capacitor or capacitors. These electronic switches may be IGBT, IGCT, IEGT, thyristor, diode or other electronic switches. Each switch may comprise only one or multiple of these devices connected in series or in parallel. According to one arrangement of the invention, in series with each AC terminal 23 there is a capacitor 35 which is then connected to the AC load or AC power system 37. These capacitors prevent DC current flow from the converter to the AC load or the AC power system. In another arrangement like that of FIG. 8 the VSC is connected to the AC load or AC power system through a set of transformers. There is a capacitor in series with each secondary transformer winding. The windings may be connected either in Y or Delta. If windings are connected in Y the neutral point of the Y connection can be left open or connected to ground either directly or through an impedance (such as a resistor, reactor, capacitor, or arrester). In the example of FIG. 8 the VSC is connected to the AC system or load 37 through three single phase transformers. There is a capacitor 35 in series with each of the converter side windings (secondary windings) of these transformers. In this example the windings are connected in Y and the neutral point of the Y is connected to ground through an impedance. In another arrangement of the VSC of the present invention, one of the AC connections does not have a capacitor 35 in series. If the current in AC terminals are required to be balanced, i.e. equal in magnitude, properly selected reactances can be added in series with each phase. The phase currents can also be made to balance by proper control of the converter. The VSC of the present invention may also include one or more Fundamental Frequency (FF) filters. Such filter is designed to provide a low impedance path to the AC currents that are at the same frequency as the AC terminal, i.e. the fundamental frequency. According to one arrangement of the VSC, one FF filter is connected between the DC terminal connections. FIG. 5 shows a three phase VSC example of such an arrangement with series capacitors at all three AC connections and one FF filter at the DC terminal. With reference to FIG. 5, in this arrangement the modules connected between phase A and phase B are controlled to carry Idc+Iab, modules connected between phase B and phase C are controlled to carry Idc+Ibc, modules connected between phase A and the DC terminal and modules connected between phase C and the DC terminal are controlled to carry Idc+Ica. The low impedance current path provided by the FF filter allows majority of Ica flow from one connection of the DC terminal to the other. FIG. 7 shows another arrangement where there is a series capacitor at all AC connections except for one. Any of the AC connections can be left without a series capacitor, in this example phase C is directly connected to the transformer without a series capacitor. Similar to FIG. 5 this example has one FF filter at DC terminals. In both these examples the AC terminals are connected to the AC power system through a transformer. Transformer windings can be connected in any format. In a three phase system the commonly used Y and delta (A) connections are possible both for the primary and secondary windings. In another arrangement of the VSC a FF filter is connected across the modules associated with each AC phase. For example in a three phase VSC there are three FF filters 42A through 42C. FIG. 7 shows a three phase VSC example of such an arrangement with a total of three FF filters, one for each phase. With reference to FIG. 9, in this arrangement the modules connected between the phase A and the connection point of the first filter 42A are controlled to carry Idc−Ia/2; modules connected between the same filter connection point and the phase B connection are designed to carry Idc+Ib/2; the difference between these two currents will flow into the FF filter. Similarly the modules between phase B and the connection point of the second FF filter 42B are controlled to carry Idc−Ib/2 and modules connected between this second filter connection point and phase C connection are controlled to carry Idc+Ic/2, the difference between these two currents flows into the second FF filter. Other FF filters operate based on the same principle. FIG. 10 shows the same converter with one of the series capacitors removed. In another arrangement two or more converters can be connected between the DC ter
[EN CN110383659B]: Energization of a hybrid converter including half-bridge sub-modules and full-bridge sub-modules [FR EP3756273A1]: MISE SOUS TENSION D'UN CONVERTISSEUR COMPRENANT UN MÉLANGE DE SOUS-MODULES EN DEMI-PONT ET EN PONT COMPLET [ZH CN110383659B]: 包括半桥子模块和全桥子模块的混合的变流器的通电 [DE EP3756273A1]: BESTROMUNG EINES UMRICHTERS MIT EINER MISCHUNG VON HALBBRÜCKEN- UND VOLLBRÜCKEN-SUBMODULEN | [EN CN110383659B]: A method for energizing a converter based on a hybrid of a half-bridge (HB) converter unit and a full-bridge (FB) converter unit and its converter station is provided. According to one embodiment, a method for energizing a converter may include: establishing a direct electrical connection between the DC terminals of the converter; electrically connecting the converter to an AC power source via an AC connector; and The AC voltage between the two electric phase lines is obtained from the AC power source and for a specific time period for charging the capacitor of the FB unit connected to the two electric phase lines. Therefore, the FB units will be charged to a higher value, and they can be controlled for charging the capacitor of the HB sub-module by drawing power from the AC power source to at least initiate switching of the switching device of the HB sub-module The minimum voltage required. [FR WO2019161907A1]: L'invention concerne des procédés de mise sous tension de convertisseurs, et des stations de conversion correspondantes, reposant sur un mélange de cellules de convertisseur en demi-pont (HB) et de cellules de convertisseur en pont complet (FB). Selon un mode de réalisation, un procédé de mise sous tension d'un convertisseur peut consister : à établir une connexion électrique directe entre des bornes CC d'un convertisseur, à connecter électriquement le convertisseur à une source d'alimentation CA par l'intermédiaire de connecteurs CA et à obtenir, de la source d'alimentation CA et pendant une certaine période de temps, une tension alternative entre deux lignes de phase électrique de manière à charger des condensateurs des cellules FB connectées aux deux lignes de phase électrique. De cette façon, les cellules FB sont chargées à une valeur supérieure et peuvent être commandées de façon à charger des condensateurs des sous-modules HB à au moins une tension minimale requise pour le démarrage de la commutation de dispositifs de commutation des sous-modules HB en tirant le courant de la source d'alimentation CA. [ZH CN110383659B]: 提供了使基于半桥(HB)变流器单元和全桥(FB)变流器单元的混合的变流器及其换流站通电的方法。根据一个实施例，一种用于使变流器通电的方法可以包括：在变流器的DC端子之间建立直接电连接；经由AC连接器而将该变流器电连接至AC电源；以及从该AC电源并且针对特定时间段获得两个电相线之间的AC电压，以用于对被连接至该两个电相线的该FB单元的电容器进行充电。因此，该FB单元将被充电到较高的值，并且它们可以被控制，以用于通过从该AC电源汲取功率来将该HB子模块的电容器充电到至少启动切换该HB子模块的开关装置所需的最小电压。 | WO2019161907A1 | 2019-08-29 | EP2018054494W | 2018-02-23 | EP2018054494W, 2018-02-23 | WO2019161907A1: 2019-08-29 CN110383659B: 2021-09-17 US2020350767A1: 2020-11-05 EP3756273A1: 2020-12-30 | ABB SCHWEIZ AG ABB电网瑞士股份公司 ABB POWER GRIDS SWITZERLAND AG | BARUPATI PRAVEEN KUMAR JIANG-HÄFNER YING JIANG-HAFNER YING | H02M1/36: I H02J3/36: I H02M7/483: I H02M7/219: I | H02J3/36: A H02M1/36: I H02M7/483: I H02M7/4835: A Y02E60/60: A H02M1/0077: A | CN107681877A CN106487033A CN105207504A US2016056727A1 CN106712238A CN107317472A | CN110739715A CN110739715 110739715 | [EN CN110383659B]: 1 A method of starting the operation of a converter (400, 500) in a high voltage direct current HVDC converter station, wherein the converter is a modular multilevel converter MMC, and the MMC is on the direct current DC side ( 420) includes two DC terminals (422, 424) for connecting to a DC transmission system (430) and includes electrical phase wires (442, 444, 446) on the AC side (410) that can be connected to an AC power source (440) ) AC connectors (472, 474, 476), wherein the converter includes a valve arm (550), each of the valve arms (550) is connected to a DC terminal and an AC connected to an electric phase line Between the connectors, where each valve arm includes at least one full-bridge FB sub-module (305) and at least one half-bridge HB sub-module (310) connected in series, the method includes: Establish (S610, S710) direct electrical connection between the DC terminals; electrically connect the converter (S620, S720) to the AC power source via the AC connector; From the AC power source and for a specific time Obtain (S630, S730) the AC voltage between the two electric phase lines for charging the capacitor of the FB sub-module connected to the two electric phase lines; and after the time period Control (S640, S750) the switch device of the FB sub-module for the HB sub-module The capacitor of the block is charged to at least the minimum voltage required to initiate switching of the switching device of the HB sub-module. 2 The method according to claim 1, further comprising: once the switching device of the HB sub-module is charged to at least the minimum voltage, activating (S650, S760) the switching device of the HB sub-module And maintaining the DC voltage at approximately the same level as the level reached before the activation of the control of the switching device of the HB sub-module. 3 The method according to claim 1 or 2, wherein the capacitor of the HB sub-module is charged by drawing electric power from the AC power source through the electric phase line connected to the AC power source. 4 The method according to claim 1 or 2, wherein the converter is configured to use reactive power to support all while charging the capacitor of the HB sub-module to at least the minimum voltage. The AC side. 5 The method according to claim 1 or 2, further comprising: after the capacitor of the HB sub-module is charged to at least the minimum voltage, disconnecting the DC terminals of the converter from each other Connecting (S660); and electrically connecting (S660) the DC terminal to the DC transmission system. 6 The method according to claim 1 or 2, further comprising: before controlling the switching device of the FB sub-module for charging the capacitor of the HB sub-module to at least the minimum voltage, making The DC terminals of the converter are electrically disconnected from each other (S740), and the DC terminals are electrically connected (S740) to the DC transmission system. 7 The method of claim 5, further comprising: once the DC terminal is connected to the DC transmission system, and the capacitors of the FB sub-module and the HB sub-module are charged to their rated values, Start (S670, S770) ramp up the DC voltage to the selected value for transmitting/receiving electric power. 8 The method of claim 6, further comprising: once the DC terminal is connected to the DC transmission system, and the capacitors of the FB sub-module and the HB sub-module are charged to their rated values, Start (S670, S770) ramp up the DC voltage to the selected value for transmitting/receiving electric power. 9 A method of starting the operation of a first converter (801) in an HVDC converter station (800, 900), the HVDC converter station (800, 900) comprising being connected in series with the first converter The second converter (802), wherein the first converter is a modular multilevel converter, and the modular multilevel converter uses a collection of connectors (836, 837) in its The DC side (821) can be connected to the DC transmission line (832) of the DC transmission system (830) via the first DC terminal (822), and can be connected to the other of the transmission system via the second DC terminal (828) DC transmission line (834) or the DC end of the second converter Any one of sub (826), wherein each valve arm of the first converter includes at least one FB sub-module and at least one HB sub-module, wherein the converter station includes a sub-module for bypassing the first The bypass switch (825) of the converter, wherein the first converter further comprises on its AC side (811) an AC connection that can be connected to the electric phase lines (842, 844, 846) of the AC power source (840) (872, 874, 876), wherein the second converter is initially operated to transmit or receive electric power, and is directly connected to the DC transmission system on its DC side via its two DC terminals, wherein The first converter is bypassed and the set of connectors is used to disconnect the electrical connection from the DC transmission system and the second converter on the DC side thereof, the method It includes: establishing (S1001) a direct electrical connection between the DC terminals of the first converter; electrically connecting (S1002) the first converter to the AC power source; from the AC power source and Obtain (S1003) the AC voltage between the two electric phase lines for a specific time period for charging the capacitor of the FB sub-module connected between the two electric phase lines; and After a period of time, the switching device of the FB sub-module is controlled (S1004) to charge the capacitor of the HB sub-module to at least the minimum voltage required to start switching the switching device of the HB sub-module. 10 The method according to claim 9, further comprising: once the switching device of the HB sub-module is charged to at least the minimum voltage, activating (S650, S760) the switching device of the HB sub-module And maintaining the DC voltage at approximately the same level as the level reached before the activation of the control of the switching device of the HB sub-module. 11 The method according to claim 9, wherein the capacitor of the HB sub-module of the first converter is charged by drawing electric power from the AC power source through the electric phase line connected to the AC power source. 12 The method according to claim 9, wherein the converter is configured to use reactive power while charging the capacitor of the HB sub-module of the first converter to at least the minimum voltage. Support the AC side. 13 The method according to any one of claims 9 to 12, wherein the method comprises: after the capacitor of the HB sub-module is charged to at least the minimum voltage, or after controlling the FB sub-module The switching device is used to electrically disconnect the DC terminals of the first converter from each other before charging the capacitor of the HB sub-module to at least the minimum voltage (S1005). 14 The method according to claim 13, further comprising: using the set of connectors to electrically connect (S1006) the first DC terminal to the DC transmission line of the DC transmission system and connect the first DC terminal to the DC transmission line of the DC transmission system. The two DC terminals are electrically connected to the DC terminal of the second converter. 15 The method of claim 14, further comprising: once the first DC terminal and the second DC terminal of the first converter are connected to the DC transmission system and the second converter, respectively The DC terminal of the converter controls (S1007) the switching devices of the HB sub-module and the FB sub-module of the first converter so that the DC current flowing from the DC transmission system through the bypass switch Is directed to the first converter. 16 The method of claim 15, further comprising: turning off (S1008) the bypass switch when the DC current across the bypass switch becomes substantially zero, and switching across the first converter The DC voltage of the converter is increased (S1009) to the first selected value to transfer/receive electric power to/from the DC transmission system. 17 The method according to any one of claims 9 to 12, wherein the converter station further comprises a method for connecting the first DC terminal (822) of the first converter to the second DC Another bypass switch (890) that establishes a direct electrical connection between the terminals (828). 18 . A control unit adapted to control the charging of the converter according to the method of any one of the preceding claims. 19 A converter station adapted to transmit/receive electric power, the converter station comprising a controller configured to operate at least one converter according to the method of any one of claims 1-17. [ZH CN110383659B]: 1 .一种启动高压直流HVDC换流站中的变流器(400、500)的操作的方法，其中所述变流 器是模块化多电平变流器MMC,所述MMC在直流DC侧(420)包括用于连接至DC传输系统(430) 的两个DC端子(422、424)并且在交流AC侧(410)包括可连接至AC电源(440)的电相线(442、 444、446)的AC连接器(472、474、476)，其中所述变流器包括阀臂(550)，所述阀臂(550)各自 被连接在DC端子与用于连接到一个电相线的AC连接器之间，其中每个阀臂包括被串联连接 的至少一个全桥FB子模块(305)和至少一个半桥HB子模块(310)，所述方法包括： 在所述变流器的所述DC端子之间建立(S610、S710)直接电连接； 经由所述AC连接器而将所述变流器电连接(S620、S720)至所述AC电源； 从所述AC电源并且针对特定时间段获得(S630、S730)两个电相线之间的AC电压，以用 于对被连接至所述两个电相线的所述FB子模块的电容器进行充电；以及 在所述时间段之后控制(S640、S750)所述FB子模块的开关装置，以用于将所述HB子模 块的电容器充电到至少启动切换所述HB子模块的开关装置所需的最小电压。 2 .根据权利要求1所述的方法，进一步包括:一旦所述HB子模块的所述开关装置被充电 到至少所述最小电压，激活(S650、S760)对所述HB子模块的所述开关装置的控制；以及将DC 电压维持在与所述激活对所述HB子模块的所述开关装置的控制之前所达到的水平大致相 同的水平。 3 .根据权利要求1或2所述的方法，其中所述HB子模块的电容器通过从所述AC电源经由 被连接至所述AC电源的所述电相线汲取电功率来被充电。 4 .根据权利要求1或2所述的方法，其中所述变流器被配置为：在将所述HB子模块的所 述电容器充电到至少所述最小电压的同时，利用无功功率来支撑所述AC侧。 5 .根据权利要求1或2所述的方法，进一步包括： 在所述HB子模块的所述电容器被充电到至少所述最小电压之后,使所述变流器的所述 DC端子彼此断开电连接(S660)；以及 将所述DC端子电连接(S660)至所述DC传输系统。 6 .根据权利要求1或2所述的方法，进一步包括： 在控制所述FB子模块的所述开关装置以用于将所述HB子模块的所述电容器充电到至 少所述最小电压之前，使所述变流器的所述DC端子彼此断开电连接(S740)，以及 将所述DC端子电连接(S740)至所述DC传输系统。 7 .根据权利要求5所述的方法，进一步包括：一旦所述DC端子被连接至所述DC传输系 统、并且所述FB子模块和所述HB子模块的所述电容器被充电到其额定值，开始(S670、S770) 使DC电压斜坡上升至所选择的值以用于传递/接收电功率。 8 .根据权利要求6所述的方法，进一步包括：一旦所述DC端子被连接至所述DC传输系 统、并且所述FB子模块和所述HB子模块的所述电容器被充电到其额定值，开始(S670、S770) 使DC电压斜坡上升至所选择的值以用于传递/接收电功率。 9 .一种启动HVDC换流站(800、900)中的第一变流器(801)的操作的方法，所述HVDC换流 站(800、900)包括与所述第一变流器串联连接的第二变流器(802)，其中所述第一变流器是 模块化多电平变流器，所述模块化多电平变流器使用连接器(836、837)的集合在其DC侧 (821)经由第一DC端子(822)而可连接至DC传输系统(830)的DC传输线(832)、并且经由第二 DC端子(828)而可连接至所述传输系统的另一个DC传输线(834)或所述第二变流器的DC端 子(826)中的任何一个，其中所述第一变流器的每个阀臂包括至少一个FB子模块和至少一 个HB子模块，其中所述换流站包括用以旁路所述第一变流器的旁路开关(825)，其中所述第 一变流器在其AC侧(811)进一步包括可连接至AC电源(840)的电相线(842、844、846)的AC连 接器(872、874、876)，其中所述第二变流器在初始时操作以传递或接收电功率、并且在其DC 侧经由其两个DC端子而被直接连接至所述DC传输系统，其中所述第一变流器被旁路并且使 用所述连接器的集合而在其DC侧与所述DC传输系统断开电连接并与所述第二变流器断开 电连接，所述方法包括： 在所述第一变流器的所述DC端子之间建立(S1001)直接电连接； 将所述第一变流器电连接(S1002)至所述AC电源； 从所述AC电源并且针对特定时间段获得(S1003)两个电相线之间的AC电压，以用于对 被连接在所述两个电相线之间的所述FB子模块的电容器进行充电；以及 在所述时间段之后控制(S1004)所述FB子模块的开关装置，以用于将所述HB子模块的 电容器充电到至少启动切换所述HB子模块的开关装置所需的最小电压。 10 .根据权利要求9所述的方法，进一步包括:一旦所述HB子模块的所述开关装置被充 电到至少所述最小电压，激活(S650、S760)对所述HB子模块的所述开关装置的控制；以及 将DC电压维持在与所述激活对所述HB子模块的所述开关装置的控制之前所达到的水 平大致相同的水平。 11 .根据权利要求9所述的方法，其中所述第一变流器的HB子模块的电容器通过从所述 AC电源经由被连接至所述AC电源的所述电相线汲取电功率来被充电。 12 .根据权利要求9所述的方法，其中所述变流器被配置为:在将所述第一变流器的HB 子模块的电容器充电到至少所述最小电压的同时，利用无功功率来支撑所述AC侧。 13 .根据权利要求9至12中任一项所述的方法，其中所述方法包括:在所述HB子模块的 所述电容器被充电到至少所述最小电压之后、或者在控制所述FB子模块的所述开关装置以 用于将所述HB子模块的所述电容器充电到至少所述最小电压之前，使所述第一变流器的 所述DC端子彼此断开电连接(S1005)。 14 .根据权利要求13所述的方法，进一步包括:使用所述连接器的集合，来将所述第一 DC端子电连接(S1006)至所述DC传输系统的所述DC传输线并且将所述第二DC端子电连接至 所述第二变流器的DC端子。 15 .根据权利要求14所述的方法，进一步包括:一旦所述第一变流器的所述第一DC端子 和所述第二DC端子分别被连接至所述DC传输系统和所述第二变流器的DC端子，控制 (S1007)所述第一变流器的所述HB子模块和所述FB子模块的开关装置，使得从所述DC传输 系统流过所述旁路开关的DC电流被引导至所述第一变流器。 16 .根据权利要求15所述的方法，进一步包括：当跨所述旁路开关的所述DC电流大致变 为零时断开(S1008)所述旁路开关，以及将跨所述第一变流器的DC电压增加(S1009)至第一 所选择的值以向/从所述DC传输系统传递/接收电功率。 17 .根据权利要求9至12中任一项所述的方法，其中所述换流站进一步包括用以在所述 第一变流器的所述第一DC端子(822)与所述第二DC端子(828)之间建立直接电连接的另一 旁路开关(890)。 18 . 一种控制单元，适于根据前述权利要求中任一项所述的方法来控制变流器的充电。 19 .一种换流站，适于传递/接收电功率，所述换流站包括被配置为根据权利要求1至17 中任一项所述的方法来操作至少一个变流器的控制器。 | [EN CN110383659B]: The technical field of energization of a hybrid converter including a half-bridge sub-module and a full-bridge sub-module [0001] The present disclosure generally relates to the field of power transmission systems to transmit or receive high voltage direct current HVDC electric power. More specifically, the present disclosure relates to the power-on process or start-up process of a converter (or converter station) including a valve arm based on a mixture of a half-bridge sub-module and a full-bridge sub-module. Background technique [0002] Due to the low loss and cost of the high-voltage direct current (HVDC) power transmission system, the high-voltage direct current (HVDC) power transmission system has become a better choice than its high-voltage alternating current (HVAC) competitors for the large amount of transmission of electric power. In a modern HVDC power transmission system (having a voltage of several hundred kV), the size of the power can reach several gigawatts, and the power can be transmitted over distances of up to several thousand kilometers. [0003] At each end of the HVDC power transmission system, a converter station can be used to convert between AC and DC electric power. Converter stations based on current source converters (CSC) using thyristors as switching devices have been widely used in HVDC applications. However, with the recent development of semiconductor technology, voltage source converters (VSC) using, for example, insulated gate bipolar transistors (IGBT) as switching devices have become popular because they are self-commutated and fail to commutate. Not so sensitive. [0004] For example, a VSC may be a modular multilevel converter (MMC) including a unit or sub-module (SM) including a switching device such as an IGBT and an energy storage element such as a capacitor . The switching device can be arranged in a full-bridge FB sub-module or FB unit. In the FB sub-module or FB unit, each includes four switching devices or units with insulated gate bipolar transistors (IGBT) and parallel freewheeling diodes and a charging capacitor Connected together in an H-bridge configuration; or can be arranged in a half-bridge HB sub-module or HB unit. In the HB sub-module or HB unit, two switching devices (or units) are connected in series and connected together with a parallel charging capacitor . Examples of the FB unit and the HB unit will be described with reference to FIGS. 1 and 2 respectively. [0005] The cell of the MMC may include capacitors as energy storage elements for the operation/commutation of the IGBT, and therefore there is a need to charge these capacitors first before the converter can start operation. Depending on the symmetry provided by the arrangement of the switching device, electric power from an AC power source (on the AC side) or a DC transmission system (on the DC side) can be used to charge the capacitor. [0006] However, in the case of a VSC based on a hybrid of the HB unit and the FB unit, the capacitor will be charged unevenly. Specifically, using charging from the AC side (this is the most general way to charge the MMC), the capacitor of the HB unit will be charged to a very low value compared with the capacitor of the FB unit. Further, the charge level reached in both the HB unit and the FB unit may not be sufficient to activate the operating switch device. [0007] Therefore, there is a need for an improved method and associated converter station for the energization of a converter based on a hybrid of FB unit and HB unit. Summary of the invention [0008] In order to at least partially meet the above requirements, the present disclosure seeks to provide at least an improved method for starting the operation of the converter and the corresponding converter station (or a method for energizing the converter and the corresponding converter station). The present disclosure also relates to the start-up process (or energization) of a converter in a converter station including at least two converters connected in series. [0009] In order to achieve this, the operation of starting the converter and its converter station as defined in the independent claims is provided Methods. Other embodiments are provided in the dependent claims. [0010] According to one aspect, a method of starting the operation of a converter in an HVDC converter station is provided. In this method, the converter is an MMC that includes two DC terminals for connection with a DC transmission system on the DC side, and an AC connector that can be connected to an electric phase line of an AC power source on the AC side. The converter includes valve arms respectively connected between a DC terminal and an AC connector for connecting with an electric phase line, and each valve arm includes at least one FB sub-module and at least one HB sub-module connected in series . In other words, the FB sub-module and the HB sub-module are connected in series between the AC power line and one of the DC terminals of the converter. [0011] The method may include: establishing a direct electrical connection between the DC terminals of the converter; and electrically connecting the converter to an AC power source via an AC connector. The AC voltage between the two electric phase lines can then be obtained from the AC power supply and for a specific period of time for charging the capacitors of the FB sub-modules connected to the two electric phase lines. After the period of time, the switching device of the FB sub-module can then be controlled to charge the capacitor of the HB sub-module to at least the minimum voltage required to initiate the switching of the switching device of the HB sub-module (by drawing power from the AC power supply) . [0012] The minimum voltage required to start the switching device of the HB sub-module can also be referred to as the HB sub-module "deblock" voltage. This minimum voltage corresponds to the voltage at which the HB sub-module (or at least the switching device of the HB sub-module) can start operation. [0013] In the converter of the present aspect, each valve arm may include at least one FB unit and at least one HB unit, that is , a mixture of the FB unit and the HB unit. In the simplest configuration of the valve arm, that is, in some embodiments, the valve arm may include an equal number of FB units and HB units, such as one FB unit and one HB unit. However, other compositions (or mixtures) of FB units and HB units can be envisaged. [0014] In the present disclosure, the terms unit and sub-module may be used interchangeably to refer to the FB unit or the FB sub-module, or to refer to the HB unit or the HB sub-module. [0015] It will be understood that it would be interesting to combine both FB units and HB units in series in the valve arm of a converter station, because the resulting valve arm does not have the following disadvantages: only having FB units connected in series ( This may result in higher losses and higher costs) or only have HB units connected in series (this may result in fewer control features). [0016] Turning to the charging of the MMC as a whole, and more precisely the charging of the capacitors of the valve arm including the FB unit and/or the HB unit, the general way to charge these capacitors is to use electric power from an AC power source. When the AC circuit breaker that connects the converter to the AC line is closed, the voltage between the AC lines (ie, the voltage between the wires of the first phase (for example, phase A) and the wires of the second phase (for example, phase B) Voltage) will appear across the two phases of the positive valve arm and the negative valve arm, thereby charging the capacitor of the unit. [0017] It should be understood that under blocking conditions, the HB unit can only be charged in one current direction, while the FB unit can be charged in two directions. [0018] Therefore, in the case where the valve arm includes only the HB unit, one of the phase valve arms is bypassed, and the capacitor of the other valve arm is charged to the AC line voltage. During this charging process, the capacitor of the HB unit can be charged to approximately 85% of its nominal value, depending on the level of the peak voltage of the AC line voltage. [0019] In the case that the valve arm only includes the FB unit, the AC line-to-line voltage will fall on both ends of the series connection of the two valve arms, thereby charging each valve arm to half the line-to-line voltage and half of the line-to-line voltage Corresponds to half of the value obtained in the case of the valve arm based only on the HB unit. During this charging process, the DC voltage remains at zero volts, and the capacitor of the FB sub-module is charged to approximately 43% of its nominal value. [0020] However, as mentioned above, in the case where the valve arm includes, for example, at least one HB unit and at least one FB unit (ie, a mixture of the HB unit and the FB unit), the capacitors between the units are very uneven Charge. Specifically, with the FB single Compared with the capacitor of the element, the capacitor of the HB unit will be charged to a very low value. The charging value (ie, the charging level, which can be expressed as a percentage of the rated value of the capacitor or unit) depends on the ratio of the HB unit and the FB unit in the valve arm (or converter). The lower the number of HB units in the valve arm, the lower the charge level of the capacitors of the HB units. It will be understood that during this charging period, the voltage of the HB SM will appear across the DC terminal and will not be zero. [0021] Further, although the FB unit can be charged at a higher level than the HB unit, the charging of the FB unit may still be insufficient to activate the device (for example, IGBT) of the switching unit. [0022] Generally, in order to start the operation of the converter, and specifically the IGBT of the switching unit, the capacitor needs to be charged to at least 40%-50% of its rated value (or also referred to as the rated cell voltage). Valve electronics (such as the power supply of the gate unit) draw power from the unit capacitor to initiate operation, but they can only start to function if sufficient energy is stored in the unit's capacitor. [0023] With a valve arm that includes a hybrid of the HB unit and the FB unit, this charging may then be insufficient to activate the IGBT of the switching unit. Further, even if the IGBT of the cell can be switched, the charge level may not be sufficient to meet the AC voltage requirement while keeping the DC voltage at zero at the same time (this may be an important requirement during startup under certain conditions). [0024] As mentioned above, with a hybrid valve arm including the HB unit and the FB unit, the capacitors of the HB unit and the FB unit will be charged unevenly during the initial charging process. Further, the capacitors of the FB unit and the HB unit may be charged to a very low value, so that they cannot even be switched to start functioning. To overcome this problem, the converter can be equipped with a dedicated external power source derived from the line voltage, or have a rechargeable battery. However, this solution increases the complexity of the construction of the system and involves additional costs. [0025] In the concept of the present invention, a startup process is provided, which overcomes or at least alleviates the above-mentioned problems, and particularly overcomes or at least alleviates the low capacitance of the HB unit and the FB unit. Charging problem. [0026] The inventors have realized that by electrically connecting the DC terminals of the converter (ie, by establishing a direct electrical connection between the DC terminals of the converter), when the line-to-line voltage crosses the positive of the two phases When the valve arm and the negative valve arm appear, compared with the charge level of the capacitor of the HB sub-module, the capacitor of the FB sub-module is charged to a higher level, which will be connected to the FB sub-module of the two electric phase wires. The capacitor is charged to a level sufficient to initiate the operation of the switching device of the FB unit. For illustrative purposes, simulations have shown that for a certain proportion of FB units and HB units, when the DC terminals are not electrically connected (ie, not short-circuited), the charging levels of the FB units and HB units can reach approximately At 70% and 35% (as a percentage of its rated value), the charging level of the FB unit and the HB unit can reach almost 80-90% and 0-20%, respectively, when the DC terminal of the converter is electrically short-circuited. Here, it is understood that the percentage of charging may depend on the AC pre-insertion resistor selected for the ac circuit breaker configured to connect or disconnect the converter station from the AC source. Then, this initial energization of the FB unit is sufficient to start switching/operating the switching device of the FB unit, so as to meet the required AC voltage requirements and DC voltage requirements. The switching device of the FB unit can be controlled to charge the capacitor of the HB unit and complete the charging of the capacitor of the FB unit. [0027] It will be appreciated that once the capacitor of the FB unit is charged to a sufficiently high level (ie, as a device for switching the FB unit), the switching device of the FB unit can be controlled to guide the FB unit in one direction or the other The current in the capacitor of the FB unit allows control of the charging and discharging of the capacitor of the FB unit. [0028] It will also be understood that during the control of the FB unit to charge the capacitor of the HB unit (and to some extent, the FB unit), the switching device of the FB unit can be controlled to generate a standard for drawing power from the AC power source. Called AC voltage. During this charging period, the switching of the FB unit can be controlled to generate a zero DC voltage across the two DC terminals. [0029] Therefore, the inventive concept is based on the charging process including the initial stage and the subsequent stage (once the FB unit is charged). During this initial stage, the FB unit is charged to a high level (approximately 90% of its rated value, in which the DC terminal is electrically shorted), and during this subsequent stage, the HB unit is charged from a low level (approximately 0-10% ) Charge to a level where they can start operation. Then you can control the HB sub-module and the FB sub-module to charge the HB unit to a high level (about 100%). The FB unit will then also be charged from an already high level (about 80-90%) to almost fully charged (ie , About 100%). [0030] As expressed above, the AC voltage between the two electrical phase lines can be obtained from the AC power source and for a specific time period (ie, during the initial charging phase or step) for the pair to be connected to the two electrical phases. The capacitor of the FB sub-module of the phase line is charged. It will be appreciated that during this initial charging phase or step, the capacitor of the HB unit can also be charged, but only slightly, that is, it is charged to a much lower value (and is not charged) compared to the capacitor of the FB unit The level at which the device charged to the HB unit can initiate switching). [0031] After the period of time or after the device of the FB sub-module can start switching during the initial charging stage of the FB sub-module, the switching device of the FB sub-module can be controlled to be used (by sub-module from AC (Drawing power) Charge the capacitor of the HB sub-module to at least the minimum voltage value at which the HB sub-module can initiate switching. This minimum voltage value is also referred to as the sub-module "unblocking" voltage. [0032] The HB sub-module can then also be switched for charging (all) the FB sub-module and the HB sub-module to their rated value. [0033] According to an embodiment, the method may further include: once the HB sub-module is charged to the minimum voltage required to start switching the switching device of the HB sub-module, activating the control of the switching device of the HB sub-module; and reducing the DC voltage Maintained at approximately the same level as the level reached before activating the control of the switching device of the HB sub-module. If the DC terminals are still electrically connected to each other, the zero DC voltage is maintained. [0034] According to an embodiment, the capacitor may be charged by drawing electric power from the AC power source via an electric phase line connected to the AC power source. [0035] According to an embodiment, during the charging of the capacitor of the HB sub-module, the switching device of the FB sub-module is controlled to (mainly) charge the capacitor of the HB sub-module from a very low level (0-10%) to HB The sub-module can initiate the switching level and charge to a high level (approximately 100%) if possible. However, the switching of the FB sub-module and the HB sub-module can be controlled to charge the capacitors of the FB sub-module and the HB sub-module to their rated values. [0036] According to an embodiment, the converter may be configured to use reactive power to support the AC side while charging the capacitor of the HB sub-module (ie, once the FB unit has been fully charged and switching has been initiated). [0037] According to an embodiment, the method may further include: electrically disconnecting the DC terminals of the converter from each other after the capacitor of the HB sub-module is charged to at least the minimum voltage required to start switching the HB sub-module; and The terminal is electrically connected to the DC transmission system. [0038] In this embodiment, the switching device is controlled so that the zero DC voltage is maintained before the DC terminal is disconnected. According to another embodiment, the method may further include: before controlling the switching device of the FB sub-module to charge the capacitor of the HB sub-module to at least the minimum voltage required to start switching the switching device of the HB sub-module, the DC of the converter The terminals are electrically disconnected from each other; and the DC terminal is electrically connected to the DC transmission system. [0039] According to an embodiment, the method may further include: once the DC terminal is connected to the DC transmission system and the capacitors of the FB sub-module and the HB sub-module are charged to their rated values, starting to ramp up the DC voltage to the selected value The value is used to transmit/receive electric power. [0040] According to an embodiment, for a symmetrical DC power transmission system with a midpoint ground, the first DC terminal of the converter may be connected to the first pole having a positive potential with respect to ground, and the second DC of the converter The terminal can be connected to The ground has a second pole of negative potential. In other embodiments, for an asymmetric system, one of the DC terminals may be connected to the neutral line (or may be a neutral point), and the other DC terminal may be connected to a pole with a higher potential. [0041] According to another aspect, there is provided a method of starting the operation of a first converter in an HVDC converter station including a second converter connected in series with the first converter. [0042] Connecting two converters in series can allow for higher availability and reliability, because if one of the converters fails, only a part of the total power supply capacity will be lost. Moreover, a plurality of converters connected in series may allow, for example, a transformer connected to the converter to be manufactured to have a reduced size. This can provide both reduced cost and reduced space requirements as well as easier transportation of the transformer. [0043] In order to achieve high power transmission similar to the conventional one, it is necessary to connect the converters in series. In this embodiment, an independent, smoother and online (without interfering with the running system) startup process of a separate converter is provided to improve system availability. It is preferable for the converter to operate at zero DC voltage to smoothly start the converter in a series connection system. [0044] In the converter station, the first converter may be a modular multi-level converter that uses a collection of connectors (or switches) on its DC side via the first DC The terminal can be connected to the DC transmission line of the DC transmission system, and can be connected to either of another DC transmission line of the transmission system or the DC terminal of the second converter via the second DC terminal. Further, each valve arm of the first converter includes at least one FB sub-module and at least one HB sub-module. [0045] The converter station may include a first bypass switch to electrically connect the first and second DC terminals of the first converter and a second bypass switch to bypass the first converter. However, it will be appreciated that the first bypass switch may be optional, and the first and second DC terminals may be electrically connected by closing the second bypass switch and by closing the set of connectors, that is, short-circuited. Other alternatives for short-circuiting the DC terminals are also conceivable. [0046] Further, the first converter may further include an AC connector connectable to the electric phase line of the AC power source on the AC side thereof. [0047] In this method (or charging process), the second converter is initially operated to transmit or receive electric power, and is directly connected to the DC transmission system on its DC side via its two DC terminals. Further, the first converter uses the set of connectors to disconnect the electrical connection from the DC transmission system and the second converter on its DC side. The first converter is also bypassed using the second bypass switch. [0048] In a converter station including converters connected in series as mentioned above, a process similar to one of the processes described in the foregoing embodiment for the case of a single converter in the pole can be used. Process to energize the converter. The advantage of this aspect is that it allows converters to be connected in series and allows a smoother start-up process. [0049] More specifically, the method may include: establishing a direct electrical connection between the DC terminals of the first converter (for example, by closing the first bypass switch); and electrically connecting the first converter to the AC power supply. Further, the AC voltage between the two electric phase lines can be obtained from the AC power supply and for a specific period of time, so as to charge the capacitor of the FB sub-module connected between the two electric phase lines. After the period of time, the switching device of the FB sub-module can be controlled for charging (by drawing power from the AC power supply) the capacitor of the HB sub-module to at least start the switching (or operation) of the switching device of the HB sub-module. The minimum voltage required. [0050] According to an embodiment, after the capacitor of the HB sub-module is charged to at least the minimum voltage required to start the device for switching the HB sub-module (for example, by opening the first bypass switch), the The DC terminals are electrically disconnected from each other. Alternatively, the DC terminals of the first converter may be electrically disconnected from each other before controlling the switching device of the FB sub-module to charge the capacitor of the HB sub-module to at least the minimum voltage required to start the device for switching the HB sub-module . [0051] According to an embodiment, the method may further include: using a set of connectors, electrically connecting the first DC terminal to The DC transmission line of the DC transmission system and electrically connects the second DC terminal to the second DC terminal of the second converter. [0052] According to an embodiment, the switching devices of the HB and FB sub-modules of the first converter can be controlled so that the DC current flowing from the DC transmission system through the second bypass switch is guided to the first converter. [0053] Further, when the DC current passing through the second bypass switch becomes approximately zero, the second bypass switch may be turned off. [0054] According to an embodiment, the DC voltage on the first converter may be increased to a first selected value to transfer/receive electric power to/from the DC transmission system. [0055] According to another aspect, there is provided a control unit adapted to control the charging of the converter (or converter station) according to any of the foregoing embodiments. [0056] According to yet another aspect, a converter station suitable for transmitting/receiving electric power is passed. The converter station may include a controller configured to operate at least one converter according to the method described in any of the foregoing embodiments. [0057] It will be appreciated that in the context of the present invention, the converter station may operate as an inverter and/or rectifier, depending on the situation and/or application. [0058] The present disclosure also provides a power transmission system including the converter station according to any one of the foregoing embodiments. [0059] It will be understood that all the embodiments described with reference to the first aspect of the present disclosure can be combined with any of the embodiments described with reference to the other aspects of the present disclosure, and vice versa. [0060] The present disclosure relates to all possible combinations of the features recited in the claims. The further objects and advantages of the various embodiments of the present disclosure will be described below with the help of exemplary embodiments. Description of the drawings [0061] Exemplary embodiments will be described below with reference to the accompanying drawings, in which: [0062] FIG. 1 is a schematic diagram of an FB unit or sub-module; [0063] FIG. 2 is a schematic diagram of an HB unit or sub-module; [0064] FIG. 3 is a schematic diagram of a valve arm including one FB unit and one HB unit connected in series, in which the flow of current in the unit is illustrated under blocking conditions; [0065] FIG. 4 illustrates a converter station including a single converter according to an embodiment; [0066] FIG. 5 is a schematic diagram of a converter station including a single converter such as in FIG. 4, wherein each valve arm includes a mixture of FB units and HB units, according to one embodiment; [0067] FIG. 6 is a flowchart of a start-up process for charging a converter station such as that shown in, for example, FIG. 5, according to an embodiment; [0068] FIG. 7 is a flowchart of a start-up process for charging a converter station such as that shown in, for example, FIG. 5 according to another embodiment; [0069] FIG. 8 is a schematic diagram of a converter station including two VSCs connected in series according to an embodiment; [0070] FIG. 9 is a schematic diagram of a converter station including two VSCs connected in series, such as in FIG. 8, according to one embodiment, where each valve arm includes a mixture of FB units and HB units; and [0071] FIG. 10 is a flowchart for the process of starting the operation of one of the two series-connected converters in the converter station. [0072] In the drawings, the same reference numerals will be used for the same elements unless otherwise noted. Unless explicitly stated to the contrary Otherwise, the drawings only show these elements necessary to illustrate the example embodiments, and for the sake of clarity, other elements may be omitted or merely implied. As illustrated in the drawings, for illustrative purposes, the sizes of elements and regions may be enlarged, and thus the sizes of these elements and regions are provided to illustrate the general structure of the embodiment. Detailed ways [0073] FIG. 1 illustrates an FB unit or sub-module 100. In the FB unit 100, four switching units 102 each including switching devices such as insulated gate bipolar transistors (IGBT) 101 and parallel freewheeling diodes 103 (for example, self-commutated electronic switching devices) are connected together with a charging capacitor 104 In the H-bridge configuration and charging capacitor 104. The FB unit 100 can be inserted into a circuit of any polarity. [0074] FIG. 2 illustrates an HB unit or sub-module 200. In the sub-unit 200, two switching units 202 of the switching device 102 of the FB unit described with reference to FIG. 1 are connected in series, and a parallel charging capacitor 204 is connected together. Since the HB unit 200 includes a smaller number of semiconductors (for example, there are only two IGBTs compared to the four IGBTs used in the sub-unit 100 of the FB-MMC), the manufacturing of the HB unit is not so expensive and can provide more Low loss. However, with respect to polarity, the HB unit cannot provide the same flexibility as the HB unit. [0075] It will be appreciated that the switching components may not be limited to IGBTs, and for example, they may be integrated gate commutated thyristors (IGCT), dual-mode insulated gate transistors (BIGT), etc. [0076] FIG. 3 shows that the valve arm 3000 FB unit 305 including one FB unit 305 and one HB unit 310 connected in series may be equivalent to the FB unit 100 described with reference to FIG. 1, and the HB unit 310 may be equivalent to Refer to the HB unit described in Figure 2. [0077] FIG. 3 also illustrates the flow of current in the cell under blocking conditions, where some of the switching devices of the FB cell 305 and the HB cell 310 or the diodes of the cell are forward biased, The other diodes are reverse biased. In Figure 3, the dashed arrows illustrate how current flows through the valve arm in a first direction, and the continuous arrows illustrate current flow in the opposite direction. [0078] As can be seen, in the current flow indicated by the continuous arrow, the current flows only through the capacitor of the FB unit 305, while in the current flow indicated by the dashed arrow, the current flows through the capacitor of the FB unit 305 and the HB The capacitors of the unit 310 are both. Therefore, in the charging process using AC electric power, the capacitor of the HB unit will be charged only during the half period when the AC signal is in, for example, the positive part (corresponding to the current direction indicated by the dashed arrow), while the capacitor of the FB unit will be charged at Both current directions are charged, regardless of whether the specific AC phase voltage is positive or negative. [0079] FIGS. 4 and 5 illustrate converter stations 400 and 500 according to some embodiments of the present disclosure. [0080] In this embodiment, the converter station 400 includes a voltage source converter VSC, which is a modular multi-level converter. The converter station is configured to convert between AC and DC electric power. The converter station 400 is an HVDC converter station, and on the DC side 420 includes two DC terminals 422, 424° for connecting with the DC transmission system 430. The DC transmission system 430 includes two DC transmission lines 432, 434, of which the first DC The transmission line 432 may be referred to as overhead line neutral, and the second DC transmission line 434 may be referred to as an overhead line pole, or vice versa. The voltage across the two DC transmission lines 432 and 434 is a DC voltage, which can be in the range of several hundred kV. Each DC transmission line 432 and 434 may represent a pole, and it may be assumed that, for example, with respect to ground, the DC transmission line 432 is arranged to carry a positive DC voltage, and the DC transmission line 434 is arranged to carry a negative DC voltage. [0081] The DC terminals 422, 424 of the converter station 400 may be conn
[DE EP3788707A1]: POTENTIALAUSGLEICHSYSTEM FÜR EINEN MODULAREN MULTILEVEL-STROMRICHTER [EN US11081972B2]: Potential equalization system for a modular multilevel converter [FR EP3788707A1]: SYSTÈME DE LIAISON ÉQUIPOTENTIELLE POUR UN CONVERTISSEUR MODULAIRE À PLUSIEURS NIVEAUX [ZH CN112425055A]: 用于模块化多电平变流器的电势均衡系统 | [DE WO2019242843A1]: Die Erfindung betrifft ein Potentialausgleichsystem für einen modularen Multilevel-Stromrichter (1) mit mehreren Stromrichtermodulen (3), die jeweils eine Gleichspannungsquelle (13) aufweisen. Das Potentialausgleichsystem umfasst Polkontakte (15), die jeweils mit einem Pol einer Gleichspannungsquelle (13) elektrisch verbunden sind, und wenigstens ein elektrisch leitfähiges Kontaktierelement (17), das zwischen einer ersten Endlage, in der es von den Stromrichtermodulen (3) elektrisch getrennt ist, und einer zweiten Endlage, in der es Polkontakte (15) verschiedener Gleichspannungsquellen (13) kontaktiert und auf ein Erdpotential legbar ist, bewegbar ist. [EN US11081972B2]: A potential equalization system for a modular multi-level converter. The converter has a plurality of converter modules and each of the modules has a direct current source. The potential equalization system includes pole contacts, which are each electrically connected to one pole of a direct current source, and at least one electrically conductive contacting element, which can be moved between a first end position in which the contacting element is electrically isolated from the converter modules and a second end position in which the contacting element contacts pole contacts of different direct current sources and can be put on ground potential. [FR WO2019242843A1]: L'invention concerne un système de liaison équipotentielle pour un convertisseur à plusieurs niveaux modulaire (1) comportant plusieurs modules convertisseurs (3), chacun d'eux ayant une source de tension continue (13). Le système de liaison équipotentielle comprend des contacts polaires (15) qui sont reliés électriquement chacun à un pôle d'une source de tension continue (13), et au moins un élément de contact électroconducteur (17) qui est mobile entre une première position finale, dans laquelle il est électriquement séparé des modules convertisseurs (3), et une seconde position finale, dans laquelle il est en contact avec des contacts polaires (15) de différentes sources de tension continue (13) et peut être relié à une terre. [ZH CN112425055A]: 本发明涉及一种用于模块化多电平变流器(1)的电势均衡系统，模块化多电平变流器具有多个变流器模块(3)，变流器模块分别具有直流电压源(13)。电势均衡系统包括极触点(15)和至少一个导电的接触元件(17)，这些极触点分别与直流电压源(13)的一个极电气连接，该接触元件能够在第一端位置与第二端位置之间移动，在第一端位置，接触元件与变流器模块(3)电气分离，在第二端位置，接触元件与不同的直流电压源(13)的极触点(15)接触并且能够置于地电势。 | WO2019242843A1 | 2019-12-26 | EP2018066230W | 2018-06-19 | EP2018066230W, 2018-06-19 | WO2019242843A1: 2019-12-26 CA3101379A1: 2019-12-26 EP3788707A1: 2021-03-10 CN112425055A: 2021-02-26 US11081972B2: 2021-08-03 | SIEMENS AG SIEMENS ENERGY GLOBAL GMBH & CO KG | ANHEUER MATHIAS BÖHME DANIEL DALLMEIER JOHANNES DÄUMLER FELIX EISMANN CHRISTOPHER GRIESSL JOHANNES HOLWEG JOHANN HUBER ADRIAN KAPELKE MARTIN RUDEK MICHAEL SCHRAMMEL CHRISTIAN STOLTZE TORSTEN WAHLE MARCUS WEBER JOHANNES BOHME DANIEL DAUMLER FELIX BOEHME DANIEL DAEUMLER FELIX | H02M1/44: I H01H31/00: I H02B1/16: I H02B13/075: I H02M7/483: I H05K9/00: I | H01H31/003: A H02M1/44: I H02M7/483: I H02M7/4835: A | WO2008074275A1 US2017129423A1 WO2017088922A1 WO2004093276A2 CN102185266A US2010059245A1 CN103050966A CN107710368A US3567949A US2007098419A1 US2010025126A1 US2011051371A1 US2011096575A1 US2012267955A1 US2017025866A1 US2018043789A1 US2018069469A1 US2018212530A1 US2018226882A1 US2019052187A1 US2019098777A1 US2019116778A1 US2019280614A1 US2019288526A1 US2019320549A1 US2020044580A1 US2020053900A1 US2020067421A1 US2020161987A1 US2020266725A1 US2020389084A1 US8120888B2 US2006124599A1 US2016329176A1 EP3236484A1 |  | [DE EP3788707A1]: Patentansprüche1. Potentialausgleichsystem für einen modularen Multilevel- Stromrichter (1), der mehrere Stromrichtermodule (3) mit jeweils einer Gleichspannungsquelle (13) aufweist, dasPotentialausgleichsystem umfassend - Polkontakte (15), die jeweils mit einem Pol einerGleichspannungsquelle (13) elektrisch verbunden sind, und- wenigstens ein elektrisch leitfähiges Kontaktierelement (17), das zwischen einer ersten Endlage, in der es von den Stromrichtermodulen (3) elektrisch getrennt ist, und einer zweiten Endlage, in der es Polkontakte (15) verschiedener Gleichspannungsquellen (13) kontaktiert und auf ein Erdpotential legbar ist, bewegbar ist. 2. Potentialausgleichsystem nach Anspruch 1 mit einemmanuellen, mechanischen oder elektrischen Antrieb (27) zum Bewegen des wenigstens einen Kontaktierelements (17) zwischen seinen beiden Endlagen. 3. Potentialausgleichsystem nach einem der vorhergehenden Ansprüche, wobei wenigstens ein Kontaktierelement (17) eine elektrische Abschirmung zum Abschirmen mehrererStromrichtermodule (3) ist, die um eine Drehachse (31) zwischen der ersten Endlage und der zweiten Endlage drehbar ist . 4. Potentialausgleichsystem nach Anspruch 3, wobei dieAbschirmung ein Abschirmrohr (29) aufweist, von demwenigstens ein Abschirmkontakt (33) absteht, der in der zweiten Endlage der Abschirmung wenigstens einenPolkontakt (15) kontaktiert, und die Drehachse (31) derAbschirmung eine Längsachse des Abschirmrohrs (29) ist. 5. Potentialausgleichsystem nach Anspruch 4, wobei wenigstens ein Abschirmkontakt (33) als ein an dem Abschirmrohr (29) angeordneter Henkel ausgebildet ist, der in der zweitenEndlage der Abschirmung mehrere Polkontakte (15) kontaktiert. 6. Potentialausgleichsystem nach einem der Ansprüche 3 bis 5, wobei die Abschirmung aus Aluminium gefertigt ist. 7. Potentialausgleichsystem nach einem der vorhergehenden Ansprüche, wobei wenigstens ein Kontaktierelement (17) ein elektrisch leitfähiges Kontaktseil ist, das an einemelektrisch isolierenden, über Polkontakte (15) verschiedener Gleichspannungsquellen (13) geführten Führungsseil (39) führbar ist, in der ersten Endlage an keinem Polkontakt (15) anliegt und in der zweiten Endlage an den Polkontakten (15), über die das Führungsseil (39) geführt ist, anliegt. 8. Potentialausgleichsystem nach Anspruch 7, wobei dasKontaktseil aus Kupfer gefertigt ist. 9. Potentialausgleichsystem nach Anspruch 7 oder 8, wobei das Führungsseil (39) über eine erste Seiltrommel (41) geführt ist, das Kontaktseil über eine zweite Seiltrommel (42) geführt ist und beide Seiltrommeln (41, 42) auf einermanuell, mechanisch oder elektrisch antreibbarenAntriebswelle (45) montiert sind. 10. Modularer Multilevel-Stromrichter (1), umfassend - mehrere Stromrichtermodule (3) mit jeweils einerGleichspannungsquelle (13) und - ein gemäß einem der vorhergehenden Ansprüche ausgebildetes Potentialausgleichsystem. 11. Modularer Multilevel-Stromrichter (1) nach Anspruch 10, wobei jede Gleichspannungsquelle (13) als ein Kondensator oder eine elektrische Verschaltung mehrerer Kondensatoren ausgebildet ist. 12. Modularer Multilevel-Stromrichter (1) nach Anspruch 10 oder 11, der mehrere Modulgruppen (5 bis 7) aufweist, die jeweils mehrere Stromrichtermodule (3) mit jeweils wenigstens einem Polkontakt (15) aufweisen, und dessen Potentialausgleichsystem für jede Modulgruppe (5 bis 7) ein Kontaktierelement (17) aufweist, das in seiner zweitenEndlage alle Polkontakte (15) der Modulgruppe (5 bis 7) kontaktiert . 13. Modularer Multilevel-Stromrichter (1) nach Anspruch 12, wobei alle Kontaktierelemente (17) in ihren zweiten Endlagen elektrisch miteinander verbunden sind. 14. Modularer Multilevel-Stromrichter (1) nach Anspruch 12 oder 13 mit einem gemeinsamen Antrieb (27), mit dem alle Kontaktierelemente (17) gleichzeitig antreibbar sind. 15. Modularer Multilevel-Stromrichter (1) nach einem der Ansprüche 10 bis 14, der als ein selbstgeführter Stromrichter ausgebildet ist. [EN US11081972B2]: 1. A potential equalization system for a modular multilevel power converter, the modular multilevel power converter having a plurality of power converter modules, each with a direct voltage source, the potential equalization system comprising: a plurality of pole contacts each electrically connected to a pole of a respective direct voltage source; andat least one, electrically conductive, contacting element rotatably mounted about an axis of rotation between a first end position, in which said at least one contacting element is electrically disconnected from the power converter modules, and a second end position, in which said at least one contacting element connects respective pole contacts of different direct voltage sources and in which said at least one contacting element is connected to ground potential;said at least one contacting element being an electrical shield for shielding said plurality of power converter modules;wherein said electrical shield includes a shield tube from which at least one shield contact protrudes which, in the second end position of said electrical shield, connects at least two pole contacts of said plurality of pole contacts, and wherein a longitudinal axis of said shield tube forms the axis of rotation of said electrical shield; andwherein said at least one shield contact is a handle arranged at said shield tube that connects said at least two pole contacts of said plurality of pole contacts in the second end position of said electrical shield. 2. The potential equalization system according to claim 1, further comprising a drive selected from the group consisting of a manual drive, a mechanical drive, and an electrical drive for moving the at least one contacting element between said first and second end positions. 3. The potential equalization system according to claim 1, wherein said electrical shield is an aluminum shield. 4. The potential equalization system according to claim 1, wherein said at least one contacting element is an electrically conductive contact cable to be guided by an electrically insulating guide cable guided via said pole contacts of different direct voltage sources, wherein said contact cable does not connect any of said pole contacts in the first end position and said contact cable connects said pole contacts in the second end position via which the guide cable is guided. 5. The potential equalization system according to claim 4, wherein said contact cable is a copper cable. 6. The potential equalization system according to claim 4, wherein said guide cable is guided by a first cable drum, said contact cable is guided by a second cable drum, and said first and second cable drums are mounted on a drive shaft to be driven manually, mechanically, or electrically. 7. A modular multilevel power converter, comprising: a plurality of power converter modules each having a direct voltage source and a pole contact carrying a direct voltage of the direct voltage source; anda potential equalization system including:at least one, electrically conductive, contacting element rotatably mounted about an axis of rotation between a first end position, in which said at least one contacting element is electrically disconnected from said power converter modules, and a second end position, in which said at least one contacting element connects said pole contacts of different direct voltage sources of said plurality of power converter modules and in which said at least one contacting element is connected to ground potential;said at least one contacting element being an electrical shield for shielding said plurality of power converter modules, said electrical shield having a shield tube from which at least one shield contact protrudes which, in the second end position of said electrical shield, connects at least two pole contacts of said pole contacts of said plurality of power converter modules;wherein a longitudinal axis of said shield tube forms the axis of rotation of said electrical shield; andwherein said at least one shield contact is a handle arranged at said shield tube that connects said at least two pole contacts of said pole contacts of said plurality of power converter modules in the second end position of said electrical shield. 8. The modular multilevel power converter according to claim 7, wherein each of said direct voltage sources is a capacitor or an electrical interconnection of a plurality of capacitors. 9. The modular multilevel power converter according to claim 7, comprising a plurality of module groups each formed with at least two of said plurality of power converter modules, and wherein each of said at least two of said plurality of power converter modules includes at least one pole contact of said pole contacts, and wherein each of said module groups has a respective contacting element for the respective said module group and which, in the second end position, connects all of said pole contacts of the respective said module group. 10. The modular multilevel power converter according to claim 9, wherein all of said contacting elements of said module groups are electrically connected to one another in the second end positions thereof. 11. The modular multilevel power converter according to claim 9, further comprising a common drive configured for driving all of said contacting elements of said module groups simultaneously. 12. The modular multilevel power converter according to claim 7, configured as a self-commutated power converter. 13. A potential equalization system for a modular multilevel power converter, the modular multilevel power converter having a plurality of power converter modules, each with a direct voltage source, the potential equalization system comprising: a plurality of pole contacts each electrically connected to a pole of a respective direct voltage source; andat least one, electrically conductive, contacting element rotatably mounted about an axis of rotation between a first end position, in which said at least one contacting element is electrically disconnected from the power converter modules, and a second end position, in which said at least one contacting element connects respective pole contacts of different direct voltage sources and in which said at least one contacting element is connected to ground potential;said at least one contacting element being an electrical shield for shielding said plurality of power converter modules;wherein said at least one contacting element is an electrically conductive contact cable to be guided by an electrically insulating guide cable guided via said pole contacts of different direct voltage sources, wherein said contact cable does not connect any of said pole contacts in the first end position and said contact cable connects said pole contacts in the second end position via which the guide cable is guided; andwherein said guide cable is guided by a first cable drum, said contact cable is guided by a second cable drum, and said first and second cable drums are mounted on a drive shaft to be driven manually, mechanically, or electrically. 14. The potential equalization system according to claim 13, wherein said electrical shield comprises a rotatably mounted shield tube from which at least one shield contact protrudes which, in the second end position of said electrical shield, connects at least one pole contact of said plurality of pole contacts, and a longitudinal axis of said shield tube forms the axis of rotation of said electrical shield. 15. The potential equalization system according to claim 14, wherein said at least one shield contact is a handle arranged at said shield tube that connects at least two pole contacts of said plurality of pole contacts in the second end position of said electrical shield. [ZH CN112425055A]: 1.一种用于模块化多电平变流器(1)的电势均衡系统，所述模块化多电平变流器具有 分别带有直流电压源(13)的多个变流器模块(3)，所述电势均衡系统包括 -极触点(15)，所述极触点分别与直流电压源(13)的一个极电气连接，和 -至少一个导电的接触元件(17)，所述接触元件能够在第一端位置与第二端位置之间 移动，在所述第一端位置，所述接触元件与所述变流器模块⑶电气分离，在所述第二端位 置，所述接触元件与不同的直流电压源(13)的极触点(15)接触并且能够置于地电势。 2 .根据权利要求1所述的电势均衡系统，所述电势均衡系统具有手动、机械或电气的驱 动器(27)，以使至少一个接触元件(17)在其两个端位置之间移动。 3 .根据上述权利要求中任一项所述的电势均衡系统，其中，至少一个接触元件(17)是 用于屏蔽多个变流器模块⑶的电气屏蔽部，所述屏蔽部能够围绕旋转轴(31)在第一端位 置与第二端位置之间旋转。 4 .根据权利要求3所述的电势均衡系统，其中，所述屏蔽部具有屏蔽管(29)，从所述屏 蔽管突出至少一个屏蔽触点(33)，所述屏蔽触点在屏蔽部的第二端位置接触至少一个极触 点(15)，并且屏蔽部的旋转轴(31)是屏蔽管(29)的纵轴。 5 .根据权利要求4所述的电势均衡系统，其中，至少一个屏蔽触点(33)被构建为布置在 屏蔽管(29)处的柄，所述柄在屏蔽部的第二端位置接触多个极触点(15)。 6 .根据权利要求3至5中任一项所述的电势均衡系统，其中，所述屏蔽部由铝制成。 7 .根据上述权利要求中任一项所述的电势均衡系统，其中，至少一个接触元件(17)是 导电的接触缆线,所述接触缆线能够在电气绝缘的引导缆线(39)上被引导,所述引导缆线 被引导经过不同的直流电压源(13)的极触点(15)，所述接触缆线在第一端位置不与极触点 (15)毗连并且在第二端位置与所述引导缆线(39)所引导经过的极触点(15)毗连。 8 .根据权利要求7所述的电势均衡系统，其中，所述接触缆线由铜制成。 9 .根据权利要求7或8所述的电势均衡系统，其中，所述引导缆线(39)被引导经过第一 缆线卷筒(41)，所述接触缆线被引导经过第二缆线卷筒(42)，并且两个缆线卷筒(41，42)安 装在驱动轴(45)上，所述驱动轴能够手动、机械或电气地驱动。 10 .一种模块化多电平变流器(1)，所述模块化多电平变流器包括 -分别带有直流电压源(13)的多个变流器模块(3)，和 -根据上述权利要求中任一项来构建的电势均衡系统。 11 .根据权利要求10所述的模块化多电平变流器(1)，其中，每个直流电压源(13)被构 建为电容器或多个电容器的电气互连。 12 .根据权利要求10或11所述的模块化多电平变流器(1)，所述模块化多电平变流器具 有多个模块组(5至7)，所述多个模块组分别具有多个变流器模块(3)，所述多个变流器模块 分别具有至少一个极触点(15)，并且模块化多电平变流器的电势均衡系统对于每个模块组 (5至7)具有接触元件(17)，所述接触元件在其第二端位置接触模块组(5至7)的所有极触点 (15)。 13 .根据权利要求12所述的模块化多电平变流器(1)，其中，所有接触元件(17)在其第 二端位置彼此电气连接。 14 .根据权利要求12或13所述的模块化多电平变流器(1)，所述模块化多电平变流器具 有共同的驱动器(27)，利用所述共同的驱动器能够同时驱动所有接触元件(17)。 15 .根据权利要求10至14中任一项所述的模块化多电平变流器（1） 变流器被构建为自换向变流器。 ，所述模块化多电平 | [DE EP3788707A1]: Beschreibung Potentialausgleichsystem für einen modularen Multilevel- Stromrichter Die Erfindung betrifft einen modularen Multilevel- Stromrichter mit mehreren Stromrichtermodulen, die jeweils eine Gleichspannungsquelle, beispielsweise einen Kondensator, aufweisen . Um Wartungsarbeiten an einem solchen Stromrichter auszuführen, muss vorher sichergestellt sein, dass die Gleichspannungsquellen entladen sind und mindestens ein Pol jeder Gleichspannungsquelle auf Erdpotential liegt. Beispielsweise wird die Potentialanbindung über eine hohe Anzahl in Reihe geschalteter Schiebekontakte oder durch von Hand eingelegte Überbrückungsseile erreicht. Die hohe Anzahl von in Reihe geschalteten Kontakten kann bei Ausfall von zwei Kontakten jedoch zu einer Unterbrechung des Erdpotentials führen . Der Erfindung liegt die Aufgabe zugrunde, ein Potentialausgleichsystem für einen modularen Multilevel- Stromrichter mit mehreren Stromrichtermodulen, die jeweils eine Gleichspannungsquelle aufweisen, anzugeben, das die Anbindbarkeit der Gleichspannungsquellen an ein Erdpotential verbessert . Die Aufgabe wird erfindungsgemäß durch ein Potentialausgleichsystem mit den Merkmalen des Anspruchs 1 und einen modularen Multilevel-Stromrichter mit den Merkmalen des Anspruchs 10 gelöst. Vorteilhafte Ausgestaltungen der Erfindung sind Gegenstand der Unteransprüche. Ein erfindungsgemäßes Potentialausgleichsystem für einen modularen Multilevel-Stromrichter, der mehrere Stromrichtermodule (3) mit jeweils einer Gleichspannungsquelle (13) aufweist, umfasst Polkontakte, die jeweils mit einem Pol einer Gleichspannungsquelle elektrisch verbunden sind, und wenigstens ein elektrisch leitfähiges Kontaktierelement, das zwischen einer ersten Endlage, in der es von den Stromrichtermodulen elektrisch getrennt ist, und einer zweiten Endlage, in der es Polkontakte verschiedener Gleichspannungsquellen kontaktiert und auf ein Erdpotential legbar ist, bewegbar ist, beispielsweise durch einen manuellen, mechanischen oder elektrischen Antrieb. Bei einem erfindungsgemäßen Potentialausgleichsystem für einen modularen Multilevel-Stromrichter können also Pole von Gleichspannungsquellen verschiedener Stromrichtermodule des Stromrichters auf ein Erdpotential gelegt werden, indem mit den Polen jeweils verbundene Polkontakte durch ein Kontaktierelement elektrisch miteinander verbunden werden und das Kontaktierelement auf das Erdpotential gelegt wird. Dadurch bleiben bei einem Ausfall einzelner Polkontakte die über die anderen Polkontakte mit dem Kontaktierelement verbundenen Gleichspannungsquellen an das Erdpotential angeschlossen. Dies erhöht vorteilhaft die Sicherheit der Anbindung vieler Gleichspannungsquellen an das Erdpotential gegenüber einer Anbindung über eine Vielzahl in Reihe geschalteter Kontakte. Eine Ausgestaltung der Erfindung sieht vor, dass wenigstens ein Kontaktierelement eine elektrische Abschirmung zum Abschirmen mehrerer Stromrichtermodule ist, die um eine Drehachse zwischen der ersten Endlage und der zweiten Endlage drehbar ist. Beispielsweise weist die Abschirmung ein Abschirmrohr auf, von dem wenigstens ein Abschirmkontakt absteht, der in der zweiten Endlage der Abschirmung wenigstens einen Polkontakt kontaktiert, und die Drehachse der Abschirmung ist eine Längsachse des Abschirmrohrs. Beispielsweise ist wenigstens ein Abschirmkontakt als ein an dem Abschirmrohr angeordneter Henkel ausgebildet, der in der zweiten Endlage der Abschirmung mehrere Polkontakte kontaktiert. Die Abschirmung ist beispielsweise aus Aluminium gefertigt . Die vorgenannten Ausgestaltungen der Erfindung nutzen eine in der Regel ohnehin erforderliche Abschirmung von Stromrichtermodulen als ein Kontaktierelement beziehungsweise versehen das Kontaktierelement mit einer Abschirmfunktion. Dadurch wird der Material- und Konstruktionsaufwand gegenüber separat ausgeführten Abschirmungen und Kontaktierelementen vorteilhaft reduziert. Eine weitere Ausgestaltung der Erfindung sieht vor, dass wenigstens ein Kontaktierelement ein elektrisch leitfähiges Kontaktseil, beispielsweise ein Kupferseil, ist, das an einem elektrisch isolierenden, über Polkontakte verschiedener Gleichspannungsquellen geführten Führungsseil führbar ist, in der ersten Endlage an keinem Polkontakt anliegt und in der zweiten Endlage an den Polkontakten, über die das Führungsseil geführt ist, anliegt. Beispielsweise ist das Führungsseil über eine erste Seiltrommel geführt, das Kontaktseil ist über eine zweite Seiltrommel geführt und beide Seiltrommeln sind auf einer manuell, mechanisch oder elektrisch antreibbaren Antriebswelle montiert. Ein als Kontaktseil ausgebildetes Kontaktierelement ermöglicht eine der räumlichen Verteilung der Polkontakte flexibel anpassbare elektrische Verbindung der Polkontakte, insbesondere auch eine Verbindung räumlich relativ weit voneinander entfernter Polkontakte. Ein erfindungsgemäßer modularer Multilevel-Stromrichter, insbesondere ein selbstgeführter modularer Multilevel- Stromrichter, umfasst mehrere Stromrichtermodule mit jeweils einer Gleichspannungsquelle, die beispielsweise als ein Kondensator oder eine elektrische Verschaltung mehrerer Kondensatoren ausgebildet ist, und ein erfindungsgemäßes Potentialausgleichsystem. Die Vorteile eines derartigen Stromrichters ergeben sich aus den oben bereits genannten Vorteilen eines erfindungsgemäßen Potentialausgleichsystems und werden daher hier nicht noch einmal aufgeführt. Bei einer weiteren Ausgestaltung der Erfindung weist der Stromrichter mehrere Modulgruppen auf, die jeweils mehrere Stromrichtermodule mit jeweils wenigstens einem Polkontakt aufweisen. Für jede Modulgruppe weist das Potentialausgleichsystem ein Kontaktierelement auf, das in seiner zweiten Endlage alle Polkontakte der Modulgruppe kontaktiert. Diese Ausgestaltung der Erfindung berücksichtigt, dass die Stromrichtermodule eines modularen Multilevel-Stromrichters häufig mehrere Modulgruppen bilden, die beispielsweise räumlich voneinander beabstandet angeordnet sind. In diesem Fall kann es vorteilhaft sein, für jede Modulgruppe ein Kontaktierelement vorzusehen. Dabei kann vorgesehen sein, dass alle Kontaktierelemente in ihren zweiten Endlagen elektrisch miteinander verbunden sind. Dies vereinfacht vorteilhaft die Anbindung an das Erdpotential. Ferner kann ein gemeinsamer Antrieb vorgesehen sein, mit dem alle Kontaktierelemente gleichzeitig antreibbar sind. Dadurch kann einerseits der Kosten- und Materialaufwand für das Bewegen der Kontaktierelemente reduziert werden und andererseits können die Bewegungen der Kontaktierelemente einfacher synchronisiert werden. Die oben beschriebenen Eigenschaften, Merkmale und Vorteile dieser Erfindung sowie die Art und Weise, wie diese erreicht werden, werden klarer und deutlicher verständlich im Zusammenhang mit der folgenden Beschreibung von Ausführungsbeispielen, die im Zusammenhang mit den Zeichnungen näher erläutert werden. Dabei zeigen: FIG 1 einen Schaltplan eines modularen Multilevel- Stromrichters, FIG 2 als Abschirmungen ausgebildete Kontaktierelemente und einen Antrieb zum Bewegen der Abschirmungen, FIG 3 eine perspektivische Darstellung von Polkontakten und eines als Abschirmung ausgebildeten Kontaktierelements in einer ersten Endlage der Abschirmung, FIG 4 eine perspektivische Darstellung der in Figur 3 gezeigten Polkontakte und der Abschirmung in einer zweiten Endlage der Abschirmung, FIG 5 Polkontakte und ein als ein Kontaktseil ausgebildetes Kontaktierelement, das an einem Führungsseil geführt wird, in einer Zwischenlage des Kontaktseils , FIG 6 die in Figur 5 gezeigten Polkontakte und das an dem Führungsseil geführte Kontaktseil in einer zweiten Endlage des Kontaktseils . Einander entsprechende Teile sind in den Figuren mit den gleichen Bezugszeichen versehen. Figur 1 zeigt einen Schaltplan eines selbstgeführten modularen Multilevel-Stromrichters 1. Der Stromrichter 1 weist mehrere im Normalbetrieb des Stromrichters 1 in Reihe geschaltete Stromrichtermodule 3 auf, von denen nur einige dargestellt sind. Die Stromrichtermodule 3 bilden drei übereinander angeordnete Modulgruppen 5 bis 7. Ferner weist der Stromrichter 1 ein erfindungsgemäßes Potentialausgleichsystem auf, das für jede Modulgruppe 5 bis 7 ein elektrisch leitfähiges Kontaktierelement 17 und für jedes Stromrichtermodul 3 einen Polkontakt 15 aufweist. Jedes Stromrichtermodul 3 weist eine Halbbrücke aus Halbleiterschaltern 9 auf, die beispielsweise jeweils als ein Bipolartransistor mit isoliertem Gate (IGBT = Insulated-Gate Bipolar Transistor) ausgebildet sind, zu dem eine Freilaufdiode 11 antiparallel geschaltet ist. Ferner weist jedes Stromrichtermodul 3 eine Gleichspannungsquelle 13 auf, die als ein Kondensator ausgebildet ist. Ein Pol der Gleichspannungsquelle 13 ist mit dem Polkontakt 15 des Stromrichtermoduls 3 elektrisch verbunden, über den der Pol elektrisch kontaktierbar ist. Das Kontaktierelement 17 jeder Modulgruppe 5 bis 7 ist zwischen einer ersten Endlage, in der es von den Stromrichtermodulen 3 der Modulgruppe 5 bis 7 elektrisch getrennt ist, und einer zweiten Endlage, in der es alle Polkontakte 15 der Modulgruppe 5 bis 7 kontaktiert und die Gleichspannungsquellen 13 der Stromrichtermodule 3 der Modulgruppe 5 bis 7 parallel schaltet, bewegbar. Das Kontaktierelement 17 einer ersten Modulgruppe 5 kontaktiert in seiner zweiten Endlage zusätzlich einen Erdungskontakt 19, an den über einen ersten Erdungsschalter 21 ein Erdpotential legbar ist. Das Kontaktierelement 17 einer zweiten Modulgruppe 6 kontaktiert in seiner zweiten Endlage zusätzlich einen ersten Verbindungskontakt 23, der elektrisch mit einem Polkontakt 15 der ersten Modulgruppe 5 verbunden ist. Das Kontaktierelement 17 der dritten Modulgruppe 7 kontaktiert in seiner zweiten Endlage zusätzlich einen zweiten Verbindungskontakt 25, der elektrisch mit einem Polkontakt 15 der zweiten Modulgruppe 6 verbunden ist. An einen Polkontakt 15 der dritten Modulgruppe 7 ist über einen zweiten Erdungsschalter 22 das Erdpotential legbar. Wenn sich alle Kontaktierelemente 17 in ihrer zweiten Endlage befinden, ist daher durch Schließen wenigstens eines Erdungsschalters 21, 22 das Erdpotential an alle Polkontakte 15 legbar. Jedes Kontaktierelement 17 ist über einen Antrieb 27 zwischen seinen beiden Endlagen bewegbar. Die Antriebe 27 der Kontaktierelemente 17 können auch als ein gemeinsamer Antrieb 27 für alle Kontaktierelemente 17 ausgeführt sein. Figur 2 zeigt als Abschirmungen ausgebildete Kontaktierelemente 17 und einen gemeinsamen Antrieb 27 für die Kontaktierelemente 17. Jede Abschirmung ist zum Abschirmen der Stromrichtermodule 3 einer Modulgruppe 5 bis 7 ausgebildet . Jede Abschirmung weist ein Abschirmrohr 29 auf und ist um eine Drehachse 31, die eine Längsachse des Abschirmrohrs 29 ist, zwischen seinen beiden Endlagen drehbar. Von jedem Abschirmrohr 29 steht ein Abschirmkontakt 33 ab, der als ein an dem Abschirmrohr 29 angeordneter Henkel ausgebildet ist. Die Abschirmungen sind beispielsweise aus Aluminium gefertigt . Der Antrieb 27 umfasst eine Antriebsstange 35, die manuell, mechanisch oder elektrisch angetrieben um ihre Längsachse drehbar ist, und für jedes Abschirmrohr 29 ein Getriebeelement 37, das aus einer Drehung der Antriebsstange 35 um deren Längsachse eine Drehung des Abschirmrohrs 29 um die Drehachse 31 bewirkt. Beispielsweise bilden die Antriebsstange 35 und jedes Getriebeelement 37 ein Schneckengetriebe, wobei die Antriebsstange 35 als Schnecke des Schneckengetriebes ausgebildet ist und das Getriebeelement 37 als Schneckenrad des Schneckengetriebes ausgebildet ist. Die Figuren 3 und 4 zeigen zwei Polkontakte 15 einer Modulgruppe 5 bis 7 und einen Abschnitt einer dazu gehörenden Abschirmung in den beiden Endlagen der Abschirmung, wobei Figur 3 die erste Endlage zeigt und Figur 4 die zweite Endlage zeigt. Die Polkontakte 15 der Modulgruppe 5 bis 7 sind entlang einer Parallelen zu der Drehachse 31 der Abschirmung nebeneinander angeordnet. In der ersten Endlage der Abschirmung ist der Abschirmkontakt 33 der Abschirmung von den Polkontakten 15 beabstandet. In der zweiten Endlage ist das Abschirmrohr 29 gegenüber der ersten Endlage um etwa 90 Grad um die Drehachse 31 gedreht und der Abschirmkontakt 33 der Abschirmung liegt an den Polkontakten 15 an. Die Figuren 5 und 6 zeigen Polkontakte 15 und ein als ein elektrisch leitfähiges Kontaktseil ausgebildetes Kontaktierelement 17, das an einem elektrisch isolierenden Führungsseil 39 geführt wird. Das Führungsseil 39 ist über eine erste Seiltrommel 41, Umlenkrollen 43, die Polkontakte 15 und einen Erdungskontakt 19 geführt. Das Kontaktseil ist in seiner ersten Endlage auf einer zweiten Seiltrommel 42 aufgewickelt und wird mit dem Führungsseil 39 von der ersten Endlage über eine in Figur 5 gezeigte Zwischenlage in die in Figur 6 gezeigte zweite Endlage gezogen, in der es an allen Polkontakten 15 und dem Erdungskontakt 19 anliegt. Das Kontaktseil ist beispielsweise aus Kupfer gefertigt. Die Seiltrommeln 41, 42 sind auf einer Antriebswelle 45 montiert, die manuell, mechanisch oder elektrisch antreibbar ist . Obwohl die Erfindung im Detail durch bevorzugte Ausführungsbeispiele näher illustriert und beschrieben wurde, so ist die Erfindung nicht durch die offenbarten Beispiele eingeschränkt und andere Variationen können vom Fachmann hieraus abgeleitet werden, ohne den Schutzumfang der Erfindung zu verlassen. Bezugs zeichenliste 1 Stromrichter 3 Stromrichtermodul 5 bis 7 Modulgruppe 9 HalbleiterSchalter 11 Freilaufdiode 13 Gleichspannungsquelle 15 Polkontakt 17 Kontaktierelement 19 Erdungskontakt 21, 22 ErdungsSchalter 23, 25 Verbindungskontakt 27 Antrieb 29 Abschirmrohr 31 Drehachse 33 Abschirmkontakt 35 AntriebsStange 37 Getriebeelernent 39 Führungsseil 41, 42 Seiltrommel 43 Umlenkrolle 45 Antriebswelle [EN US11081972B2]: BACKGROUND OF THE INVENTION Field of the Invention The invention relates to a modular multilevel power converter with a plurality of power converter modules each of which comprises a direct voltage source, for example a capacitor. In order to perform maintenance work on such a power converter, it is necessary to ensure beforehand that the direct voltage sources are discharged, and that at least one pole of each direct voltage source is at ground potential. The potential connection is, for example, achieved through a large number of sliding contacts connected in series, or through manually inserted bridging cables. However, if two contacts fail the large number of contacts connected in series can lead to interrupting the ground potential. SUMMARY OF THE INVENTION The invention is based on the object of providing a potential equalization system for a modular multilevel power converter with a plurality of power converter modules each of which comprises a direct voltage source, which improves the connectability of the direct voltage sources to a ground potential. The object is achieved according to the invention through a potential equalization system as claimed and a modular multilevel power converter as claimed. Advantageous elaborations of the invention are the object of the subsidiary claims. A potential equalization system according to the invention for a modular multilevel power converter that comprises a plurality of power converter modules (3), each with a direct voltage source (13), comprises pole contacts, each of which is electrically connected to one pole of a direct voltage source, and at least one electrically conductive contacting element that is movable between a first end position in which it is electrically disconnected from the power converter modules and a second end position in which it contacts pole contacts of different direct voltage sources and which can be placed at a ground potential, for example by a manual, mechanical or electrical drive. Thus in a potential equalization system for a modular multilevel power converter according to the invention, poles of direct voltage sources of different power converter modules of the power converter can be placed at a ground potential in that pole contacts, each of which is joined to the poles, are electrically connected to one another by a contacting element, and the contacting element is placed at the ground potential. As a result, in the event of a failure of individual pole contacts, the direct voltage sources that are connected via the other pole contacts to the contacting element remain connected to the ground potential. This advantageously increases the safety of the connection of many direct voltage sources to the ground potential in comparison to a connection through a plurality of contacts connected in series. One embodiment of the invention provides that at least one contacting element is an electrical shield (i.e., a shielding screen) for shielding a plurality of power converter modules that can be rotated about an axis of rotation between the first end position and the second end position. The electrical shield for example comprises a shielding tube (shield tube) from which at least one shield contact protrudes which, in the second end position of the shield, contacts at least one pole contact, and the axis of rotation of the shield is a longitudinal axis of the shield tube. At least one shield contact is, for example, designed as a handle arranged at the shield tube which, in the second end position of the shield, contacts a plurality of pole contacts. The shield is, for example, manufactured of aluminum. The elaborations of the invention referred to above make use of a shield of power converter modules, which is a rule is in any case necessary, as a contacting element, or they provide the contacting element with a shielding function. The material and construction effort is thereby advantageously reduced in comparison with separately implemented shields and contacting elements. A further elaboration of the invention provides that at least one contacting element is an electrically conductive contact cable, for example a copper cable, that can be guided by an electrically insulating guide cable guided via pole contacts of different direct voltage sources, is, in the first end position, not adjacent to any pole contact and is, in the second end position, adjacent to the pole contacts via which the guide cable is guided. The guide cable is, for example, guided by a first cable drum, the contact cable is guided by a second cable drum, and both cable drums are mounted on a drive shaft that can be driven manually, mechanically, or electrically. A contacting element implemented as a contact cable enables an electrical connection of the pole contacts that can be adjusted flexibly to the spatial distribution of the pole contacts, and also in particular a connection of pole contacts that are spaced relatively far apart from one another. A modular multilevel power converter according to the invention, in particular a self-commutated modular multilevel power converter, comprises a plurality of power converter modules, each with a direct voltage source which is for example designed as a capacitor or as an electrical interconnection of a plurality of capacitors, and a potential equalization system according to the invention. The advantages of a power converter of this sort result from the advantages referred to above of a potential equalization system according to the invention, and are therefore not described here again. In a further elaboration of the invention, the power converter comprises a plurality of module groups each of which comprises a plurality of power converter modules, each with at least one pole contact. For each module group, the potential equalization system comprises a contacting element that contacts all the pole contacts of the module group in its second end position. This elaboration of the invention takes into consideration the fact that the power converter modules of a modular multilevel power converter frequently form a plurality of module groups that are, for example, disposed at a spatial distance from one another. In this case it can be advantageous to provide a contacting element for each module group. It can be provided here that all the contacting elements are electrically connected together in their second end positions. This advantageously simplifies the connection to the ground potential. A common drive can furthermore be provided with which all the contacting elements can be driven simultaneously. As a result, the expenditure of costs and material for moving the contact elements can on the one hand be reduced, and the movements of the contacting elements can on the other hand be more easily synchronized. The above-described properties, features and advantages of this invention, as well as the manner in which these are achieved, will be made clearer and more easily understandable in connection with the following description of exemplary embodiments that are explained in more detail in connection with the drawings. BRIEF DESCRIPTION OF THE SEVERAL VIEWS OF THE DRAWING FIG. 1 shows a circuit diagram of a modular multilevel power converter, FIG. 2 shows contacting elements designed as shields, and a drive for moving the shields, FIG. 3 shows a perspective illustration of pole contacts and a contacting element designed as a shield in a first end position of the shield, FIG. 4 shows a perspective illustration of the pole contacts shown in FIG. 3 and the shield in a second end position of the shield, FIG. 5 shows pole contacts and a contacting element designed as a contact cable that is guided at a guide cable in an intermediate position of the contact cable, FIG. 6 shows the pole contacts shown in FIG. 5 and the contact cable guided at the guide cable in a second end position of the contact cable. DETAILED DESCRIPTION OF THE INVENTION Parts that correspond to one another are given the same reference signs in the figures. FIG. 1 shows a circuit diagram of a self-commutated modular multilevel power converter 1. The power converter 1 comprises a plurality of power converter modules 3 that are connected in series when the power converter 1 is in normal operation, of which only a few are illustrated. The power converter modules 3 form three module groups 5 to 7 arranged one above the other. The power converter 1 further comprises a potential equalization system according to the invention that comprises an electrically conductive contacting element 17 for each module group 5 to 7, and a pole contact 15 for each power converter module 3. Each power converter module 3 comprises a half-bridge of semiconductor switches 9 each of which is, for example, designed as a bipolar transistor with an insulated gate (IGBT: insulated gate bipolar transistor), with which a freewheeling diode 11 is connected antiparallel. Each power converter module 3 further comprises a direct voltage source 13 that is designed as a capacitor. One pole of the direct voltage source 13 is electrically connected to the pole contact 15 of the power converter module 3, via which the pole can be electrically contacted. The contacting element 17 of each module group 5 to 7 can be moved between a first end position in which it is electrically disconnected from the power converter modules 3 of the module group 5 to 7, and a second end position, in which it contacts all of the pole contacts 15 of the module group 5 to 7 and connects the direct voltage sources 13 of the power converter modules 3 of the module group 5 to 7 in parallel. The contacting element 17 of a first module group 5 also contacts, in its second end position, a grounding contact 19 to which a ground potential can be applied via a first grounding switch 21. The contacting element 17 of a second module group 6 also contacts, in its second end position, a first connecting contact 23 that is electrically connected to a pole contact 15 of the first module group 5. The contacting element 17 of the third module group 7 also contacts, in its second end position, a second connecting contact 25 that is electrically connected to a pole contact 15 of the second module group 6. The ground potential can be applied via a second grounding switch 22 to a pole contact 15 of the third module group 7. When all of the contacting elements 17 are in their second end position, the ground potential can therefore be applied to all the pole contacts 15 by closing at least one grounding switch 21, 22. Each contacting element 17 can be moved by a drive 27 between its two end positions. The drives 27 of the contacting elements 17 can also be implemented as a common drive 27 for all contacting elements 17. FIG. 2 shows contacting elements 17 designed as shields, and a common drive 27 for the contacting elements 17. Each shield is designed to shield the power converter modules 3 of a module group 5 to 7. Each shield comprises a shield tube 29 and can be rotated between its two end positions about an axis of rotation 31 that is a longitudinal axis of the shield tube 29. A shield contact 33 protrudes from each shield tube 29, and is designed as a handle arranged at the shield tube 29. The shields are manufactured, for example, from aluminum. The drive 27 comprises a drive bar 35 that can be rotated about its longitudinal axis under manual, mechanical or electrical drive, and for each shield tube 29 a gear element 37 that brings about a rotation of the shield tube 29 about the axis of rotation 31 from a rotation of the drive bar 35 about its longitudinal axis. For example, the drive bar 35 and each gear element 37 form a worm gear, wherein the drive bar 35 is designed as the worm of the worm gear, and the gear element 37 is designed as the worm wheel of the worm gear. The FIGS. 3 and 4 show two pole contacts 15 of a module group 5 to 7, and a section of a shield that belongs to it in the two end positions of the shield, wherein FIG. 3 shows the first end position and FIG. 4 shows the second end position. The pole contacts 15 of the module group 5 to 7 are arranged next to one another along a line parallel to the axis of rotation 31 of the shield. In the first end position of the shield, the shield contact 33 of the shield is at a position away from the pole contacts 15. In the second end position, the shield tube 29 is rotated through about 90 degrees about the axis of rotation 31 with respect to the first end position, and the shield contact 33 of the shield is adjacent to the pole contacts 15. FIGS. 5 and 6 show pole contacts 15 and a contacting element 17 designed as an electrically conductive contact cable that is guided at an electrically insulating guide cable 39. The guide cable 39 is guided via a first cable drum 41, deflection rollers 43, the pole contacts 15 and a grounding contact 19. When in its first end position, the contact cable is wound around a second cable drum 42, and is pulled by the guide cable 39 from the first end position, via an intermediate position shown in FIG. 5, into the second end position shown in FIG. 6, in which it is adjacent to all of the pole contacts 15 and the grounding contact 19. The contact cable is manufactured, for example, from copper. The cable drums 41, 42 are mounted on a drive shaft 45 that can be driven manually, mechanically or electrically. Although the invention has been illustrated and described in more detail through preferred exemplary embodiments, the invention is not restricted by the disclosed examples, and other variations can be derived from this by the expert without leaving the protective scope of the invention. LIST OF REFERENCE SIGNS 1 Power converter 3 Power converter module 5 to 7 Module group 9 Semiconductor switch 11 Freewheeling diode 13 Direct voltage source 15 Pole contact 17 Contacting element 19 Grounding contact 21, 22 Grounding switch 23, 25 Connecting contact 27 Drive 29 Shield tube 31 Axis of rotation 33 Shield contact 35 Drive bar 37 Gear element 39 Guide cable 41, 42 Cable drum 43 Deflection roller 45 Drive shaft [ZH CN112425055A]: 用于模块化多电平变流器的电势均衡系统 技术领域 [0001]本发明涉及一种具有多个变流器模块的模块化多电平变流器，这些变流器模块分 别具有直流电压源、例如电容器。 背景技术 [0002] 为了对这种变流器实施维护工作，必须事先确保直流电压源已放电，并且每个直 流电压源的至少一个极处于地电势。例如，通过大量串联连接的滑动触点或通过手动插入 的桥接缆线来实现电势连接。然而，在两个触点发生故障的情况下，大量串联连接的触点可 能导致地电势中断。 发明内容 [0003]本发明要解决的技术问题是，提供一种用于具有多个变流器模块的模块化多电平 变流器的电势均衡系统，这些变流器模块分别具有直流电压源，该电势均衡系统改善了直 流电压源到地电势的可连接性。 [0004]根据本发明，上述技术问题通过具有权利要求1的特征的电势均衡系统和具有权 利要求10的特征的模块化多电平变流器来解决。 [0005]本发明的有利的设计方案是从属权利要求的主题。 [0006]根据本发明的用于模块化多电平变流器的电势均衡系统包括极触点和至少一个 导电的接触元件，该模块化多电平变流器具有分别带有直流电压源（13）的多个变流器模块 ⑶，该极触点分别与直流电压源的一个极电气连接，该接触元件可以例如通过手动、机械 或电气的驱动器，在第一端位置与第二端位置之间移动，在该第一端位置接触元件与变流 器模块电气分离，在该第二端位置接触元件与不同的直流电压源的极触点接触并且可置于 地电势。 [0007]因此，在根据本发明的用于模块化多电平变流器的电势均衡系统中，通过由接触 元件将分别与极连接的极触点彼此电气连接并且将接触元件置于地电势，可以将变流器的 不同变流器模块的直流电压源的极置于地电势。由此，在各个极触点发生故障的情况下，经 由另外的极触点与接触元件连接的直流电压源保持与地电势连接。相对于经由串联连接的 多个触点的连接，这有利地提高了多个直流电压源到地电势的连接的安全性。 [0008]本发明的一种设计方案规定，至少一个接触元件是用于屏蔽多个变流器模块的电 气屏蔽部，该屏蔽部可以围绕旋转轴在第一端位置与第二端位置之间旋转。例如，屏蔽部具 有屏蔽管，从屏蔽管突出至少一个屏蔽触点，该屏蔽触点在屏蔽部的第二端位置接触至少 一个极触点，并且屏蔽部的旋转轴是屏蔽管的纵轴。例如，至少一个屏蔽触点被构建为布置 在屏蔽管处的柄，该柄在屏蔽部的第二端位置接触多个极触点。屏蔽部例如由铝制成。 [0009]本发明的上述设计方案利用通常本来就需要的变流器模块的屏蔽部作为接触元 件，或者为接触元件设置屏蔽功能。由此，相对于分开实施的屏蔽部和接触元件，有利地减 少了材料开销和结构开销。 [0010]本发明的另外的设计方案规定，至少一个接触元件是导电的接触缆线、例如铜缆 线，该接触缆线可以在电气绝缘的引导缆线上被引导，该引导缆线被引导经过不同的直流 电压源的极触点，该接触缆线在第一端位置不与极触点毗连并且在第二端位置与引导缆线 所引导经过的极触点毗连。例如，引导缆线被引导经过第一缆线卷筒，接触缆线被引导经过 第二缆线卷筒，并且两个缆线卷筒都安装在驱动轴上，该驱动轴可以手动、机械或电气地驱 动。 [0011]构建为接触缆线的接触元件能够实现可与极触点的空间分布灵活匹配地电气连 接极触点，特别是还能够实现连接空间上彼此相距相对远的极触点。 [0012]根据本发明的模块化多电平变流器、特别是自换向模块化多电平变流器包括多个 变流器模块和根据本发明的电势均衡系统，多个变流器模块分别具有直流电压源，该直流 电压源例如被构建为电容器或多个电容器的电气互连。这种变流器的优点来自根据本发明 的电势均衡系统的以上已经提到的优点，并且因此在此不会再一次提及。 [0013]在本发明的另外的设计方案中，变流器具有多个模块组，多个模块组分别具有多 个变流器模块，多个变流器模块分别具有至少一个极触点。对于每个模块组，电势均衡系统 具有接触元件，该接触元件在其第二端位置接触模块组的所有极触点。本发明的这种设计 方案考虑了：模块化多电平变流器的变流器模块通常形成多个模块组，这些模块组例如布 置为空间上彼此间隔。在该情况下可能有利的是，为每个模块组设置接触元件。在此可以规 定，所有接触元件在其第二端位置彼此电气连接。有利地，这简化了与地电势的连接。此外， 可以设置共同的驱动器，利用该共同的驱动器可以同时驱动所有接触元件。由此，一方面可 以降低用于移动接触元件的成本开销和材料开销，并且另一方面可以更容易地同步接触元 件的移动。 附图说明 [0014]结合以下对结合附图更详细地阐述的实施例的描述，上面所描述的本发明的特 性、特征和优点以及如何实现其的方式将变得更加清楚并且更显著地容易理解。在此附图 中： [0015]图1示出了模块化多电平变流器的电路图， [0016]图2示出了被构建为屏蔽部的接触元件以及用于移动屏蔽部的驱动器， [0017]图3示出了的极触点和被构建为屏蔽部的、在屏蔽部的第一端位置的接触元件的 立体图， [0018]图4示出了图3中所示的极触点和在屏蔽部的第二端位置的屏蔽部的立体图， [0019]图5示出了极触点和被构建为接触缆线的、在接触缆线的中间位置的接触元件，在 引导缆线上引导该接触缆线， [0020]图6示出了图5中所示的极触点和在引导缆线上被引导的、在接触缆线的第二端位 置的接触缆线。 [0021]在附图中，彼此对应的部分设置有相同的附图标记。 具体实施方式 [0022]图1示出了自换向模块化多电平变流器1的电路图。变流器1具有多个在变流器1的 正常运行中串联连接的变流器模块3,仅示出了其中一些变流器模块。变流器模块3形成三 个相叠地布置的模块组5至7。此外，变流器1具有根据本发明的电势均衡系统，其对于每个 模块组5至7具有导电的接触元件17并且对于每个变流器模块3具有极触点15。 [0023]每个变流器模块3具有由半导体开关9构成的半桥，半导体开关例如分别被构建为 绝缘栅双极晶体管QGBT=Insulated-Gate Bipolar Transistor),续流二极管11与该绝 缘栅双极晶体管反并联连接。此外，每个变流器模块3具有被构建为电容器的直流电压源 13。直流电压源13的一个极与变流器模块3的极触点15电气连接，经由该极触点可以电气接 触该极。 [0024]每个模块组5至7的接触元件17可以在第一端位置与第二端位置之间移动，在该第 一端位置接触元件与模块组5至7的变流器模块3电气分离，在该第二端位置接触元件与模 块组5至7的所有极触点15接触并且并联地连接模块组5至7的变流器模块3的直流电压源 13。附加地，第一模块组5的接触元件17在其第二端位置接触接地触点19,可以经由第一接 地开关21将地电势施加到该接地触点。附加地，第二模块组6的接触元件17在其第二端位置 接触第一连接触点23,该第一连接触点与第一模块组5的极触点15电气连接。附加地，第三 模块组7的接触元件17在其第二端位置接触第二连接触点25,该第二连接触点与第二模块 组6的极触点15电气连接。可以经由第二接地开关22将地电势施加到第三模块组7的极触点 15。因此，当所有接触元件17都处于其第二端位置时，可以通过闭合至少一个接地开关21、 22来将地电势施加到所有极触点15。 [0025] 每个接触元件17可以通过驱动器27在其两个端位置之间移动。接触元件17的驱动 器
[JA WO2020085172A1]: チョッパ回路 [EN EP3872974A1]: CHOPPER CIRCUIT [FR EP3872974A1]: CIRCUIT D'INTERRUPTION PÉRIODIQUE [DE EP3872974A1]: HÄCKSELSCHALTUNG | [JA WO2020085172A1]: 第１の外部接続端子における第１の直流電圧と第２の外部接続端子における第２の直流電圧との間で電圧変換するチョッパ回路１は、第１の外部接続端子を有する第１のスイッチ部１１と、第１のスイッチ部１１とオン時の導通方向が揃うように第１のスイッチ部１１に対して直列に接続され、第１のスイッチ部１１が接続される側とは反対側に第２の外部接続端子を有する第２のスイッチ部１２と、第１のスイッチ部１１と第２のスイッチ部１２とを接続する配線から分岐した配線上に設けられる、１個もしくは互いにカスケード接続された複数個の半導体電力変換器１３と、第１のスイッチ部１１と第２のスイッチ部１２とを接続する配線から分岐した配線上において、半導体電力変換器１３に対して直列に接続されるインダクタ１４とを備える。 [EN EP3872974A1]: This chopper circuit 1 performs voltage conversion between a first DC voltage at a first external connection terminal and a second DC voltage at a second external connection terminal and is provided with: a first switch portion 11 having the first external connection terminal; a second switch portion 12 connected in series with the first switch portion 11 so that the conducting direction during ON-time matches that of the first switch portion 11 and having the second external connection terminal on the opposite side to the side where the first switch portion 11 is connected; one or a plurality of semiconductor power converters 13 cascade-connected to each other, which are provided on a wire branched from the wire for connecting the first switch portion 11 and the second switch portion 12; and an inductor 14 connected in series with the semiconductor power converters 13 on the wire branched from the wire for connecting the first switch portion 11 and the second switch portion 12. [FR WO2020085172A1]: L'invention concerne un circuit d'interruption périodique 1 qui effectue une conversion de tension entre une première tension CC au niveau d'une première borne de connexion externe et une seconde tension CC au niveau d'une seconde borne de connexion externe et comprend : une première partie de commutation 11 ayant la première borne de connexion externe ; une seconde partie de commutation 12 connectée en série avec la première partie de commutation 11 de telle sorte que la direction de conduction pendant le temps de marche correspond à celle de la première partie de commutation 11 et ayant la seconde borne de connexion externe sur le côté opposé au côté auquel la première partie de commutation 11 est connectée ; un ou plusieurs convertisseurs de puissance à semi-conducteurs 13 connectés en cascade les uns aux autres, qui sont disposés sur un fil ramifié à partir du fil pour connecter la première partie de commutation 11 et la seconde partie de commutation 12 ; et une bobine d'induction 14 connectée en série aux convertisseurs de puissance à semi-conducteur 13 sur le fil ramifié à partir du fil pour connecter la première partie de commutation 11 et la seconde partie de commutation 12. | EP3872974A1 | 2021-09-01 | EP19876152A | 2019-10-16 | JP2018199400A, 2018-10-23 JP2019040752W, 2019-10-16 | WO2020085172A1: 2020-04-30 EP3872974A1: 2021-09-01 | TOKYO INST TECH | HAGIWARA MAKOTO | H02M3/155: I | H02M3/158: I H02M3/1584: I H02M1/0054: I H02M7/4835: A | WO2017038122A1 WO2011021443A1 JP2010213506A JP2016226127A US6002603A |  | [JA WO2020085172A1]: 第1の外部接続端子における第1の直流電圧と第2の外部接続端子における第2の直流電圧との間で電圧変換するチョッパ回路であって、 第1の外部接続端子を有する第1のスイッチ部と、 前記第1のスイッチ部とオン時の導通方向が揃うように前記第1のスイッチ部に対して直列に接続され、前記第1のスイッチ部が接続される側とは反対側に第2の外部接続端子を有する第2のスイッチ部と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上に設けられる、1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上において、前記半導体電力変換器に対して直列に接続されるインダクタと、 直流成分及び所定周期の交流成分を有する電流を出力するよう、前記半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、 前記第1のスイッチ部及び前記第2のスイッチ部のうちいずれか一方をオンに制御し、他の一方をオフに制御するスイッチ用制御部であって、前記半導体電力変換器用制御部により前記半導体電力変換器が出力する電流の値が所定値以下に制御された時に、前記第1のスイッチ部及び前記第2のスイッチ部についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、 を備える、チョッパ回路。 第1の外部接続端子における第1の直流電圧と第2の外部接続端子における第2の直流電圧との間で電圧変換するチョッパ回路であって、 第1の外部接続端子を有する第1のスイッチ部と、 前記第1のスイッチ部とオン時の導通方向が揃うように前記第1のスイッチ部に対して直列に接続され、前記第1のスイッチ部が接続される側とは反対側に第2の外部接続端子を有する第2のスイッチ部と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上に設けられる、1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上において、前記半導体電力変換器に対して直列に接続されるインダクタと、 を備え、 前記第1のスイッチ部及び前記第2のスイッチ部を、それぞれ2個ずつ備える、チョッパ回路。 直流成分及び所定周期の交流成分を有する電流を出力するよう、前記半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、 前記第1のスイッチ部及び前記第2のスイッチ部のうちいずれか一方をオンに制御し、他の一方をオフに制御するスイッチ用制御部であって、前記半導体電力変換器用制御部により前記半導体電力変換器が出力する電流の値が所定値以下に制御された時に、前記第1のスイッチ部及び前記第2のスイッチ部についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、 をさらに備える、請求項2に記載のチョッパ回路。 一対の第1の外部接続端子間における第1の直流電圧と一対の第2の外部接続端子間における第2の直流電圧との間で電圧変換するチョッパ回路であって、 オン時の導通方向が揃うように互いに直列接続される第1のスイッチ部、第2のスイッチ部、第3のスイッチ部及び第4のスイッチ部と、 前記第1のスイッチ部と前記第2のスイッチ部との接続点と、前記第3のスイッチ部と前記第4のスイッチ部との接続点と、を結ぶ配線上に設けられる、1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、 前記第1のスイッチ部と前記第2のスイッチ部との接続点と、前記第3のスイッチ部と前記第4のスイッチ部との接続点と、を結ぶ配線上において、前記半導体電力変換器に対して直列に接続されるインダクタと、 直流成分及び所定周期の交流成分を有する電流を出力するよう、前記半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、 前記第1のスイッチ部と前記第3のスイッチ部との組及び前記第2のスイッチ部と前記第4のスイッチ部との組のうちいずれか一方の組をオンに制御し、他の一方の組をオフに制御するスイッチ用制御部であって、前記半導体電力変換器用制御部により前記半導体電力変換器が出力する電流の値が所定値以下に制御された時に、前記第1のスイッチ部と前記第3のスイッチ部との組及び前記第2のスイッチ部と前記第4のスイッチ部との組の各組についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、 を備え、 前記第1のスイッチ部と前記第2のスイッチ部との接続側とは反対側の端子と、前記第3のスイッチ部と前記第4のスイッチ部との接続側とは反対側の端子と、を前記一対の第1の外部接続端子とし、 前記第2のスイッチ部と前記第3のスイッチ部との接続側の端子と、前記第4のスイッチ部の、前記第3のスイッチ部に対する接続側とは反対側の端子と、を前記一対の第2の外部接続端子とする、チョッパ回路。 一対の第1の外部接続端子間における第1の直流電圧と一対の第2の外部接続端子間における第2の直流電圧との間で電圧変換するチョッパ回路であって、 オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第1のスイッチ部及び第2のスイッチ部を有し、前記第1のスイッチ部と前記第2のスイッチ部との接続側とは反対側の両側端子を前記一対の第1の外部接続端子とする第1の主電力変換器と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上に設けられる、1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上において、前記半導体電力変換器に対して直列に接続されるインダクタと、 オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第3のスイッチ部及び第4のスイッチ部を有し、前記第3のスイッチ部と前記第4のスイッチ部との接続側とは反対側の両側端子を前記一対の第2の外部接続端子とする第2の主電力変換器と、 を備え、 前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した前記半導体電力変換器及び前記インダクタが設けられた配線が、前記第3のスイッチ部と前記第4のスイッチ部との接続点に接続される、チョッパ回路。 直流成分及び所定周期の交流成分を有する電流を出力するよう、前記半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、 前記第1のスイッチ部と前記第3のスイッチ部との組及び前記第2のスイッチ部と前記第4のスイッチ部との組のうちいずれか一方の組をオンに制御し、他の一方の組をオフに制御するスイッチ用制御部であって、前記半導体電力変換器用制御部により前記半導体電力変換器が出力する電流の値が所定値以下に制御された時に、前記第1のスイッチ部と前記第3のスイッチ部との組及び前記第2のスイッチ部と前記第4のスイッチ部との組の各組についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、 をさらに備える、請求項5に記載のチョッパ回路。 前記半導体電力変換回路は、直列接続された2つの半導体スイッチと前記2つの半導体スイッチに並列接続された直流コンデンサとからなり前記2つの半導体スイッチのうちの一方の半導体スイッチの各端子を出力端とするチョッパセルからなる、請求項1~6のいずれか一項に記載のチョッパ回路。 各前記半導体スイッチは、 オン時に一方向に電流を通す半導体スイッチング素子と、 該半導体スイッチング素子に逆並列に接続された帰還ダイオードと、 を有する、請求項7に記載のチョッパ回路。 [EN EP3872974A1]: A chopper circuit which converts a voltage between a first direct-current voltage on a first external connection terminal and a second direct-current voltage on a second external connection terminal, the circuit comprising: a first switch unit including a first external connection terminal;a second switch unit connected in series with the first switch unit to conduct electricity in a direction identical to a direction in which the first switch unit conducts electricity in an ON state, and including a second external connection terminal on a side opposite to a side on which the first switch unit is connected to the second switch unit;at least one semiconductor power converter comprising one of a single semiconductor power converter and a plurality of semiconductor power converters cascaded to each other, provided on wiring branching from wiring connecting the first switch unit to the second switch unit;an inductor connected in series with the at least one semiconductor power converter, on wiring branching from wiring connecting the first switch unit to the second switch unit;a semiconductor power converter control unit configured to control a power conversion operation of the at least one semiconductor power converter to output a current containing a direct-current component and an alternating-current component having a predetermined period; anda switch control unit configured to control one of the first switch unit and the second switch unit to be ON and control the other switch unit to be OFF, the switch control unit being configured to perform switching from ON to OFF and switching from OFF to ON for the first switch unit and the second switch unit when a value of a current output from the at least one semiconductor power converter is controlled to be not more than a predetermined value by the semiconductor power converter control unit. A chopper circuit which converts a voltage between a first direct-current voltage on a first external connection terminal and a second direct-current voltage on a second external connection terminal, the circuit comprising: a first switch unit including a first external connection terminal;a second switch unit connected in series with the first switch unit to conduct electricity in a direction identical to a direction in which the first switch unit conducts electricity in an ON state, and including a second external connection terminal on a side opposite to a side on which the first switch unit is connected to the second switch unit;at least one semiconductor power converter comprising one of a single semiconductor power converter and a plurality of semiconductor power converters cascaded to each other, provided on wiring branching from wiring connecting the first switch unit to the second switch unit; andan inductor connected in series with the at least one semiconductor power converter, on wiring branching from wiring connecting the first switch unit to the second switch unit,wherein the first switch unit comprises two first switch units, and the second switch unit comprises two second switch units. The chopper circuit according to claim 2, further comprising: a semiconductor power converter control unit configured to control a power conversion operation of the at least one semiconductor power converter to output a current containing a direct-current component and an alternating-current component having a predetermined period; anda switch control unit configured to control one of the first switch unit and the second switch unit to be ON and control the other switch unit to be OFF, the switch control unit being configured to perform switching from ON to OFF and switching from OFF to ON for the first switch unit and the second switch unit when a value of a current output from the at least one semiconductor power converter is controlled to be not more than a predetermined value by the semiconductor power converter control unit. A chopper circuit which converts a voltage between a first direct-current voltage across a pair of first external connection terminals and a second direct-current voltage across a pair of second external connection terminals, the circuit comprising: a first switch unit, a second switch unit, a third switch unit, and a fourth switch unit connected in series with each other to conduct electricity in an identical direction in an ON state;at least one semiconductor power converter comprising one of a single semiconductor power converter and a plurality of semiconductor power converters cascaded to each other, provided on wiring connecting a connection point between the first switch unit and the second switch unit to a connection point between the third switch unit and the fourth switch unit;an inductor connected in series with the at least one semiconductor power converter, on wiring connecting a connection point between the first switch unit and the second switch unit to a connection point between the third switch unit and the fourth switch unit;a semiconductor power converter control unit configured to control a power conversion operation of the at least one semiconductor power converter to output a current containing a direct-current component and an alternating-current component having a predetermined period; anda switch control unit configured to control one of a set of the first switch unit and the third switch unit and a set of the second switch unit and the fourth switch unit to be ON and control the other set of switch units to be OFF, the switch control unit being configured to perform switching from ON to OFF and switching from OFF to ON for each of a set of the first switch unit and the third switch unit and a set of the second switch unit and the fourth switch unit when a value of a current output from the at least one semiconductor power converter is controlled to be not more than a predetermined value by the semiconductor power converter control unit, whereina terminal on a side opposite to a side on which the first switch unit is connected to the second switch unit, and a terminal on a side opposite to a side on which the third switch unit is connected to the fourth switch unit are provided as the pair of first external connection terminals, anda terminal on a side on which the second switch unit is connected to the third switch unit, and a terminal on a side of the fourth switch unit opposite to a side of the fourth switch unit on which the third switch unit is connected to the fourth switch unit are provided as the pair of second external connection terminals. A chopper circuit which converts a voltage between a first direct-current voltage across a pair of first external connection terminals and a second direct-current voltage across a pair of second external connection terminals, the circuit comprising: a first main power converter comprising a first switch unit and a second switch unit which are connected in series with each other to conduct electricity in an identical direction in an ON state, and one of which is turned on when the other switch unit is turned off, the first main power converter having, as the pair of first external connection terminals, two side terminals on a side opposite to a side on which the first switch unit is connected to the second switch unit;at least one semiconductor power converter comprising one of a single semiconductor power converter and a plurality of semiconductor power converters cascaded to each other, provided on wiring branching from wiring connecting the first switch unit to the second switch unit;an inductor connected in series with the at least one semiconductor power converter, on wiring branching from wiring connecting the first switch unit to the second switch unit; anda second main power converter comprising a third switch unit and a fourth switch unit which are connected in series with each other to conduct electricity in an identical direction in an ON state, and one of which is turned on when the other switch unit is turned off, the second main power converter having, as the pair of second external connection terminals, two side terminals on a side opposite to a side on which the third switch unit is connected to the fourth switch unit,wherein wiring that branches from wiring connecting the first switch unit to the second switch unit, and is provided with the at least one semiconductor power converter and the inductor is connected to a connection point between the third switch unit and the fourth switch unit. The chopper circuit according to claim 5, further comprising: a semiconductor power converter control unit configured to control a power conversion operation of the at least one semiconductor power converter to output a current containing a direct-current component and an alternating-current component having a predetermined period; anda switch control unit configured to control one of a set of the first switch unit and the third switch unit and a set of the second switch unit and the fourth switch unit to be ON and control the other set of switch units to be OFF, the switch control unit being configured to perform switching from ON to OFF and switching from OFF to ON for each of a set of the first switch unit and the third switch unit and a set of the second switch unit and the fourth switch unit when a value of a current output from the at least one semiconductor power converter is controlled to be not more than a predetermined value by the semiconductor power converter control unit. The chopper circuit according to any one of claims 1 to 6, wherein the at least one semiconductor power converter circuit comprises a chopper cell formed by two series-connected semiconductor switches and a direct-current capacitor connected in parallel with the two semiconductor switches, and having, as an output terminal, each terminal of one semiconductor switch of the two semiconductor switches. The chopper circuit according to claim 7, wherein each of the semiconductor switches comprises: a semiconductor switching element configured to conduct a current in one direction in an ON state; anda feedback diode connected in antiparallel with the semiconductor switching element. | [JA WO2020085172A1]: チョッパ回路 本発明は、第1の外部接続端子間における第1の直流電圧と第2の外部接続端子間における第2の直流電圧との間で電圧変換するチョッパ回路に関する。 近年、直流電気鉄道への電池電力貯蔵システムの適用が進んでいる。例えば、鉄道車両に搭載した大容量リチウムイオン電池を使用することで、架線からの電力供給がゼロの場合においても、1回の充電で25[km]以上の走行距離を実現している。 一般に直流電気鉄道の架線電圧とエネルギー蓄積要素の動作電圧は異なるため、双方向チョッパ回路を用いて電圧変換(電力変換)を行う必要がある。図28は、一般的な双方向チョッパ回路の回路図である。双方向チョッパ回路101は、オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第1のスイッチ部(正側バルブデバイス)121-1及び第2のスイッチ部(負側バルブデバイス)121-2と、第1のスイッチ部121-1及び第2のスイッチ部121-2との接続点に接続されるインダクタ113とを備える。第1のスイッチ部121-1及び第2のスイッチ部121-2は、ぞれぞれ、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。電池電力貯蔵システムを有する直流電気鉄道の場合、高圧側直流電圧Vdc1は架線電圧に相当し、低圧側直流電圧Vdc2はエネルギー蓄積要素の動作電圧に相当する。例えば架線の標準電圧がVdc1=1500[V]の場合、Vdc2は600[V]から700[V]程度に設定される。近年、変換器容量が単機で500[kW]の大容量双方向チョッパが開発されている。この場合、インダクタ電流iLの直流成分は500[A]以上となる。 また、近年では、補助変換器を用いた双方向チョッパ回路が提案されている。 例えば、一対の第1の外部接続端子間における第1の直流電圧と一対の第2の外部接続端子間における第2の直流電圧との間で双方向に電圧変換する双方向チョッパ回路であって、オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第1および第2のスイッチ部を有し、前記第1のスイッチ部と前記第2のスイッチ部との接続側とは反対側の両側端子を前記一対の第1の外部接続端子とする主電力変換器と、前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上に設けられる、1個もしくは互いにカスケード接続された複数個の単相フルブリッジ電力変換器と、前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した配線上において、前記単相フルブリッジ電力変換器に対して直列接続されるインダクタと、 を備え、前記第1のスイッチ部と前記第2のスイッチ部とを接続する配線から分岐した前記インダクタおよび前記単相フルブリッジ電力変換器が設けられた配線上の、いずれかの位置に前記一対の第2の外部接続端子が設けられることを特徴とする双方向チョッパ回路が知られている(例えば、特許文献1参照。)。 国際公開第2017/038122号 チョッパ回路において、インダクタの小型化及び軽量化は重要な課題であり、直流電気鉄道などの移動体に搭載する場合は特に重要である。インダクタの重量及び体積は蓄積エネルギーに比例するので、インダクタのインダクタンスを低減することで小型化及び軽量化を実現することができる。しかしながら、インダクタンスの低減はインダクタを流れる電流に含まれるリプル電流の増大を招くため、電力品質低下や変換器の不安定動作を引き起こす恐れがある。 例えば図28に示す双方向チョッパ回路では、インダクタ113がシステムの高重量化・高体積化を引き起こす主要因となる。また、高圧側及び低圧側それぞれに直流遮断器114及び115を設置する必要があり、高コスト化や信頼性低下の要因となる。また、インダクタ電流iLが直流の場合、高圧側電流idc1にステップ状に変化する方形波電流が流れる。方形波電流が流れると、高圧側における配線インダクタンスの影響で過電圧が生じる恐れがある。また、第1のスイッチ部121-1及び第2のスイッチ部121-2では、デバイス通電時に電流を遮断するいわゆる「ハードスイッチング」を行う。その結果、第1のスイッチ部121-1及び第2のスイッチ部121-2でスイッチング損失が発生し、変換器効率低下を引き起こす。 したがって、過電圧が発生せず、小型、軽量で信頼性が高く低損失のチョッパ回路の実現が望まれている。 本開示の第1の態様によれば、第1の外部接続端子における第1の直流電圧と第2の外部接続端子における第2の直流電圧との間で電圧変換するチョッパ回路は、第1の外部接続端子を有する第1のスイッチ部と、第1のスイッチ部とオン時の導通方向が揃うように第1のスイッチ部に対して直列に接続され、第1のスイッチ部が接続される側とは反対側に第2の外部接続端子を有する第2のスイッチ部と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上に設けられる1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上において半導体電力変換器に対して直列に接続されるインダクタと、直流成分及び所定周期の交流成分を有する電流を出力するよう、半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、第1のスイッチ部及び第2のスイッチ部のうちいずれか一方をオンに制御し、他の一方をオフに制御するスイッチ用制御部であって、半導体電力変換器用制御部により前記半導体電力変換器が出力する電流の値が所定値以下に制御された時に、第1のスイッチ部及び前記第2のスイッチ部についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、を備える。 ここで、第1の態様の変形例によるチョッパ回路は、第1の外部接続端子における第1の直流電圧と第2の外部接続端子における第2の直流電圧との間で電圧変換するチョッパ回路は、第1の外部接続端子を有する第1のスイッチ部と、第1のスイッチ部とオン時の導通方向が揃うように第1のスイッチ部に対して直列に接続され、第1のスイッチ部が接続される側とは反対側に第2の外部接続端子を有する第2のスイッチ部と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上に設けられる1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上において半導体電力変換器に対して直列に接続されるインダクタと、を備え、第1のスイッチ部及び第2のスイッチ部を、それぞれ2個ずつ備えてもよい。 また、第1の態様の変形例によるチョッパ回路は、直流成分及び所定周期の交流成分を有する電流を出力するよう、半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、第1のスイッチ部及び第2のスイッチ部のうちいずれか一方をオンに制御し、他の一方をオフに制御するスイッチ用制御部であって、半導体電力変換器用制御部により半導体電力変換器が出力する電流の値が所定値以下に制御された時に、第1のスイッチ部及び第2のスイッチ部についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、をさらに備えてもよい。 また、本開示の第2の態様によれば、一対の第1の外部接続端子間における第1の直流電圧と一対の第2の外部接続端子間における第2の直流電圧との間で電圧変換するチョッパ回路は、オン時の導通方向が揃うように互いに直列接続される第1のスイッチ部、第2のスイッチ部、第3のスイッチ部及び第4のスイッチ部と、第1のスイッチ部と第2のスイッチ部との接続点と第3のスイッチ部と第4のスイッチ部との接続点とを結ぶ配線上に設けられる1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、第1のスイッチ部と第2のスイッチ部との接続点と第3のスイッチ部と第4のスイッチ部との接続点とを結ぶ配線上において半導体電力変換器に対して直列に接続されるインダクタと、直流成分及び所定周期の交流成分を有する電流を出力するよう、半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、第1のスイッチ部と第3のスイッチ部との組及び第2のスイッチ部と第4のスイッチ部との組のうちいずれか一方の組をオンに制御し、他の一方の組をオフに制御するスイッチ用制御部であって、半導体電力変換器用制御部により半導体電力変換器が出力する電流の値が所定値以下に制御された時に、第1のスイッチ部と第3のスイッチ部との組及び第2のスイッチ部と第4のスイッチ部との組の各組についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、を備え、第1のスイッチ部と第2のスイッチ部との接続側とは反対側の端子と、第3のスイッチ部と第4のスイッチ部との接続側とは反対側の端子と、を一対の第1の外部接続端子とし、第2のスイッチ部と第3のスイッチ部との接続側の端子と、第4のスイッチ部の、第3のスイッチ部に対する接続側とは反対側の端子と、を一対の第2の外部接続端子とする。 また、本開示の第3の態様によれば、一対の第1の外部接続端子間における第1の直流電圧と一対の第2の外部接続端子間における第2の直流電圧との間で電圧変換するチョッパ回路は、オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第1のスイッチ部及び第2のスイッチ部を有し、第1のスイッチ部と第2のスイッチ部との接続側とは反対側の両側端子を一対の第1の外部接続端子とする第1の主電力変換器と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上に設けられる1個もしくは互いにカスケード接続された複数個の半導体電力変換器と、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した配線上において半導体電力変換器に対して直列に接続されるインダクタと、オン時の導通方向が揃うように互いに直列接続され、一方がオンのときは他方がオフする第3のスイッチ部及び第4のスイッチ部を有し、第3のスイッチ部と第4のスイッチ部との接続側とは反対側の両側端子を一対の第2の外部接続端子とする第2の主電力変換器と、を備え、第1のスイッチ部と第2のスイッチ部とを接続する配線から分岐した半導体電力変換器及びインダクタが設けられた配線が、第3のスイッチ部と第4のスイッチ部との接続点に接続される。 ここで、第3の態様によるチョッパ回路は、直流成分及び所定周期の交流成分を有する電流を出力するよう、半導体電力変換器の電力変換動作を制御する半導体電力変換器用制御部と、第1のスイッチ部と第3のスイッチ部との組及び第2のスイッチ部と第4のスイッチ部との組のうちいずれか一方の組をオンに制御し、他の一方の組をオフに制御するスイッチ用制御部であって、半導体電力変換器用制御部により半導体電力変換器が出力する電流の値が所定値以下に制御された時に、第1のスイッチ部と第3のスイッチ部との組及び第2のスイッチ部と第4のスイッチ部との組の各組についてのオンからオフへの切替え及びオフからオンへの切替えを実行するスイッチ用制御部と、をさらに備えてもよい。 また、第1の態様、第1の態様の変形例、第2の態様及び第3の態様によるチョッパ回路においては、上記所定値はゼロであってもよい。 また、第1の態様、第1の態様の変形例、第2の態様及び第3の態様によるチョッパ回路においては、半導体電力変換回路は、直列接続された2つの半導体スイッチと2つの半導体スイッチに並列接続された直流コンデンサとからなり2つの半導体スイッチのうちの一方の半導体スイッチの各端子を出力端とするチョッパセルからなってもよい。 また、第1の態様、第1の態様の変形例、第2の態様及び第3の態様によるチョッパ回路においては、各半導体スイッチは、オン時に一方向に電流を通す半導体スイッチング素子と、この半導体スイッチング素子に逆並列に接続された帰還ダイオードと、を有してもよい。 本開示の第1の態様、第1の態様の変形例、第2の態様及び第3の態様によれば、過電圧が発生せず、小型、軽量で信頼性が高く低損失のチョッパ回路を実現することができる。 本開示の第1の実施形態によるチョッパ回路を示す回路図である。 本開示の第1~第3の実施形態によるチョッパ回路における半導体電力変換器を説明する回路図である。 本開示の第1~第3の実施形態によるチョッパ回路における半導体電力変換器及びインダクタの配置例を示す回路図である。 本開示の第1の実施形態によるチョッパ回路の第1の変形例を示す回路図である。 本開示の第1の実施形態によるチョッパ回路の第2の変形例を示す回路図である。 本開示の第1の実施形態によるチョッパ回路の理想的な各部波形を示す図であって、(A)はスイッチ用制御部において用いられる三角波と変調波との関係を示し、(B)は第1のスイッチ部の両端に現れる電圧を示し、(C)は第2のスイッチ部の両端に現れる電圧を示し、(D)は補助電力変換器の出力電圧を示し、(E)はインダクタ電流を示し、(F)は第1のスイッチ部及び第2のスイッチ部に流れる電流を示す。 本開示の第1の実施形態によるチョッパ回路を複数並列接続したチョッパ回路システムを示す回路図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける正相電流制御系を示すブロック線図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の直流電圧一括制御系を示すブロック線図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の相間バランス制御系を示すブロック線図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の零相電流制御系を示すブロック線図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の個別バランス制御系を示すブロック線図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける各半導体電力変換器(チョッパセル)に対する電圧指令値を示すブロック図である。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムのシミュレーションに用いた回路定数を示す図である。シミュレーションには「PSCAD/EMTDC」を使用した。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第1の直流電圧側から第2の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第2の直流電圧側から第1の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、400[kW]の電力伝送の向きを5msの時点で第1の直流電圧側と第2の直流電圧側とで反転された場合におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第2の実施形態によるチョッパ回路を示す回路図である。 本開示の第2の実施形態によるチョッパ回路の理想的な各部波形を示す図であって、(A)はスイッチ用制御部において用いられる三角波と変調波との関係を示し、(B)は第1のスイッチ部及び第2のスイッチ部の両端に現れる電圧を示し、(C)補助電力変換器の出力電圧を示し、(D)はインダクタ電流を示し、(E)は第1のスイッチ部に流れる電流を示し、(F)は第2のスイッチ部に流れる電流を示す。 本開示の第2の実施形態または第3の実施形態によるチョッパ回路を複数並列接続したチョッパ回路システムを示す回路図である。 本開示の第2の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムのシミュレーションに用いた回路定数を示す図である。 本開示の第2の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第1の直流電圧側から第2の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第2の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第2の直流電圧側から第1の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第2の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、400[kW]の電力伝送の向きを5msの時点で第1の直流電圧側と第2の直流電圧側とで反転された場合におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 本開示の第3の実施形態によるチョッパ回路を示す回路図である。 本開示の第3の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムのシミュレーションに用いた回路定数を示す図である。 本開示の第3の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第1の直流電圧側から第2の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第3のスイッチ部及び第4のスイッチ部のそれぞれの両端に現れる電圧を示し、(D)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(E)は第1ユニットにおける第3のスイッチ部及び第4のスイッチ部のそれぞれに流れる電流を示し、(F)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(G)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 一般的な双方向チョッパ回路の回路図である。 以下図面を参照して、チョッパ回路について説明する。理解を容易にするために、これらの図面は縮尺を適宜変更している。図面に示される形態は実施するための一つの例であり、図示された実施形態に限定されるものではない。 図1は、本開示の第1の実施形態によるチョッパ回路を示す回路図である。図2は、本開示の第1~第3の実施形態によるチョッパ回路における半導体電力変換器を説明する回路図である。 本開示の第1の実施形態によるチョッパ回路1は、一対の第1の外部接続端子T1及びG1間における第1の直流電圧vdc1と一対の第2の外部接続端子T2及びG2間における第2の直流電圧vdc2との間で双方向に電圧変換する。第1の外部接続端子T1及びG1と第2の外部接続端子T2及びG2のうち、一方に直流電源が接続され、もう一方に負荷もしくは他の直流電源が接続される。 例えば、第1の外部接続端子T1及びG1に直流電源を接続し、第2の外部接続端子T2及びG2に負荷を接続した場合、チョッパ回路1は降圧チョッパとして動作する。この場合、直流電源が出力する電圧が第1の直流電圧vdc1であり、負荷に印加される電圧が第2の直流電圧vdc2である。 また例えば、第1の外部接続端子T1及びG1に負荷を接続し、第2の外部接続端子T2及びG2に直流電源を接続した場合、チョッパ回路1は昇圧チョッパとして動作する。この場合、負荷に印加される電圧が第1の直流電圧vdc1であり、直流電源が出力する電圧が第2の直流電圧vdc2である。 また例えば、第1の外部接続端子T1及びG1に直流電源を接続し、第2の外部接続端子T2及びG2に他の直流電源を接続してもよい。 チョッパ回路1は、第1のスイッチ部11と、第2のスイッチ部12と、半導体電力変換器13と、インダクタ14とを備える。また、チョッパ回路1は、その制御系として、半導体電力変換器用制御部15とスイッチ用制御部16とを備える。 第1のスイッチ部11は、単方向の電流遮断が可能な半導体バルブデバイスである。第1のスイッチ部11は、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。半導体スイッチング素子の例としては、IGBT、SiC(Silicon Carbide)-MOSFET(Metal-Oxide-Semiconductor Field-Effect Transistor)、サイリスタ、GTO(Gate Turn-OFF Thyristor:ゲートターンオフサイリスタ)、トランジスタなどがあるが、半導体スイッチング素子の種類自体は本発明を限定するものではなく、その他の半導体素子であってもよい。 第1のスイッチ部11は、第1の外部接続端子T1を有する。第1のスイッチ部11と第2のスイッチ部12との接続点をP1で表記する。すなわち、第1のスイッチ部11の、第1の外部接続端子T1が設けられる側とは反対側に、接続点P1が位置する。ここで、第1のスイッチ部11の順方向電圧(すなわち第1の外部接続端子T1と接続点P1との電位差)をvS1uで表す。 第2のスイッチ部12は、単方向の電流遮断が可能な半導体バルブデバイスである。第1のスイッチ部11は、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。半導体スイッチング素子の例としては、IGBT、SiC(Silicon Carbide)-MOSFET(Metal-Oxide-Semiconductor Field-Effect Transistor)、サイリスタ、GTO(Gate Turn-OFF Thyristor:ゲートターンオフサイリスタ)、トランジスタなどがあるが、半導体スイッチング素子の種類自体は本発明を限定するものではなく、その他の半導体素子であってもよい。 第2のスイッチ部12は、第1のスイッチ部11とオン時の導通方向が揃うように、接続点P1において第1のスイッチ部11に対して直列に接続される。第2のスイッチ部12は、第1のスイッチ部11が接続される側(接続点P1)とは反対側に、第2の外部接続端子T2を有する。ここで、第2のスイッチ部12の順方向電圧(すなわち接続点P1と第1の外部接続端子T2との電位差)をvS2uで表す。 本明細書では、第1のスイッチ部11と第2のスイッチ部12とからなる電力変換器の組を、主電力変換器10と称する。後述するように、第1のスイッチ部11及び第2のスイッチ部12のうちいずれか一方をオンに制御されている間は、他の一方はオフに制御される。 第1のスイッチ部11と第2のスイッチ部12との接続点P1からから分岐した配線上に、半導体電力変換器13を用いた可変制御電圧源とインダクタ14とが設けられる。 半導体電力変換器13は、第1のスイッチ部11と第2のスイッチ部12との接続点P1からから分岐した配線上に、1個単独でもしくは複数個が互いにカスケード接続された状態で設けられる。本明細書では、1個でもしくは複数個からなる半導体電力変換器13を、補助電力変換器19と称する。また、本明細書では、半導体電力変換器13が1個の場合は、後述するインダクタ14が接続される側を「第1の直流側」と称し、複数個の半導体電力変換器13が互いにカスケード接続される場合は、当該半導体電力変換器13とは異なる他の半導体電力変換器13が接続される側を同じく「第1の直流側」と称する。また、「第1の直流側」とは反対側の直流側を、「第2の直流側」と称する。一例として、図1では、複数個(N個、ただしNは2以上の整数)の半導体電力変換器13が第1の直流側にて互いにカスケード接続された場合を示している。以下、半導体電力変換器13のカスケード数をj(ただし、jは1~Nの自然数)で表す。カスケード接続する半導体電力変換器13の個数を適宜調整するだけでチョッパ回路1の高耐圧化を容易に実現できる。 半導体電力変換器13は、DCDCコンバータ131とコンデンサ132とを有する双方向チョッパセルとして構成される。すなわち、半導体電力変換器13は、直列接続された2つの半導体スイッチと2つの半導体スイッチに並列接続された直流コンデンサとからなり2つの半導体スイッチのうちの一方の半導体スイッチの各端子を出力端とするチョッパセルからなる。すなわち、DCDCコンバータ131は、互いに直列接続された2つの半導体スイッチング素子Sと、該半導体スイッチング素子Sの各々に逆並列に接続された帰還ダイオードDとからなる。半導体スイッチング素子Sの例としては、IGBT、SiC(Silicon Carbide)-MOSFET(Metal-Oxide-Semiconductor Field-Effect Transistor)、サイリスタ、GTO(Gate Turn-OFF Thyristor:ゲートターンオフサイリスタ)、トランジスタなどがあるが、半導体スイッチング素子の種類自体は本発明を限定するものではなく、その他の半導体素子であってもよい。コンデンサ132は、半導体電力変換器13の第2の直流側に設けられる。チョッパ回路1を動作させる際にはDCDCコンバータ131を動作させてコンデンサ132を初期充電しておく。ここで、各半導体電力変換器13の直流コンデンサの電圧をvCju、補助電力変換器19の第1の直流側の電圧をvuとする。詳細については後述するが、補助電力変換器19を用いてインダクタ電流iuを制御することで、インダクタ14及び補助電力変換器19は制御電流源として動作する。なお, 図1では複数個の半導体電力変換器13(チョッパセル)をカスケード接続することで補助電力変換器を実現しているが、同様の機能を有する任意の半導体電力変換器を代用することもできる。 インダクタ14は、第1のスイッチ部11と第2のスイッチ部12とを接続する配線上にある接続点P1から分岐した配線上において、半導体電力変換器13に対して直列接続される。また、接続点P1と接続点P2との間に設けられるインダクタ14を流れるインダクタ電流をiuとする。 したがって、主電力変換器10内の第1のスイッチ部11と第2のスイッチ部12とを接続する配線上にある接続点P1から分岐した同一配線上には、半導体電力変換器13及びインダクタ14が設けられることになる。図1に示す例では、インダクタ14を接続点P1と半導体電力変換器13との間に配置し、第2の外部接続端子T2およびG2を補助電力変換器19の、インダクタ14が接続される側とは反対側の接続点P2(すなわち、複数の半導体電力変換器13の組の、インダクタ14が接続される側とは反対側)に配置しているが、これら半導体電力変換器13及びインダクタ14の配置順は、接続点P1と接続点P2との間の配線上において任意に設計可能である。図3は、本開示の第1~第3の実施形態によるチョッパ回路における半導体電力変換器及びインダクタの配置例を示す回路図である。なお、図3における半導体電力変換器13については、理解を容易にするために、図1及び図2に示す半導体電力変換器13におけるコンデンサC(コンデンサ132)を当該半導体電力変換器13の外側に記載している。また、N個(ただし、Nは自然数)の半導体電力変換器13のそれぞれを、セル1、・・・、セルj、・・・セルNで表す。図3(A)に示す例では、インダクタ14を接続点P1と半導体電力変換器13のセル1との間に配置している。また、図3(B)に示す例では、インダクタ14を半導体電力変換器13のセルNと接続点P2との間に配置している。また、図3(C)に示す例では、インダクタ14を半導体電力変換器13のセルNの、接続点P2とは反対側に配置している。 半導体電力変換器用制御部15は、直流成分及び所定周期の交流成分を有する電流を出力するよう、半導体電力変換器13の電力変換動作を制御する。 スイッチ用制御部16は、第1のスイッチ部11及び第2のスイッチ部12のうちいずれか一方をオンに制御し、他の一方をオフに制御する。また、スイッチ用制御部16は、半導体電力変換器用制御部15により半導体電力変換器13が出力する電流の値が所定値以下に制御された時に、第1のスイッチ部11及び第2のスイッチ部12についてのオンからオフへの切替え及びオフからオンへの切替えを実行する。ここで、所定値は、半導体電力変換器13の定格電流よりも十分に小さい値である。一例を挙げると、所定値は、半導体電力変換器13の定格電流の例えば0%~10%程度の値であるが、チョッパ回路1の適用環境によっては、半導体電力変換器13の定格電流の10%を超える値となり得る。 半導体電力変換器用制御部15及びスイッチ用制御部16は、例えばソフトウェアプログラム形式で構築されてもよく、あるいは各種電子回路とソフトウェアプログラムとの組み合わせで構築されてもよい。例えばこれらをソフトウェアプログラム形式で構築する場合は、演算処理装置をこのソフトウェアプログラムに従って動作させることで、上述の各部の機能を実現することができる。またあるいは、半導体電力変換器用制御部15及びスイッチ用制御部16を、各部の機能を実現するソフトウェアプログラムを書き込んだ半導体集積回路として実現してもよい。なお、半導体電力変換器用制御部15及びスイッチ用制御部16の動作の詳細については後述する。 第1の実施形態によるチョッパ回路1は、一対の第1の外部接続端子T1及びG1間における第1の直流電圧vdc1と一対の第2の外部接続端子T2及びG2間における第2の直流電圧vdc2との間で双方向に電圧変換することができる。ただし、図1に示すように主電力変換器10として2個の半導体バルブデバイスすなわち第1のスイッチ部11及び第2のスイッチ部12を有するチョッパ回路1においては、第1の直流電圧vdc1が第2の直流電圧vdc2よりも大きい関係「vdc1&gt;vdc2」を有する必要がある。第1のスイッチ部11及び第2のスイッチ部12のうちいずれか一方をオンに制御されている間は、他の一方はオフに制御される。 第1の直流電圧vdc1と第2の直流電圧vdc2との大小関係によらずに第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するためには、主電力変換器として、4個の単方向の電流遮断が可能な半導体バルブデバイスを設けるか、2個の双方向の電流遮断が可能な半導体バルブデバイスを設ける必要がある。 図4は、本開示の第1の実施形態によるチョッパ回路の第1の変形例を示す回路図である。第1の実施形態によるチョッパ回路の第1の変形例では、主電力変換器10として4個の半導体バルブデバイスすなわち第1のスイッチ部11-1及び11-2並びに第2のスイッチ部12-1及び12-2を有する。第1のスイッチ部11-1及び11-2並びに第2のスイッチ部12-1及び12-2はいずれも、単方向の電流遮断が可能な半導体バルブデバイスであり、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。第1のスイッチ部11-1は、第1の外部接続端子T1と接続点P1との間に設けられる。第1のスイッチ部11-2は、第1の外部接続端子におけるグランド端子G1と接続点P2との間に設けられる。第2のスイッチ部12-1は、接続点P1と第2の外部接続端子T2との間に設けられる。第2のスイッチ部12-2は、接続点P2と第2の外部接続端子におけるグランド端子G2との間に設けられる。第2のスイッチ部12-1は、第1のスイッチ部11-1とオン時の導通方向が揃うように、接続点P1において第1のスイッチ部11-1に対して直列に接続される。第2のスイッチ部12-2は、第1のスイッチ部11-2とオン時の導通方向が揃うように、接続点P2において第1のスイッチ部11-2に対して直列に接続される。第1の直流電圧vdc1が第2の直流電圧vdc2よりも大きいという関係「vdc1&gt;vdc2」の下で第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するためには、第1のスイッチ部11-2及び第2のスイッチ部12-2を常時オン状態とし、第1のスイッチ部11-1及び第2のスイッチ部12-1について、いずれか一方をオンに制御されている間は、他の一方はオフに制御される。この場合、図4のチョッパ回路1は図1のチョッパ回路と等価となる。一方、第1の直流電圧vdc1が第2の直流電圧vdc2よりも小さいという関係「vdc1&lt;vdc2」の下で第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するためには、第1のスイッチ部11-1及び第2のスイッチ部12-1を常時オン状態とし、第1のスイッチ部11-2及び第2のスイッチ部12-2について、いずれか一方をオンに制御されている間は、他の一方はオフに制御される。 図5は、本開示の第1の実施形態によるチョッパ回路の第2の変形例を示す回路図である。第1の実施形態によるチョッパ回路の第1の変形例では、主電力変換器10として4個の半導体バルブデバイスすなわち第1のスイッチ部11-1及び11-2並びに第2のスイッチ部12-1及び12-2を有する。第1のスイッチ部11-1及び11-2並びに第2のスイッチ部12-1及び12-2はいずれも、単方向の電流遮断が可能な半導体バルブデバイスであり、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。第1のスイッチ部11-1及び第1のスイッチ部11-2は、第1の外部接続端子T1と接続点P1との間に設けられる。第1のスイッチ部11-1は、第1のスイッチ部11-2とオン時の導通方向が逆向きになるように設けられる。第1のスイッチ部11-1と第1のスイッチ部11-2とは入れ替えて設けられてもよい。第2のスイッチ部12-1及び第2のスイッチ部12-2は、接続点P1と第2の外部接続端子T2との間に設けられる。第2のスイッチ部12-1は、第2のスイッチ部12-2とオン時の導通方向が逆向きになるように設けられる。第2のスイッチ部12-1と第2のスイッチ部12-2とは入れ替えて設けられてもよい。第2のスイッチ部12-1は、第1のスイッチ部11-1とオン時の導通方向が揃うように設けられる。第2のスイッチ部12-2は、第1のスイッチ部11-2とオン時の導通方向が揃うように設けられる。第1の直流電圧vdc1が第2の直流電圧vdc2よりも大きいという関係「vdc1&gt;vdc2」の下で第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するためには、第1のスイッチ部11-2及び第2のスイッチ部12-2を常時オン状態とし、第1のスイッチ部11-1及び第2のスイッチ部12-1について、いずれか一方をオンに制御されている間は、他の一方はオフに制御される。一方、第1の直流電圧vdc1が第2の直流電圧vdc2よりも小さいという関係「vdc1&lt;vdc2」の下で第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するためには、第1のスイッチ部11-1及び第2のスイッチ部12-1を常時オン状態とし、第1のスイッチ部11-2及び第2のスイッチ部12-2について、いずれか一方をオンに制御されている間は、他の一方はオフに制御される。 また、第1の直流電圧vdc1と第2の直流電圧vdc2との大小関係によらずに第1の直流電圧vdc1と第2の直流電圧vdc2との間で双方向に電圧変換するために、主電力変換器として、2個の双方向の電流遮断が可能な半導体バルブデバイスを設ける場合は、図1に示すチョッパ回路1において、第1のスイッチ部11及び第2のスイッチ部12を、それぞれ双方向の電流遮断が可能な半導体バルブデバイスにて構成すればよい。 また、図1に示すチョッパ回路1における第1のスイッチ部11及び第2のスイッチ部12、図4及び図5に示すチョッパ回路1における第1のスイッチ部11-1及び11-2並びに第2のスイッチ部12-1及び12-2の各半導体バルブデバイスに対して、並列に過電圧抑制用スナバ回路を接続してもよい。 続いて、本開示の第1の実施形態によるチョッパ回路1の動作原理について説明する。図4に示す第1の実施形態の第1の変形例によるチョッパ回路1の動作及び図5に示す第1の実施形態の第2の変形例によるチョッパ回路1の動作は、図1に示す第1の実施形態によるチョッパ回路1の動作と同様に考えることができるため、ここでは、図1に示す第1の実施形態によるチョッパ回路1の動作について説明する。図6は、本開示の第1の実施形態によるチョッパ回路の理想的な各部波形を示す図であって、(A)はスイッチ用制御部において用いられる三角波と変調波との関係を示し、(B)は第1のスイッチ部の両端に現れる電圧を示し、(C)は第2のスイッチ部の両端に現れる電圧を示し、(D)は補助電力変換器の出力電圧を示し、(E)はインダクタ電流を示し、(F)は第1のスイッチ部及び第2のスイッチ部に流れる電流を示す。図6(A)において、三角波vtriを実線で示し、変調波dを一点鎖線で示す。また、図6(F)において、第1のスイッチ部に流れる電流iu1を実線で示し、第2のスイッチ部に流れる電流iu2を破線で示す。 第1のスイッチ部11及び第2のスイッチ部12のオンオフは、スイッチ用制御部16において、最小値が0で最大値が1の三角波vtriと変調波dとの比較結果に基づき決定する。変調波dの決定方法の詳細については後述するが、第1の直流電圧vdc1と第2の直流電圧vdc2との関係により決定される。スイッチ用制御部16は、第1のスイッチ部11及び第2のスイッチ部12のうちいずれか一方をオンに制御し、他の一方をオフに制御する。例えば、図6(A)に示すように三角波vtriが変調波dより小さい場合、スイッチ用制御部16は、第1のスイッチ部11に対してはオンとなるように制御し、第2のスイッチ部12に対してはオフとなるように制御する。この場合、図6(B)に示すように第1のスイッチ部11の両端に現れる電圧はvS1u=0となり、図6(C)に示すように第2のスイッチ部12の両端に現れる電圧はvS2u=vdc1-vdc2となる。また例えば、図6(A)に示すように三角波vtriが変調波dより大きい場合、スイッチ用制御部16は、第1のスイッチ部11に対してはオフとなるように制御し、第2のスイッチ部12に対してはオンとなるように制御する。この場合、図6(B)に示すように第1のスイッチ部11の両端に現れる電圧はvS1u=vdc1-vdc2となり、図6(C)に示すように第2のスイッチ部12の両端に現れる電圧はvS2u=0となる。 半導体電力変換器用制御部15は、インダクタ14に、直流成分及び所定周期の交流成分を有するインダクタ電流iuが流れるよう、半導体電力変換器13(補助電力変換器19)の電力変換動作を制御する。インダクタ電流iuの直流成分をIdc(ただし、Idc&gt;0)、交流成分をIac(ただし、Iac&gt;0)とし、三角波vtriのキャリア周波数をfSMとすると、インダクタ電流iuは式1のように表される。 以下、インダクタ電流iuが直流成分Idcと交流成分Iacを含む理由について説明する。 後述する図13に示す通り、補助電力変換器19の出力電圧vuは、フィードフォワード制御として式2に示すように第1のスイッチ部11がオンの場合はvdc1を出力し第2のスイッチ部12がオンの場合はvdc2を出力する電圧項vfuを含む(図6(D))。電圧項vfuは補助電力変換器19の出力電圧vuに含まれる他の電圧項より大きく、したがって、補助電力変換器19の出力電圧vuは電圧項vfuにほぼ等しいとみなすことができる(vu≒vfu)。 式2及び図6(D)より、電圧項vfuは、等価的に直流電圧とキャリア周波数fSMと同周波数の交流電圧とを含む。 一方、補助電力変換器19において各半導体電力変換器13内のコンデンサCの直流コンデンサ電圧を一定にするために、補助電力変換器19の電力「vfu×iu」が平均的にゼロであるように補助電力変換器19を制御する必要がある。これを実現するために、半導体電力変換器用制御部15は、交流成分Iacに直流成分Idcが重畳された電流がインダクタ電流iuとしてインダクタ14に流れるよう、半導体電力変換器13(補助電力変換器19)の電力変換動作を制御する。図6(D)及び図6(E)に示すように、電力潮流の向きが第1の直流電圧vdc1側から第2の直流電圧vdc2側に向かう向きである場合、電圧項vfu及びインダクタ電流iuそれぞれに含まれる交流成分は同相であるため、両者は正の有効電力「vfu×iu」を形成する。したがって、電圧項vfu及びインダクタ電流iuそれぞれに含まれる直流成分が負の有効電力を形成するようにすれば、補助電力変換器19の電力「vfu×iu」を平均的にゼロにすることができる。電圧項vfuに含まれる直流成分は図6(D)及び式2より正となるため、インダクタ電流iuに含まれる直流成分の極性は負となる。 一方、電力潮流の向きが第2の直流電圧vdc2側から第1の直流電圧vdc1側に向かう向きである場合、インダクタ電流iuに含まれる交流成分の位相は、第1の直流電圧vdc1側から第2の直流電圧vdc2側に向かう電力潮流の場合とは180度変化したものとなる。すなわち、電圧項vfu及びインダクタ電流iuそれぞれに含まれる交流成分は逆相であるため、両者は負の有効電力「vfu×iu」を形成する。したがって、電圧項vfu及びインダクタ電流iuそれぞれに含まれる直流成分が正の有効電力を形成するようにすれば、補助電力変換器19の電力「vfu×iu」を平均的にゼロにすることができる。電圧項vfuに含まれる直流成分は図6(D)及び式2より負となるため、インダクタ電流iuに含まれる直流成分の極性は正となる。よって、電力潮流の向きが第2の直流電圧vdc2側から第1の直流電圧vdc1側に向かう向きである場合は、インダクタ電流iuは式3のように表される。 図1に示すチョッパ回路1において、インダクタ電流iuが負から正に切り替わる瞬間の位相をα(ただし、0&lt;α&lt;π/2)、インダクタ電流iuが正から負に切り替わる瞬間の位相をπ-αとする。一周期(0≦θ≦2π)において、「α≦θ≦π-α」のときは、第1のスイッチ部11がオンであり第2のスイッチ部12がオフであるため、図6(F)に示すように第1のスイッチ部11に流れる電流はiu1=iuとなり、第2のスイッチ部12に流れる電流はiu2=0となる。一方、「0≦θ≦α」及び「π-α≦θ≦2π」の場合は、第1のスイッチ部11がオフであり第2のスイッチ部12がオンであるため、図6(F)に示すように第1のスイッチ部11に流れる電流はiu1=0となり、第2のスイッチ部12に流れる電流はiu2=-iuとなる。また、図6(E)及び式1より、インダクタ電流iuの直流成分Idcは、交流成分Iac及びαを用いて式4のように表すことができる。 なお、第1のスイッチ部11及び第2のスイッチ部12がともにオフとなるデッドタイム期間に関しては、インダクタ電流iuが正の場合(iu&gt;0)は第2のスイッチ部12の帰還ダイオードを介して電流が流れるため、第1のスイッチ部11に流れる電流はiu1=0となり、第2のスイッチ部12に流れる電流はiu2=-iuとなる。一方、インダクタ電流iuが負の場合(iu&lt;0)は第1のスイッチ部11の帰還ダイオードを介して電流が流れるため、第1のスイッチ部11に流れる電流はiu1=iuとなり、第2のスイッチ部12に流れる電流はiu2=0となる。また、式1及び式3より、電力潮流の向きが変化しても、式4は常に成り立つ。 一方、第1のスイッチ部11及び第2のスイッチ部12のターンオン時とターンオフ時に着目すると、電圧変化時における第1のスイッチ部11に流れる電流iu1及び第2のスイッチ部12に流れる電流iu2はともにゼロとなる。このことは、理想状態における第1のスイッチ部11及び第2のスイッチ部12はスイッチング損失を発生しないことを意味する。 以上がインダクタ電流iuが直流成分Idcと交流成分Iacを含む理由である。 続いて、変調波d及び位相αの決定方法について説明する。以下では, 各変換器の損失がゼロの理想状態を仮定する。第1の直流電圧vdc1側の平均電力をPdc1、第2の直流電圧vdc2側の平均電力をPdc2とすると、両者の間では定常的に式5が成立する。 第1の直流電圧vdc1側の平均電力Pdc1及び第2の直流電圧vdc2側の平均電力Pdc2は、第1のスイッチ部11に流れる電流iu1及び第2のスイッチ部12に流れる電流iu2の一周期平均値をそれぞれIu1及びIu2とすると式6及び式7のように表すことができる。 図6(F)、式1及び式4より、第1のスイッチ部11に流れる電流iu1は式8で表すことができる。 同様に、図6(F)、式1及び式4より、第2のスイッチ部12に流れる電流iu2は式9で表すことができる。 式5~式9より、位相αについて式10が成り立つ。 式10より、位相αは、第1の直流電圧vdc1と第2の直流電圧vdc2とにより決定され、インダクタ電流iuの交流成分Iacには依存しないことがわかる。このことは、位相αは電力伝送量に依存しない値であることを意味する。 式10を簡略化するため、「sinα≒α」、「cosα≒1-α2/2」の近似式を適用すると、式10は式11のように変形することができる。 式11は位相αに関する二次方程式であり、位相αについて解くと式12が得られる。 位相に関する条件「0&lt;α&lt;π/2」より、位相αは式13のように表すことができる。 図6(A)において、位相π/2から位相3π/2までの間の三角波vtriの傾きは「1/π」であり、また、位相πのときの三角波vtriの値は「0.5」である。また、位相π-αのときの三角波vtriの値は「d」である。これらの関係から、dは式14のように表すことができる。 以上説明したように、変調波dは式14に基づき決定され、位相αは式13に基づき決定される。スイッチ用制御部16は、三角波vtriが式14に基づいて決定された変調波dより小さい場合、第1のスイッチ部11に対してはオンとなるように制御し、第2のスイッチ部12に対してはオフとなるように制御する。また、スイッチ用制御部16は、三角波vtriが式14に基づいて決定された変調波dより大きい場合、第1のスイッチ部11に対してはオフとなるように制御し、第2のスイッチ部12に対してはオンとなるように制御する。スイッチ用制御部16は、半導体電力変換器用制御部15により半導体電力変換器13が出力する電流がゼロに制御された位相α及び位相π-αの時に、第1のスイッチ部11及び第2のスイッチ部12についてのオンからオフへの切替え及びオフからオンへの切替えを実行する。 上述した位相αの決定方法においては、各変換器の損失がゼロの理想状態を仮定した。この理想状態の下では、半導体電力変換器用制御部15により半導体電力変換器13が出力する電流の位相がα及びπ-αの時に、半導体電力変換器13が出力する当該電流はゼロになる。ただし、実際のチョッパ回路1では、チョッパ回路1内の各変換器には損失が存在するので、半導体電力変換器用制御部15により半導体電力変換器13が出力する電流の位相がα及びπ-αの時であっても、半導体電力変換器13が出力する当該電流がゼロにはならず、微小電流が流れる。そこで、スイッチ用制御部16は、半導体電力変換器用制御部15により半導体電力変換器13が出力する電流が所定値以下に制御された位相α及び位相π-αの時に、第1のスイッチ部11及び第2のスイッチ部12についてのオンからオフへの切替え及びオフからオンへの切替えを実行する。ここで、所定値は、半導体電力変換器13の定格電流よりも十分に小さい値である。一例を挙げると、所定値は、半導体電力変換器13の定格電流の例えば0%~10%程度の値であるが、チョッパ回路1の適用環境によっては、半導体電力変換器13の定格電流の10%を超える値となり得る。 図1に示したチョッパ回路1を実際に適用する際、直流電流の平滑化や変換器容量の増大を目的として、複数のチョッパ回路1を並列接続したチョッパ回路システム(DCDCコンバータシステム)での適用が想定される。図7は、本開示の第1の実施形態によるチョッパ回路を複数並列接続したチョッパ回路システムを示す回路図である。 図7に示すように、チョッパ回路システム1000は、複数のチョッパ回路1が並列接続されて構成される。チョッパ回路1の個数をユニット数M(ただし、Mは自然数)で表し、各チョッパ回路1を、第1ユニット、第2ユニット、・・・、第Mユニットで表す。また、各チョッパ回路1内の補助電力変換器19は等価制御電圧源vuで表している。各ユニット(チョッパ回路1)は、高圧側は共通の直流電源vdc1に対して並列に接続し、低圧側は共通の直流電源vdc2に対して並列に接続する。なお、各ユニットにおける主電力変換器10の三角波初期位相はユニット毎にそれぞれ180/M度ずつ移相させる。また、各インダクタ電流iuの位相も同様に180/M度ずつ移相させる。 以下、3つのチョッパ回路1を有するチョッパ回路システム1000(ユニット数M=3)の制御について説明する。なお、ユニット数Mが3以外の場合も、同様に制御系を構築することができ、すなわち以下の説明を適用することができる。 ユニット数M=3の場合、チョッパ回路システム1000は、三相電力変換器と類似の動作を行うことから、便宜上、チョッパ回路1の第1ユニットをu相電力変換器、チョッパ回路1の第2ユニットをv相電力変換器、チョッパ回路1の第3ユニットをw相電力変換器と呼称する。ただし、チョッパ回路システム1000のuvw相は、本来の三相電力変換器におけるuvw相とは意味合いが異なる点に留意すべきである。 チョッパ回路システム1000の制御系は、インダクタ電流制御系(電力制御系)と直流コンデンサ電圧制御系とから構成される。 初めに、チョッパ回路システム1000のインダクタ電流制御系(電力制御系)の構成について説明する。 チョッパ回路システム1000のインダクタ電流制御系は、電力変換システムで一般的に適用される座標変換をベースとした電流制御系を適用することができる。各相のインダクタ電流をiu、iv、iwとする。各相のインダクタ電流iu、iv、iwは120度位相が異なる正相電流及び逆相電流と、同相の零相電流から構成される。各相のインダクタ電流iu、iv、iwにdq座標変換を適用することで、d軸電流id及びq軸電流iqを算出することができる。一方、零相電流i0に関しては、式15より算出する。 なお、d軸電流id及びq軸電流iqを算出する際、チョッパ回路1内の第1のスイッチ部11及び第2のスイッチ部12に適用する三角波vtriと同周波数fSMの基準正弦波を使用する点に特長がある。具体的には、一般の電力変換システムでは50[Hz]または60[Hz]の正弦波電流を制御するのに対し、チョッパ回路システム1000ではキャリア周波数fSM(例えば数百[Hz]以上)の正弦波電流を制御する。チョッパ回路システム1000において、d軸電流idは第1の直流電圧vdc1と第2の直流電圧vdc2との間の電力伝送に寄与する電流成分を表し、q軸電流iqは第1の直流電圧vdc1と第2の直流電圧vdc2との間の電力伝送に寄与しない電流成分を表す。すなわち、チョッパ回路システム1000のd軸電流idは一般の電力変換システムにおける有効電流に相当し, チョッパ回路システム1000のq軸電流iqは一般の電力変換システムにおける無効電流に相当する。 チョッパ回路システム1000におけるd軸電流id及びq軸電流iqの制御は、一般の電力変換システムで通常に適用される非干渉電流制御を適用することで実現する。図8は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける正相電流制御系を示すブロック線図である。q軸電流iqは第1の直流電圧vdc1と第2の直流電圧vdc2との間の電力伝送に寄与しないq軸電流iqの指令値iq*は常にゼロとする(iq*=0)。一方、q軸電流iqは第1の直流電圧vdc1と第2の直流電圧vdc2との間の電力伝送に寄与するd軸電流idの指令値id*は、第1の直流電圧vdc1側から第2の直流電圧vdc2側への電力潮流指令値p*より決定する。式6及び式8より、第1の直流電圧vdc1側の平均電力は式16のように表される。 ここで、式16における係数3は三相分(3台分)のチョッパ回路1の合計電力を意味する。また、式16では、第1ユニットのチョッパ回路1内の第1のスイッチ部に流れる電流iu1と、第2ユニットのチョッパ回路1内の第1のスイッチ部に流れる電流iv1と、第3ユニットのチョッパ回路1内の第1のスイッチ部に流れる電流iw1とは一周期平均値が等しいと仮定している(Iu1=Iv1=Iw1)。また、式16において、インダクタ電流iu、iv、iwの交流成分Iacとd軸電流idとの間には、「id=√(3/2)×Iac」の関係式が成り立つ。よって、電力潮流指令値p*とd軸電流指令値id*との関係は、式17のように表される。 なお、式17では、第1の直流電圧vdc1側の電力よりd軸電流指令値id*を算出したが、第2の直流電圧vdc2側の電力からd軸電流指令値id*を算出することもできる。具体的には、式7及び式9より、電力潮流指令値p*とd軸電流指令値id*との関係は、式18のように表される。 以上が、チョッパ回路システム1000のインダクタ電流制御系(電力制御系)の構成である。 続いて、チョッパ回路システム1000の直流コンデンサ電圧制御系の構成について説明する。 図1に示したチョッパ回路1内の補助電力変換器19の動作に着目すると、第1のスイッチ部11がオンで第2のスイッチ部12がオフのときは補助電力変換器19は第1の直流電圧vdc1側から電力を吸収し、第1のスイッチ部11がオフで第2のスイッチ部12がオンのときは補助電力変換器19は第2の直流電圧vdc2側へ電力を放出する。定常状態では、式5の関係が成り立つので、補助電力変換器19に流出入する電力の一周期の平均値はゼロとなる。すなわち、補助電力変換器19において定常的な電力の流出入は発生しないため、各半導体電力変換器13(チョッパセル)内のコンデンサにおける直流コンデンサ電圧の直流分は理想的には変動しない。しかし、実際は過渡変動や変換器損失の影響で変動するので、各半導体電力変換器13(チョッパセル)内のコンデンサについて、直流コンデンサ電圧制御を適用する必要がある。 チョッパ回路システム1000の直流コンデンサ電圧制御系は、直流電圧一括制御系、相間バランス制御系、零相電流制御系、及び段間バランス制御系から構成される。 図9は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の直流電圧一括制御系を示すブロック線図である。直流電圧一括制御系は、チョッパ回路システム1000内の全での半導体電力変換器13(チョッパセル)に使用する直流コンデンサ電圧の算術平均値vCaveを指令値vC*に追従させるフィードバックループを構成する。具体的には、零相電流i0に含まれる直流成分i0dcを調整することで実現する。vCaveは式19のように表される。 式19において、vCuave、vCvave、vCwaveは各相に使用する直流コンデンサ電圧の算術平均値を表し、それぞれ式20のように表される。 「vC*&gt;vCave」の場合、零相電流i0に含まれる直流成分i0dcの指令値i0dc*は増加するため、各半導体電力変換器13(チョッパセル)に流入する有効電力は増加する。その結果、各半導体電力変換器13内のコンデンサの直流コンデンサ電圧は増加する。一方、「vC*&lt;vCave」の場合、零相電流i0に含まれる直流成分i0dcの指令値i0dc*は減少するため、各半導体電力変換器13(チョッパセル)から有効電力が流出する。その結果、各半導体電力変換器13内のコンデンサの直流コンデンサ電圧は減少する。 図10は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の相間バランス制御系を示すブロック線図である。相関バランス制御系は、零相電流i0に含まれるキャリア周波数成分i0acを利用して実現する。図10において、sinωtは、第1ユニットのチョッパ回路1内のインダクタ電流iuと同相成分を表し、sin(ωt-2π/3)は、第2ユニットのチョッパ回路1内のインダクタ電流ivと同相成分を表し、sin(ωt-4π/3)は第3ユニットのチョッパ回路1内のインダクタ電流iwと同相成分を表す。例えば、「vCave&gt;vCuave」の場合、図10より、零相電流i0に含まれるキャリア周波数成分i0acの指令値i0ac*は第1ユニットのチョッパ回路1内のインダクタ電流iuと同相成分を発生する。この場合、零相電流i0に含まれるキャリア周波数成分i0acが図6における電圧項vfuに含まれる交流成分と正の有効電力を形成することでvCaveは上昇する。他の相(他のユニットのチョッパ回路1)に関しても同様である。 図11は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の零相電流制御系を示すブロック線図である。零相電流制御系は、零相電流i0を指令値「i0dc*+i0ac*」に追従させるフィードバックループを形成し、各相(各ユニット)共通の電圧指令値v0*を生成する。 図12は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける直流コンデンサ電圧制御系内の個別バランス制御系を示すブロック線図である。個別バランス制御系は、各半導体電力変換器13(チョッパセル)の出力電圧とインダクタ電流との間で有効電力を形成することで電圧バランスを実現する。 図13は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおける各半導体電力変換器(チョッパセル)に対する電圧指令値を示すブロック図である。図13において、vfu*、vfv*、vfw*はフィードフォワード項の電圧指令値を表し、例えばvfu*は式21で与えられる。 ただし、第1のスイッチ部11及び第2のスイッチ部12がともにオフとなるデッドタイム期間は、インダクタ電流iuがゼロより大きい場合(iu&gt;0)は「vfu*=vdc2」とし、インダクタ電流iuがゼロより小さい場合(iu&lt;0)は「vfu*=vdc1」とする。各チョッパセル電圧指令値vju*、vjv*、vjw*(j:1-N)は、直流コンデンサ電圧で規格化された後に、最大値が1で最小値が0のキャリア周波数fSAの三角波と比較される。 以上が、チョッパ回路システム1000の直流コンデンサ電圧制御系の構成である。 続いて、チョッパ回路システム1000のシミュレーション結果について説明する。 図14は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムのシミュレーションに用いた回路定数を示す図である。シミュレーションには「PSCAD/EMTDC」を使用した。チョッパ回路システム1000のユニット数Mは3であり、各ユニットであるチョッパ回路1内に設けられる半導体電力変換器13の数(チョッパセル数)Nは3とした。また、第1の直流電圧vdc1は1.5[kV]、第2の直流電圧vdc2は0.75[kV]とし、各半導体電力変換器13(チョッパセル)内のコンデンサの直流コンデンサ電圧VCは0.6[kV]とした。また、各ユニット内の主電力変換器10のキャリア周波数fSMは450[Hz]とし、補助電力変換器19のキャリア周波数fSAは10[kHz]とした。各チョッパセルには位相シフトPWMを適用しているため、補助電力変換器19の等価キャリア周波数は30[kHz](=NfSA)となる。なお、このシミュレーションは原理の確認が目的であるので、理想状態を想定している。すなわち、制御遅延がゼロのアナログ制御系を仮定し、デッドタイムがゼロの理想スイッチを使用した。 図15は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第1の直流電圧側から第2の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 図15(A)に示すインダクタ電流iu、iv、iwに着目すると、450[Hz]の交流成分に、負の直流電流が重畳していることがわかる。一方、450[Hz]の交流成分は正弦波状となり、高調波電流は少ない。図15(B)に示す第1ユニットにおける第1のスイッチ部11及び第2のスイッチ部12のそれぞれの両端に現れる電圧(半導体バルブデバイスの順方向電圧)vS1u、vS2uに着目すると、第1のスイッチ部11がオン状態となるvS1u=0のときは図15(C)に示すように第1のスイッチ部11に流れる電流はiu1=iu、第2のスイッチ部12に流れる電流はiu2=0となり、第2のスイッチ部12がオン状態となる「vS1u=vdc1-vdc2=750[V]」のときは図15(C)に示すように第1のスイッチ部11に流れる電流はiu1=0、第2のスイッチ部12に流れる電流はiu2=-iuとなる。このシミュレーション結果より、式12で表される変調率dを与えることで、第1のスイッチ部11及び第2のスイッチ部12において、ターンオフ時及び ターンオン時いずれもソフトスイッチング動作(すなわち、流れる電流が微小な所定値以下(例えばゼロ)のタイミングでのスイッチング動作)が実現できていることがわかる。よって、第1のスイッチ部11及び第2のスイッチ部12においてスイッチング損失は発生しない。 また、図15(D)に示すチョッパ回路システム1000における第1の直流電圧vdc1側に流れる電流idc1及び第2の直流電圧vdc2側に流れる電流idc2に着目すると、第1のユニットのチョッパ回路1、第2のユニットのチョッパ回路1及び第3のユニットのチョッパ回路1の各電流が足し合わさることで、チョッパ回路1単体時の直流電流と比較して、より直流電流に近づいていることがわかる。また、従来のチョッパ回路で発生していたステップ状の電流変化は、チョッパ回路システム1000では発生していないこともわかる。したがって、ステップ状電流に起因する過電圧は、チョッパ回路システム1000では発生しない。 また、図15(E)に示す半導体電力変換器13(チョッパセル)内のコンデンサの直流コンデンサ電圧vC1u、vC1v、vC1wに関しては、直流分と交流分を含み、このうち直流分は指令値である600[V]に良好に追従していることがわかる。また交流分に関しては、450[Hz]の交流成分が存在するが、その大きさは直流分と比較し十分に小さいことがわかる。 図16は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、第2の直流電圧側から第1の直流電圧側に400[kW]の電力伝送時におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。すなわち、図16は、上述の図15のシミュレーションとは逆向き(第2の直流電圧側から第1の直流電圧側)に電力伝送を行ったシミュレーション結果を示している。 図16(A)に示すインダクタ電流iu、iv、iwに着目すると、450[Hz]の交流成分に、正の直流電流が重畳していることがわかる。また、図15と比較して電力伝送の向きが変わった場合であっても、式11で表される位相αは変化していないことがわかる。つまり、第1のスイッチ部11及び第2のスイッチ部12において、ターンオフ時及び ターンオン時いずれもソフトスイッチング動作(すなわち、流れる電流が微小な所定値以下(例えばゼロ)のタイミングでのスイッチング動作)が実現できていることがわかる。他のシミュレーション波形については、図15と同様である。 図17は、本開示の第1の実施形態によるチョッパ回路を3台並列接続したチョッパ回路システムにおいて、400[kW]の電力伝送の向きを5msの時点で第1の直流電圧側と第2の直流電圧側とで反転された場合におけるシミュレーション波形を示す図であって、(A)は各ユニットのインダクタ電流を示し、(B)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれの両端に現れる電圧を示し、(C)は第1ユニットにおける第1のスイッチ部及び第2のスイッチ部のそれぞれに流れる電流を示し、(D)はチョッパ回路システムにおける第1の直流電圧側及び第2の直流電圧側のそれぞれに流れる電流を示し、(E)は半導体電力変換器(チョッパセル)内のコンデンサの直流コンデンサ電圧を示す。 図17に示すように、電力伝送の向きを5ms時点で高速に変化させた場合も、チョッパ回路システム1000は、過電圧及び過電流を生じることなく良好に動作することがわかる。このことは、補助電力変換器19が高速な電流制御機能を有していることを示している。 以上が本開示の第1の実施形態によるチョッパ回路の説明である。続いて、本開示の第2の実施形態によるチョッパ回路について説明する。 図18は、本開示の第2の実施形態によるチョッパ回路を示す回路図である。 本開示の第2の実施形態によるチョッパ回路2は、一対の第1の外部接続端子T1及びG1間における第1の直流電圧vdc1と一対の第2の外部接続端子T2及びG2間における第2の直流電圧vdc2との間で双方向に電圧変換する。第1の外部接続端子T1及びG1と第2の外部接続端子T2及びG2のうち、一方に直流電源が接続され、もう一方に負荷もしくは他の直流電源が接続される。 例えば、第1の外部接続端子T1及びG1に直流電源を接続し、第2の外部接続端子T2及びG2に負荷を接続した場合、チョッパ回路2は降圧チョッパとして動作する。この場合、直流電源が出力する電圧が第1の直流電圧vdc1であり、負荷に印加される電圧が第2の直流電圧vdc2である。 また例えば、第1の外部接続端子T1及びG1に負荷を接続し、第2の外部接続端子T2及びG2に直流電源を接続した場合、チョッパ回路2は昇圧チョッパとして動作する。この場合、負荷に印加される電圧が第1の直流電圧vdc1であり、直流電源が出力する電圧が第2の直流電圧vdc2である。 また例えば、第1の外部接続端子T1及びG1に直流電源を接続し、第2の外部接続端子T2及びG2に他の直流電源を接続してもよい。 チョッパ回路2は、第1のスイッチ部21と、第2のスイッチ部22と、第3のスイッチ部23と、第4のスイッチ部24と、半導体電力変換器25と、インダクタ26とを備える。また、チョッパ回路2は、その制御系として、半導体電力変換器用制御部27とスイッチ用制御部28とを備える。 第1のスイッチ部21、第2のスイッチ部22、第3のスイッチ部23、及び第4のスイッチ部24は、単方向の電流遮断が可能な半導体バルブデバイスである。第1のスイッチ部21、第2のスイッチ部22、第3のスイッチ部23、及び第4のスイッチ部24は、オン時に一方向に導通する半導体スイッチング素子と該半導体スイッチング素子に逆並列に接続された帰還ダイオードとからなる。半導体スイッチング素子の例としては、IGBT、SiC(Silicon Carbide)-MOSFET(Metal-Oxide-Semiconductor Field-Effect Transistor)、サイリスタ、GTO(Gate Turn-OFF Thyristor:ゲートターンオフサイリスタ)、トランジスタなどがあるが、半導体スイッチング素子の種類自体は本発明を限定するものではなく、その他の半導体素子であ
[EN US2021234475A1]: SCALABLE MULTI-LEVEL POWER CONVERTER [FR EP3803979A1]: CONVERTISSEUR DE PUISSANCE À NIVEAUX MULTIPLES ÉVOLUTIF [ZH CN112534585A]: 可扩展的多电平电力转换器 [DE EP3803979A1]: SKALIERBARER MEHRSTUFIGER STROMRICHTER | [EN US2021234475A1]: A multilevel power converter, or inverter, for converting a direct current electrical power to an alternating current electrical power includes one or more 2-level converters each including gallium nitride (GaN) transistors configured to switch two input lines to a three-phase output line. The multilevel power converter may be used in a motor drive circuit, which may provide a 3-phase AC supply. Two power converters, which may be 2-level or 3-level power converters, may be alternately switched to provide the AC power to an AC motor by an output stage including bi-directional switching transistors configured to switch a corresponding three-phase output lines from the multilevel power converters. The multilevel power converters switch input lines from a neutral-point clamped input stage including capacitors connected in series across input terminals having a DC voltage therebetween to energize a midpoint terminal with an intermediate voltage half of the voltage between the input terminals. [FR WO2019236861A8]: L'invention concerne un convertisseur de puissance à niveaux multiples, ou un onduleur, destiné à convertir une puissance électrique à courant continu en une puissance électrique à courant alternatif, comprenant un ou plusieurs convertisseurs à 2 niveaux comprenant chacun des transistors au nitrure de gallium (GaN) configurés pour commuter deux lignes d'entrée vers une ligne de sortie triphasée. Le convertisseur de puissance à niveaux multiples peut être utilisé dans un circuit d'excitation de moteur, qui peut fournir une alimentation en CA triphasée. Deux convertisseurs de puissance, qui peuvent être des convertisseurs de puissance à 2 niveaux ou à 3 niveaux, peuvent être commutés en alternance pour fournir la puissance CA à un moteur CA par un étage de sortie comprenant des transistors de commutation bidirectionnels configurés pour commuter les lignes d'une sortie triphasée correspondante provenant des convertisseurs de puissance à niveaux multiples. Les convertisseurs de puissance à niveaux multiples commutent des lignes d'entrée d'un étage d'entrée calé sur point neutre comprenant des condensateurs branchés en série entre des bornes d'entrée entre lesquelles est appliquée une tension continue pour alimenter une borne de point milieu avec une tension intermédiaire égale à la moitié de la tension entre les bornes d'entrée. [ZH CN112534585A]: 用于将直流电力转换成交流电力的多电平电力转换器或逆变器包括一个或更多个2电平转换器，每个2电平转换器均包括被配置成将两根输入线切换至三相输出线的氮化镓(GaN)晶体管。该多电平电力转换器可以用在可以提供3相AC供应的电机驱动电路中。两个电力转换器——其可以是2电平电力转换器或3电平电力转换器——可以通过包括双向开关晶体管的输出级交替地切换以向AC电机提供AC电力，所述双向开关晶体管被配置成切换来自多电平电力转换器的对应的三相输出线。多电平电力转换器切换来自中性点钳位输入级的输入线，所述中性点钳位输入级包括跨其间具有DC电压的输入端子串联连接的电容器以使中点端子被加电有输入端子之间的电压的一半的中间电压。 | WO2019236861A8 | 2019-12-12 2021-02-18 | US2019035812W | 2019-06-06 2019-06-06 | US201862681244P, 2018-06-06 US201862681244P, 2018-06-06 | WO2019236861A8: 2021-02-18 CA3101212A1: 2019-12-12 CN112534585A: 2021-03-19 EP3803979A1: 2021-04-14 US2021234475A1: 2021-07-29 | MAGNA INT INC UNIV OF WINDSOR BANERJEE DEBMALYA LAI CHUNYAN TIAN JIANGBO KUNDU ANIMESH GHOSH ESHAAN KAR NARAYAN CHANDRA SINKULAR JASMIN JIJINA IYER LAKSHMI VARAHA KORTA PHILIP | BANERJEE DEBMALYA LAI CHUNYAN TIAN JIANGBO KUNDU ANIMESH GHOSH ESHAAN KAR NARAYAN SINKULAR JASMIN IYER LAKSHMI KORTA PHILIP SINKULAR JASMIN JIJINA IYER LAKSHMI VARAHA KAR NARAYAN CHANDRA | H01L29/66: I H02M7/00: I H02M7/72: I H02M7/483: I H02P27/08: I | H02M7/483: I H02M7/00: I H02M7/72: I Y02B70/10: A H02P27/08: I H02M7/4835: I | US2011115532A1 US2013155736A1 US2013187473A1 US9479075B2 US8228695B2 US2013044527A1 |  | [EN US2021234475A1]: 1. A multilevel power converter for converting a direct current electrical power to an alternating current electrical power, comprising: a plurality of converter inputs for receiving a direct current voltage of the direct current electrical power;a primary phase final output line for outputting a primary phase output of the alternating current electrical power;a secondary phase final output line for outputting a secondary phase output of the alternating current electrical power;a tertiary phase final output line for outputting a tertiary phase output of the alternating current electrical power; anda plurality of solid-state converter switches coupled to the plurality of converter inputs and to the primary phase final output line and the secondary phase final output line and the tertiary phase final output line and configured to switch the plurality of converter inputs to the primary phase final output line and the secondary phase final output line and the tertiary phase final output line, the plurality of solid-state converter switches comprise at least one 2-level converter including: a positive direct current input line and a negative direct current input line coupled to the plurality of converter inputs,a primary phase high transistor including one of a primary phase high drain and a primary phase high collector connected to the positive direct current input line, the primary phase high transistor including one of a primary phase high gate and a primary phase high base, the primary phase high transistor including one of a primary phase high source and a primary phase high emitter connected to a primary phase output line,a primary phase low transistor including one of a primary phase low drain and a primary phase low collector connected to the one of the primary phase high source and the primary phase high emitter and the primary phase output line, the primary phase low transistor including one of a primary phase low gate and a primary phase low base, the primary phase low transistor including one of a primary phase low source and a primary phase low emitter connected to the negative direct current input line,a secondary phase high transistor including one of a secondary phase high drain and a secondary phase high collector connected to the positive direct current input line, the secondary phase high transistor including one of a secondary phase high gate and a secondary phase high base, the secondary phase high transistor including one of a secondary phase high source and a secondary high emitter connected to a secondary phase output line,a secondary phase low transistor including one of a secondary phase low drain and a secondary phase low collector connected to the secondary phase high source and the secondary phase output line, the secondary phase low transistor including one of a secondary phase low gate and a secondary phase low base, the secondary phase low transistor including one of a secondary phase low source and a secondary phase low emitter connected to the negative direct current input line;a tertiary phase high transistor including one of a tertiary phase high drain and a tertiary phase high collector connected to the positive direct current input line, the tertiary phase high transistor including one of a tertiary phase high gate and a tertiary phase high base, the tertiary phase high transistor including one of a tertiary phase high source and a tertiary phase high emitter connected to a tertiary phase output line, anda tertiary phase low transistor including one of a tertiary phase low drain and a tertiary phase low collector connected to the tertiary phase high source and the tertiary phase output line, the tertiary phase low transistor including one of a tertiary phase low gate and a tertiary phase low base, the tertiary phase low transistor including one of a tertiary phase low source and a tertiary phase low emitter connected to the negative direct current input line. 2. The multilevel power converter as set forth in claim 1, wherein each of the primary phase high transistor and the primary phase low transistor and the secondary phase high transistor and the secondary phase low transistor and the tertiary phase high transistor and the tertiary phase low transistor is a gallium nitride transistor. 3. The multilevel power converter as set forth in claim 1, wherein each of the primary phase high transistor and the primary phase low transistor and the secondary phase high transistor and the secondary phase low transistor and the tertiary phase high transistor and the tertiary phase low transistor is an insulated gate bipolar transistor. 4. The multilevel power converter as set forth in claim 1, wherein the plurality of converter inputs includes a 3-level positive direct current input line and a 3-level intermediate power input line and a 3-level negative direct current input line and the primary phase final output line is a 3-level primary phase output line and the secondary phase final output line is a 3-level secondary phase output line and the tertiary phase final output line is a 3-level tertiary phase output line and the plurality of solid state converter switches comprise at least one 2-level converter comprises: a first 2-level converter configured to switch a first positive direct current input line coupled to the 3-level positive direct current input line and a first negative direct current input line coupled to the 3-level intermediate direct current input line to a first primary phase output line and a first secondary phase output line and a first tertiary phase output line, anda second 2-level converter configured to switch a second positive direct current input line coupled to the 3-level positive direct current input line and a second negative direct current input line coupled to the 3-level negative direct current input line to a second primary phase output line and a second secondary phase output line and a second tertiary phase output line; andthe plurality of solid-state converter switches includes:a 3-level output stage including a plurality of bi-directional solid-state switches configured to switch a corresponding one of the output lines from one of the first 2-level power converter and the second 2-level power converter to the 3-level primary phase output and the 3-level secondary phase output and the 3-level tertiary phase output. 5. A motor drive circuit for an electric motor, comprising: a plurality of converter inputs for receiving a direct current voltage;a first power converter including a plurality of solid-state converter switches configured to switch a plurality of first input lines coupled to at least one of the plurality of converter inputs to a first primary phase output line and a first secondary phase output line and a first tertiary phase output line for three AC phases of the electric motor;a second power converter including a plurality of solid-state converter switches configured to switch a plurality of second input lines coupled to at least one of the plurality of converter inputs to a second primary phase output line and a second secondary phase output line and a second tertiary phase output line for the three AC phases of the electric motor; andan output stage including a plurality of bi-directional solid-state switches configured to switch a corresponding one of the output lines from one of the first power converter and the second power converter to a primary phase final output line and a secondary phase final output line and a tertiary phase final output line to provide an AC power including the three AC phases to the electric motor. 6. The motor drive circuit as set forth in claim 5, wherein the plurality of converter inputs includes a 3-level positive direct current input line and a 3-level negative direct current input line; the motor drive circuit further including a neutral-point clamped input stage coupled to the first power converter and the second power converter and including a first input capacitor and a second input capacitor connected in series across the 3-level positive direct current input line and the 3-level negative direct current input line having a DC voltage therebetween and including a midpoint terminal disposed between the first input capacitor and a second input capacitor and being energized to half of the DC voltage;the first power converter being a first 2-level converter and the plurality of first input lines includes a first positive direct current input line coupled to the 3-level positive direct current input line and a first negative direct current input line coupled to the midpoint terminal, the first 2-level converter configured to switch the first positive direct current input line and the first negative direct current input line to the first primary phase output line and the first secondary phase output line and the first tertiary phase output line; andthe second power converter being a second 2-level converter and plurality of second input lines includes a second positive direct current input line coupled to the midpoint terminal and a second negative direct current input line coupled to the 3-level negative direct current input line, the second 2-level converter configured to switch the second positive direct current input line and the second negative direct current input line to the second primary phase output line and the second secondary phase output line and the second tertiary phase output line. 7. The motor drive circuit as set forth in claim 5, wherein the plurality of converter inputs includes a 5-level positive direct current input line and a 5-level first intermediate direct current input line and a 5-level second intermediate direct current input line and a 5-level third intermediate direct current input line and a 5-level negative direct current input line and each of the first power converter and the second power converter is a 3-level converter comprising: a 3-level positive direct current input line coupled to one of the 5-level positive direct current input line and the 5-level second intermediate direct current input line and a 3-level intermediate direct current input line coupled to one of the 5-level first intermediate direct current input line and the 5-level third direct current input line and a 3-level negative direct current input line coupled to one of the 5-level second intermediate direct current input line and the 5-level negative direct current input line;a first 2-level converter configured to switch a first positive direct current input line coupled to the 3-level positive direct current input line and a first negative direct current input line coupled to the 3-level intermediate direct current input line to a first primary phase output line and a first secondary phase output line and a first tertiary phase output line;a second 2-level converter configured to switch a second positive direct current input line coupled to the 3-level intermediate direct current input line and a second negative direct current input line coupled to the 3-level negative direct current input line to the second primary phase output line and the second secondary phase output line and the second tertiary phase output line; anda 3-level output stage including a plurality of 3-level bi-directional solid-state switches configured to switch a corresponding one of the output lines from one of the first 2-level power converter and the second 2-level power converter to a 3-level primary phase output line and a 3-level secondary phase output line and a 3-level tertiary phase output line. 8. The motor drive circuit as set forth in claim 5, wherein each of the plurality of solid-state converter switches is a gallium nitride (GaN) transistor. 9. The motor drive circuit as set forth in claim 8, wherein the plurality of solid-state converter switches includes: a primary phase high gallium nitride transistor including a primary phase high drain connected to the positive direct current input line and a primary phase high gate and a primary phase high source connected to the primary phase output line;a primary phase low gallium nitride transistor including a primary phase low drain connected to the primary phase high source and the primary phase output line and a primary phase low gate and a primary phase low source connected to the negative direct current input line;a secondary phase high gallium nitride transistor including a secondary phase high drain connected to the positive direct current input line and a secondary phase high gate and a secondary phase high source connected to the secondary phase output line;a secondary phase low gallium nitride transistor including a secondary phase low drain connected to the secondary phase high source and the secondary phase output line and a secondary phase low gate and a secondary phase low source connected to the negative direct current input line;a tertiary phase high gallium nitride transistor including a tertiary phase high drain connected to the positive direct current input line and a tertiary phase high gate and a tertiary phase high source connected to the tertiary phase output line; anda tertiary phase low gallium nitride transistor including a tertiary phase low drain connected to the tertiary phase high source and the tertiary phase output line and a tertiary phase low gate and a tertiary phase low source connected to the negative direct current input line. 10. The motor drive circuit as set forth in claim 5, wherein each of the plurality of solid-state converter switches is an insulated gate bipolar transistor. 11. The motor drive circuit as set forth in claim 10, wherein the plurality of solid-state converter switches includes: a primary phase high insulated gate bipolar transistor including a primary phase high collector connected to the positive direct current input line and a primary phase high base and a primary phase high emitter connected to the primary phase output line;a primary phase low insulated gate bipolar transistor including a primary phase low collector connected to the primary phase high emitter and the primary phase output line and a primary phase low base and a primary phase low emitter connected to the negative direct current input line;a secondary phase high insulated gate bipolar transistor including a secondary phase high collector connected to the positive direct current input line and a secondary phase high base and a secondary phase high emitter connected to the secondary phase output line;a secondary phase low insulated gate bipolar transistor including a secondary phase low collector connected to the secondary phase high emitter and the secondary phase output line and a secondary phase low base and a secondary phase low emitter connected to the negative direct current input line;a tertiary phase high insulated gate bipolar transistor including a tertiary phase high collector connected to the positive direct current input line and a tertiary phase high base and a tertiary phase high emitter connected to the tertiary phase output line; anda tertiary phase low insulated gate bipolar transistor including a tertiary phase low collector connected to the tertiary phase high emitter and the tertiary phase output line and a tertiary phase low base and a tertiary phase low emitter connected to the negative direct current input line. 12. The motor drive circuit as set forth in claim 5, wherein each of the plurality of bi-directional solid-state switches is an insulated gate bipolar transistor. 13. The motor drive circuit as set forth in claim 12, wherein the plurality of bi-directional solid-state switches includes: a first primary phase upper insulated gate bipolar transistor including a first primary phase upper drain coupled to the first primary phase output line of the first power converter and a first primary phase upper gate and a first primary phase upper source;a second primary phase upper insulated gate bipolar transistor including a second primary phase upper drain coupled to the primary phase final output line and a second primary phase upper gate and a second primary phase upper source coupled to the first primary phase upper source;a first primary phase lower insulated gate bipolar transistor including a first primary phase lower drain coupled to the primary phase final output line and a first primary phase lower gate and a first primary phase lower source;a second primary phase lower insulated gate bipolar transistor including a second primary phase lower drain coupled to the second primary phase output line of the second power converter and a second primary phase lower gate and a second primary phase lower source coupled to the first primary phase lower source;a first secondary phase upper insulated gate bipolar transistor including a first secondary phase upper drain coupled to the first secondary phase output line of the first power converter and a first secondary phase upper gate and a first secondary phase upper source;a second secondary phase upper insulated gate bipolar transistor including a second secondary phase upper drain coupled to the secondary phase final output line and a second secondary phase upper gate and a second secondary phase upper source coupled to the first secondary phase upper source;a first secondary phase lower insulated gate bipolar transistor including a first secondary phase lower drain coupled to the secondary phase final output line and a first secondary phase lower gate and a first secondary phase lower source;a second secondary phase lower insulated gate bipolar transistor including a second secondary phase lower drain coupled to the second secondary phase output line of the second power converter and a second secondary phase lower gate and a second secondary phase lower source coupled to the first secondary phase lower source;a first tertiary phase upper insulated gate bipolar transistor including a first tertiary phase upper drain coupled to the first tertiary phase output line of the first power converter and a first tertiary phase upper gate and a first tertiary phase upper source;a second tertiary phase upper insulated gate bipolar transistor including a second tertiary phase upper drain coupled to the tertiary phase final output line and a second tertiary phase upper gate and a second tertiary phase upper source coupled to the first tertiary phase upper source;a first tertiary phase lower insulated gate bipolar transistor including a first tertiary phase lower drain coupled to the secondary phase final output line and a first tertiary phase lower gate and a first tertiary phase lower source; anda second tertiary phase lower insulated gate bipolar transistor including a second tertiary phase lower drain coupled to the second tertiary phase output line of the second power converter and a second tertiary phase lower gate and a second tertiary phase lower source coupled to the first tertiary phase lower source. 14. The motor drive circuit as set forth in claim 5, wherein each of the plurality of bi-directional solid-state switches is a metal oxide silicon controlled triode for alternating current. 15. The motor drive circuit as set forth in claim 14, wherein the plurality of bi-directional solid-state switches includes: a primary phase high triode for alternating current including a primary phase high triode first anode coupled to the primary phase final output line and a primary phase high triode gate and a primary phase high triode second anode coupled to the first primary phase output line of the first power converter;a primary phase low triode for alternating current including a primary phase low triode first anode coupled to the second primary phase output line of the second power converter and a primary phase low triode gate and a primary phase low triode second anode coupled to the primary phase high triode first anode and the primary phase final output line;a secondary phase high triode for alternating current including a secondary phase high triode first anode coupled to the secondary phase final output line and a secondary phase high triode gate and a secondary phase high triode second anode coupled to the first secondary phase output line of the first power converter;a secondary phase low triode for alternating current including a secondary phase low triode first anode coupled to the second secondary phase output line of the second power converter and a secondary phase low triode gate and a secondary phase low triode second anode coupled to the secondary phase high triode first anode and the secondary phase final output line;a tertiary phase high triode for alternating current including a tertiary phase high triode first anode coupled to the tertiary phase final output line and a tertiary phase high triode gate and a tertiary phase high triode second anode coupled to the first tertiary phase output line of the first power converter; anda tertiary phase low triode for alternating current including a tertiary phase low triode first anode coupled to the second tertiary phase output line of the second power converter and a tertiary phase low triode gate and a tertiary phase low triode second anode coupled to the tertiary phase high triode first anode and the tertiary phase final output line. 16. The multilevel power converter as set forth in claim 1, wherein the plurality of converter inputs includes a 5-level positive direct current input line and a 5-level first intermediate direct current input line and a 5-level second intermediate direct current input line and a 5-level third intermediate direct current input line and a 5-level negative direct current input line and the primary phase final output line is a 5-level primary phase final output line and the secondary phase final output line is a 5-level secondary phase final output line and the tertiary phase final output line is a 5-level tertiary phase final output line and the at least one 2-level converter includes a plurality of 2-level converters comprising a plurality of 3-level converters each including: a 3-level positive direct current input line coupled to one of the 5-level positive direct current input line and the 5-level second intermediate direct current input line and a 3-level intermediate direct current input line coupled to one of the 5-level first intermediate direct current input line and the 5-level third direct current input line and a 3-level negative direct current input line coupled to one of the 5-level second intermediate direct current input line and the 5-level negative direct current input line;a first 2-level converter configured to switch a first positive direct current input line coupled to the 3-level positive direct current input line and a first negative direct current input line coupled to the 3-level intermediate direct current input line to a first primary phase output line and a first secondary phase output line and a first tertiary phase output line;a second 2-level converter configured to switch a second positive direct current input line coupled to the 3-level intermediate direct current input line and a second negative direct current input line coupled to the 3-level negative direct current input line to the second primary phase output line and the second secondary phase output line and the second tertiary phase output line; anda 3-level output stage including a plurality of 3-level bi-directional solid-state switches configured to switch a corresponding one of the output lines from one of the first 2-level power converter and the second 2-level power converter to a 3-level primary phase output line and a 3-level secondary phase output line and a 3-level tertiary phase output line. 17. The multilevel power converter as set forth in claim 16, further including a 5-level output stage including a plurality of bi-directional solid-state switches configured to switch a corresponding one of the 3-level primary phase output line and the 3-level secondary phase output line and the 3-level tertiary phase output line from each of the plurality of 3-level converters to the 5-level primary phase final output line and the 5-level secondary phase final output line and the 5-level tertiary phase final output line. 18. The multilevel power converter as set forth in claim 17, wherein each of the plurality of bi-directional solid-state switches is an insulated gate bipolar transistor. 19. The motor drive circuit as set forth in claim 7, further including a 5-level output stage including a plurality of bi-directional solid-state switches configured to switch a corresponding one of the 3-level primary phase output line and the 3-level secondary phase output line and the 3-level tertiary phase output line from each of the first power converter and the second power converter to the 5-level primary phase final output line and the 5-level secondary phase final output line and the 5-level tertiary phase final output line. 20. The motor drive circuit as set forth in claim 19, wherein each of the plurality of bi-directional solid-state switches is an insulated gate bipolar transistor. [ZH CN112534585A]: 1. 一种用于将直流电力转换成交流电力的多电平电力转换器，包括： 多个转换器输入，其用于接收所述直流电力的直流电压； 第一相最终输出线，其用于输出所述交流电力的第一相输出； 第二相最终输出线，其用于输出所述交流电力的第二相输出； 第三相最终输出线，其用于输出所述交流电力的第三相输出；以及 多个固态转换器开关，其耦接至所述多个转换器输入并且耦接至所述第一相最终输出 线、所述第二相最终输出线和所述第三相最终输出线，并且所述多个固态转换器开关被配 置成将所述多个转换器输入切换至所述第一相最终输出线、所述第二相最终输出线和所述 第三相最终输出线。 2. 根据权利要求1所述的多电平电力转换器，其中，所述多个转换器输入包括正直流输 入线和负直流输入线，并且所述多个固态转换器开关包括2电平转换器，所述2电平转换器 包括： 第一相高氮化线晶体管，其包括连接至所述正直流输入线的第一相高漏极、第一相高 栅极以及连接至第一相输出线的第一相高源极； 第一相低氮化线晶体管，其包括连接至所述第一相高源极和所述第一相输出线的第一 相低漏极、第一相低栅极以及连接至所述负直流输入线的第一相低源极； 第二相高氮化线晶体管，其包括连接至所述正直流输入线的第二相高漏极、第二相高 栅极以及连接至第二相输出线的第二相高源极； 第二相低氮化线晶体管，其包括连接至所述第二相高源极和所述第二相输出线的第二 相低漏极、第二相低栅极以及连接至所述负直流输入线的第二相低源极； 第三相高氮化线晶体管，其包括连接至所述正直流输入线的第三相高漏极、第三相高 栅极以及连接至第三相输出线的第三相高源极；以及 第三相低氮化线晶体管，其包括连接至所述第三相高源极和所述第三相输出线的第三 相低漏极、第三相低栅极以及连接至所述负直流输入线的第三相低源极。 3. 根据权利要求1所述的多电平电力转换器，其中，所述多个转换器输入包括正直流输 入线和负直流输入线，并且所述多个固态转换器开关包括2电平转换器，所述2电平转换器 包括： 第一相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第一相高集电极、 第一相高基极以及连接至第一相输出线的第一相高发射极； 第一相低绝缘栅双极型晶体管，其包括连接至所述第一相高发射极和所述第一相输出 线的第一相低集电极、第一相低基极以及连接至所述负直流输入线的第一相低发射极； 第二相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第二相高集电极、 第二相高基极以及连接至第二相输出线的第二相高发射极； 第二相低绝缘栅双极型晶体管，其包括连接至所述第二相高发射极和所述第二相输出 线的第二相低集电极、第二相低基极以及连接至所述负直流输入线的第二相低发射极； 第三相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第三相高集电极、 第三相高基极以及连接至第三相输出线的第三相高发射极；以及 第三相低绝缘栅双极型晶体管，其包括连接至所述第三相高发射极和所述第三相输出 线的第三相低集电极、第三相低基极以及连接至所述负直流输入线的第三相低发射极。 4. 根据权利要求1所述的多电平电力转换器，其中，所述多个转换器输入包括3电平正 直流输入线、3电平中间电力输入线和3电平负直流输入线，并且所述第一相最终输出线是3 电平第一相输出线，并且所述第二相最终输出线是3电平第二相输出线，并且所述第三相最 终输出线是3电平第三相输出线，并且所述多个固态转换器开关包括： 第一2电平转换器，其被配置成将耦接至所述3电平正直流输入线的第一正直流输入线 和耦接至所述3电平中间直流输入线的第一负直流输入线切换至第一第一相输出线、第一 第二相输出线以及第一第三相输出线； 第二2电平转换器，其被配置成将耦接至所述3电平正直流输入线的第二正直流输入线 和耦接至所述3电平负直流输入线的第二负直流输入线切换至第二第一相输出线、第二第 二相输出线以及第二第三相输出线；以及 3电平输出级，其包括多个双向固态开关，所述多个双向固态开关被配置成将所述第一 2电平电力转换器和所述第二2电平电力转换器之一的输出线中的对应输出线切换至所述3 电平第一相输出、所述3电平第二相输出以及所述3电平第三相输出。 5. 一种用于电动机的电机驱动电路，包括： 多个转换器输入，其用于接收直流电压； 第一电力转换器，其包括多个固态转换器开关，所述多个固态转换器开关被配置成将 耦接至所述多个转换器输入中的至少一个转换器输入的多个第一输入线切换至针对所述 电动机的三个AC相的第一第一相输出线、第一第二相输出线和第一第三相输出线； 第二电力转换器，其包括多个固态转换器开关，所述多个固态转换器开关被配置成将 耦接至所述多个转换器输入中的至少一个转换器输入的多个第二输入线切换至针对所述 电动机的三个AC相的第二第一相输出线、第二第二相输出线和第二第三相输出线；以及 输出级，其包括多个双向固态开关，所述多个双向固态开关被配置成将来自所述第一 电力转换器和所述第二电力转换器之一的输出线中的对应输出线切换至第一相最终输出 线、第二相最终输出线和第三相最终输出线以将包括所述三个AC相的AC电力提供给所述电 动机。 6. 根据权利要求5所述的电机驱动电路，其中，所述多个转换器输入包括3电平正直流 输入线和3电平负直流输入线； 所述电机驱动电路还包括中性点钳位输入级，所述中性点钳位输入级耦接至所述第一 电力转换器和所述第二电力转换器并且包括跨其间具有DC电压的所述3电平正直流输入线 和所述3电平负直流输入线串联连接的第一输入电容器和第二输入电容器，并且所述中性 点钳位输入级包括设置在所述第一输入电容器与所述第二输入电容器之间并且被加电至 所述DC电压的一半的中点端子； 所述第一电力转换器是第一2电平转换器，并且所述多个第一输入线包括耦接至所述3 电平正直流输入线的第一正直流输入线和耦接至所述中点端子的第一负直流输入线，所述 第一2电平转换器被配置成将所述第一正直流输入线和所述第一负直流输入线切换至所述 第一第一相输出线、所述第一第二相输出线和所述第一第三相输出线;并且 所述第二电力转换器是第二2电平转换器，并且所述多个第二输入线包括耦接至所述 中点端子的第二正直流输入线和耦接至所述3电平负直流输入线的第二负直流输入线，所 述第二2电平转换器被配置成将所述第二正直流输入线和所述第二负直流输入线切换至所 述第二第一相输出线、所述第二第二相输出线和所述第二第三相输出线。 7. 根据权利要求5所述的电机驱动电路，其中，所述多个转换器输入包括5电平正直流 输入线、5电平第一中间直流输入线、5电平第二中间直流输入线、5电平第三中间直流输入 线和5电平负直流输入线，并且所述第一电力转换器和所述第二电力转换器中的每一个都 是3电平转换器，所述3电平转换器包括： 耦接至所述5电平正直流输入线和所述5电平第二中间直流输入线之一的3电平正直流 输入线、耦接至所述5电平第一中间直流输入线和所述5电平第三直流输入线之一的3电平 中间直流输入线以及耦接至所述5电平第二中间直流输入线和所述5电平负直流输入线之 一的3电平负直流输入线； 第一2电平转换器，其被配置成将耦接至所述3电平正直流输入线的第一正直流输入线 和耦接至所述3电平中间直流输入线的第一负直流输入线切换至第一第一相输出线、第一 第二相输出线以及第一第三相输出线； 第二2电平转换器，其被配置成将耦接至所述3电平中间直流输入线的第二正直流输入 线和耦接至所述3电平负直流输入线的第二负直流输入线切换至所述第二第一相输出线、 所述第二第二相输出线和所述第二第三相输出线；以及 3电平输出级，其包括多个3电平双向固态开关，所述多个3电平双向固态开关被配置成 将所述第一2电平电力转换器和所述第二2电平电力转换器之一的输出线中的对应输出线 切换至3电平第一相输出线、3电平第二相输出线和3电平第二相输出线。 8. 根据权利要求5所述的电机驱动电路，其中，所述多个固态转换器开关中的每个固态 转换器开关是氮化钱(GaN)晶体管。 9. 根据权利要求8所述的电机驱动电路，其中，所述多个固态转换器开关包括： 第一相高氮化线晶体管，其包括连接至所述正直流输入线的第一相高漏极、第一相高 栅极以及连接至所述第一相输出线的第一相高源极； 第一相低氮化线晶体管，其包括连接至所述第一相高源极和所述第一相输出线的第一 相低漏极、第一相低栅极以及连接至所述负直流输入线的第一相低源极； 第二相高氮化线晶体管，其包括连接至所述正直流输入线的第二相高漏极、第二相高 栅极以及连接至所述第二相输出线的第二相高源极； 第二相低氮化线晶体管，其包括连接至所述第二相高源极和所述第二相输出线的第二 相低漏极、第二相低栅极以及连接至所述负直流输入线的第二相低源极； 第三相高氮化线晶体管，其包括连接至所述正直流输入线的第三相高漏极、第三相高 栅极以及连接至所述第三相输出线的第三相高源极；以及 第三相低氮化线晶体管，其包括连接至所述第三相高源极和所述第三相输出线的第三 相低漏极、第三相低栅极以及连接至所述负直流输入线的第三相低源极。 10 .根据权利要求5所述的电机驱动电路，其中，所述多个固态转换器开关中的每个固 态转换器开关是绝缘栅双极型晶体管。 11 .根据权利要求10所述的电机驱动电路，其中，所述多个固态转换器开关包括： 第一相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第一相高集电极、 第一相高基极以及连接至所述第一相输出线的第一相高发射极； 第一相低绝缘栅双极型晶体管，其包括连接至所述第一相高发射极和所述第一相输出 线的第一相低集电极、第一相低基极以及连接至所述负直流输入线的第一相低发射极； 第二相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第二相高集电极、 第二相高基极以及连接至所述第二相输出线的第二相高发射极； 第二相低绝缘栅双极型晶体管，其包括连接至所述第二相高发射极和所述第二相输出 线的第二相低集电极、第二相低基极以及连接至所述负直流输入线的第二相低发射极； 第三相高绝缘栅双极型晶体管，其包括连接至所述正直流输入线的第三相高集电极、 第三相高基极以及连接至所述第三相输出线的第三相高发射极；以及 第三相低绝缘栅双极型晶体管，其包括连接至所述第三相高发射极和所述第三相输出 线的第三相低集电极、第三相低基极以及连接至所述负直流输入线的第三相低发射极。 12 .根据权利要求5所述的电机驱动电路，其中，所述多个双向固态开关中的每个双向 固态开关是绝缘栅双极型晶体管。 13 .根据权利要求12所述的电机驱动电路，其中，所述多个双向固态开关包括： 第一第一相上部绝缘栅双极型晶体管，其包括耦接至所述第一电力转换器的所述第一 第一相输出线的第一第一相上部漏极、第一第一相上部栅极和第一第一相上部源极； 第二第一相上部绝缘栅双极型晶体管，其包括耦接至所述第一相最终输出线的第二第 一相上部漏极、第二第一相上部栅极以及耦接至所述第一第一相上部源极的第二第一相上 部源极； 第一第一相下部绝缘栅双极型晶体管，其包括耦接至所述第一相最终输出线的第一第 一相下部漏极、第一第一相下部栅极和第一第一相下部源极； 第二第一相下部绝缘栅双极型晶体管，其包括耦接至所述第二电力转换器的所述第二 第一相输出线的第二第一相下部漏极、第二第一相下部栅极以及耦接至所述第一第一相下 部源极的第二第一相下部源极； 第一第二相上部绝缘栅双极型晶体管，其包括耦接至所述第一电力转换器的所述第一 第二相输出线的第一第二相上部漏极、第一第二相上部栅极和第一第二相上部源极； 第二第二相上部绝缘栅双极型晶体管，其包括耦接至所述第二相最终输出线的第二第 二相上部漏极、第二第二相上部栅极以及耦接至所述第一第二相上部源极的第二第二相上 部源极； 第一第二相下部绝缘栅双极型晶体管，其包括耦接至所述第二相最终输出线的第一第 二相下部漏极、第一第二相下部栅极和第一第二相下部源极； 第二第二相下部绝缘栅双极型晶体管，其包括耦接至所述第二电力转换器的所述第二 第二相输出线的第二第二相下部漏极、第二第二相下部栅极以及耦接至所述第一第二相下 部源极的第二第二相下部源极； 第一第三相上部绝缘栅双极型晶体管，其包括耦接至所述第一电力转换器的所述第一 第三相输出线的第一第三相上部漏极、第一第三相上部栅极和第一第三相上部源极； 第二第三相上部绝缘栅双极型晶体管，其包括耦接至所述第三相最终输出线的第二第 三相上部漏极、第二第三相上部栅极以及耦接至所述第一第三相上部源极的第二第三相上 部源极； 第一第三相下部绝缘栅双极型晶体管，其包括耦接至所述第二相最终输出线的第一第 三相下部漏极、第一第三相下部栅极和第一第三相下部源极；以及 第二第三相下部绝缘栅双极型晶体管，其包括耦接至所述第二电力转换器的所述第二 第三相输出线的第二第三相下部漏极、第二第三相下部栅极以及耦接至所述第一第三相下 部源极的第二第三相下部源极。 14 .根据权利要求5所述的电机驱动电路，其中，所述多个双向固态开关中的每个双向 固态开关是用于交流电的金属氧化物可控硅三极管。 15 .根据权利要求14所述的电机驱动电路，其中，所述多个双向固态开关包括： 用于交流电的第一相高三极管，其包括耦接至所述第一相最终输出线的第一相高三极 管第一阳极、第一相高三极管门极以及耦接至所述第一电力转换器的所述第一第一相输出 线的第一相高三极管第二阳极； 用于交流电的第一相低三极管，其包括耦接至所述第二电力转换器的所述第二第一相 输出线的第一相低三极管第一阳极、第一相低三极管门极以及耦接至所述第一相高三极管 第一阳极和所述第一相最终输出线的第一相低三极管第二阳极； 用于交流电的第二相高三极管，其包括耦接至所述第二相最终输出线的第二相高三极 管第一阳极、第二相高三极管门极以及耦接至所述第一电力转换器的所述第一第二相输出 线的第二相高三极管第二阳极； 用于交流电的第二相低三极管，其包括耦接至所述第二电力转换器的所述第二第二相 输出线的第二相低三极管第一阳极、第二相低三极管门极以及耦接至所述第二相高三极管 第一阳极和所述第二相最终输出线的第二相低三极管第二阳极； 用于交流电的第三相高三极管，其包括耦接至所述第三相最终输出线的第三相高三极 管第一阳极、第三相高三极管门极以及耦接至所述第一电力转换器的所述第一第三相输出 线的第三相高三极管第二阳极；以及 用于交流电的第三相低三极管，其包括耦接至所述第二电力转换器的所述第二第三相 输出线的第三相低三极管第一阳极、第三相低三极管门极以及耦接至所述第三相高三极管 第一阳极和所述第三相最终输出线的第三相低三极管第二阳极。 | [EN US2021234475A1]: CROSS-REFERENCE TO RELATED APPLICATIONS This PCT International Patent Application claims the benefit of and priority to U.S. Provisional Patent Application Ser. No. 62/681,244 filed on Jun. 6, 2018, titled “Scalable Multi-Level Power Converter,” the entire disclosure of which is hereby incorporated by reference. FIELD The present disclosure relates generally to multilevel power converters for converting direct current (DC) electrical power to alternating current (AC) electrical power. More specifically, the present disclosure relates to such multilevel power converters for use in motor drive circuits. BACKGROUND This section provides background information related to the present disclosure which is not necessarily prior art. Electric motor drives, also known as variable frequency drives (VFDs) are used in a variety of applications to provide alternating current (AC) electrical power to an electric motor. Electric motor drives are frequently used in electric vehicles for powering traction motors at a range of different speeds. Electric motor drives also have industrial and commercial applications such as for running blowers, conveyors, or other machines at a range of different speeds. Such variable frequency drives commonly include multilevel voltage converters that use solid state switches to switch a DC source in order to generate an output having multiple different voltage levels. Historically, insulated gate bipolar transistors (IGBTs) or metal-oxide-semiconductor field-effect transistors (MOSFETs) are used as the switches. However, IGBTs and MOSFETs are limited in their operating speed and are not generally able to operate at more than 10 kHz to switch the high electrical currents required for motor drive applications. Gallium Nitride (GaN) solid-state switches have the ability to rapidly switch the electrical currents required for motor drive applications. However, commercially available Gallium Nitride (GaN) solid-state switches are rated for operation at a maximum of 650V, less than the input DC voltage required for modern electric vehicles, which can have DC bus voltages of 800V or greater. Thus, there is a need for multilevel power converters and motor drive circuits that overcome these shortcomings. SUMMARY This section provides a general summary of the present disclosure and is not a comprehensive disclosure of its full scope or all of its features and advantages. According to an aspect of the disclosure, a multilevel power converter for converting a direct current electrical power to an alternating current electrical power. The multilevel power converter includes a plurality of converter inputs for receiving a direct current voltage of the direct current electrical power. The multilevel power converter also includes a primary phase final output line for outputting a primary phase output of the alternating current electrical power, a secondary phase final output line for outputting a secondary phase output of the alternating current electrical power, and a tertiary phase final output line for outputting a tertiary phase output of the alternating current electrical power. In addition, the multilevel power converter includes a plurality of solid-state converter switches coupled to the plurality of converter inputs and to the primary phase final output line and the secondary phase final output line and the tertiary phase final output line. The plurality of solid-state converter switches are configured to switch the plurality of converter inputs to the primary phase final output line and the secondary phase final output line and the tertiary phase final output line. According to another aspect, the multilevel power converter includes one or more 2-level converters, each including six Gallium Nitride (GaN) transistors or IGBTs configured to switch input DC lines to a three-phase output line. In this way, a multilevel power converter, such as a 3-level converter may be constructed using 2-level converters as a unit building block. Use of 650V Gallium Nitride devices in the 2-level converter will produce a multilevel power converter capable to withstand an 800V DC input voltage. According to yet another aspect of the disclosure, a motor drive circuit for an electric motor is also provided. The motor drive circuit includes a plurality of converter inputs for receiving a direct current voltage. The motor drive circuit also includes a first power converter including a plurality of solid-state converter switches. The plurality of solid-state converter switches of the first power converter are configured to switch a plurality of first input lines coupled to at least one of the plurality of converter inputs to a first primary phase output line and a first secondary phase output line and a first tertiary phase output line for three AC phases of the electric motor. The motor drive circuit additionally includes a second power converter including a plurality of solid-state converter switches. The plurality of solid-state converter switches of the second power converter are configured to switch a plurality of second input lines coupled to at least one of the plurality of converter inputs to a second primary phase output line and a second secondary phase output line and a second tertiary phase output line for the three AC phases of the electric motor. The motor drive circuit also includes an output stage including a plurality of bi-directional solid-state switches. The plurality of bi-directional solid-state switches of the output stage are configured to switch a corresponding one of the output lines from one of the first power converter and the second power converter to a primary phase final output line and a secondary phase final output line and a tertiary phase final output line to provide an AC power including the three AC phases to the electric motor. Further areas of applicability will become apparent from the description provided herein. The description and specific examples in this summary are intended for purposes of illustration only and are not intended to limit the scope of the present disclosure. DRAWINGS The drawings described herein are for illustrative purposes only of selected embodiments and not all possible implementations, and are not intended to limit the scope of the present disclosure. FIG. 1 is a schematic diagram of a motor drive including a conventional two-level inverter; FIG. 2 illustrates an output voltage and current of the conventional two-level inverter of FIG. 1; FIG. 3 is a circuit diagram of one phase leg of a prior art neutral point clamped multilevel power converter; FIG. 4A is a schematic diagram of a 2-level converter using Galium Nitride (GaN) transistors according to aspects of the disclosure; FIG. 4B is a schematic diagram of another 2-level converter using insulated-gate bipolar transistors (IGBTs) according to aspects of the disclosure; FIG. 5A is a schematic diagram of a 3-level converter including two 2-level converters of the design shown in FIG. 4A according to aspects of the disclosure; FIG. 5B is a schematic diagram of another 3-level converter including two 2-level converters of the design shown in FIG. 4B according to aspects of the disclosure; FIG. 6A is a schematic diagram of a motor drive circuit including two 2-level converters according to aspects of the disclosure; FIG. 6B is a schematic diagram of a bi-directional switch used in the motor drive circuit of FIG. 6A according to aspects of the disclosure; FIG. 7A is a schematic diagram of a motor drive circuit including two 3-level converters according to aspects of the disclosure; FIG. 7B is a schematic diagram of a bi-directional switch used in the motor drive circuit of FIG. 7A according to aspects of the disclosure; FIG. 8 shows an additional motor drive circuit with metal oxide silicon controlled triodes for alternating current according to aspects of the disclosure; FIG. 9 shows example pulse width modulation waveforms of a primary phase operation of a primary phase high insulated gate bipolar transistor and a primary phase low insulated gate bipolar transistor of a first power converter and the primary phase high triode for alternating current of the motor drive circuit of FIG. 8 according to aspects of the disclosure; FIG. 10 shows a pulse width modulation logic generation structure for a primary phase of the motor drive circuit of FIG. 8 according to aspects of the disclosure; FIGS. 11 and 12 show waveforms of positive and negative carrier signals with the corresponding reference voltage waveforms used by the pulse width modulation logic generation structure of FIG. 10 according to aspects of the disclosure; FIG. 13 shows voltage and current waveforms for a 400V input voltage to the motor drive circuit of FIG. 8 according to aspects of the disclosure; FIG. 14 shows an example line to line voltage of the motor drive circuit shown in FIG. 8 according to aspects of the disclosure; FIG. 15 shows three phase current waveforms output by the motor drive circuit of FIG. 8 and Fast Fourier Transform (FFT) results of the three phase output according to aspects of the disclosure; FIG. 16 illustrates the calculation of power for two converters of the motor drive circuit of FIG. 8 according to aspects of the disclosure; and FIG. 17 shows another motor drive circuit with metal oxide silicon controlled triodes for alternating current. DETAILED DESCRIPTION In the following description, details are set forth to provide an understanding of the present disclosure. In some instances, certain circuits, structures and techniques have not been described or shown in detail in order not to obscure the disclosure. In general, the present disclosure relates to a multilevel power converter and motor drive circuit of the type well-suited for use in many applications. The multilevel power converter and motor drive circuit of this disclosure will be described in conjunction with one or more example embodiments. However, the specific example embodiments disclosed are merely provided to describe the inventive concepts, features, advantages and objectives with sufficient clarity to permit those skilled in this art to understand and practice the disclosure. Specifically, the example embodiments are provided so that this disclosure will be thorough, and will fully convey the scope to those who are skilled in the art. Numerous specific details are set forth such as examples of specific components, devices, and methods, to provide a thorough understanding of embodiments of the present disclosure. It will be apparent to those skilled in the art that specific details need not be employed, that example embodiments may be embodied in many different forms and that neither should be construed to limit the scope of the disclosure. In some example embodiments, well-known processes, well-known device structures, and well-known technologies are not described in detail. FIG. 1 illustrates a motor drive 10, having a conventional two-level inverter. The motor drive 10 includes a battery as a direct current (DC) source 20 to supply a DC electrical power upon a DC link bus 22 including a high-side conductor 22a and a low-side conductor 22b , with the high-side conductor 22a having a higher voltage potential than the low-side conductor 22b . A set of two smoothing capacitors 24 are connected across the DC link bus 22 between the high-side conductor 22a and the low-side conductor 22b to maintain the DC voltage thereacross. The first motor drive 10 also includes a first inverter 26 having three phase drivers 28a , 28b , 28c , with each of the phase drivers 28a , 28b , 28c configured to switch current from the DC link bus 22 to supply AC power upon a corresponding output terminal 29a , 29b , 29c . The output terminals 29a , 29b , 29c are connected to corresponding ones of three output terminals 30, which deliver the alternating current (AC) power as three-phase AC power to an electric motor 32. Each of the phase drivers 28 within the first inverter 26 of the first motor drive 10 includes a high-side solid-state switch Sh configured to selectively conduct current between a corresponding one of the output terminals 29a , 29b , 29c and the high-side conductor 22a of the DC link bus 22. Each of the phase drivers 28 also includes a low-side solid-state switch Sl configured to selectively conduct current between a corresponding one of the output terminals 29a , 29b , 29c and the low-side conductor 22b of the DC link bus 22. Each of the solid-state switches Sh, Sl includes a switching transistor 34 and a body diode 36. FIG. 2 shows the output voltage and current of a conventional two-level inverter, such as the motor drive 10 shown in FIG. 1. While motor drives can utilize two-level inverters as discussed above, some applications also utilize three level converters. As disclosed in U.S. Pat. No. 8,228,695 and reproduced in FIG. 3, a circuit diagram of one leg of a neutral point clamped (NPC) three level converter 40 is provided and utilizes insulated-gate bipolar transistor (IGBT) modules coupled to a DC link 41 to provide input voltages V1 and V2. The converter 40 includes three dual IGBT modules 42, 44, 46 for each leg of the NPC three level converter 40. If the converter 40 is a three-phase converter, nine dual IGBT modules are used. Each of the dual IGBT modules 42, 44, 46 comprises two IGBTs (IGBTs 48, 50 for top IGBT module, 52, 54 for middle IGBT module and 56, 58 for bottom IGBT module). The two IGBTs of each of the IGBT modules are connected in series and provide a first mid-point 49, a second mid-point 53, and a third point 57. IGBTs modules include anti-parallel diodes connected across the midpoints (shown as 60, 62, 64, 66, 68, 70). With these conventional or known multilevel power converter designs in mind, an objective of the present disclosure is to provide a high-performance Gallium Nitride (GaN)/Silicon Carbide (SiC) based power converter with benefits in performance of thermal design of the converter. GaN or SiC based devices may provide lower converter losses compared to devices used in the prior art such that it may be implemented with simplified cooling that does not require cumbersome and costly liquid cooled converter systems. Referring initially to FIGS. 4A-7B, example embodiments of multilevel power converters 80, 280, 380, 480, 580, 680 are shown for converting a direct current electrical power to an alternating current electrical power, with recurring features marked with identical reference numerals. The multilevel power converter 80, 280, 380, 480, 580, 680 may also be called a multilevel or multi-level inverter. The multilevel power converters 80, 280, 380, 480, 580, 680 described herein include two or more 2-level converters 82, 84. An example embodiment of such a 2-level converter 82 is shown in FIG. 4A. Each of the 2-level converters 82 include a positive direct current input line 86 and a negative direct current input line 88 and a plurality of solid-state converter switches 90, 100, 108, 118, 126, 136. Specifically, the plurality of solid-state converter switches are each configured to switch the positive direct current input line 86 and the negative direct current input line 88 to a three-phase output 98, 116, 134. The plurality of solid-state converter switches 90, 100, 108, 118, 126, 136 include six gallium nitride (GaN) transistors 90, 100, 108, 118, 126, 136. As shown, each 2-level converter 82 includes a primary phase high gallium nitride transistor 90 including a primary phase high drain 92 connected to the positive direct current input line 86 and a primary phase high gate 94 and a primary phase high source 96 connected to a primary phase output line 98. Each 2-level converter 82 also includes a primary phase low gallium nitride transistor 100 including a primary phase low drain 102 connected to the primary phase high source 96 and the primary phase output line 98 and a primary phase low gate 104 and a primary phase low source 106 connected to the negative direct current input line 88. The 2-level converter 82 additionally includes a secondary phase high gallium nitride transistor 108 including a secondary phase high drain 110 connected to the positive direct current input line 84 and a secondary phase high gate 112 and a secondary phase high source 114 connected to a secondary phase output line 116. In addition, the 2-level converter 82 includes a secondary phase low gallium nitride transistor 118 including a secondary phase low drain 120 connected to the secondary phase high source 114 and the secondary phase output line 116 and a secondary phase low gate 122 and a secondary phase low source 124 connected to the negative direct current input line 88. The 2-level converter 82 additionally includes a tertiary phase high gallium nitride transistor 126 including a tertiary phase high drain 128 connected to the positive direct current input line 84 and a tertiary phase high gate 130 and a tertiary phase high source 132 connected to a tertiary phase output line 134. Each 2-level converter 82 also includes a tertiary phase low gallium nitride transistor 136 including a tertiary phase low drain 138 connected to the tertiary phase high source 132 and the tertiary phase output line 134 and a tertiary phase low gate 140 and a tertiary phase low source 142 connected to the negative direct current input line 88. Each of the gallium nitride (GaN) transistors 90, 100, 108, 118, 126, 136 is operated by a control signal which may be provided by a controller and which may be, for example a pulse-width modulation (PWM) signal, discussed in more detail below. Another example of such a 2-level converter 84 is shown in FIG. 4B. Again, the positive direct current input line 86 and the negative direct current input line 88 are provided along with the plurality of solid-state converter switches 144, 152, 160, 168, 176, 184. In more detail, the plurality of solid-state converter switches 144, 152, 160, 168, 176, 184 can include six insulated gate bipolar transistors (IGBTs) 144, 152, 160, 168, 176, 184. So, each 2-level converter 84 includes a primary phase high insulated gate bipolar transistor 144 including a primary phase high collector 146 connected to the positive direct current input line 84 and a primary phase high base 148 and a primary phase high emitter 150 connected to the primary phase output line 98. The 2-level converter 84 also includes a primary phase low insulated gate bipolar transistor 152 including a primary phase low collector 154 connected to the primary phase high emitter 150 and the primary phase output line 98 and a primary phase low base 156 and a primary phase low emitter 158 connected to the negative direct current input line 88. In addition, the 2-level converter 84 includes a secondary phase high insulated gate bipolar transistor 160 including a secondary phase high collector 162 connected to the positive direct current input line 86 and a secondary phase high base 164 and a secondary phase high emitter 166 connected to the secondary phase output line 116. Each 2-level converter 84 also includes a secondary phase low insulated gate bipolar transistor 168 including a secondary phase low collector 170 connected to the secondary phase high emitter 166 and the secondary phase output line 116 and a secondary phase low base 172 and a secondary phase low emitter 174 connected to the negative direct current input line 88. The 2-level converter 84 additionally includes a tertiary phase high insulated gate bipolar transistor 176 including a tertiary phase high collector 178 connected to the positive direct current input line 86 and a tertiary phase high base 180 and a tertiary phase high emitter 182 connected to the tertiary phase output line 134. The 2-level converter 84 also includes a tertiary phase low insulated gate bipolar transistor 184 including a tertiary phase low collector 186 connected to the tertiary phase high emitter 182 and the tertiary phase output line 134 and a tertiary phase low base 188 and a tertiary phase low emitter 190 connected to the negative direct current input line 88. Each of the IGBTs 144, 152, 160, 168, 176, 184 is operated by a control signal which may be provided by a controller and which may be, for example a pulse-width modulation (PWM) signal. More specifically, the 2-level converters 82, 84 disclosed herein are voltage source inverters (VSIs), since the DC voltage supplied at the positive direct current input line 84 and the negative direct current input line 86 remains constant. As shown in FIGS. 5A and 5B, exemplary embodiments of multilevel power converters 80, 280 each include a plurality of the 2-level converters 82, 84 discussed above. More specifically, the multilevel power converters 80, 280 shown in FIGS. 5A and 5B include two of the 2-level converters 82, 82′, 84, 84′ connected through a 3-level output stage 200 to function as a 3-level converter. The multilevel power converter 80, 280 include a plurality of converter inputs 204, 206, 208 for receiving a direct current voltage of the direct current electrical power. Because the multilevel power converters 80, 280 shown in FIG. 5A and 5B are 3-level converters, the plurality of converter inputs includes a 3-level positive direct current input line 204 and a 3-level intermediate direct current input line 206 and a 3-level negative direct current input line 208. The multilevel power converters 80, 280 each also include a 3-level primary phase final output line 210 for outputting a primary phase output of the alternating current electrical power and a 3-level secondary phase final output line 212 for outputting a secondary phase output of the alternating current electrical power and a 3-level tertiary phase final output line 214 for outputting a tertiary phase output of the alternating current electrical power. So, the multilevel power converters 80, 280 include a plurality of solid-state converter switches (GaN transistors 90, 100, 108, 118, 126, 136 as part of two 2-level converters 82, 82′) or a plurality of solid-state converter switches (IGBTs 144, 152, 160, 168, 176, 184 as part of two 2-level converters 84, 84′) coupled to the plurality of converter inputs 204, 206, 208 and to the primary phase final output line 210 and the secondary phase final output line 212 and the tertiary phase final output line 214 through the 3-level output stage 200. Thus, the multilevel power converters 80, 280 are configured to switch the plurality of converter inputs 204, 206, 208 to the primary phase final output line 210 and the secondary phase final output line 212 and the tertiary phase final output line 214. The plurality of 2-level converters 82, 82′, 84, 84′ include a first 2-level converter 82, 84 (first power converter) and a second 2-level converter 82′, 84′ (second power converter). The 2-level converters 82, 82′ shown in FIG. 5A utilize GaN transistors (as in FIG. 4A), while the 2-level converters shown 84, 84′ in FIG. 5B are IGBTs (as in FIG. 4B). As discussed, the first 2-level converter 82, 84 is configured to switch the 3-level positive direct current input line 204 (a first positive direct current input line 86 of the first 2-level converter 82, 84) and the 3-level intermediate direct current input line 206 (a first negative direct current input line 88 of the first 2-level converter 82, 84) to a first primary phase output line 216 and a first secondary phase output line 218 and a first tertiary phase output line 220. The second 2-level converter 82′, 84′ is configured to switch the 3-level intermediate direct current input line 206 (a second positive direct current input line 86′ of the second 2-level converter 82′, 84′) and the 3-level negative direct current input line 208 (a second negative direct current input line 88′ of the second 2-level converter 82′, 84′) to a second primary phase output line 222 and a second secondary phase output line 224 and a second tertiary phase output line 226. As mentioned above, the 3-level converters or multilevel power converters 80, 280 also include a 3-level output stage 200 including a plurality of bi-directional solid-state switches 227 configured to switch a corresponding one of the output lines 216, 218, 220, 222, 224, 226 from one of the first 2-level power converter 82, 84 and the second 2-level power converter 82′, 84′ to the 3-level primary phase final output line 210 and the 3-level secondary phase final output line 212 and the 3-level tertiary phase final output line 214. As shown in FIGS. 4A and 5A, the GaN transistor-based 2-level converters 82, 82′ do not include anti-parallel diodes 225 for any of the gallium nitride (GaN) transistors 90, 100, 108, 118, 126, 136. Instead, they have reverse conducting capability through the source-to-drain channel. As shown in FIGS. 4B and 5B, each of the IGBT-based 2-level converters 84, 84′ include an anti-parallel diode 225 connected in parallel across switched output terminals of each of the IGBTs 144, 152, 160, 168, 176, 184. As shown in FIG. 6A, a motor drive circuit 300 including a scalable 3-level converter 380 for an electric motor (e.g., electric motor 32 of FIG. 1) is provided. Similar to the 3-level converters or multilevel power converters 80, 280 discussed above and shown in FIGS. 5A and 5B, the motor drive circuit 300 includes a plurality of converter inputs 204, 208 for receiving a direct current voltage (e.g., a 3-level positive direct current input line 204 and a 3-level negative direct current input line 208). The motor drive circuit 300 includes a first power converter 82, 84 that includes a plurality of solid-state converter switches (e.g., configured as the 2-level converter 82, 84 shown in FIGS. 4A and 4B) that are configured to switch the plurality of first input lines 86, 88 coupled to at least one of the plurality of converter inputs 204, 208 to a first primary phase output line 216 and a first secondary phase output line 218 and a first tertiary phase output line 220 for three AC phases of the electric motor 32. The motor drive circuit 300 also includes a second power converter 82′, 84′ (another 2-level converter) that includes a plurality of solid-state converter switches that are configured to switch the plurality of second input lines 86′, 88′ coupled to at least one of the plurality of converter inputs 204, 208 to a second primary phase output line 222 and a second secondary phase output line 224 and a second tertiary phase output line 226 for the three AC phases of the electric motor 32. The motor drive circuit 300 additionally includes the 3-level output stage 200. As mentioned, the 3-level output stage 200 includes a plurality of bi-directional solid-state switches 227, discussed in further detail below, that are configured to switch a corresponding one of the output lines 216, 218, 220, 222, 224, 226 from one of the first power converter 82, 84 and the second power converter 82′, 84′ to a primary phase final output line 210 and a secondary phase final output line 212 and a tertiary phase final output line 214 to provide an AC power including the three AC phases to the electric motor 32. Although the example motor drive circuit 300 is configured for 3-phase operation, it should be appreciated that a similar motor drive circuit may be constructed for single phase operation. By appropriately switching using bi-directional switches 227, the motor drive circuit 300 can be used for multi-phase and open end winding motor drive. The motor drive circuit 300 also includes a neutral-point clamped input stage 382 coupled to the first power converter 82, 84 and the second power converter 82′, 84′. The neutral-point clamped input stage 382 includes a first input capacitor 384 and a second input capacitor 386 connected in series across the 3-level positive direct current input line 204 and the 3-level negative direct current input line 208. The 3-level positive direct current input line 204 and the 3-level negative direct current input line 208 have a DC voltage (Vp−Vn) therebetween. A midpoint terminal 388 is disposed between the first input capacitor 384 and a second input capacitor 386 and is energized to half of the DC voltage. Other configurations or arrangements may be provided for the input stage 382 such as, for example, an active device having one or more switches or a battery having one or more first battery cells connected between the midpoint terminal 388 and 3-level positive direct current input line 204 and one or more second battery cells connected between the midpoint terminal 388 and 3-level negative direct current input line 208. The 2-level converters 82, 82′, 84, 84′ shown in FIG. 6A consist of reduced leakage inductance bus bar systems. The connection between the bi-directional switches 227 to the load terminals, or three-phase output lines 210, 212, 214 of the multilevel power converter 380 have higher leakage inductance, which is not a problem as far as the functionality of the multilevel power converter 380 is concerned. As shown in the example of FIG. 7A, another motor drive circuit 400 includes a scalable 5-level converter 480. The scalable 5-level converter 480 is constructed from two 3-level converters 380, 380′, each configured to switch three DC input lines 204, 204′, 206, 206′, 208, 208′ ultimately coupled to a three-phase final output line 484, 486, 488. Specifically, the plurality of converter inputs of the scalable 5-level converter 480 includes a 5-level positive direct current input line 402 and a 5-level first intermediate direct current input line 404 and a 5-level second intermediate direct current input line 406 and a 5-level third intermediate direct current input line 408 and a 5-level negative direct current input line 410. Each of the first power converter 380 and the second power converter 380′ is a 3-level converter 380, 380′. Each of the 3-level converters 380, 380′ may be similar to the 3-level converter 380 shown in FIG. 6A and each comprises a 3-level positive direct current input line 204, 204′ coupled to one of the 5-level positive direct current input line 402 and the 5-level second intermediate direct current input line 406. A 3-level intermediate direct current input line 206, 206′ of each of the 3-level converters 380, 380′ is coupled to one of the 5-level first intermediate direct current input line 404 and the 5-level third direct current input line 408. A 3-level negative direct current input line 208, 208′ of each of the 3-level converters 380, 380′ is coupled to one of the 5-level second intermediate direct current input line 406 and the 5-level negative direct current input line 410. As discussed above, each of the 3-level converters 380, 380′ also includes a first 2-level converter 82, 84 configured to switch a first positive direct current input line 86 coupled to the 3-level positive direct current input line 204, 204′ and a first negative direct current input line 88 coupled to the 3-level intermediate direct current input line 206, 206′ and to a first primary phase output line 416 and a first secondary phase output line 418 and a first tertiary phase output line 420. In addition, each of the 3-level converters 380, 380′ includes a second 2-level converter 82′, 84′ configured to switch a second positive direct current input line 86′ coupled to the 3-level intermediate direct current input line 206, 206′ and a second negative direct current input line 88′ coupled to the 3-level negative direct current input line 208, 208′ and to a second primary phase output line 422 and the second secondary phase output line 424 and the second tertiary phase output line 426. Each 3-level converter 380, 380′ also includes a 3-level output stage 200 including a plurality of 3-level bi-directional solid-state switches 227 configured to switch a corresponding one of the output lines 216, 218, 220, 222, 224, 226 from one of the first 2-level power converter 82, 84 and the second 2-level power converter 82′, 84′ to a 3-level primary phase output line 210 and a 3-level secondary phase output line 212 and a 3-level secondary phase output line 214 (each being one o
[DE EP3776836A1]: MODULARER STROMRICHTER [EN US2021297001A1]: MODULAR POWER CONVERTER [FR EP3776836A1]: CONVERTISSEUR DE PUISSANCE MODULAIRE [ZH CN112512858A]: 模块化变流器 | [DE WO2020025376A1]: Die Erfindung betrifft einen modularen Stromrichter (1) mit Wide-Bandgap Halbleitern (2), insbesondere SiC Halbleitern. Zur Optimierung des Stromrichter hinsichtlich des des Einsatzes von Wide-Bandgap Halbleitern wird vorgeschlagen, dass der modulare Stromrichter (1) mindestens zwei Grundeinheiten (10) aufweist, wobei die Grundeinheiten (10) eingangsseitig miteinander verbunden sind, wobei eine Grundeinheit eingangsseitig eine EingangsSchaltung (11) und ausgangsseitig eine Ausgangschaltung (12) aufweist, wobei EingangsSchaltung (11) und AusgangsSchaltung (12) jeweils durch die Wide-Bandgap Halbleiter (2) gebildet werden, die in einer B6 BrückenSchaltung angeordnet sind mit, wobei ein Zwischenkreiskondensator (3) parallel sowohl zur EingangsSchaltung (11) als auch zur AusgangsSchaltung (12) verbunden ist und damit die Zwischenkreise der EingangsSchaltung (11) und der AusgangsSchaltung (12) zu einem Zwischenkreis (13) miteinander verbindet, wobei die Eingangsschaltungen (11) der Grundeinheiten (10) oder einer Teilmenge der Grundeinheiten (10) in einer Reihenschaltung angeordnet sind, wobei jeweils zwischen zwei EingangsSchaltungen (11) mindestens eine Induktivität (15) angeordnet ist. Ferner betrifft die Erfindung ein Fahrzeug (100), insbesondere ein Schienenfahrzeug, mit einem derartigen modularen Stromrichter (1), wobei der modulare Stromrichter (1) ein Teil des Antriebs (101) des Fahrzeugs (100) ist. [EN US2021297001A1]: A modular power converter with wide-bandgap semiconductors, in particular SiC semiconductors. The modular power converter has at least two base units. The base units are connected together on the input side, and each base unit has an input circuit on the input side and an output circuit on the output side. The input circuit and the output circuit are each formed by the wide-bandgap semiconductors arranged in a B6-bridge circuit. An intermediate circuit capacitor is connected in parallel with the input circuit and the output circuit forming an intermediate circuit. The input circuits of the base units or a sub-quantity of the base units are arranged in a series circuit. At least one inductor is arranged between each pair of input circuits. [FR WO2020025376A1]: L'invention concerne un convertisseur de puissance modulaire (1) à semi-conducteurs à large bande interdite (2), notamment des semi-conducteurs SiC. Pour optimiser le convertisseur en termes d'utilisation de semi-conducteurs à large bande interdite, il est proposé que le convertisseur de puissance modulaire (1) comporte au moins deux unités de base (10). Les unités de base (10) sont reliées les unes aux autres côté entrée. Une unité de base comporte un circuit d'entrée (11) côté entrée et un circuit de sortie (12) côté sortie. Le circuit d'entrée (11) et le circuit de sortie (12) sont chacun formés par les semi-conducteurs à large bande interdite (2) qui sont disposés dans un circuit en pont B6. Un condensateur de circuit intermédiaire (3) est relié en parallèle au circuit d'entrée (11) et au circuit de sortie (12) et relie ainsi les circuits intermédiaires du circuit d'entrée (11) et du circuit de sortie (12) pour former un circuit intermédiaire (13). Les circuits d'entrée (11) des unités de base (10) ou un sous-ensemble d'unités de base (10) sont disposés dans un circuit série. Au moins une inductance (15) est disposée à chaque fois entre deux circuits d'entrée (11). L'invention concerne en outre un véhicule (100), notamment un véhicule ferroviaire, comprenant un tel convertisseur de puissance modulaire (1). Le convertisseur de puissance modulaire (1) fait partie de l'entraînement (101) du véhicule (100). [ZH CN112512858A]: 本发明涉及一种具有宽带隙半导体(2)、特别是SiC半导体的模块化变流器(1)。为了在使用宽带隙半导体方面优化变流器而提出：模块化变流器(1)具有至少两个基础单元(10)，其中，基础单元(10)在输入侧彼此连接，其中，基础单元在输入侧具有输入电路(11)并且在输出侧具有输出电路(12)，其中，输入电路(11)和输出电路(12)分别通过宽带隙半导体(2)形成，该宽带隙半导体布置在B6桥式电路中，其中，中间电路电容器(3)与输入电路(11)和输出电路(12)并联连接，进而输入电路(11)和输出电路(12)的中间电路彼此连接成中间电路(13)，其中，基础单元(10)或基础单元(10)的子集的输入电路(11)布置在串联电路中，其中，在两个输入电路(11)之间相应地设置有至少一个电感(15)。此外，本发明涉及一种交通工具(100)、特别是轨道交通工具，其具有这种模块化变流器(1)，其中，模块化变流器(1)是交通工具(100)的驱动器(101)的一部分。 | WO2020025376A1 | 2020-02-06 | EP2019069649W | 2019-07-22 | EP18000636A, 2018-07-31 | WO2020025376A1: 2020-02-06 EP3776836A1: 2021-02-17 CA3108004A1: 2020-02-06 CN112512858A: 2021-03-16 US2021297001A1: 2021-09-23 | SIEMENS AG | BAKRAN MARK-MATTHIAS BÖHMER JÜRGEN HELSPER MARTIN KRAFFT EBERHARD ULRICH LASKA BERND NAGEL ANDREAS SCHÖNEWOLF STEFAN HANS WERNER WEIGEL JAN BOHMER JURGEN SCHONEWOLF STEFAN HANS WERNER | H02M7/5387: I B60L15/00: I H02M5/458: I | B60L15/007: I H02M5/4585: I H02M1/007: A H02M1/0074: A Y02T10/64: A B60L15/002: I H02M5/458: I | KR100970566B1 US2013248883A1 DE102013215992A1 DE8810279U1 EP3184351A1 |  | [DE EP3776836A1]: Patentansprüche1. Modularer Stromrichter (1) mit Wide-Bandgap Halbleitern (2), insbesondere SiC Halbleitern, wobei der modulare Strom richter (1) mindestens zwei Grundeinheiten (10) aufweist, wo bei die Grundeinheiten (10) eingangsseitig miteinander ver bunden sind, wobei eine Grundeinheit eingangsseitig eine Ein gangsschaltung (11) und ausgangsseitig eine Ausgangschaltung (12) aufweist, wobei Eingangsschaltung (11) und Ausgangs schaltung (12) jeweils durch die Wide-Bandgap Halbleiter (2) gebildet werden, die in einer B6 Brückenschaltung angeordnet sind, wobei ein Zwischenkreiskondensator (3) parallel sowohl zur Eingangsschaltung (11) als auch zur Ausgangsschaltung (12) verbunden ist und damit die Zwischenkreise der Eingangs schaltung (11) und der Ausgangsschaltung (12) zu einem Zwi schenkreis (13) miteinander verbindet, wobei die Eingangs schaltungen (11) der Grundeinheiten (10) oder einer Teilmenge der Grundeinheiten (10) in einer Reihenschaltung angeordnet sind, wobei jeweils zwischen zwei Eingangsschaltungen (11) mindestens eine Induktivität (15) angeordnet ist. 2. Modularer Stromrichter (1) nach Anspruch 1, wobei die Grundeinheit (10) eine Kühleinheit (14) aufweist, wobei die Kühleinheit (14) gegenüber den Wide-Bandgap Halbleitern (2) elektrisch isoliert ist. 3. Modularer Stromrichter (1) nach einem der Ansprüche 1 oder2, wobei eine weitere Teilmenge der Grundeinheiten (10) oder die Eingangsschaltungen (10) einer weiteren Teilmenge der Grundeinheiten (10) in einer Parallelschaltung angeordnet sind . 4. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis3, wobei eine erste Phase (21) der Eingangsschaltung (11) ei ner ersten Grundeinheit (10) mit der ersten Phase (21) der Eingangsschaltung (11) einer zweiten Grundeinheit (10) ver bunden ist. 5. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis4, wobei eine erste Phase (21) der Eingangsschaltung (11) ei ner ersten Grundeinheit (10) mit dem Zwischenkreis (13) einer zweiten Grundeinheit (10) verbunden ist. 6. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis5, wobei eine zweite Phase (22) der Eingangsschaltungen (11) der ersten Grundeinheit (10) mit der zweiten Phase (22) der Eingangsschaltung (11) der zweiten Grundeinheit (10) verbun den ist. 7. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis 5, wobei eine zweite Phase (22) der Eingangsschaltungen (11) der ersten Grundeinheit (10) mit dem Zwischenkreis (13) der zweiten Grundeinheit (10) verbunden ist. 8. Modularer Stromrichter (1) nach einem der Ansprüche 4 bis 5, wobei der modulare Stromrichter (1) mindestens drei Grund einheiten (10) aufweist, wobei eine zweite Phase (22) der Eingangsschaltung (11) der zweiten Grundeinheit (10) mit ei ner Phase (21,22,23) der Eingangsschaltung (11) einer dritten Grundeinheit (10) verbunden ist. 9. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis8, wobei die Eingangsschaltungen (11) zweier Grundeinheiten (10) gleichspannungsseitig in einer Reihenschaltung angeord net sind. 10. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis9, wobei die Ausgangsschaltungen (12) von mindestens zwei der Grundeinheiten (10) jeweils mit unterschiedlichen Wicklungs systemen (41) eines Motors (4) verbunden sind. 11. Modularer Stromrichter (1) nach einem der Ansprüche 1 bis10, wobei eine dritte Phase (23) der Grundeinheit (10) derart mit einem Widerstand (5) verbunden ist, um die Funktion eines Bremsstellers zu realisieren. 12. Fahrzeug (100), insbesondere ein Schienenfahrzeug, mit einem modularen Stromrichter (1) nach einem der Ansprüche 1 bis 11, wobei der modulare Stromrichter (1) ein Teil des An triebs (101) des Fahrzeugs (100) ist. [EN US2021297001A1]: 1.-12. (canceled) 13. A modular power converter, comprising: at least two basic units, each of the at least two basic units comprising an input side having an input circuit, and an output side having an output circuit, said at least two basic units connected to one another on the input sides, said input circuits of the at least two basic units or a subset of the at least two basic units being arranged in a series circuit, each of the input circuits and output circuits comprising wide-bandgap semiconductors in a B6 bridge circuit configuration;an intermediate circuit in each of the at least two basic units, each said intermediate circuit comprising an intermediate circuit capacitor connected in parallel to both the input circuit and output circuit and connecting the input circuit to the output circuit;an inductor arranged between two input circuits;a first connection between a first phase of the input circuit of a first one of the at least two basic units and a first phase of the input circuit of a second one of the at least two basic units; anda second connection between a second phase of the input circuit of the first one of the at least two basic units and a second phase of the input circuit of the second one of the at least two basic units. 14. The modular power converter of claim 13, further comprising a further said inductor, the first connection comprising one of the inductors, and the second connection comprising the further one of the inductors. 15. The modular power converter of claim 13, wherein a further subset of the at least two basic units or the input circuits of a further subset of the at least two basic units are connected in parallel. 16. The modular power converter of claim 13, wherein each of the at least two basic units comprises a cooling unit electrically insulated against the wide-bandgap semiconductors. 17. The modular power converter of claim 13, wherein the input circuits of the at least two basic units are arranged in a series circuit on a direct voltage side. 18. The modular power converter of claim 13, wherein the output circuits of the at least two basic units are connected to different winding systems of a motor. 19. The modular power converter of claim 13, further comprising resistors functioning as braking choppers and connected to a third phase of each the at least two basic units in one-to-one correspondence. 20. The modular power converter of claim 13, wherein the wide-bandgap semiconductors are embodied as SiC semiconductors and have a blocking voltage of 1700V. 21. A vehicle, comprising: a drive comprising a modular power converter, said modular power converter comprising at least two basic units, each of the at least two basic units comprising an input side having an input circuit, and an output side having an output circuit, said at least two basic units connected to one another on the input sides, said input circuits of the at least two basic units or a subset of the at least two basic units being arranged in a series circuit, each of the input circuits and output circuits comprising wide-bandgap semiconductors in a B6 bridge circuit configuration, an intermediate circuit in each of the at least two basic units, each said intermediate circuit comprising an intermediate circuit capacitor connected in parallel to both the input circuit and output circuit and connecting the input circuit to the output circuit, an inductor arranged between two input circuits, a first connection between a first phase of the input circuit of a first one of the at least two basic units and a first phase of the input circuit of a second one of the at least two basic units, and a second connection between a second phase of the input circuit of the first one of the at least two basic units and a second phase of the input circuit of the second one of the at least two basic units; anda current collector configured to supply electrical energy to the input circuits of the modular power converter from a catenary. 22. The vehicle of claim 21, wherein the modular power converter includes a further said inductor, the first connection comprising one of the inductors, and the second connection comprising the further one of the inductors. 23. The vehicle of claim 21, wherein a further subset of the at least two basic units or the input circuits of a further subset of the at least two basic units are connected in parallel. 24. The vehicle of claim 21, wherein each of the at least two basic units comprises a cooling unit electrically insulated against the wide-bandgap semiconductors. 25. The vehicle of claim 21, wherein the input circuits of the at least two basic units are arranged in a series circuit on a direct voltage side. 26. The vehicle of claim 21, wherein the output circuits of the at least two basic units are connected to different winding systems of a motor. 27. The vehicle of claim 21, wherein the modular power converter includes resistors functioning as braking choppers and connected to a third phase of each the at least two basic units in one-to-one correspondence. 28. The vehicle of claim 21, wherein the wide-bandgap semiconductors are embodied as SIC semiconductors and have a blocking voltage of 1700V. 29. The vehicle of claim 21, wherein the vehicle is a rail vehicle. [ZH CN112512858A]: 1 .一种模块化变流器(1),具有宽带隙半导体(2)、特别是SiC半导体，其中，所述模块化 变流器⑴具有至少两个基础单元(10)，其中，所述基础单元(10)在输入侧彼此连接，其中， 所述基础单元在输入侧具有输入电路(11)并且在输出侧具有输出电路(12)，其中，所述输 入电路(11)和所述输出电路(12)分别通过所述宽带隙半导体⑵形成，所述宽带隙半导体 布置在B6桥式电路中，其中，中间电路电容器⑶与所述输入电路(11)和所述输出电路(12) 并联连接，进而所述输入电路(11)和所述输出电路(12)的中间电路彼此连接成中间电路 (13)，其中，所述基础单元(10)的所述输入电路或所述基础单元(10)的子集的所述输入电 路(11)布置在串联电路中，其中，在两个所述输入电路(11)之间相应地布置有至少一个电 感(15)。 2 .根据权利要求1所述的模块化变流器(1)，其中，所述基础单元(10)具有冷却单元 (14)，其中，所述冷却单元(14)相对于所述宽带隙半导体⑵电绝缘。 3 .根据权利要求1或2所述的模块化变流器(1)，其中，所述基础单元(10)的另一子集或 者所述基础单元的另一子集的所述输入电路(10)布置在并联电路中。 4 .根据权利要求1至3中任一项所述的模块化变流器(1)，其中，第一基础单元(10)的输 入电路(11)的第一相(21)与第二基础单元(10)的输入电路(11)的第一相(21)连接。 5 .根据权利要求1至4中任一项所述的模块化变流器(1)，其中，第一基础单元(10)的输 入电路(11)的第一相(21)与第二基础单元(10)的中间电路(13)连接。 6 .根据权利要求1至5中任一项所述的模块化变流器(1)，其中，所述第一基础单元(10) 的输入电路(11)的第二相(22)与所述第二基础单元(10)的输入电路(11)的第二相(22)连 接。 7 .根据权利要求1至5中任一项所述的模块化变流器(1)，其中，所述第一基础单元(10) 的输入电路(11)的第二相(22)与所述第二基础单元(10)的中间电路(13)连接。 8 .根据权利要求4至5中任一项所述的模块化变流器(1)，其中，所述模块化变流器(1) 具有至少三个基础单元(10)，其中所述第二基础单元(10)的输入电路(11)的第二相(22)与 第三基础单元(10)的输入电路(11)的相(21、22、23)连接。 9 .根据权利要求1至8中任一项所述的模块化变流器(1)，其中，两个所述基础单元(10) 的所述输入电路(11)在直流电压侧布置在串联电路中。 10 .根据权利要求1至9中任一项所述的模块化变流器(1)，其中，所述基础单元(10)中 的至少两个基础单元的输出电路(12)分别与马达⑷的不同的绕组系统(41)连接。 11 .根据权利要求1至10中任一项所述的模块化变流器⑴，其中，所述基础单元(10)的 第三相(23)与电阻(5)连接，以便实现制动斩波器的功能。 12 . 一种交通工具(100)，特别是轨道交通工具，所述交通工具具有根据权利要求1至11 中任一项所述的模块化变流器⑴，其中，所述模块化变流器⑴是所述交通工具(100)的驱 动器(101)的一部分。 | [DE EP3776836A1]: Beschreibung Modularer Stromrichter Die Erfindung betrifft einen modularen Stromrichter mit Wide- Bandgap-Halbleitern . Ferner betrifft die Erfindung ein Fahr zeug, insbesondere ein Schienenfahrzeug, mit einem derartigen modularen Stromrichter. Halbleiter mit breitem Bandabstand (englisch wide-bandgap se- miconductors , davon abgeleitet Wide-Bandgap-Halbleiter aber breitbandige Halbleiter) sind Halbleiter, deren Bandabstand/- Bandlücke (Energieabstand zwischen Valenzband und Leitungs band) am oberen Ende des Bereichs der Halbleiter (3 eV bis über 4 eV) liegt (Quelle: Wikipedia.de) . Diese kommen auf grund ihrer Leistungsfähigkeit voraussichtlich in naher Zu kunft auch in dem Antrieb von Fahrzeugen zum Einsatz. Diese Antriebe werden auch als Traktion, die dazugehörigen Strom richter als Traktionsumrichter bezeichnet. Halbleiter auf der Basis von Siliziumcarbid (SiC) , SiC Halbleiter, sind Wide- Bandgap-Halbleiter . Traktionsumrichter für Bahnantriebe sind durch einen großen Einsatzbereich geprägt. Der Leistungsbereich liegt auf der Motorseite in dem Bereich von etwa 100kW bis 2000kW. Bei der Eingangsspannung muss der Bereich von 750V bis 3000V abge deckt werden. Die zukünftig eingesetzten SiC Halbleiter (MOSFET) zeigen die typische Charakteristik eines unipolaren Bauelementes, nämlich, dass die Leistungsfähigkeit stark nachlässt bei höheren Auslegungsspannungen. Es gilt der Zu sammenhang, dass RDS on in etwa proportional zu Usperr2'5 ist. Ferner haben SiC Halbleiter pro Chip nur eine geringe Strom tragfähigkeit . Der heutige Stand der Technik bei Traktionsumrichtern ist der Einsatz von IGBTs. Diese existieren heute in passenden Span nungsklassen, bei Traktionsumrichtern in Schienenfahrzeugen typisch 1700V, 3300V und 6500V, womit sie direkt zu den Bahn- betriebsspannungen 750V, 1500V und 3000V DC passen. Auch existieren viele Stromklassen. Der Stand der Technik ist da mit die Verwendung eines passenden IGBT Halbleiters für die jeweils benötigte Spannungs- und Stromklasse des Traktionsum richters im Schienenfahrzeug. Der Erfindung liegt die Aufgabe zugrunde einen Stromrichter hinsichtlich des Einsatzes von Wide-Bandgap-Halbleitern zu optimieren . Diese Aufgabe wird durch einen modularer Stromrichter mit Wi de-Bandgap-Halbleitern, insbesondere SiC Halbleitern, gelöst, wobei der modulare Stromrichter mindestens zwei Grundeinhei ten aufweist, wobei die Grundeinheiten eingangsseitig mitei nander verbunden sind, wobei eine Grundeinheit eingangsseitig eine Eingangsschaltung und ausgangsseitig eine Ausgangschal tung aufweist, wobei Eingangsschaltung und Ausgangsschaltung jeweils durch die Wide-Bandgap Halbleiter gebildet werden, die in einer B6 Brückenschaltung angeordnet sind mit, wobei ein Zwischenkreiskondensator parallel sowohl zur Eingangs schaltung als auch zur Ausgangsschaltung verbunden ist und damit die Zwischenkreise der Eingangsschaltung und der Aus gangsschaltung zu einem Zwischenkreis miteinander verbindet, wobei die Eingangsschaltungen der Grundeinheiten oder einer Teilmenge der Grundeinheiten in einer Reihenschaltung ange ordnet sind, wobei jeweils zwischen zwei Eingangsschaltungen mindestens eine Induktivität angeordnet ist. Die Aufgabe wird weiter durch ein Fahrzeug, insbesondere durch ein Schienen fahrzeug, mit einem derartigen modularen Stromrichter gelöst, wobei der modulare Stromrichter zumindest ein Teil des An triebs des Fahrzeugs ist. Weitere vorteilhafte Ausgestaltungen der Erfindung sind in den abhängigen Ansprüchen angegeben. Der Erfindung liegt die Erkenntnis zugrunde, dass sich die Aufgabe durch das Verschalten mehrerer, d.h. mindestens zwei er, Grundeinheiten lösen lässt. Dabei wird das Problem durch eine standardisierte Grundeinheit gelöst, welche als Halblei ter Wide-Bandgap Halbleiter (typischerweise auf der Basis von SiC) einsetzt von der optimalen Spannungsklasse, was etwa 1700V Sperrspannung sind. 1700V ergeben sich als etwa optima ler Wert, da dort bei dem SiC Bauelement die Dicke noch rela tiv gering ist und der Durchlassspannungsabfall noch stark vom Kanalwiderstand geprägt ist. Die typische Leistungsklasse der Grundeinheit liegt bei etwa 100kW. Mit anderen Worten weiden die Halbleiter der Eingangsschaltung und/oder der Aus gangschaltung bei einer vorteilhaften Ausgestaltung eine Sperrspannung von 1700V auf. Die Erfindung stellt eine Lösung dar, wie mit einer in Span nung und Strom kleinen SiC Halbleitern basierten Grundeinheit der gesamte Leistungs- und Spannungsbereich abgedeckt werden kann. Dazu wird die Eigenschaft verwendet, dass immer nur SiC Halbleiter der optimalen kleinen Sperrspannung und des opti malen kleinen Stromes zur Anwendung kommen und die Grundein heit bilden, von denen dann mehrere je nach Anforderung in Bezug auf Leistung und/oder Versorgungsspannung zusammenge schaltet werden können. Aus diesen Wide-Bandgap Halbleitern wird eine Grundeinheit definiert, die zweimal drei Phasen, d.h. jeweils eine Ein gangsschaltung und eine Ausgangsschaltung mit jeweils drei Phasen, umfasst, sowie einen Zwischenkreis mit einem Zwi schenkreiskondensator, sowie zugehörige Verbindungen und die Ansteuerung der Halbleiter. Ferner umfasst die Grundeinheit eine mechanische Integration inklusive Kühlvorrichtung für die Halbleiter. Dabei sind die elektrischen Teile der Grund einheit gegen die Mechanik und die Kühlung isoliert. Vorteilhaft dabei ist, dass die Grundeinheit auf der Ein gangsseite und/oder der Ausgangsseite parallel und/oder in Reihe zu einer oder mehreren weiteren identischen Grundein heiten geschaltet wird, und dadurch der Gesamtstrom oder die erreichbare Spannung erhöht wird. Durch eine Parallelschal tung kann der Gesamtstrom, den der modulare Stromrichter zur Verfügung stellen kann, erhöht werden. Dabei kann der modula re Stromrichter auch eine Reihenschaltung, parallelgeschalte ter Grundeinheiten aufweisen, die damit sowohl Gesamtstrom erhöhen auch als die erreichbare Spannung vergrößern. Die Grundeinheiten werden auf der Eingangsseite mit Hilfe von In duktivitäten in Reihe geschaltet, um so an eine höhere Span nung anschließbar zu sein. Durch die Induktivitäten ist der Eingangsstrom des modularen Stromrichters Steuer- bzw. regel bar. Dabei erfolgt die Serienschaltung so, dass eine Phase einer Grundeinheit jeweils mit einer Induktivität an den Zwi schenkreis, beispielsweise an die Minus-Schiene, der nächsten Grundeinheit angeschlossen wird. Die potentialmäßig nächsten Induktivitäten werden dann an die eingangsseitige versorgende positive Seite der DC-Spannung angeschlossen, während die po tentialmäßig unterste Minusschiene an dem Minuspol der ein gangsseitigen DC Spannung angeschlossen wird. An der dreipha sigen Ausgangsseite kann ein Motor angeschlossen werden mit einem dreisträngigen Wicklungssystem. Besonders vorteilhaft ist es, wenn bei Verwendung mehrerer Grundeinheiten an den mehreren dreiphasigen Ausgangsseiten ein Motor mit mehreren 3phasigen Wicklungssystemen ange schlossen wird. Das sind zum Beispiel Motoren mit einem 6- oder 9- oder 12-strängigen Wicklungssystem. Für den Fall einer AC Versorgung ist es vorteilhaft, wenn die eingangsseitige Serienschaltung der Grundeinheiten so er folgt, dass an der untersten Grundschaltung ein Phasenan schluss an einem Pol der AC-Spannung liegt. Der zweite ein gangsseitige Phasenanschluss dann wird mit der zweiten Phase der nächsten Grundeinheit verbunden. Auf eine Induktivität zwischen den Grundeinheiten kann, allerdings nicht notwendi gerweise, bei der Verwendung für eine Eingangsseitig anlie gende Wechselspannung verzichtet werden. Die erste Phase wird dann wieder mit der ersten Phase der nächsten Grundeinheit verbunden. Dann wieder die zweite Phase mit der darauf fol genden zweiten Phase usw. bis die letzte Phase dann mit dem anderen AC-Anschluss verbunden wird. Darüber hinaus ist vorteilhaft, dass an der Eingangsseite die speisende Spannung sowohl DC als auch AC sein kann, indem entweder die Grundeinheiten alle wie ein Hochsetzsteller in Serie geschaltet werden oder zwei der Eingangs Phasen jeweils so in Serie mit den zwei Phasen der nächsten Grundeinheit ge schaltet werden, dass ein sogenannter 4-Qudrantensteller ent steht . Darüber hinaus ist es vorteilhaft, wenn an die dritte ein gangsseitige Phase der Grundeinheit ein Widerstand ange schlossen wird, der zur Vernichtung von Leistung eingesetzt wird, wenn bei einem Bremsvorgang das Netz nicht die gesamte Bremsleistung aufnehmen kann. Die Funktion dieser Phase wird auch als Bremssteller bezeichnet. Im Folgenden wird die Erfindung anhand der in den Figuren dargestellten Ausführungsbeispiele näher beschrieben und er läutert. Es zeigen: FIG 1 eine Grundeinheit, FIG 2 das Schaltbild eines Wide-Bandgap Halb leiters, FIG 3 eine Parallelschaltung zweier Grundein heiten, FIG 4 bis FIG 8 Reihenschaltungen von Grundeinheiten, FIG 9 einen Motor am Ausgang eines modularen Stromrichters und FIG 10 ein Fahrzeug mit einem modularen Stromrich ter als Teil des Antriebs. Die FIG 1 zeigt eine Grundeinheit 10. Diese weist eine Ein gangsschaltung 11 und eine Ausgangsschaltung 12 auf. Diese sind gleichspannungsseitig zu einem Zwischenkreis 13 mitei nander verbunden. Im Zwischenkreis 13 ist ein Kondensator 3 angeordnet. Die Eingangsschaltung 11 und die Ausgangsschal tung 12 weisen jeweils eine B6 Brückenschaltung aus Wide- Bandgap Halbleitern 2 auf. Die Phasenanschlüsse, auch als Phasen bezeichnet sind als Eingänge und Ausgänge nach außen geführt. Zudem weist die Grundeinheit eine Kühleinheit 14 auf. Die Strömung des Kühlmittels, Luft oder Flüssigkeit ist mit Pfeilen gekennzeichnet. Die FIG 2 zeigt einen Wide-Bandgap Halbleiter 2 mit seiner Ansteuerung 25. In Rückwärtsrichtung ist dieser leitend. Für den Fall, dass dieser in einer Ausführung rückwärts sperrend ausgelegt ist, wird zu dem Halbleiterschalter eine hier nicht dargestellte antiparallele Diode angeordnet, die dem Halblei ter 2 seine Eigenschaft verleiht, in Rückwärtsrichtung lei tend zu sein. Die FIG 3 zeigt eine Parallelschaltung zweier Grundeinheiten 10. Diese sind sowohl eingangsseitig als auch ausgangsseitig an allen drei Phasen parallelgeschaltet. Die FIG 4 zeigt eine Reihenschaltung zweier Grundeinheiten 10. Diese Abbildung zeigt nur das Prinzip der Reihenschal tung. Diese ist auf beliebig viele Grundeinheiten 10 erwei terbar. Ebenso kann eine hier dargestellte Grundeinheit 10 eine Parallelschaltung mehrerer Grundeinheiten 10 sein. Die Parallelschaltung erfolgt eingangsseitig an der Eingangs schaltung. Die erste Phase 21 der ersten Eingangsschaltung ist mit der ersten Phase 21 der zweiten Eingangsschaltung über eine Induktivität 15 verbunden. Darüber hinaus ist auch die zweite Phase 22 der ersten Eingangsschaltung mit der zweiten Phase 22 der zweiten Eingangsschaltung über eine wei tere Induktivität 15 verbunden. Die dritte Phase 23 weist ei nen Bremswiderstand 5 auf, der zu einem Bremssteller ver schaltet ist. Die FIG 5 zeigt ein weiteres Ausführungsbeispiel einer Rei henschaltung. Auch hier können die einzelnen Grundeinheiten 10 eine beliebige Parallelschaltung mehrerer Grundeinheiten 10 darstellen. Auch lässt sich diese dargestellte Schaltung auf eine Reihenschaltung beliebig vieler Grundeinheiten er weitern. Dabei ist es möglich, zwei Grundeinheiten 10 an der Eingangsschaltung 11 gleichspannungsseitig in Reihe zu schal- ten. Damit sind dann die Zwischenkreise 13 der betreffenden Grundeinheiten 10 in Reihe geschaltet. Zur Vermeidung von Wiederholungen wird auf die Beschreibung zu der FIG 4 sowie auf die dort eingeführten Bezugszeichen verwiesen. Die FIG 6 zeigt ein weiteres Ausführungsbeispiel einer Rei henschaltung. Auch hier können die einzelnen Grundeinheiten 10 eine beliebige Parallelschaltung mehrerer Grundeinheiten 10 darstellen. Auch lässt sich diese dargestellte Schaltung auf eine Reihenschaltung beliebig vieler Grundeinheiten 10 erweitern. Bei dieser Schaltung sind die erste Phase 21 und die zweite Phase 22 einer ersten Grundeinheit 10 jeweils über eine Induktivität 15 mit dem Zwischenkreis einer zweiten Grundeinheit 10 verbunden. Auch hier können Grundeinheiten 10 auch Verschaltungen der Figuren 4 und 5 aufweisen. Zur Ver meidung von Wiederholungen wird auf die Beschreibung zu den Figuren 4 und 5 sowie auf die dort eingeführten Bezugszeichen verwiesen . Die FIG 7 zeigt ein weiteres Ausführungsbeispiel einer Rei henschaltung. Auch hier können die einzelnen Grundeinheiten 10 eine beliebige Parallelschaltung mehrerer Grundeinheiten 10 darstellen. Auch lässt sich diese dargestellte Schaltung auf eine Reihenschaltung beliebig vieler Grundeinheiten 10 erweitern. Dabei können Grundeinheiten 10 auch Kombinationen der Figuren 4 bis 6 aufweisen. Bei dieser Schaltung sind nicht nur die erste Phase 21 und die zweite Phase 22 der ers ten Grundeinheit 10 jeweils über Induktivitäten 15 mit dem Zwischenkreis 13 der zweiten Grundeinheit 10 verbunden son dern darüber hinaus auch die erste Phase 21 und die zweite Phase 22 der zweiten Grundeinheit 10 jeweils über Induktivi täten 15 mit dem Zwischenkreis 13 der ersten Grundeinheit 10 verbunden. Zur Vermeidung von Wiederholungen wird auf die Be schreibung zu den Figuren 4 bis 6 sowie auf die dort einge führten Bezugszeichen verwiesen. Die FIG 8 zeigt ein Ausführungsbeispiel für eine Reihenschal tung, die sich im Besonderen für eine Versorgung der Ein- gangsseite mit einer Wechselspannung eignet. Durch die Induk tivität des Transformators kann auf das Einbringen von weite ren Induktivitäten zwischen den Grundeinheiten 10 verzichtet werden. Auch hier können die einzelnen Grundeinheiten 10 eine beliebige Parallelschaltung mehrerer Grundeinheiten 10 dar stellen. Auch lässt sich diese dargestellte Schaltung auf ei ne Reihenschaltung beliebig vieler Grundeinheiten 10 erwei tern. In diesem Ausführungsbeispiel ist die erste Phase 21 der ersten Grundeinheit 10 direkt mit der ersten Phase der zweiten Grundeinheit 10 verbunden und die zweite Phase 22 der zweiten Grundeinheit 10 direkt mit einer Phase, in diesem Fall die erste Phase 21, einer dritten Grundeinheit verbun den. Dabei können Grundeinheiten 10 auch Kombinationen der Figuren 4 bis 8 aufweisen. Zur Vermeidung von Wiederholungen wird auf die Beschreibung zu den Figuren 4 bis 8 sowie auf die dort eingeführten Bezugszeichen verwiesen. Die FIG 9 zeigt eine mögliche Verbindung der Ausgangsschal tungen 12 mit einem Motor 4. Aus Gründen der Übersichtlich keit sind die Eingangsschaltungen 11 nicht dargestellt. Diese können beliebig nach einer der Figuren 3 bis 8, oder einer Kombination aus diesen verschaltet sein. Dabei sind die Aus gangschaltungen unterschiedlicher Grundeinheiten 10 jeweils mit einem Wicklungssystem 41 des Motors verbunden. Somit kann auch bei vergleichsweise geringer Leistungsfähigkeit einer Grundeinheit ein Motor 4 mit großer Leistungsfähigkeit ange trieben werden. Die FIG 10 zeigt ein Fahrzeug 100, das als Schienenfahrzeug ausgebildet ist. Dabei ist der modulare Stromrichter 1 Teil des Antriebs 101 des Fahrzeugs 100. Das Fahrzeug 100 bezieht seine elektrische Anergie über einen Stromabnehmer 102 aus einer nicht dargestellten Fahrleitung und führt diese der Eingangsschaltung des modularen Stromrichters 1 zu. Die Aus gangsschaltung ist mit den hier nicht dargestellten Motoren des Fahrzeugs 100 verbunden und treibe diese an. Zusammenfassend betrifft die Erfindung einen modularen Strom richter mit Wide-Bandgap Halbleitern, insbesondere SiC Halb leitern. Zur Optimierung des Stromrichter hinsichtlich des des Einsatzes von Wide-Bandgap Halbleitern wird vorgeschla gen, dass der modulare Stromrichter mindestens zwei Grundein heiten aufweist, wobei die Grundeinheiten eingangsseitig mit einander verbunden sind, wobei eine Grundeinheit eingangssei tig eine Eingangsschaltung und ausgangsseitig eine Ausgang schaltung aufweist, wobei Eingangsschaltung und Ausgangs schaltung jeweils durch die Wide-Bandgap Halbleiter gebildet werden, die in einer B6 Brückenschaltung angeordnet sind mit, wobei ein Zwischenkreiskondensator parallel sowohl zur Ein gangsschaltung als auch zur Ausgangsschaltung verbunden ist und damit die Zwischenkreise der Eingangsschaltung und der Ausgangsschaltung zu einem Zwischenkreis miteinander verbin det, wobei die Eingangsschaltungen der Grundeinheiten oder einer Teilmenge der Grundeinheiten in einer Reihenschaltung angeordnet sind, wobei jeweils zwischen zwei Eingangsschal tungen mindestens eine Induktivität angeordnet ist. Ferner betrifft die Erfindung ein Fahrzeug, insbesondere ein Schie nenfahrzeug, mit einem derartigen modularen Stromrichter, wo bei der modulare Stromrichter ein Teil des Antriebs des Fahr zeugs ist. [EN US2021297001A1]: The invention relates to a modular power converter with wide-bandgap semiconductors. The invention further relates to a vehicle, in particular a rail vehicle, with such a modular power converter. Wide-bandgap semiconductors are semiconductors whose bandgap (energy gap between valence band and conduction band) is at the upper end of the range of semiconductors (3 eV to over 4 eV) (source: Wikipedia.de). Because of their performance they are expected to be used in the near future in vehicle drives as well. These drives are also known as traction, and the associated power converters are known as traction converters. Semiconductors based on silicon carbide (SiC), SiC semiconductors, are wide-bandgap semiconductors. Traction converters for rail drives are characteristically used in a wide range of functions. On the motor side the power range is between approximately 100 kW and 2000 kW. In respect of the input voltage the range from 750V to 3000V must be covered. The SiC semiconductors (MOSFET) used in future are typically characterized by a unipolar component, namely the performance decreases significantly at higher design voltages. RDS on correlates approximately proportionally to Ublock2,5. Furthermore, SiC semiconductors only have a low current-carrying capacity per chip. The current prior art for traction converters entails the use of IGBTs. These currently exist in suitable voltage classes, in the case of traction converters in rail vehicles typically 1700V, 3300V and 6500V, meaning that they directly match the rail operating voltages of 750V, 1500V and 3000V DC. There are also many current classes. The prior art thus entails the use of a suitable IGBT semiconductor for the respectively required voltage class and current class of the traction converter in the rail vehicle. The object underlying the invention is to optimize a power converter in respect of the use of wide-bandgap semiconductors. This object is achieved by a modular power converter with wide-bandgap semiconductors, in particular SiC semiconductors, wherein the modular power converter has at least two basic units, wherein the basic units are connected to one another on the input side, wherein a basic unit has an input circuit on the input side and an output circuit on the output side, wherein input circuit and output circuit are each formed by the wide-bandgap semiconductors which are arranged in a B6 bridge circuit, wherein an intermediate circuit capacitor is connected in parallel both to the input circuit and to the output circuit and thus the intermediate circuits of the input circuit and the output circuit are connected to one another to form an intermediate circuit, wherein the input circuits of the basic units or a subset of the basic units are arranged in a series circuit, wherein at least one inductor is arranged between two input circuits. The object is further achieved by a vehicle, in particular by a rail vehicle, with such a modular power converter, wherein the modular power converter is at least one part of the drive of the vehicle. Further advantageous embodiments of the invention are specified in the dependent claims. The invention is based on the finding that the object can be achieved by interconnecting several, i.e. at least two, basic units. In this case the problem is solved by a standardized basic unit which as semiconductors uses wide-bandgap semiconductors (typically based on SiC) from the optimum voltage class, which are approximately 1700V blocking voltage. 1700V proves to be approximately the optimum value, since in the case of the SiC component the thickness is still relatively small there and the on-state voltage drop is still strongly characterized by the channel resistance. The typical performance class of the basic unit is approximately 100 kW. In other words, in an advantageous embodiment the semiconductors of the input circuit and/or of the output circuit have a blocking voltage of 1700V. The invention represents a solution for how the total power and voltage range can be covered with a basic unit based on low-voltage and low-current SiC semiconductors. To this end, use is made of the attribute that only SiC semiconductors featuring the optimum small blocking voltage and the optimum small current are used and form the basic unit, several of which can then be connected together as required in respect of power and/or supply voltage. From these wide-bandgap semiconductors a basic unit is defined which comprises two times three phases, i.e. in each case an input circuit and an output circuit with three phases each, as well as an intermediate circuit with an intermediate circuit capacitor, and associated connections and the activation of the semiconductors. The basic unit further comprises a mechanical integration including a cooling device for the semiconductors. The electrical parts of the basic unit are here insulated against the mechanism and the cooling. It is advantageous here that the basic unit is connected on the input side and/or the output side in parallel and/or in series to one or more further identical basic units, and as a result the overall current or the achievable voltage is increased. Thanks to a parallel connection the overall current that the modular power converter can provide is increased. The modular power converter can also have a series circuit of basic units connected in parallel, which thereby both increase overall current and enlarge the achievable voltage. The basic units are connected in series on the input side with the help of inductors in order thus to enable connection to a higher voltage. Thanks to the inductors the input current of the modular power converter can be controlled and regulated. The series connection is such that a phase of a basic unit is in each case connected with an inductor to the intermediate circuit, for example to the negative rail, of the next basic unit. The next inductors in terms of potential are then connected to the input-side-supplying positive side of the DC voltage, while the lowest negative rail in terms of potential is connected to the negative pole of the input-side DC voltage. A motor with a three-wire winding system can be connected to the three-phase output side. It is particularly advantageous if when using several basic units a motor with several three-phase winding systems is connected to the several three-phase output sides. Examples include motors with a 6- or 9- or 12-wire winding system. In the event of an AC supply it is advantageous if the input-side series connection of the basic units is such that on the lowest basic circuit there is a phase connection to a pole of the AC voltage. The second input-side phase connection is then connected to the second phase of the next basic unit. An inductor between the basic units may be, but does not have to be, dispensed with for use for an AC voltage present on the input side. The first phase is then again connected to the first phase of the next basic unit. Then in turn the second phase is connected to the subsequent second phase and so on until the last phase is connected to the other AC connection. It is additionally advantageous if the supply voltage on the input side can be both DC and AC, in that either the basic units are all connected in series like a step-up converter or two of the input phases are each connected in series to the two phases of the next basic unit, such that what is known as a 4-quadrant chopper is produced. It is additionally advantageous if a resistor is connected to the third input-side phase of the basic unit, and is used to dissipate power if during a braking operation the network cannot take up the total braking power. The function of this phase is also known as a braking chopper. The invention is described and explained in greater detail below using the exemplary embodiments illustrated in the figures, which show: FIG. 1 a basic unit, FIG. 2 the circuit diagram a wide-bandgap semiconductor, FIG. 3 a parallel connection of two basic units, FIG. 4 to FIG. 8 series circuits of basic units, FIG. 9 a motor at the output of a modular power converter, and FIG. 10 a vehicle with a modular power converter as part of the drive. FIG. 1 shows a basic unit 10. This has an input circuit 11 and an output circuit 12. On the DC voltage side these are connected to one another to form an intermediate circuit 13. A capacitor 3 is arranged in the intermediate circuit 13. The input circuit 11 and the output circuit 12 each have a B6 bridge circuit made of wide-bandgap semiconductors 2. The phase connections, also called phases, are guided outward as inputs and outputs. Furthermore the basic unit has a cooling unit 14. The flow of the coolant, air or liquid is indicated with arrows. FIG. 2 shows a wide-bandgap semiconductor 2 with its control 25. This is conductive in the rearward direction. If in an embodiment this is designed so as to block rearward, an antiparallel diode (not shown here) is arranged for the semiconductor switch and imparts to the semiconductor 2 its attribute of being conductive in the rearward direction. FIG. 3 shows a parallel connection of two basic units 10. These are connected in parallel to all three phases on both the input side and the output side. FIG. 4 shows a series circuit of two basic units 10. This figure only shows the principle of the series circuit. This can be expanded to any number of basic units 10. Likewise a basic unit 10 illustrated here can be a parallel connection of several basic units 10. The parallel connection takes place on the input side on the input circuit. The first phase 21 of the first input circuit is connected to the first phase 21 of the second input circuit via an inductor 15. In addition, the second phase 22 of the first input circuit is also connected to the second phase 22 of the second input circuit via a further inductor 15. The third phase 23 has a braking resistor 5 which is interconnected to form a braking chopper. FIG. 5 shows a further exemplary embodiment of a series circuit. Here too the individual basic units 10 can represent a random parallel connection of several basic units 10. This circuit as illustrated can also be expanded to form a series circuit comprising any number of basic units. In this case it is possible to connect two basic units 10 in series to the input circuit 11 on the DC voltage side. The intermediate circuits 13 of the basic units 10 in question are then therefore connected in series. To avoid repetitions, reference is made to the description for FIG. 4 and to the reference characters introduced there. FIG. 6 shows a further exemplary embodiment of a series circuit. Here too, the individual basic units 10 can represent any parallel connection of several basic units 10. This circuit as illustrated can also be expanded to form a series circuit comprising any number of basic units 10. In this circuit the first phase 21 and the second phase 22 of a first basic unit 10 are each connected via an inductor 15 to the intermediate circuit of a second basic unit 10. Here too, basic units 10 can also have interconnections from FIGS. 4 and 5. To avoid repetitions, reference is made to the description for FIGS. 4 and 5 and to the reference characters introduced there. FIG. 7 shows a further exemplary embodiment of a series circuit. Here too, the individual basic units 10 can represent any parallel connection of several basic units 10. This circuit as illustrated can also be expanded to form a series circuit comprising any number of basic units 10. In this case basic units 10 can also comprise combinations of FIGS. 4 to 6. In this circuit, not only are the first phase 21 and the second phase 22 of the first basic unit 10 each connected via inductors 15 to the intermediate circuit 13 of the second basic unit 10 but in addition the first phase 21 and the second phase 22 of the second basic unit 10 are each also connected via inductors 15 to the intermediate circuit 13 of the first basic unit 10. To avoid repetitions, reference is made to the description for FIGS. 4 to 6 and to the reference characters introduced there. FIG. 8 shows an exemplary embodiment of a series circuit, which is in particular suitable for supplying the input side with an alternating voltage. Thanks to the inductor of the transformer it is not necessary to introduce further inductors between the basic units 10. Here too the individual basic units 10 can represent any parallel connection composed of several basic units 10. This illustrated circuit can also be expanded to a series circuit containing any number of basic units 10. In this exemplary embodiment the first phase 21 of the first basic unit 10 is connected directly to the first phase of the second basic unit 10 and the second phase 22 of the second basic unit 10 is connected directly to a phase, in this case the first phase 21, of a third basic unit. Basic units 10 can here also comprise combinations of FIGS. 4 to 8. To avoid repetitions, reference is made to the description for FIGS. 4 to 8 and to the reference characters introduced there. FIG. 9 shows a possible connection of the output circuits 12 to a motor 4. For reasons of clarity the input circuits 11 are not shown. These can be interconnected as desired in accordance with one of FIGS. 3 to 8, or a combination of these. The output circuits of different basic units 10 are here in each case connected to a winding system 41 of the motor. Thus a high-performance motor 4 can be driven even if the performance of a basic unit is comparatively low. FIG. 10 shows a vehicle 100 embodied as a rail vehicle. The modular power converter 1 is here part of the drive 101 of the vehicle 100. The vehicle 100 obtains its electrical energy via a current collector 102 from a catenary (not shown) and supplies this to the input circuit of the modular power converter 1. The output circuit is connected to the motors (not shown here) of the vehicle 100 and drives them. To summarize, the invention relates to a modular power converter with wide-bandgap semiconductors, in particular SiC semiconductors. To optimize the power converter in respect of the use of wide-bandgap semiconductors, it is proposed that the modular power converter has at least two basic units, wherein the basic units are connected to one another on the input side, wherein a basic unit on the input side has an input circuit and on the output side an output circuit, wherein input circuit and output circuit are each formed by the wide-bandgap semiconductors which are arranged in a B6 bridge circuit, wherein an intermediate circuit capacitor is connected in parallel both to the input circuit and to the output circuit and thus the intermediate circuits of the input circuit and of the output circuit are connected to one another to form an intermediate circuit, wherein the input circuits of the basic units or of a subset of the basic units are arranged in a series circuit, wherein in each case at least one inductor is arranged between two input circuits. The invention further relates to a vehicle, in particular a rail vehicle, with such a modular power converter, wherein the modular power converter is a part of the drive of the vehicle. [ZH CN112512858A]: 模块化变流器 技术领域 [0001]本发明涉及一种具有宽带隙半导体的模块化变流器。本发明还涉及一种具有这种 模块化变流器的交通工具、特别是轨道交通工具。 背景技术 [0002] 具有宽带隙的半导体（英语为wide - bandgap semiconductors，由此得出德语 Wide-Bandgap-Halbleiter即宽带的半导体）是其带隙/带间距（价带和导带之间的能隙）在 半导体范围（3eV至超过4eV）的上限的半导体（来源:Wikipedia.de）。这种半导体由于其有 效功率预计在不久的将来也使用在交通工具的驱动器中。该驱动器也称作为牵引装置，其 配属的变流器称作为牵引变流器。基于碳化硅（SiC）的
[PT BR102012020499A2]: DISPOSITIVO DE CONVERSÃO DE ENERGIA DE MULTINÍVEL CONECTADO EM SÉRIE [EN EP2587658B1]: Series-connected multi-level power conversion device [ZH CN103095147B]: 串联多重电力变换装置 [DE EP2587658B1]: In Reihe verbundene Stromwandlungsvorrichtung mit mehreren Stufen [FR EP2587658B1]: Dispositif de conversion d'énergie à plusieurs niveaux connectés en série [JA JP5652416B2]: 直列多重電力変換装置 | [PT BR102012020499A2]: DISPOSITIVO DE CONVERSÃO DE ENERGIA DE MULTINÍVEL CONECTADO EM SÉRIE Um dispositivo de conversão de energia de multinível conectado em série de acordo com um aspecto de modalidades inclui um transformador de multienrolamentos e uma unidade de conversão. O transformador de multienrolamento tem uma relação em que n enrolamentos secundários conectados respectivamente a n conversos de energia monofásico na mesma fase de saída têm uma diferença de fase de voltagem de 60/n graus e uma relação e que uma relação em que os m enrolamentos secundários respectivamente conectados aos m conversores de energia monofásicos correspondentes às m fases de saída têm uma diferença de fase de voltagem de 60/m graus. [EN EP2587658B1]: A series-connected multi-level power conversion device (1, 1A, 1B) according to an aspect of embodiments includes a multi-winding transformer (10) and a power conversion unit (20). The multi-winding transformer (10) has a relationship that n secondary windings (12a to 12f) respectively connected to n single-phase power converters (21a to 21f) in the same output phase have a voltage phase difference of 60/n degrees and a relationship that the m secondary windings (12a to 12f) respectively connected to the m single-phase power converters (21a to 21f) corresponding to the m output phases have a voltage phase difference of 60/m degrees. [ZH CN103095147B]: 本发明的目的在于获取种串联多重电力变换装置，其具有多重变压器及电压变换单元。多重变压器中，设置于同输出相的n个单相电力变换器所分别连接的n个次级绕组的相位关系为依次相差60/n度；m个输出相之间，m个单相电力变换器所分别连接的m个次级绕组的电压相位关系为依次相差60/m度。 | EP2587658B1 | 2013-05-01 2017-12-27 2021-03-10 | EP12179687A | 2012-08-08 2012-08-08 2012-08-08 | JP2011237705A, 2011-10-28 JP2012062698A, 2012-03-19 JP2011237705A, 2011-10-28 JP2012062698A, 2012-03-19 JP2011237705A, 2011-10-28 JP2012062698A, 2012-03-19 | BR102012020499A2: 2013-12-03 CN103095147B: 2016-08-17 EP2587658B1: 2021-03-10 JP5652416B2: 2015-01-14 KR101462721B1: 2014-11-17 US8923024B2: 2014-12-30 | YASKAWA DENKI SEISAKUSHO KK 株式会社安川电机 YASKAWA ELECTRIC CORP 株式会社安川電機 KATAYAMA TAISUKE SUENAGA RYUJI UMEO KAZUHIRO YAMAMOTO EIJI | KATAYAMA TAISUKE SUENAGA RYUJI UMEO KAZUHIRO YAMAMOTO EIJI | H02M7/25: I H02M5/44: I H01F27/28: I H02M7/49: I H02J3/12: N H02M1/42: I H02M7/483: N H02M7/497: I H02M7/48: I H02M5/458: I | H02J3/12: A H02M7/49: I H02M7/4835: A | US5625545A US7307361B1 CN101166004A JPH01125811A JP2008295149A JP2000243636A JPH11150869A JPH11122943A JPH11266586A US6762947B2 KR100738571B1 US5008797A US5079499A US5986909A US6014323A US6229722B1 | CN107395025A CN107395025 107395025 CN104348343A CN104348343 104348343 CN104283435A CN104283435 104283435 US9831846B2 US9831846 09831846 WO2016198370A1 WO2016198370 2016/198370 WO2016/198370A1 EP2840706A3 EP2840706 2840706 EP3236571A1 EP3236571 3236571 JP2015035948A JP2015035948 2015035948 US9225278B2 US9225278 09225278 US10236685B2 US10236685 10236685 US9214875B2 US9214875 09214875 US09214875B2 US8976554B2 US8976554 08976554 US08976554B2 US10868423B2 US10868423 10868423 EP2849332B1 EP2849332 2849332 US2015009731A1 US2015009731 20150009731 US20150009731A1 | [ZH CN103095147B]: 1.一种串联多重电力变换装置，其特征在于包括: 多重变压器，用于将输入至初级绕组的交流电分配至mXn个次级绕组，其中，n、m是互为素数;以及 电力变换单元，具有分别连接于上述m X η个次级绕组的m X η个单相电力变换器，该单相电力变换器的输出按每η个串联连接而构成m个输出相，其中， 上述多重变压器中， 上述mXn个次级绕组的电压相位是分别不同的关系， 设置于同一输出相的上述η个单相电力变换器所分别连接的η个上述次级绕组的电压相位关系为依次相差60/η度， 在上述m个输出相间，于输出相中位置关系相同的单相电力变换器所连接的上述次级绕组的电压相位关系为依次相差60/m度， 由于所述m X η个次级绕组的电流矢量而在所述初级绕组中流过的电流的电流矢量，相对于交流电的电压最大的相位对称地以相互之间相位相差的状态分布。 2.根据权利要求1所述的串联多重电力变换装置，其特征在于: 上述多重变压器的各次级绕组由扩展三角形接线所构成。 [EN EP2587658B1]: A series-connected multi-level power conversion device (1, 1A, 1B) comprising: a multi-winding transformer (10) configured to distribute AC power input into a primary winding (11) to m×n secondary windings (12a to 12f), wherein n and m are coprime; anda power conversion unit (20) comprising m×n single-phase power converters (21a to 21f), wherein each of mxn single-phase converters (21a to 21f) is connected to one of the mxn secondary windings (12a to 12f), and m output phases, wherein each of the m output phases is constituted by the serially connected outputs of n single-phase power converters (21a to 21f) out of the m×n single-phase power converters (21a to 21f);whereinthe multi-winding transformer (10) has a first relationship that, for each of the m output phases, each one of the secondary windings (12a to 12f) connected to the n power converters in the respective output phase has a different voltage phase and differs 60/n degrees from at least one of the secondary windings connected to the remaining n-1 power converters in the respective output phase;characterized in thatconsidering n groups of secondary windings (12a to 12f), wherein each one of the groups is formed by m secondary windings (12a to 12f) and each of the secondary windings (12a to 12f) within one group is taken from a different one of the m output phases and wherein each of the mxn secondary windings (12a to 12f) is assigned exclusively to one single group among the n groups,the multi-winding transformer (10) has a second relationship that, for each group, each one of the m secondary windings (12a to 12f) in the respective group has a different voltage phase and differs 60/m degrees from at least one of the remaining m-1 secondary windings (12a to 12f) in the respective group. The series-connected multi-level power conversion device (1, 1A, 1B) according to claim 1, wherein the multi-winding transformer (10) has a relationship that the secondary windings (12a to 12f) connected to the m representative single-phase power converters (21a to 21f) corresponding to the m output phases, in which each of the m representative single-phase power converters (21a to 21f) is on a position which has the same stage number in the corresponding output phase, have the voltage phase difference of 60/m degrees. The series-connected multi-level power conversion device (1, 1A, 1B) according to claim 1 or 2, wherein each of the mxn secondary windings (12a to 12f) of the multi-winding transformer (10) is formed by extended delta connection. [DE EP2587658B1]: In Reihe geschaltete mehrstufige Stromrichter-Vorrichtung (1, 1A, 1B), die umfasst: einen Mehrfachwicklungs-Transformator (10), der so ausgeführt ist, dass er in eine Primärwicklung (11) eingeleiteten Wechselstrom auf m x n Sekundärwicklungen (12a bis 12f) verteilt, wobei n und m koprim sind; undeine Stromrichter-Einheit (20), die m x n einphasige Stromrichter (21a bis 21f) umfasst, wobei jeder von m x n einphasigen Stromrichtern (21a bis 21f) mit einer der m x n Sekundärwicklungen (12a bis 12f) verbunden ist, und m Ausgangsphasen umfasst, wobei jede der m Ausgangsphasen durch die in Reihe verbundenen Ausgänge n einphasiger Stromrichter (21a bis 21f) der m x n einphasigen Stromrichter (21a bis 21f) gebildet wird; undder Mehrfachwicklungs-Transformator(10) eine erste Beziehung dahingehend aufweist, dass für jede der m Ausgangsphasen jede der Sekundärwicklungen (12a bis 12f), die mit den n Stromrichtern in der jeweiligen Ausgangsphase verbunden sind, eine andere Spannungsphase aufweist und sich um 60/n Grad von wenigstens einer der Sekundärwicklungen unterscheidet, die mit den übrigen n-1 Stromrichtern in der jeweiligen Ausgangsphase verbunden sind;dadurch gekennzeichnet, dassin Bezug auf n Gruppen von Sekundärwicklungen (12a bis 12f), bei denen jede der Gruppen durch m Sekundärwicklungen (12a bis 12f) gebildet wird und jede der Sekundärwicklungen (12a bis 12f) innerhalb einer Gruppe von einer anderen der m Ausgangsphasen ausgeht und jede der m x n Sekundärwicklungen (12a bis 12f) ausschließlich einer einzigen Gruppe der n Gruppen zugeordnet ist,der Mehrfachwicklungs-Transformator (10) eine zweite Beziehung dahingehend aufweist, dass für jede Gruppe jede der m Sekundärwicklungen (12a bis 12f) in der jeweiligen Gruppe eine andere Spannungsphase aufweist und sich um 60/m Grad von wenigstens einer der übrigen m-1 Sekundärwicklungen (12a bis 12f) in der jeweiligen Gruppe unterscheidet. In Reihe geschaltete mehrstufige Stromrichter-Vorrichtung (1, 1A, 1B) nach Anspruch 1, wobei der Mehrfachwicklungs-Transformator (10) eine Beziehung dahingehend aufweist, dass die Sekundärwicklungen (12a bis 12f), die mit den m repräsentativen einphasigen Stromrichtern (21a bis 21f) verbunden sind, die den m Ausgangsphasen entsprechen, in denen jeder der m repräsentativen einphasigen Stromrichter (21a bis 21f) sich an einer Position, die die gleiche Stufen-Nummer hat, in der entsprechenden Ausgangsphase befindet, die Spannungsphasen-Differenz von 60/m Grad aufweisen. In Reihe geschaltete mehrstufige Stromrichter-Vorrichtung (1, 1A, 1B) nach Anspruch 1 oder 2, wobei jede der m x n Sekundärwicklungen (12a bis 12f) des Mehrfachwicklungs-Transformators (10) durch erweiterte Dreieckschaltung gebildet wird. [FR EP2587658B1]: Dispositif de conversion de puissance à niveaux multiples reliés en série (1, 1A, 1B) comprenant : un transformateur à enroulements multiples (10) configuré pour répartir de la puissance alternative appliquée en entrée à l'enroulement primaire (11) sur m × n enroulements secondaires (12a à 12f), n et m étant premiers entre eux, etune unité de conversion de puissance comprenant m × n convertisseurs de puissance monophasés (21a à 21f), chacun des m × n convertisseurs de puissance monophasés (21a à 21f) étant relié à l'un des m × n enroulements secondaires (12a à 12f), ainsi que m phases de sortie, chacune des m phases de sortie étant constituée par les sorties reliées en série de n convertisseurs de puissance monophasés (21a à 21f), oùle transformateur à enroulements multiples (10) présente une première relation indiquant que, pour chacune des m phases de sortie, chacun des enroulements secondaires (12a à 12f) reliés aux n convertisseurs de puissance dans la phase de sortie respective présente une phase de tension différente et diffère de 60 / n degrés d'au moins l'un des enroulements secondaires reliés aux n - 1 convertisseurs de puissance restants dans la phase de sortie respective,caractérisé en ce queen prenant en considération n groupes d'enroulements secondaires (12a à 12f), où chacun des groupes est formé par m enroulements secondaires (12a à 12f) et chacun des enroulements secondaires (12a à 12f) à l'intérieur d'un groupe est pris à partir de l'une différente des m phases de sortie, et où chacun des m × n enroulements secondaires (12a à 12f) est assigné exclusivement à un seul groupe parmi les n groupes,le transformateur à enroulements multiples (10) présente une seconde relation indiquant que, pour chaque groupe, chacun des m enroulements secondaires (12a à 12f) dans le groupe respectif présente une phase de tension différente et diffère de 60 / m degrés d'au moins l'un des m - 1 enroulements secondaires (12a à 12f) restants dans le groupe respectif. Dispositif de conversion de puissance à niveaux multiples reliés en série (1, 1A, 1B) selon la revendication 1, dans lequel le transformateur à enroulements multiples (10) présente une relation indiquant que les enroulements secondaires (12a à 12f), reliés aux m convertisseurs de puissance monophasés (21a à 21f) correspondant aux m phases de sortie, dans lesquels chacun des m convertisseurs de puissance monophasés (21a à 21f) représentatifs se trouve sur une position qui présente le même numéro d'étage dans la phase de sortie correspondante, présentent une différence de phase de tension de 60 / m degrés. Dispositif de conversion de puissance à niveaux multiples reliés en série (1, 1A, 1B) selon la revendication 1 ou la revendication 2, dans lequel chacun des m × n enroulements secondaires (12a à 12f) du transformateur à enroulements multiples (10) est formé par une connexion en triangle étendue. [JA JP5652416B2]: 一次巻線に入力される交流電力をｍ×ｎ個（ｎ、ｍは互いに素）の二次巻線に分配する多重変圧器と、 前記ｍ×ｎ個の二次巻線にそれぞれ接続されたｍ×ｎ個の単相電力変換器を有し、当該単相電力変換器の出力が直列にｎ個ずつ接続されてｍ個の出力相が構成される電力変換部と、を備え、 前記多重変圧器は、 前記ｍ×ｎ個の二次巻線の電圧位相がそれぞれ異なる関係にあり、 同一の出力相に設けられた前記出力が直列に接続されたｎ個の単相電力変換器のそれぞれに接続されるｎ個の前記二次巻線の電圧位相が６０／ｎ度ずつずれた関係にあり、 前記ｍ個の出力相間で、前記ｎ個の前記二次巻線の電圧位相の組が６０／ｍ度ずつずれた関係にあることを特徴とする直列多重電力変換装置。 前記ｍ個の出力相間で、出力相における位置関係が同一の単相電力変換器に接続される前記二次巻線の電圧位相が６０／ｍ度ずつずれた関係にあることを特徴とする請求項１に記載の直列多重電力変換装置。 前記多重変圧器の各二次巻線は、辺延長デルタ結線により形成されることを特徴とする請求項１又は２に記載の直列多重電力変換装置。 [KO KR101462721B1]: 1차 권선(primary winding)에 입력되는 교류 전력을 m×n개(n, m은 서로소)의 2차 권선(secondary winding)에 분배하는 다중 변압기와, 상기 m×n개의 2차 권선에 각각 접속된 m×n개의 단상 전력 변환기를 갖고, n개의 단상 전력 변환기의 출력이 직렬로 접속되어 m개의 출력 위상의 각각이 구성된 전력 변환 유닛 을 구비하고, 상기 다중 변압기는, 상기 m×n개의 2차 권선의 전압 위상이 각각 상이한 관계에 있고, 동일 출력 위상의 상기 n개의 단상 전력 변환기에 각각 접속된 n개의 상기 2차 권선이 60/n도의 전압 위상차를 갖는 관계 및 상기 m개의 출력 위상에 대응하는 상기 m개의 단상 전력 변환기에 각각 접속된, n개의 상기 2차 권선의 전압 위상 세트가 60/m도의 전압 위상차를 갖는 관계를 갖는 직렬 다중 전력 변환 장치. 제 1 항에 있어서, 상기 다중 변압기는, 상기 m개의 출력 위상에 대응하는, 각각이 대응하는 출력 위상에서 같은 순서의 위치에 있는 상기 m개의 단상 전력 변환기에 접속된 상기 2차 권선이 60/m도의 전압 위상차를 갖는 관계를 갖는 직렬 다중 전력 변환 장치. 제 1 항 또는 제 2 항에 있어서, 상기 다중 변압기의 2차 권선 중 적어도 1 이상의 2차 권선은, 연장된 델타 결선(extended delta connection)에 의해 형성되는 직렬 다중 전력 변환 장치. | [ZH CN103095147B]: 串联多重电力变换装置 技术领域 [0001]本发明所揭示的实施方式涉及一种串联多重电力变换装置。 背景技术 [0002]以往，作为电力变换装置，已知有将电力变换单元以串联方式进行多级连接，设有多个相位的串联多重(series-connected multi level)电力变换装置。串联多重电力变换装置具有:将输入至初级绕组的多相交流输入电压变压后输出至多个次级绕组的多重变压器(mult1-winding transformer)，及连接于多重变压器的各次级绕组的多个单相电力变换器。 [0003]在上述串联多重电力变换装置中，多重变压器的各次级绕组输出的电压之间相互具有相位差，以降低在初级绕组侧流过的谐波电流。具体而言，已提出有以下方案:在串联多重电力变换装置由9个单相电力变换器所组成的情况下，构成为使连接于组成U相、V相、W相中的I个相的3个单相电力变换器的次级绕组具有20度的电压相位，并使所有次级绕组的电压相位依次相差20/3度(例如参照日本专利特开2008-295149号公报)。 [0004]本发明的目的在于，提供一种作为降低在初级绕组侧流过的谐波电流的技术，以代替以往技术的新技术。 发明内容 [0005]本发明的一种串联多重电力变换装置包括:多重变压器和电力变换单元。多重变压器将输入至初级绕组的交流电分配至mXn个(n、m是互为素数)次级绕组。电力变换单元具有分别连接于上述mXn个次级绕组的mXn个单相电力变换器，该单相电力变换器的输出按每η个串联连接而构成m个输出相。上述多重变压器中，设置于同一输出相的上述η个单相电力变换器所分别连接的η个上述次级绕组的电压相位关系为依次相差60/η度。并且，上述多重变压器，在上述m个输出相间，上述m个单相电力变换器所分别连接的m个上述次级绕组的电压相位关系为依次相差60/m度。 [0006]根据本发明的一种形态的串联多重电力变换装置，能够降低在初级绕组侧流过的谐波电流。 附图说明 [0007]以下，通过对照附图来阅读本发明的详细说明，可更为完整地认识本发明及容易地理解其优点。 [0008]图1是第I实施方式串联多重电力变换装置的示意图。 [0009]图2是图1所示的单相电力变换器的电路块示意图。 [0010]图3是多重变压器的次级绕组电压相位差的示意图。 [0011 ]图4是多重变压器的次级绕组电压相位关系的示意图。 [0012]图5是多重变压器的布线示意图。 [0013]图6〜图8是多重变压器初级绕组的线间电压矢量与次级绕组的线间电压矢量关系的不意图。 [0014]图9是多重变压器各次级绕组的电流矢量示意图。 [0015]图10是多重变压器各次级绕组的电流矢量示意图。 [0016]图11是关于r相，各次级绕组中流过的电流的说明图。 [0017]图12是初级电压为正时，由于次级绕组中流过的电流而在初级绕组中流过的电流矢量的示意图。 [0018]图13是初级电压为负时，由于次级绕组中流过的电流而在初级绕组中流过的电流矢量的示意图。 [0019]图14是多重变压器中次级绕组的另外的电压相位关系的示意图。 [0020]图15是第2实施方式的串联多重电力变换装置中，多重变压器的次级绕组电压相位差的示意图。 具体实施方式 [0021]以下参照附图来详细说明本发明要揭示的串联多重电力变换装置的几种实施方式。另外，本发明并不限定于以下所示的各实施方式。 [0022](第丨实施方式) [0023]首先，对第I实施方式的串联多重电力变换装置的结构进行说明。图1是第I实施方式串联多重电力变换装置的示意图。 [0024]如图1所示，串联多重电力变换装置I具有多重变压器10及电力变换单元20，将自三相交流电源2的R相、S相及T相所供应的交流电变换后供应至交流负载3。此处举以下一例来进行说明:串联多重电力变换装置I的输出相为三相(m=3)，各输出相具备2个2级(n=2)连接的单相电力变换器，交流负载3为电动机。 [0025]多重变压器10具备初级绕组11、及6个次级绕组12a〜12f (以下有时总称为次级绕组12)，其将输入至初级绕组11的交流电变压后输出至6个次级绕组12a〜12f。该多重变压器10是使初级绕组11与次级绕组12之间产生电压相位差的移相变压器。 [0026]电力变换单元20具备分别连接于6个次级绕组12a〜12f的6个单相电力变换器21a〜21f (以下有时总称为单相电力变换器21)。各单相电力变换器21将从各次级绕组12所供应的三相交流电变换为单相交流电后，从输出端子Ta、Tb输出。 [0027]在该电力变换单元20中，各输出相由串联连接的2个单相电力变换器21的输出所组成。即U相输出的电力变换单元由单相电力变换器21a、21d组成，V相输出的电力变换单元由单相电力变换器21b、21e组成，W相输出的电力变换单元由单相电力变换器21c、21f组成。 [0028]具体而言，单相电力变换器21a的输出端子Tb连接于中性点N，单相电力变换器21a的输出端子Ta与单相电力变换器21d的输出端子Tb相连接。据此，就组成了以单相电力变换器21d的输出端子Ta作为输出端子的U相的电力变换单元。 [0029]同样的，单相电力变换器21b、21 c的输出端子Tb连接于中性点N，单相电力变换器 2 Ib、21 c的输出端子Ta分别与单相电力变换器21 e、21 f的输出端子Tb相连接。据此，就组成了以单相电力变换器21 e、21 f的输出端子Ta分别作为输出端子的V相及W相的电力变换单 J L ο [0030]在此，对单相电力变换器21的结构进行说明。图2是单相电力变换器21电路块的示意图。如图2所示，单相电力变换器21具备整流滤波单元30、逆变器单元31和控制单元32。 [0031]整流滤波单元30具备二极管DlO〜D15和电容器ClO，其将从次级绕组12输入的r相、s相及t相的3相交流电变换为直流电。另外，二极管D10、D11全波整流r相的电流，二极管D12、D13全波整流s相的电流，二极管D14、D15全波整流t相的电流。且对二极管DlO〜D15所整流的电压通过电容器ClO进行滤波。 [0032] 逆变器单元31具备三极管Q20〜Q23和二极管D20〜D23。三极管Q20、Q21串联连接于整流滤波单元30的输出之间，同样的三极管Q22〜Q23串联连接于整流滤波单元30的输出之间。另外，二极管D20〜D23是续流二极管(freewheeling d1de)。 [0033] 控制单元32通过控制逆变器单元31中三极管Q20〜Q23的0N/0FF状态，使整流滤波单元30的直流电通过逆变器单元31变换为单相交流电。另外，作为三极管Q20〜Q23，例如可采用IGBT或MOSFET等功率半导体元件。此外，逆变器单元31不限定于图2所示的二电平逆变器。例如，作为逆变器单元31，也可采用三电平逆变器等多电平逆变器，此外也可更改为许多其他种类。 [0034]接着，对多重变压器10的结构进行说明。图3是次级绕组12a〜12f电压相位差的示意图，图4是次级绕组12a〜12f电压相位关系的示意图。另外，如上所述，单相电力变换器21&amp;〜21€分别位于1]1、¥1、胃1、1]2、¥2、胃2的位置，单相电力变换器21&amp;〜21€分别与次级绕组12a〜12f连接(参照图1)。在此，从UI至W2的符号中，U、V、W表示输出相，数字I和2表示级数的顺序，分别串联连接于同一输出相。因此，次级绕组12a对应Ul的位置，次级绕组12b对应Vl的位置，次级绕组12c对应Wl的位置，次级绕组12d对应U2的位置，次级绕组12e对应V2的位置，次级绕组12f对应W2的位置。 [0035]如图3所示，在第I实施方式的多重变压器10中，同一输出相中的2个单相电力变换器21所分别连接的2个次级绕组12之间的电压相位相差30度。具体而言，在U相中，相对于与Ul位置对应的次级绕组12a，与U2位置对应的次级绕组12d具有30度的电压相位差。 [0036]同样的，在V相中，相对于与Vl位置对应的次级绕组12b，与V2位置对应的次级绕组12e具有30度的电压相位差。此外，在W相中，相对于与Wl位置对应的次级绕组12c，与W2位置对应的次级绕组12f具有30度的电压相位差。 [0037]另外，在多重变压器10中，在输出相之间，分别与2个单相电力变换器21连接的2个次级绕组12的电压相位相差20度。具体而言，相对于与Ul位置对应的次级绕组12a，与Vl位置对应的次级绕组12b具有20度的电压相位差。此外，相对于与Vl位置对应的次级绕组12b，与Wl位置对应的次级绕组12c具有20度的电压相位差。 [0038] 在此，参照图4举一例对次级绕组12a〜12f具体电压相位差进行说明。如图4所示，次级绕组12的电压相位按(1]1、¥1、1]2、胃1、¥2、胃2)的顺序，为(135度、155度、165度、175度、185度、205度)。次级绕组12的电压相位是指次级绕组12的电压与初级绕组11的电压之间的电压相位差。 [0039]因此，次级绕组12的电压相位，在U相中为(U1、U2) = ( 135度、165度)；在V相中为(¥1、¥2)=(155度、185度)；在¥相中为(¥1、评2)=(175度、205度)。即，在同一输出相中的次级绕组12之间的电压相位差为30度。此外，在输出相之间，次级绕组12的两组电压相位为(U1、¥1、町)=(135度、155度、175度)，(1]2、¥2、胃2)=(165度、185度、205度)，存在20度的电压相位差。 [0040]用图5来举一例说明具有图4中所示的次级绕组12电压相位关系的多重变压器10的结构。图5是多重变压器10布线的示意图。 [0041 ] 如图5所示，次级绕组12a由扩展三角形接线(extended delta connect1n)构成。具体而言，R相的初级绕组Ila和次级绕组12al隔着绝缘材料卷绕于同一铁芯，S相的初级绕组Ilb和次级绕组12a2隔着绝缘材料卷绕于同一铁芯，T相的初级绕组Ilc和次级绕组12a3隔着绝缘材料卷绕于同一铁芯。此外，这些次级绕组12al〜12a3在绕组端部之间都具有接 □ O [0042]图5中，各绕组具有带黑点的绕组端(coil end)和不带黑点的绕组端。采取了初级绕组和多个次级绕组之一的情况下，该两种绕组中从带黑点的绕组端流入电流的情况下，为使两个绕组各自所产生的磁通量具有相互加强的方向，而在各绕组中于一方的绕组端加上黑点。在此，将该带有黑点的绕组端称为极性端，将极性端(positive coil end)相反侧的绕组端称为反极性端(negative coil end)。图5中，次级绕组12al、12a2、12a3各自的极性端分别为r相、s相、t相的输出端。此外，次级绕组12al的反极性端连接于次级绕组12a3的接口，次级绕组12a3的反极性端连接于次级绕组12a2的接口，次级绕组12a2的反极性端连接于次级绕组12al的接口。 [0043]在此，参照图6对如图5所示接线的情况下初级绕组11的线间电压矢量与次级绕组12a的线间电压矢量的关系进行说明。图6是初级绕组11的线间电压矢量与次级绕组12a的线间电压矢量关系的示意图。另外，设三相交流电源2的输出相按R相、S相、T相的顺序，电压相位依次后移120度。 [0044] 按上述般连接次级绕组12al、12a2、12a3，则这些次级绕组12al、12a2、12a3的各相之间产生的线间电压矢量Vrs、Vst、Vtr，通过各相电压矢量Vr、Vs、Vt以下述公式(I)〜(3)来表示。 [0045] Vrs = Vr - Vs...(I) [0046] Vst = Vs - Vt...(2) [0047] Vtr = Vt - Vr...(3) [0048] 这些线间电压矢量Vrs、Vst、Vtr之中，例如线间电压矢量Vrs、Vtr即如图6所示。如将初级绕组11中从S相指向R相的线间电压矢量VRS的相位规定为基准相位，则次级绕组12a中，从s相指向r相的线间电压矢量Vrs的相位即为相对于基准相位前移了 15度的相位。 [0049]次级绕组12a中，从r相指向t相的线间电压矢量Vtr的相位为相对于线间电压矢量Vrs的相位前移了 120度的相位，即为相对于基准相位前移了 135度的相位。此外，从t相指向s相的线间电压矢量Vst的相位为相对于线间电压矢量Vrs的相位前移了 240度的相位，即为相对于基准相位前移了 255度的相位。因此，次级绕组12a是在相对于基准相位前移了 15度的电压相位的次级绕组的同时，如上所述，也是相对于基准相位前移了 135度的电压相位的次级绕组，此外，也是相对于基准相位前移了 255度的电压相位的次级绕组。 [0050] 返回图5对次级绕组12b进行说明。如图5所示，次级绕组12b也由扩展三角形接线构成。具体而言，R相的初级绕组Ila和次级绕组12bl隔着绝缘材料卷绕于同一铁芯，S相的初级绕组Ilb和次级绕组12b2隔着绝缘材料卷绕于同一铁芯，T相的初级绕组Ilc和次级绕组12b3隔着绝缘材料卷绕于同一铁芯。此外，这些次级绕组12bl〜12b3在绕组端部之间都具有接口。 [0051]次级绕组12bl、12b2、12b3各自的反极性端分别为r相、s相、t相的输出端。此外，次级绕组12bl的极性端连接于次级绕组12b2的接口，次级绕组12b2的极性端连接于次级绕组12b3的接口，次级绕组12b3的极性端连接于次级绕组12bl的接口。 [0052]在此，参照图7对如图5所示接线的情况下初级绕组11的线间电压矢量与次级绕组12b的线间电压矢量的关系进行说明。图7是初级绕组11的线间电压矢量与次级绕组12b、12c、12e的线间电压矢量关系的示意图。另外，将从S相指向R相的线间电压矢量VRS(参照图6)的相位规定为基准相位。 [0053] 如上述般连接次级绕组12131、12&amp;2、12&amp;3，则这些次级绕组12131、12&amp;2、12&amp;3的各相之间产生的线间电压矢量Vrs、Vst、Vtr，与次级绕组12a的情况相同，通过各相电压矢量Vr、Vs、Vt以上述公式(I)〜(3)表示。 [0054] 这些线间电压矢量Vrs、Vst、Vtr之中，例如线间电压矢量Vrs则如图7所示。即次级绕组12b中，从s相指向r相的线间电压矢量Vrs的相位是相对于基准相位前移了 165度的相位。 [0055]同样的，对于次级绕组12c、12e也进行与图5中次级绕组12b相同的接线，使从s相指向r相的线间电压矢量Vrs的相位为相对于基准相位分别前移了 155度、175度的相位。此时，次级绕组12c、12e相对于次级绕组12b的接线，每个接口的设置位置不同。即次级绕组12c、12e与次级绕组12b三角形部分的绕组数不同。 [0056] 返回图5对次级绕组12d进行说明。如图5所示，次级绕组12d也由扩展三角形接线构成。具体而言，R相的初级绕组Ila和次级绕组12dl隔着绝缘材料卷绕于同一铁芯，S相的初级绕组Ilb和次级绕组12d2隔着绝缘材料卷绕于同一铁芯，T相的初级绕组Ilc和次级绕组12d3隔着绝缘材料卷绕于同一铁芯。此外，这些次级绕组12dl〜12d3在绕组端部之间都具有接口。 [0057]次级绕组12dl、12d2、12d3各自的反极性端分别为r相、s相、t相的输出端。此外，次级绕组12dl的极性端连接于次级绕组12d3的接口，次级绕组12d2的极性端连接于次级绕组12dl的接口，次级绕组12d3的极性端连接于次级绕组12d2的接口。 [0058]在此，参照图8对如图5所示接线的情况下初级绕组11的线间电压矢量与次级绕组12d、12f的线间电压矢量的关系进行说明。图8是初级绕组11的线间电压矢量与次级绕组12d、12f的线间电压矢量关系的示意图。另外，将从S相指向R相的线间电压矢量VRS(参照图6)的相位规定为基准相位。 [0059] 如上述般连接次级绕组12dl、12d2、12d3，则这些次级绕组12dl、12d2、12d3的各相之间产生的线间电压矢量Vrs、Vst、Vtr与次级绕组12a的情况相同，通过各相电压矢量Vr、Vs、Vt以上述公式(I)〜(3)表示。这些线间电压矢量Vrs、Vst、Vtr之中，例如线间电压矢量Vrs的相位，如图8所示，是相对于基准相位前移了 185度的相位。 [0060]同样的，如图8所示，对于次级绕组12f也进行与图5中次级绕组12b相同的接线，使从s相指向r相的线间电压矢量Vrs的相位相对于基准相位前移了205度的相位。此时，次级绕组12f相对于次级绕组12d的接线，每个接口的设置位置不同。即次级绕组12f与次级绕组12d三角形部分的绕组数不同。 [0061]接着，参照图9及图10对多重变压器10中各次级绕组12的电流矢量进行说明。图9及图10是多重变压器10中各次级绕组12电流矢量的示意图。 [0062]图9及图10中电流矢量Irs表示r相与s相之间流过的电流，电流矢量Itr表示t相与r相之间流过的电流。该电流矢量Irs为通过图2所示的二极管D10、D11、D12和D13，借由r相和s相对电容器ClO进行充电时流过的电流。电流矢量Itr为通过二极管D10、D11、D14和D15，借由t相和r相对电容器Cl O进行充电时流过的电流。 [0063]以电流矢量Irs所表示的电流在r相与s相之间的线间电压为3个线间电压之中最大或最小时流过。此外，以电流矢量Itr所表示的电流在t相与r相之间的线间电压为3个线间电压之中最大或最小时流过。另外，以下，将表示电流矢量的符号中第一个字母所指定的相中从次级绕组12流向整流滤波单元30的电流、以及第二个字母所指定的相中从整流滤波单元30流向次级绕组12的电流设为正方向。 [0064] r相与s相之间的线间电压为最大的情况下，r相的电压为正电压，s相的电压为负电压。因此，r相与s相之间的线间电压为最大时，r相中电流沿自各次级绕组12流入整流滤波单元30，s相中电流沿自整流滤波单元30流向各次级绕组12。因此，此时电流矢量Irs的方向如图9所示为正方向，并且电流矢量Irs为与如图6至图8所示的线间电压矢量Vrs同方向的电流矢量。 [0065]此外，t相与r相之间的线间电压为最小的情况下，t相的电压为负电压，r相的电压为正电压。因此，t相与r相之间的线间电压为最小时，t相中电流沿自整流滤波单元30流入各次级绕组12，r相中电流沿自各次级绕组12流向整流滤波单元30。因此，此时电流矢量I tr的方向如图9所示为负方向，并且电流矢量Itr为与如图6至图8所示的线间电压矢量Vtr相反方向的电流矢量。 [0066] r相与s相之间的线间电压为最小的情况下，r相的电压为负电压，s相的电压为正电压。因此，r相与s相之间的线间电压为最小时，r相中电流沿自整流滤波单元30流入各次级绕组12，s相中电流沿自各次级绕组12流向整流滤波单元30。因此，此时电流矢量Ir s的方向如图10所示为负方向，并且电流矢量Irs为与如图6至图8所示的线间电压矢量Vrs相反方向的电流矢量。 [0067]此外，t相与r相之间的线间电压为最大的情况下，t相的电压为正电压，r相的电压为负电压。因此，t相与r相之间的线间电压为最大时，t相中电流沿自各次级绕组12流入整流滤波单元30，s相中电流沿自整流滤波单元30流向各次级绕组12。因此，此时t相与r相之间流过的电流的电流矢量Itr的方向如图10所示为正方向，并且电流矢量Itr为与如图6至图8所示的线间电压矢量Vtr同方向的电流矢量。 [0068]如此，关于r相，于各次级绕组12中流过的电流分别在以下4种情况下流过，S卩，r相与s相之间的线间电压最大及最小的情况、t相与r相之间的线间电压最小及最大的情况。图11是关于r相，各次级绕组12中流过的电流的说明图，表示r相与s相之间的线间电压Vrs、t相与r相之间的线间电压Vtr、r相的相电压Vr及r相的相电流Ir的关系。如图11所示，实际上上述4种情况下分别流过有尖头波状的电流。另外，关于s相及t相的各相也分别在与r相相同的情况下，各次级绕组12中流过电流。 [0069 ]接着，借由次级绕组12a〜12f中流过的电流，对R相的初级绕组11 a中流过的电流进行说明。首先，举次级绕组12a中流过的电流为例进行说明。次级绕组12al中电流流过时，R相的初级绕组Ila中流过如下电流，即抵消因卷绕于同一铁芯的次级绕组12al中流过的电流所产生的磁通势。即初级绕组Ila中流过如下电流，即抵消因上述电流矢量Irs和电流矢量Itr所产生的磁通势。 [0070]关于初级绕组I Ia中流过的电流，设从初级绕组I Ia流出的方向为正方向。图5所示的绕组的布线中，从上述极性端的定义可知，用于抵消从次级绕组12al流出的电流所产生的磁通势的、初级绕组Ila中流过的电流的方向，是流入初级绕组Ila的方向，即是与次级绕组12al相反的负方向。 [0071 ]电流矢量Irs因流过次级绕组12al的星形接线部分，因此初级绕组I Ia中流过如下电流，即相对于电流矢量Irs方向相反，且大小为其初级绕组Ila与次级绕组12al的星形接线部分的绕组数之比倍。此外，因电流矢量Itr流过次级绕组12al的星形接线部分和三角形接线部分，因此初级绕组Ila中也流过如下电流，即相对于电流矢量Itr方向相反，且大小为其初级绕组Ila与次级绕组12al的绕组数之比倍。 [0072]接着，对次级绕组12b中流过的电流进行说明。关于该次级绕组12b，初级绕组Ila中也流过如下电流，即抵消因卷绕于与初级绕组Ila同一铁芯的次级绕组12bl中流过的电流矢量Irs和电流矢量Itr所产生的磁通势。从图5所示的绕组的布线可知，用于抵消从次级绕组12bl流出的电流所产生的磁通势的、初级绕组IIa中流过的电流的方向，是从初级绕组IIa流出的方向，即是与次级绕组12b相同的正方向。 [0073]次级绕组12bl中，电流矢量Irs因流过星形接线部分和三角形接线部分，因此初级绕组Ila中也流过如下电流，即相对于电流矢量Irs方向相同，且大小为电流矢量Irs的初级绕组I Ia与次级绕组12b I的绕组数之比倍。此外，电流矢量I tr因流过次级绕组12b I的星形接线部分，因此初级绕组Ila中流过如下电流，即相对于电流矢量Itr方向相同，且大小为其初级绕组Ila与次级绕组12bl的星形接线部分的绕组数之比倍。 [0074]关于次级绕组12c、12e，初级绕组Ila中也流过如下电流，即抵消因卷绕于与初级绕组Ila同一铁芯的次级绕组12cl、12el的各自中流过的电流矢量Irs和电流矢量Itr所产生的磁通势。次级绕组12cl、12el的连接状态如图5所示，因与次级绕组12bl的连接状态相同，因此通过与次级绕组12bl情况相同的变换作用，初级绕组Ila中流过由次级绕组12cl、12e I的电流矢量Ir s、I tr而产生的电流。 [0075]接着，对次级绕组12d中流过的电流进行说明。关于该次级绕组12d，初级绕组Ila中也流过如下电流，即抵消因卷绕于与初级绕组Ila同一铁芯的次级绕组12dl中流过的电流矢量Irs和电流矢量Itr所产生的磁通势。从图5所示的绕组的布线可知，用于抵消从次级绕组12d I流出的电流所产生的磁通势的、初级绕组11 a中流过的电流的方向，与次级绕组12bl、12cl、12el相同，是从初级绕组11&amp;流出的方向，即是与次级绕组12(11相同的正方向。 [0076] 次级绕组12dl中，电流矢量Irs因流过星形接线部分，因此初级绕组IIa中也流过如下电流，即相对于电流矢量Irs方向相同，且大小为电流矢量Irs的初级绕组Ila与次级绕组12dl的星形接线部分的绕组数之比倍。此外，电流矢量Itr因流过次级绕组12dl的星形接线部分和三角形接线部分，因此初级绕组Ila中流过如下电流，即相对于电流矢量Itr方向相同，且大小为其初级绕组Ila与次级绕组12dl的绕组数之比倍。 [0077]关于次级绕组12f，初级绕组I Ia中也流过如下电流，即抵消因卷绕于与初级绕组I Ia同一铁芯的次级绕组12f I中流过的电流矢量Irs和电流矢量Itr所产生的磁通势。次级绕组12Π的连接状态如图5所示，因与次级绕组12dl的连接状态相同，因此通过与次级绕组12dl情况相同的变换作用，初级绕组Ila中流过由次级绕组12fl的电流矢量Irs、Itr而产生的电流。 [0078]如此，初级绕组Ila中流过如下电流，即其方向为相对于各次级绕组12中流过的电流矢量Irs、Itr的上述方向，且其大小与各次级绕组12之中借由电流矢量Irs、Itr而流过有r相电流的绕组与初级绕组Ila绕组的绕组数之比相对应。 [0079]因此，由于次级绕组12a〜12f而在初级绕组Ila中流过的电流的电流矢量为如图12所示的状态。图12是次级绕组12a〜12f中r相的电压为正的情况下，由于次级绕组12a〜12f中流过的电流而在初级绕组11 a中流过的电流的电流矢量的示意图。 [0080]此外，r相的相电压Vr为负的情况下，由于次级绕组12a〜12f而在初级绕组IIa中流过的电流的电流矢量如图13所示，与图12所示的状态的相位相差180度。图13是次级绕组12a〜12f中r相的相电压Vr为负的情况下，通过次级绕组12a〜12f中流过的电流而在初级绕组11 a中流过的电流的电流矢量的示意图。 [0081]因此，初级电压VR为正电压时，由于次级绕组12a〜12f中流过的电流而在初级绕组Ila中流过的电流的电流矢量如图12所示。另一方面，初级电压VR为负电压时，由于次级绕组12a〜12f中流过的电流而在初级绕组I Ia中流过的电流的电流矢量为如图13所示的电流矢量。 [0082] 如图12及图13所示，由于次级绕组12a〜12f的电流矢量Irs、Itr而在初级绕组Ila中流过的电流，相对于R相电压最大的相位，对称地以相互之间相位依次相差10度的状态分布。各次级绕组12的电流矢量Irs如上所述，于r相与s相之间的线间电压为3个线间电压之中最大或最小时流过，其波形为尖头波状。此外，各次级绕组12的电流矢量Itr如上所述，于t相与r相之间的线间电压为3个线间电压之中最大或最小时流过，其波形为尖头波状。 [0083]不过，由于通过各次级绕组12中流过的电流而在初级绕组Ila中流过的各电流的电流矢量如上述般的分布，因此分散了尖头波状电流所造成的影响，而降低了电流谐波。因S相和T相的初级绕组11b、11c中也流过有相同的电流，因此能够降低三相交流电源2侧的电流谐波。 [0084]如上所述，在第I实施方式的串联多重电力变换装置I中，同一输出相中的2个单相电力变换器21所分别连接的2个次级绕组12的电压相位的关系为相差30度。进而，3个单相电力变换器21所分别连接的3个次级绕组12的电压相位关系为，U相、V相及W相3个输出相之间依次相差20度。 [0085]因为这样的结构，在第I实施方式的串联多重电力变换装置I中，6个次级绕组12a〜12f所连接的6个单相电力变换器21a〜21f，如图12或图13所示，初级绕组11中依次相差10度产生尖头波状电流。因此，可分散尖头波状电流所造成的影响，并可降低三相交流电源2侧的电流谐波。 [0086]另外，于上述例中，在U相、V相、W相的3个输出相之间，具有同一级数的输出相中的位置关系为，连接于同一单相电力变换器21的次级绕组12的电压相位依次相差20度，但并不限定于该关系。例如，亦可为以图14所示的位置关系，将次级绕组12连接于单相电力变换器21的串联多重电力变换装置1A。图14是多重变压器10中次级绕组12另外的电压相位关系的示意图。如图14所示，从分别串联连接于各相的单相电力变换器21之中选出I个，使连接于这些单相电力变换器21的m个次级绕组12作为I组的电压相位依次相差60/m度即可。 [0087](第2实施方式) [0088]图15是第2实施方式的串联多重电力变换装置中多重变压器二次绕组的电压相位差的示意图。于第2实施方式的串联多重电力变换装置中，与第I实施方式的串联多重电力变换装置1、1A的不同点在于，其各输出相具备3(n=3)级单相电力变换器21。 [0089]如图15所示，于第2实施方式的串联多重电力变换装置IB中，设置于同一输出相的3个单相电力变换器21所分别连接的3个次级绕组12的电压相位依次相差20度。具体而言，在U相中，对应Ul和U2位置的次级绕组12之间有20度的电压相位差。此外，对应U2和U3位置的次级绕组12之间有20度的电压相位差。该关系于V相及W相也相同。 [0090]此外，于串联多重电力变换装置IB的多重变压器中，在输出相间，3个单相电力变换器21所分别连接的3个次级绕组12的电压相位依次相差20度。具体而言，对应Ul和Vl位置的次级绕组12之间有20度的电压相位差。此外，对应Vl和Wl位置的次级绕组12之间有20度的电压相位差。该关系于对应(U2、V2、W2)和(U3、V3、W3)位置的次级绕组12也相同。 [0091]另外，与第I实施方式相同，从分别串联连接于各相的单相电力变换器21之中选出I个，使连接于这些单相电力变换器21的m个次级绕组12作为I组的电压相位依次相差60/m度亦可，并不限定于图15所示的关系。 [0092]如此，第2实施方式的串联多重电力变换装置IB中，同一输出相的3个单相电力变换器21所分别连接的3个次级绕组12的电压相位的关系为依次相差20度。进而，U相、V相及W相的3个输出相间，每相各I个，合计3个的单相电力变换器21所分别连接的3个次级绕组12的电压相位关系为依次相差20度。 [0093]因此，第2实施方式的串联多重电力变换装置IB中，借由连接于9个次级绕组12的9个单相电力变换器21，初级绕组11的各相中依次相差20/3度产生尖头波状电流。其结果可分散电流脉冲所造成的影响，并可降低三相交流电源2侧的电流谐波。 [0094]另外，在上述实施方式中，虽设输出相为3相(m=3)来对具备各输出相为2级或3级(n=2或3)的单相电力变换器21的串联多重电力变换装置1、IA、IB进行了说明，但输出相的数量、组成各输出相的单相电力变换器21的数量并不限定于此。 [0095]此外，上述实施方式中，虽举了次级绕组12的电压相位按(U相—V相—W相)的顺序前移的例子(参照图4)，但并不限定于此。例如次级绕组12的电压相位亦可按(V相—W相—U相)或(W相—U相—V相)的顺序前移，此外，亦可按(V相—W相—U相)、(W相—U相—V相)或(U相—V相—W相)的顺序后移。 [0096]即在多重变压器10中，满足以下条件即可。另外，n、m为互素。 [0097] (I)设置于同一输出相的η个单相电力变换器21所分别连接的η个次级绕组12的电压相位关系为依次相差60/η度。 [0098] (2)在m个输出相间，连接于单相电力变换器21的次级绕组12的电压相位关系为依次相差60/m度。 [0099]更进一步的效果或变形例，可由本领域人员简单导出。因而本发明比起上述的这些实施例还有更加广泛的形式，不限于如以上所表达和记述的特定详情以及代表性实施方式。在不脱离通过附加的专利申请范围及其同等物所定义的总结发明概念的精神或范围，各种更新皆有可能。 [EN EP2587658B1]: The embodiments discussed herein are directed to a series-connected multi-level power conversion device. As a conventional power conversion device, there is known a series-connected multi-level power conversion device that has a plurality of output phases each of which is constituted by serially-connected power conversion cells. The series-connected multi-level power conversion device includes a multi-winding transformer and a plurality of single-phase power converters. The multi-winding transformer transforms a multiphase alternating input voltage into a primary winding and outputs the transformed voltage to a plurality of secondary windings. The plurality of single-phase power converters are respectively connected to the secondary windings of the multi-winding transformer. In the series-connected multi-level power conversion device, the secondary windings of the multi-winding transformer output voltages whose phases are different from one another in order to reduce a harmonic current in the primary winding. More specifically, there has been proposed a method in which, when the series-connected multi-level power conversion device includes nine single-phase power converters, secondary windings connected to three single-phase power converters that constitutes one of U, V, and W phases have a voltage phase difference of 20 degrees and all the secondary windings have a voltage phase difference of 20/3 degrees. This method has been known as disclosed in, for example, Japanese Laid-open Patent Publication No. 2008-295149. An aspect of embodiments has an object of the embodiments to provide a new technology substituting for a conventional technology to reduce a harmonic current in a primary winding. This is achieved by the features of independent claim 1. According to an aspect of embodiments, it is possible to reduce a harmonic current in a primary winding. A more complete appreciation of the invention and many of the attendant advantages thereof will be readily obtained as the same becomes better understood by reference to the following detailed description when considered in connection with the accompanying drawings, wherein: FIG. 1 is a diagram illustrating a series-connected multi-level power conversion device according to a first embodiment;FIG. 2 is a diagram illustrating a circuit block of a single-phase power converter illustrated in FIG. 1;FIG. 3 is a diagram illustrating voltage phase differences between secondary windings of a multi-winding transformer;FIG. 4 is a diagram illustrating a voltage phase relationship among the secondary windings of the multi-winding transformer;FIG. 5 is a diagram illustrating wiring of the multi-winding transformer;FIGs. 6 to 8 are diagrams illustrating relationships between line voltage vectors of a primary winding and line voltage vectors of the secondary winding of the multi-winding transformer;FIG. 9 is a diagram illustrating current vectors of each secondary winding of the multi-winding transformer;FIG. 10 is a diagram illustrating current vectors of each secondary winding of the multi-winding transformer;FIG. 11 is a diagram explaining a current in each secondary winding in an r phase;FIG. 12 is a diagram illustrating current vectors in the primary winding caused by currents in the secondary windings when a primary voltage is positive;FIG. 13 is a diagram illustrating current vectors in the primary winding caused by currents in the secondary windings when the primary voltage is negative;FIG. 14 is a diagram illustrating another voltage phase relationship among the secondary windings of the multi-winding transformer; andFIG. 15 is a diagram illustrating voltage phase differences between secondary windings of a multi-winding transformer of a series-connected multi-level power conversion device according to a second embodiment. Hereinafter, a series-connected multi-level power conversion device according to embodiments of the present disclosure will be explained in detail with reference to the accompanying drawings. In addition, the embodiments disclosed below are not intended to limit the present invention. First Embodiment First, the configuration of a series-connected multi-level power conversion device according to the first embodiment will be explained. FIG. 1 is a diagram illustrating a series-connected multi-level power conversion device 1 according to the first embodiment. As illustrated in FIG. 1, the series-connected multi-level power conversion device 1 includes a multi-winding transformer 10 and a power conversion unit 20. The series-connected multi-level power conversion device 1 converts an R-phase, S-phase, and T-phase AC power from a three-phase AC power source 2 into an AC power and supplies the converted power to an alternating-current load 3. Herein, as an example, it is explained that the series-connected multi-level power conversion device 1 has three output phases (m=3) each of which is constituted by two-stage (n=2) single-phase power converters and the alternating-current load 3 is a motor. The multi-winding transformer 10 includes a primary winding 11 and six secondary windings 12a to 12f (hereinafter, they may be referred to as secondary windings 12). The multi-winding transformer 10 transforms an AC power input into the primary winding 11 and outputs the transformed power to the six secondary windings 12a to 12f. The multi-winding transformer 10 is a phase-shifting transformer that generates voltage phase differences between the primary winding 11 and the secondary windings 12. The power conversion unit 20 includes six single-phase power converters 21a to 21f (hereinafter, they may be referred to as single-phase power converters 21) that are respectively connected to the six secondary windings 12a to 12f. Each of the single-phase power converters 21 converts three-phase AC power from the corresponding secondary winding 12 into single-phase AC power and outputs the converted AC power through its own output terminals Ta and Tb. In the power conversion unit 20, serially-connected outputs of the two single-phase power converters 21 constitute one output phase. In other words, a U-phase power conversion unit is constituted by the single-phase power converters 21a and 21d, a V-phase power conversion unit is constituted by the single-phase power converters 21b and 21e, and a W-phase power conversion unit is constituted by the single-phase power converters 21c and 21f. More specifically, the output terminal Tb of the single-phase power converter 21a is connected to a neutral point N, and the output terminal Ta of the single-phase power converter 21a is connected to the output terminal Tb of the single-phase power converter 21d. This connection leads to the configuration of the U-phase power conversion unit whose output terminal is the output terminal Ta of the single-phase power converter 21d. Similarly, the output terminals Tb of the single-phase power converters 21b and 21c are connected to the neutral point N, and the output terminals Ta of the single-phase power converters 21b and 21c are respectively connected to the output terminals Tb of the single-phase power converters 21e and 21f. These connections lead to the configurations of the V-phase and W-phase power conversion units whose output terminals are the output terminals Ta of the single-phase power converters 21e and 21f. Now, the configuration of the single-phase power converter 21 will be explained. FIG. 2 is a diagram illustrating a circuit block of the single-phase power converter 21. As illustrated in FIG. 2, the single-phase power converter 21 includes a rectification/smoothing unit 30, an inverter unit 31, and a control unit 32. The rectification/smoothing unit 30 includes diodes D10 to D15 and a capacitor C10. The rectification/smoothing unit 30 converts the three-phase (r phase, s phase, and t phase) AC power from the corresponding secondary winding 12 into a DC power. In this case, the diodes D10 and D11 perform full-wave rectification on the r-phase power, the diodes D12 and D13 perform full-wave rectification on the s-phase power, and the diodes D14 and D15 perform full-wave rectification on the t-phase power. Then, the voltage rectified by the diodes D10 to D15 is smoothed by the capacitor C10. The inverter unit 31 includes transistors Q20 to Q23 and diodes D20 to D23. The transistors Q20 and Q21 are serially connected between the outputs of the rectification/smoothing unit 30. Similarly, the transistors Q22 and Q23 are serially connected between the outputs of the rectification/smoothing unit 30. Herein, the diodes D20 to D23 are freewheeling diodes. The control unit 32 controls ON/OFF states of the transistors Q20 to Q23 of the inverter unit 31 to make the inverter unit 31 convert the DC power of the rectification/smoothing unit 30 into single-phase AC power. The transistors Q20 to Q23 uses power semiconductor devices such as IGBT and MOSFET. The inverter unit 31 is not limited to the configuration of the two-level inverter illustrated in FIG. 2. For example, the inverter unit 31 can employ the configuration of a multi-level inverter such as a three-level inverter. Moreover, the inverter unit 31 can employ the other various configurations. Next, the configuration of the multi-winding transformer 10 will be explained. FIG. 3 is a diagram illustrating voltage phase differences between the secondary windings 12a to 12f. FIG. 4 is a diagram illustrating a voltage phase relationship among the secondary windings 12a to 12f. As described above, the single-phase power converters 21a to 21f are respectively located at U1, V1, W1, U2, V2, and W2, and are respectively connected to the secondary windings 12a to 12f (see FIG. 1). Herein, in the symbols U1 to W2, characters U, V, and W indicate output phases and numbers "1" and "2" indicate the order of stages that are serially connected in one output phase. Therefore, the secondary winding 12a corresponds to the position U1, the secondary winding 12b corresponds to the position V1, the secondary winding 12c corresponds to the position W1, the secondary winding 12d corresponds to the position U2, the secondary winding 12e corresponds to the position V2, and the secondary winding 12f corresponds to the position W2. As illustrated in FIG. 3, in the multi-winding transformer 10 according to the first embodiment, a voltage phase difference between the two secondary windings 12 respectively connected to the two single-phase power converters 21 in the same output phase is 30 degrees. More specifically, in the case of the U phase, a voltage phase difference between the secondary winding 12a corresponding to the position U1 and the secondary winding 12d corresponding to the position U2 is 30 degrees. Similarly, in the case of the V phase, a voltage phase difference between the secondary winding 12b corresponding to the position V1 and the secondary winding 12e corresponding to the position V2 is 30 degrees. Moreover, in the case of the W phase, a voltage phase difference between the secondary winding 12c corresponding to the position W1 and the secondary winding 12f corresponding to the position W2 is 30 degrees. On the other hand, in the multi-winding transformer 10, a voltage phase difference between the two secondary windings 12 respectively connected to the two single-phase power converters 21 corresponding to the different output phases is 20 degrees. More specifically, a voltage phase difference between the secondary winding 12a corresponding to the position U1 and the secondary winding 12b corresponding to the position V1 is 20 degrees. Moreover, a voltage phase difference between the secondary winding 12b corresponding to the position V1 and the secondary winding 12c corresponding to the position W1 is 20 degrees. Now, a specific example of the voltage phase differences between the secondary windings 12a to 12f will be explained with reference to FIG. 4. As illustrated in FIG. 4, the voltage phases of the secondary windings 12 are (135 degrees, 155 degrees, 165 degrees, 175 degrees, 185 degrees, 205 degrees) in order of (U1, V1, U2, W1, V2, W2). These voltage phases of the secondary windings 12 are defined as phase differences between the voltages of the secondary windings 12 and the voltage of the primary winding 11. Therefore, the voltage phases of the secondary windings 12 are (U1, U2) = (135 degrees, 165 degrees) in the U phase, (V1, V2) = (155 degrees, 185 degrees) in the V phase, and (W1, W2) = (175 degrees, 205 degrees) in the W phase. The voltage phase difference between the voltages of the secondary windings 12 in the same output phase is 30 degrees. Moreover, two groups of the voltage phases of the secondary windings 12 corresponding to the different output phases are (U1, V1, W1) = (135 degrees, 155 degrees, 175 degrees) and (U2, V2, W2) = (165 degrees, 185 degrees, 205 degrees), and the two voltage phase differences in one group are 20 degrees. A configuration example of the multi-winding transformer 10 having the voltage phase relationship between the secondary windings 12 illustrated in FIG. 4 is explained with reference to FIG. 5. FIG. 5 is a diagram illustrating wiring of the multi-winding transformer 10. As illustrated in FIG. 5, the secondary winding 12a is formed by extended delta connection. More specifically, an R-phase primary winding 11a and a secondary winding 12a1 are wound around the same iron core isolated by an insulation member, an S-phase primary winding 11b and a secondary winding 12a2 are wound around the same iron core isolated by the insulation member, and a T-phase primary winding 11c and a secondary winding 12a3 are wound around the same iron core isolated by the insulation member. All the secondary windings 12a1 to 12a3 have taps provided between their coil ends thereof. In FIG. 5, each winding includes a coil end that has a black dot and a coil end that does not have the black dot. When considering a pair of the primary winding and one of the plurality of secondary windings, a black dot is put on one side of coil ends of each winding in such a manner that magnetic fluxes made by both the windings have directions in which the fluxes are reinforced each other when currents flow into from the coil ends of the two windings that have black dots. Herein, the coil end that has the black dot is referred to as a positive coil end and the coil end opposite to the positive coil end is referred to as a negative coil end. In FIG. 5, the positive coil ends of the secondary windings 12a1, 12a2, and 12a3 respectively correspond to the output ends of r-phase, s-phase, and t-phase. Moreover, the negative coil end of the secondary winding 12a1 is connected to the tap of the secondary winding 12a3, the negative coil end of the secondary winding 12a3 is connected to the tap of the secondary winding 12a2, and the negative coil end of the secondary winding 12a2 is connected to the tap of the secondary winding 12a1. Herein, a relationship between the line voltage vectors of the primary winding 11 and the line voltage vectors of the secondary winding 12a when the connection illustrated in FIG. 5 is made will be explained with reference to FIG. 6. FIG. 6 is a diagram illustrating a relationship between the line voltage vectors of the primary winding 11 and the line voltage vectors of the secondary winding 12a. The output phases of the three-phase AC power source 2 are delayed in order of an R phase, an S phase, and a T phase to have a voltage phase difference of 120 degrees. When the secondary windings 12a1, 12a2, and 12a3 are connected as described above, line voltage vectors Vrs, Vst, and Vtr between the phases of the secondary windings 12al, 12a2, and 12a3 are expressed with the following Equations (1) to (3) by using phase voltage vectors Vr, Vs, and Vt. Vrs=Vr−VsVst=Vs−VtVtr=Vt−Vr For example, the line voltage vectors Vrs and Vtr are as illustrated in FIG. 6. When the phase of a line voltage vector VRS from the S phase to the R phase of the primary winding 11 is defined as a base phase, the phase of the line voltage vector Vrs from the s phase to the r phase of the secondary winding 12a is advanced 15 degrees with respect to the base phase. In the secondary winding 12a, the phase of the line voltage vector Vtr from the r phase to the t phase is advanced 120 degrees with respect to the phase of the line voltage vector Vrs and 135 degrees with respect to the base phase. Moreover, the phase of the line voltage vector Vst from the t phase to the s phase is advanced 240 degrees with respect to the phase of the line voltage vector Vrs and 255 degrees with respect to the base phase. Therefore, the secondary winding 12a is a secondary winding with a voltage phase that is advanced 15 degrees with respect to the base phase and is also a secondary winding with a voltage phase that is advanced 135 degrees with respect to the base phase. Furthermore, the secondary winding 12a is a secondary winding with a voltage phase that is advanced 255 degrees with respect to the base phase. Returning to FIG. 5, the secondary winding 12b is explained. As illustrated in FIG. 5, the secondary winding 12b is formed by extended delta connection. More specifically, the R-phase primary winding 11a and a secondary winding 12b1 are wound around the same iron core isolated by the insulation member, the S-phase primary winding 11b and a secondary winding 12b2 are wound around the same iron core isolated by the insulation member, and the T-phase primary winding 11c and a secondary winding 12b3 are wound around the same iron core isolated by the insulation member. All the secondary windings 12b1 to 12b3 have taps provided between their coil ends thereof. The negative coil ends of the secondary windings 12b1, 12b2, and 12b3 respectively correspond to the output ends of r-phase, s-phase, and t-phase. Moreover, the positive coil end of the secondary winding 12b1 is connected to the tap of the secondary winding 12b2, the positive coil end of the secondary winding 12b2 is connected to the tap of the secondary winding 12b3, and the positive coil end of the secondary winding 12b3 is connected to the tap of the secondary winding 12b1. Now, a relationship between the line voltage vectors of the primary winding 11 and the line voltage vectors of the secondary winding 12b when the connection illustrated in FIG. 5 is made will be explained with reference to FIG. 7. FIG. 7 is a diagram illustrating a relationship between the line voltage vectors of the primary winding 11 and the line voltage vectors of the secondary windings 12b, 12c, and 12e. Herein, the phase of the line voltage vector VRS (see FIG. 6) from the S phase to the R phase is defined as the base phase. When the secondary windings 12b1, 12b2, and 12b3 are connected as desc
[DE EP3211784B1]: DOPPEL-SUBMODUL FÜR EINEN MODULAREN MEHRPUNKTSTROMRICHTER UND MODULARER MEHRPUNKTSTROMRICHTER MIT DIESEM [EN US11108338B2]: Dual submodule for a modular multilevel converter and modular multilevel converter including the same [FR EP3211784B1]: SOUS-MODULE DOUBLE POUR UN CONVERTISSEUR DE FRÉQUENCE MULTIPOINTS MODULAIRE ET CONVERTISSEUR DE FRÉQUENCE MULTIPOINTS MODULAIRE EN ÉTANT DOTE [ZH CN108702105B]: 用于模块化多电平换流器的双子模块和包括该双子模块的模块化多电平换流器 | [DE EP3211784B1]: Es ist ein Doppel-Submodul (18) für einen modularen Mehrpunktstromrichter (8) geschaffen, wobei das Doppel-Submodul (18) zwei miteinander verbundene Submodule (19, 21) aufweist, wobei jedes Submodul eine asymmetrische H-Brückenschaltung (22, 32) mit zwei parallelen Brückenzweigen (24, 26; 34, 36), die zwischen einem ersten und einem zweiten Polanschluss (27, 28; 37, 38) des Submoduls (19, 21) angeschlossen sind, wobei jeder Brückenzweig durch eine Reihenschaltung aus einem Leistungshalbleiterschalter (T1, T4; T6, T7) und einer Diode (D2, D3; D5, D8) gebildet ist, wobei dem Leistungshalbleiterschalter eine antiparallel geschaltete Freilaufdiode (D1, D4; D6, D7) zugeordnet ist, und einen Kondensator (23; 33) aufweist, der parallel zu der asymmetrischen H-Brückenschaltung (22; 32) zwischen dem ersten und dem zweiten Polanschluss des Moduls angeschlossen ist. Die Submodule (19, 21) sind über deren Wechselspannungsanschlüsse (29, 31; 39, 41) miteinander verbunden, um das Doppel-Submodul (18) zu bilden. Ferner ist ein modularer Mehrpunktstromrichter (8) geschaffen, der eine Anzahl derartiger Doppel-Submodule (18) in jedem seiner Stromrichterzweige (9a-9f) aufweist. [EN US11108338B2]: A dual submodule is created for a modular multilevel converter, whereby the dual submodule has two interconnected submodules, whereby each submodule has an asymmetrical half-bridge circuit with two parallel bridge branches, which are connected between a first and a second terminal connection of the submodule, whereby each bridge branch is formed from a series circuit of a power semiconductor switch, and a diode, whereby the power semiconductor switch is allocated to an antiparallel free-wheeling diode, and has a capacitor, which is connected in parallel with the asymmetrical half-bridge circuit between the first and the second terminal connections of the module. The submodules are connected to each other via their AC terminals to form the dual submodule. Further, a modular multilevel converter is created, comprising a number of such dual submodules in each of its converter branches. [FR WO2017144693A1]: Un sous-module double (18) est créé pour un convertisseur multiniveau modulaire (8), le sous-module double (18) comportant par là-même deux sous-modules (19, 21) interconnectés, chaque sous-module comprenant un circuit en demi-pont asymétrique (22, 32) à deux branches de pont parallèles (24, 26 ; 34, 36), qui sont connectées entre une première et une seconde connexion de bornes (27, 28 ; 37, 38) du sous-module (19, 21), chaque branche de pont étant constituée d'un circuit en série d'un commutateur à semi-conducteurs de puissance (T1, T4 ; T6, T7), et d'une diode (D2, D3 ; D5, D8), le commutateur à semi-conducteurs de puissance étant attribué à une diode de roue libre antiparallèle (D1, D4 ; D6, D7) et comprenant un condensateur (23 ; 33) qui est monté en parallèle avec le circuit en demi-pont asymétrique ( 22 ; 32 ) entre les première et seconde connexions de bornes du module. Les sous-modules (19, 21) sont connectés entre eux par le biais de leurs bornes c.a. (29, 31 ; 39, 41) pour former le sous-module double (18). En outre, un convertisseur multiniveau modulaire (8) est créé, comprenant un certain nombre desdits sous-modules doubles (18) dans chacune de ses branches (9a-9f) de convertisseur. [ZH CN108702105B]: 一种双子模块(18)形成用于模块化多电平换流器(8)的，其中，所述双子模块(18)具有两个互连子模块(19，21)，其中，每个子模块具有：非对称半桥电路(22，32)，所述非对称半桥电路(22，32)具有连接在所述子模块(19，21)的第一和第二端子连接(27，28；37，38)之间的两个并联桥支路(24，26；34，36)，其中，每个桥支路由电力半导体开关(T1，T4；T6，T7)和二极管(D2，D3；D5，D8)的串联电路形成，其中，所述电力半导体开关被分配给反并联续流二极管(D1，D4；D6，D7)，并且具有电容器(23；33)，所述电容器与所述非对称半桥电路(22；32)并联连接在所述模块的所述第一和所述第二端子连接之间。子模块(19，21)通过其AC端子(29，31；39，41)相互连接，形成双子模块(18)。此外，模块化多电平换流器(8)形成包括在其每一个换流器支路(9a‑9f)中的多个这种双子模块(18)。 | EP3211784B1 | 2017-08-30 2021-03-31 | EP16157275A | 2016-02-25 2016-02-25 | EP16157275A, 2016-02-25 EP16157275A, 2016-02-25 | EP3211784B1: 2021-03-31 WO2017144693A1: 2017-08-31 US11108338B2: 2021-08-31 CN108702105B: 2020-12-01 | GE ENERGY POWER CONVERSION TECHNOLOGY LTD GE ENERGY POWER CONVERSION TECHNOLOGY LIMITED 通用电气能源能量变换技术有限公司 | JANNING JÖRG GESKE MARTIN JANNING JOERG | H02M7/483: I H02M1/32: I H02M7/66: I H02M1/00: N | H02M7/483: I H02M1/0085: A H02M7/4835: A Y02B70/10: A H02M1/32: I H02M1/0054: A | EP2432109A2 DE10103031A1 WO2008110129A1 US2015009594A1 WO2014005634A1 US2018076734A1 US2012038330A1 US2013235624A1 US2016126827A1 US2014005634A1 US5467049A US2015049530A1 CN1797912A CN102403914A | US10491139B2 US10491139 US10971994B2 US10971994 10971994 DE102019120615B3 DE102019120615 102019120615 US11081972B2 US11081972 11081972 | [DE EP3211784B1]: Doppel-Submodul für einen modularen Mehrpunktstromrichter, wobei das Doppel-Submodul (18) zwei miteinander verbundene Submodule (19, 21) aufweist, wobei jedes Submodul (19, 21) aufweist: eine asymmetrische H-Brückenschaltung (22; 32) mit zwei parallelen Brückenzweigen (24, 26; 34, 36), die zwischen einem ersten und einem zweiten Polanschluss (27, 28; 37, 38) des Submoduls (19, 21) angeschlossen sind, wobei jeder Brückenzweig (24, 26; 34, 36) durch eine Reihenschaltung aus einem Leistungshalbleiterschalter (T1, T4; T6, T7) und einer Diode (D2, D3; D5, D8) gebildet ist, wobei dem Leistungshalbleiterschalter (T1, T4; T6, T7) eine antiparallel geschaltete Freilaufdiode (D1, D4; D6, D7) zugeordnet ist; undeinen Kondensator (C1, 23; C2, 33), der parallel zu der asymmetrischen H-Brückenschaltung (22; 32) zwischen dem ersten und dem zweiten Polanschluss (27, 28; 37, 38) des Submoduls (19, 21) angeschlossen ist;wobei ein Verbindungspunkt (29, 31) zwischen einem Leistungshalbleiterschalter (T1, T4) und einer Diode (D2, D3) jedes Brückenzweigs (24, 26) eines der Submodule (19, 21) mit jeweils einem Verbindungspunkt (39, 41) zwischen einem Leistungshalbleiterschalter (T6, T7) und einer Diode (D5, D8) eines Brückenzweigs (34, 36) des anderen Submoduls (21) direkt verbunden ist, um das Doppel-Submodul (18) zu bilden. Doppel-Submodul nach Anspruch 1, wobei ein erster, negativerer Polanschluss (28) eines (19) der Submodule (19, 21) eine erste Ein-/Ausgangsklemme (42) des Doppel-Submoduls (18) bildet, während ein zweiter, positiverer Polanschluss (37) des anderen Submoduls (21) eine zweite Ein-/Ausgangsklemme (43) des Doppel-Submoduls (18) bildet. Doppel-Submodul nach Anspruch 2, wobei das Doppel-Submodul (18) dazu eingerichtet ist, bei Ansteuerung der Leistungshalbleiterschalter (T1, T4, T6, T7) stets eine unipolare Ausgangsspannung (Ua) zu erzeugen und einen bipolaren Strom (Ia) zwischen der ersten und der zweiten Ein-/Ausgangsklemme (42, 43) des Doppel-Submoduls (18) zu führen. Doppel-Submodul nach Anspruch 2 oder 3, wobei das Doppel-Submodul (18) dazu eingerichtet ist, bei Ansteuerung der Leistungshalbleiterschalter (T1, T4, T6, T7) eine Null-Klemmenspannung, eine Klemmenspannung (Ua), die der positiven Spannung (UC1, UC2) eines der Kondensatoren (C1, 23; C2, 33) entspricht, oder eine Spannung zu erzeugen, die der Summe (UC1 + UC2) der positiven Spannungen der Kondensatoren (C1, 23; C2, 33) entspricht. Doppel-Submodul nach einem der Ansprüche 2-4, wobei das Doppel-Submodul (18) derart eingerichtet ist, dass bei der Führung eines Stroms zwischen der ersten und der zweiten Ein-/Ausgangsklemme (42, 43) des Doppel-Submoduls (18) in jede Richtung in jedem Submodul (19, 21) maximal nur ein einziger Leistungshalbleiterschalter (T1, T4, T6, T7) stromdurchflossen ist. Doppel-Submodul nach einem der Ansprüche 2-5, wobei das Doppel-Submodul (18) in manchen Schaltzuständen dazu eingerichtet ist, einen Strom zwischen der ersten und der zweiten Ein-/Ausgangsklemme (42, 43) des Doppel-Submoduls (18) durch zwei parallele Strompfade innerhalb des Doppel-Submoduls (18) zu führen, die jeweils zwei der Dioden bzw. Freilaufdioden (D1-D8) enthalten. Doppel-Submodul nach einem der vorstehenden Ansprüche, wobei alle Dioden (D2, D3; D5, D8) und Freilaufdioden (D1, D4; D6, D7) in Durchlassrichtung von dem zweiten (28; 38) zu dem ersten (27; 37) Polanschluss jedes Submoduls (19, 21) ausgerichtet sind. Doppel-Submodul nach einem der vorstehenden Ansprüche, wobei die Dioden (D2, D3; D5, D8) in den Brückenzweigen (24, 26; 34, 36) eines jeden Submoduls (19, 21) mit unterschiedlichen Anschlüssen des Submoduls (19, 21) direkt verbunden sind. Doppel-Submodul nach einem der vorstehenden Ansprüche, wobei die Submodule (19, 21) derart miteinander elektrisch verbunden sind, dass stets eine Anode einer Diode (D5; D3) in einem Brückenzweig (34; 26) eines der Submodule (19, 21) mit einer Kathode einer Diode (D2; D8) in einem Brückenzweig (24; 36) des anderen Submoduls (19, 21) direkt verbunden sind. Modularer Mehrpunktstromrichter zur Umwandlung einer Wechselspannung in eine Gleichspannung oder umgekehrt mit wenigstens einem Phasenzweig (11a-c), der einen Wechselspannungsanschluss (17a-c) und wenigstens einen mit einem Gleichspannungszwischenkreis verbundenen Gleichspannungsanschluss (12, 13) aufweist, wobei zwischen jedem Gleichspannungsanschluss (12, 13) und jedem Wechselspannungsanschluss (17a-c) ein Stromrichterzweig (9a-f) ausgebildet ist, wobei in jedem der Stromrichterzweige (9a-f) wenigstens ein Doppel-Submodul (18) nach einem beliebigen der vorhergehenden Ansprüche angeordnet ist. Modularer Mehrpunktstromrichter nach Anspruch 10, der eine der Anzahl von Phasen entsprechende Anzahl von Phasenzweigen (11a-c), vorzugsweise zwei oder drei Phasenzweige (11a-c), einen mit einem ersten Pol des Gleichspannungszwischenkreises verbundenen ersten Gleichspannungsanschluss (12), einen mit einem zweiten Pol des Gleichspannungszwischenkreises verbundenen zweiten Gleichspannungsanschluss (13) und in allen Stromrichterzweigen (9a-f) vorzugsweise die gleiche Anzahl von Doppel-Submodulen (18), vorzugsweise jeweils zwei oder mehrere in Reihe verbundene Doppel-Submodule (18), aufweist. Modularer Mehrpunktstromrichter nach Anspruch 10 oder 11, der ferner eine Steuereinrichtung (44) zur Steuerung des Betriebs des modularen Mehrpunktstromrichters (8) aufweist, wobei die Steuereinrichtung (44) dazu eingerichtet ist, die Leistungshalbleiterschalter derart anzusteuern, dass stets eine unipolare Ausgangsspannung (Ua) ausgegeben wird und ein bipolarer Strom zwischen Ein-/Ausgangsklemmen (42, 43) des Doppel-Submoduls (18) übertragen werden kann. Modularer Mehrpunktstromrichter nach einem der Ansprüche 10-12, wobei die Steuereinrichtung (44) dazu eingerichtet ist, einen Kurzschluss in dem Gleichspannungszwischenkreis zu erkennen und daraufhin alle Leistungshalbleiterschalter (T1, T4, T6, T7) eines Doppel-Submoduls (18) auszuschalten, um einen Kurzschlussstrom über parallele Strompfade in dem Doppel-Submodul (18) zu führen, wobei jeder Strompfad zwei in Reihe verbundene Dioden (D2, D5) bzw. Freilaufdioden (D4, D7) des Doppel-Submoduls (18) aufweist. [EN US11108338B2]: 1. A dual submodule for a modular multilevel converter being electrically coupled to a power supply network, comprising: a first submodule interconnected to a second submodule, each submodule comprising:an asymmetrical half-bridge circuit having a first bridge branch and a second bridge branch, each bridge branch (i) being arranged in parallel to the other of the first and second bridge branch between a first and a second terminal connection of the submodule; (ii) being formed from a first diode and a single series circuit of a power semiconductor switch having an antiparallel free-wheeling diode allocated to it; and (iii) comprising an AC terminal located between the first diode and the single series circuit; anda capacitor connected in parallel to the asymmetrical half-bridge circuit between the first and the second terminal connections of each submodule;wherein, the AC terminal of the first bridge branch of the first submodule forms a first connection point with the AC terminal of the first bridge branch of the second submodule, and the AC terminal of the second bridge branch of the first submodule forms a second connection point with the AC terminal of the second bridge branch of the second submodule, the direct connections between the AC terminals being in parallel to each other and forming the dual submodule;and wherein in the event of a short-circuit within the converter, the power semiconductor switches of the second bridge branches are switched off, and a current being powered by the power supply network (i) flows from an output terminal to the capacitor of the first submodule and (ii) splits into two separate paths, one path being via the free-wheeling diode of the first bridge branch of the first submodule to the first connection point, and continuing to the capacitor of the second submodule via the free-wheeling diode of the first bridge branch of the second submodule, and the second path being via the first diode of the second bridge branch of the first submodule to the second connection point, and continuing to the capacitor of the second submodule via the first diode of the second bridge branch of the second submodule. 2. The dual submodule as described claim 1, wherein a first, more negative terminal connection of the first submodule forms a first input/output terminal of the dual submodule, while a second, more positive terminal connection of the second submodule forms a second input/output terminal of the dual submodule. 3. The dual submodule as described in claim 2, wherein the dual submodule is arranged in such a way, when controlling the power semiconductor switch, a unipolar output voltage is always generated, and a bipolar current is conducted between the first and the second input/output terminal of the dual submodule. 4. The dual submodule as described in claim 2, wherein the dual submodule is arranged in such a way, when controlling the power semiconductor switch, a zero terminal voltage, a terminal voltage that corresponds to the positive voltage of one of the capacitors, or a voltage is generated that corresponds to the sum of the positive voltages of the capacitors. 5. The dual submodule as described in claim 2, wherein the dual submodule is arranged in such a way, when the current is conducted between the first and the second input/output terminal of the dual submodule in each direction in each submodule, a maximum of only one power semiconductor switch is current-conductive. 6. The dual submodule as described in claim 1, wherein all of the diodes and free-wheeling diodes are aligned in the forward direction from the second to the first terminal connections of each submodule. 7. The dual submodule as described in claim 1, wherein the diodes in the bridge branches of each submodule are connected directly to different terminals of the submodule. 8. The dual submodule as described in claim 1, wherein the submodules are connected to each other electrically in such a way that an anode of one diode in a bridge branch of one of the submodules is always connected directly to a cathode of a diode in a bridge branch of the other submodule. 9. The dual submodule as described in claim 1, wherein the power semiconductor switches of the first bridge branches are switched on. 10. The dual submodule as described in claim 1, wherein the power semiconductor switch of the first bridge branches are switched off. 11. A modular multilevel converter for converting an AC voltage into a DC voltage, or vice versa, the modular multilevel converter having at least one phase branch with an AC voltage connection and at least one DC voltage connection connected to the DC voltage intermediate circuit; wherein, a converter branch is formed between each DC voltage connection and each AC voltage connection; andwherein, in each of the converter branches, at least one dual submodule is arranged as described in claim 1. 12. The modular multilevel converter described in claim 11 which has a number of phase branches corresponding to the number of phases, a first DC voltage terminal connected to the first terminal of the DC voltage intermediate circuit, a second DC voltage terminal connected to the second terminal of the DC voltage intermediate circuit, and in all converter branches the same number of dual submodules. 13. The modular multilevel converter as described in claim 11, further comprising a control device for controlling the operation of the modular multilevel converter, wherein the control device is arranged to control the power semiconductor switch in such a way that a unipolar output voltage is always emitted and a bipolar current can be transmitted between the input/output terminals of the dual submodule. 14. The modular multilevel converter as described in claim 11, wherein the control device is arranged to detect a short-circuit in the DC voltage intermediate circuit and then switch off all of the power semiconductor switches of a dual submodule, in order to conduct a short-circuit current via parallel current paths in the dual submodule, wherein each current path has two series-connected diodes or free-wheeling diodes of the dual submodule. [FR EP3211784B1]: Sous-module double pour un convertisseur multipoints modulaire, selon lequel le sous-module double (18) présente deux sous-modules (19, 21) connectés l'un à l'autre, selon lequel chaque sous-module (19, 21) présente : un circuit en pont en H asymétrique (22 ; 32) avec deux branches de pont parallèles (24, 26 ; 34, 36), qui sont raccordées entre un premier et un second raccord polaire (27, 28 ; 37, 38) du sous-module (19, 21), selon lequel chaque branche de pont (24, 26 ; 34, 36) est formée, au travers d'un circuit en série, d'un interrupteur à semi-conducteurs de puissance (T1, T4 ; T6, T7) et d'une diode (D2, D3 ; D5, D8), selon lequel une diode de roue libre (D1, D4 ; D6, D7) montée de manière antiparallèle est associée à l'interrupteur à semi-conducteurs de puissance (T1, T4 ; T6, T7) ; etun condensateur (C1, 23 ; C2, 33) qui est raccordé en parallèle avec le circuit en pont en H asymétrique (22 ; 32), entre le premier et le second raccord polaire (27, 28 ; 37, 38) du sous-module (19, 21) ;selon lequel un point de connexion (29, 31) entre un interrupteur à semi-conducteurs de puissance (T1, T4) et une diode (D2, D3) de chaque branche de pont (24, 26) d'un des sous-modules (19, 21) est directement connecté à, respectivement, un point de connexion (39, 41) entre un interrupteur à semi-conducteurs de puissance (T6, T7) et une diode (D5, D8) d'une branche de pont (34, 36) de l'autre sous-module (21) pour former le sous-module double (18). Sous-module double selon la revendication 1, selon lequel un premier raccord polaire négatif (28) d'un (19) des sous-modules (19, 21) forme une première borne d'entrée/sortie (42) du sous-module double (18), tandis qu'un second raccord polaire positif (37) de l'autre sous-module (21) forme une seconde borne d'entrée/sortie (43) du sous-module double (18). Sous-module double selon la revendication 2, selon lequel le sous-module double (18) est configuré, lors de la commande de l'interrupteur à semi-conducteurs de puissance (T1, T4, T6, T7), pour produire en permanence une tension de sortie unipolaire (Ua) et conduire un courant bipolaire (Ia) entre la première et la seconde borne d'entrée/sortie (42, 43) du sous-module double (18). Sous-module double selon la revendication 2 ou 3, selon lequel le sous-module double (18) est configuré, lors de la commande de l'interrupteur à semi-conducteurs de puissance (T1, T4, T6, T7), pour produire une tension aux bornes nulle, une tension aux bornes (Ua), qui correspond à la tension positive (Uc1, Uc2) d'un des condensateurs (C1, 23 ; C2, 33), ou une tension qui correspond à la somme (Uc1 + Uc2) des tensions positives des condensateurs (C1, 23 ; C2, 33). Sous-module double selon l'une quelconque des revendications 2-4, selon lequel le sous-module double (18) est configuré de telle façon que, lors de l'acheminement d'un courant entre la première et la seconde borne d'entrée/sortie (42, 43) du sous-module double (18), dans chaque direction, dans chaque sous-module (19, 21), au maximum un seul interrupteur à semi-conducteurs de puissance (T1, T4, T6, T7) est parcouru par un courant. Sous-module double selon l'une quelconque des revendications 2-5, selon lequel le sous-module double (18), dans plus d'un état de commutation, est configuré pour conduire un courant entre la première et la seconde borne d'entrée/sortie (42, 43) du sous-module double (18) à travers deux trajets de courant parallèles à l'intérieur du sous-module double (18), qui contiennent respectivement deux des diodes ou diodes de roue libre (D1-D8). Sous-module double selon l'une quelconque des revendications précédentes, selon lequel toutes les diodes (D2, D3; D5, D8) et diodes de roule libre (D1, D4 ; D6, D7) sont orientées dans la direction passant de la seconde (28 ; 38) au premier (27 ; 37) raccord polaire de chaque sous-module (19, 21). Sous-module double selon l'une quelconque des revendications précédentes, selon lequel les diodes (D2, D3 ; D5, D8) sont directement connectées, dans les branches de pont (24, 26 ; 34, 36) de chaque sous-module (19, 21), à différents raccords du sous-module (19, 21). Sous-module double selon l'une quelconque des revendications précédentes, selon lequel les sous-modules (19, 21) sont électriquement connectés l'un à l'autre de telle manière qu'une anode d'une diode (D5 ; D3) dans une branche de pont (34 ; 26) d'un des sous-modules (19, 21) soit directement connectée en permanence à une cathode d'une diode (D2 ; D8) dans une branche de pont (24 ; 36) de l'autre sous-module (19, 21). Convertisseur multipoints modulaire pour convertir une tension alternative en une tension continue ou inversement avec au moins une branche de phase (11a-c) qui présente un raccord de tension alternative (17a-c) et au moins un raccord de tension continue (12, 13) connecté à un circuit intermédiaire à tension continue, selon lequel une branche de convertisseur (9a-f) est agencée entre chaque raccord de tension continue (12, 13) et chaque raccord de tension alternative (17a-c), selon lequel dans chacune des branches de convertisseur (9a-f), au moins un sous-module double (18) est disposé selon l'une quelconque des revendications précédentes. Convertisseur multipoints modulaire selon la revendication 10, qui présente un nombre de branches de phase (11a-c) correspondant au nombre de phases, de préférence deux ou trois branches de phase (11a-c), un premier raccord de tension continue (12) connecté à un premier pôle du circuit intermédiaire à tension continue, un second raccord de tension continue (13) connecté à un second pôle du circuit intermédiaire à tension continue et, dans toutes les branches de convertisseur (9a-f), de préférence le même nombre de sous-modules doubles (18), de préférence respectivement deux ou plusieurs sous-modules doubles (18) connectés en série. Convertisseur multipoints modulaire selon la revendication 10 ou 11, qui présente en outre un appareil de commande (44) pour commander le fonctionnement du convertisseur multipoints modulaire (8), selon lequel l'appareil de commande (44) est configuré pour commander les interrupteurs à semi-conducteurs de puissance de telle façon qu'en permanence, une tension de sortie unipolaire (Ua) soit délivrée et un courant bipolaire puisse être transféré entre des bornes d'entrée/sortie (42, 43) du sous-module double (18). Convertisseur multipoints modulaire selon l'une quelconque des revendications 10-12, selon lequel l'appareil de commande (44) est configuré pour reconnaître un court-circuit dans le circuit intermédiaire à tension continue et après cela, pour couper tous les interrupteurs à semi-conducteurs de puissance (T1, T4, T6, T7) d'un sous-module double (18), afin de conduire un courant de court-circuit à travers des trajets de courant parallèles dans le sous-module double (18), selon lequel chaque trajet de courant présente deux diodes (D2, D5) ou diodes de roue libre (D4, D7) du sous-module double (18) connectées en série. [ZH CN108702105B]: 1 .用于模块化多电平换流器的双子模块，其中，所述双子模块(18)具有两个互连子模 块(19,21),其中，每个子模块(19,21)具有： 非对称半桥电路(22; 32)，所述非对称半桥电路(22; 32)具有连接在所述子模块(19, 21)的第一端子连接和第二端子连接(27, 28; 37, 38)之间的两个并联桥支路(24, 26; 34, 36)，其中，每个桥支路(24, 26; 34, 36)由电力半导体开关(T1, T4; T6, T7)和二极 管(D5, D8; D2, D3)的串联电路形成，其中，反并联续流二极管(D1, D4; D6, D7)被分配 给所述电力半导体开关(T1, T4, T6, T7)，所述两个并联桥支路中的一个(24；34)的二极 管(D5; D2)与所述两个并联桥支路中的另一个(26；36)的电力半导体开关(T4; T7)连接至 第一或第二输入/输出端子(42；43)；以及 电容器(C1, 23; C2, 33)并联连接至在所述子模块(19, 21)的所述第一端子连接和 所述第二端子连接(27, 28; 37, 38)之间的所述非对称半桥电路(22; 32)； 其中，所述两个互连子模块(19,21)之一的每个桥支路(24,26)的所述电力半导体开关 (T1, T4)和所述二极管(D2, D3)之间的连接点(29, 31)直接连接至所述两个互连子模块 (19, 21)中另一个的对应桥支路(34, 36)的所述电力半导体开关(T6, T7)和所述二极管 (D5, D8)之间的相应连接点(39, 41)，以形成所述双子模块(18)。 2 .根据权利要求1所述的双子模块，其中，所述子模块(19, 21)之一(19)的第一更负的 端子连接(28)形成所述双子模块(18)的所述第一输入/输出端子(42)，而另一子模块(21) 的第二更正的端子连接(37)形成所述双子模块(18)的所述第二输入/输出端子(43)。 3 .根据权利要求2所述的双子模块，其中，所述双子模块(18)以这样的方式布置：当控 制所述电力半导体开关(T1, T4, T6, T7)时，总是生成单极输出电压(Ua)，并且在所述双 子模块(18)的所述第一输入/输出端子和所述第二输入/输出端子(42, 43)之间传导双极 电流(Ia)。 4 .根据权利要求2所述的双子模块，其中，所述双子模块(18)以这样的方式布置：当控 制所述电力半导体开关(T1, T4, T6, T7)时，生成零端子电压、与所述电容器(C1, 23; C2, 33)之一的正电压(UC1, UC2)对应的端子电压(Ua)、或者与所述电容器(C1, 23; C2, 33)的正电压的和(Uc1+Uc2)对应的电压。 5 .根据权利要求2-4中的任一项所述的双子模块，其中，所述双子模块(18)以这样的方 式布置：当在每个子模块(19, 21)中在每个方向上在所述双子模块(18)的所述第一输入/ 输出端子和所述第二输入/输出端子(42, 43)之间传导电流时，最多只有一个电力半导体 开关(T1, T4, T6, T7)是传导电流的。 6 .根据权利要求2-4中的一项所述的双子模块，其中，所述双子模块(18)以这样的方式 以特定开关状态设置：电流在所述双子模块(18)的所述第一输入/输出端子和所述第二输 入/输出端子(42, 43)之间通过所述双子模块(18)内的两个并联电流路径流动，所述两个 并联电流路径中的每一个包含所述二极管或续流二极管(D1-D8)中的两个。 7 .根据权利要求1-4中的任一项所述的双子模块，其中，所有的二极管(D2, D3; D5, D8)和续流二极管(D1, D4; D6, D7)在从每个子模块(19 , 21)的所述第二端子连接(28 ; 38)到所述第一端子连接(27; 37)的正向方向上对准。 8 .根据权利要求1-4中的任一项所述的双子模块，其中，每个子模块(19, 21)的所述桥 支路(24, 26; 34, 36)中的二极管(D2, D3; D5, D8)直接连接至所述子模块(19, 21)的 不同端子。 9 .根据权利要求1-4中的任一项所述的双子模块，其中，所述子模块(19, 21)以这样的 方式相互电连接:所述子模块(19, 21)之一的桥支路(34; 26)中的一个二极管(D5; D3)的 阳极总是直接连接至另一子模块(19, 21)的桥支路(24; 36)中的二极管(D2; D8)的阴极。 10 .一种用于将AC电压转换成DC电压或者将DC电压转换成AC电压的模块化多电平换流 器，所述模块化多电平换流器具有至少一个相支路(11a-c)，所述相支路(11a-c)具有AC电 压连接(17a-c)和连接至DC电压中间电路的至少一个DC电压连接(12, 13)，其中，在每个DC 电压连接(12, 13)和每个AC电压连接(17a-c)之间形成换流器支路(9a-f)； 其中，在所述换流器支路(9a-f)的每一个中，布置有至少一个根据权利要求1-9中的任 一项中所述的双子模块(18)。 11 .根据权利要求10所述的模块化多电平换流器，其具有与多个相对应的多个相支路 (11a-c)，优选有两个或三个相支路(11a-c)，第一DC电压端子(12)连接至所述DC电压中间 电路的第一端子，第二DC电压端子(13)连接至所述DC电压中间电路的第二端子，并且在所 有的换流器支路(9a-f)中，优选有相同数目的双子模块(18)，优选在每种情况下有两个或 更多个串联连接的双子模块(18)。 12 .根据权利要求10或权利要求11所述的模块化多电平换流器，还具有用于控制所述 模块化多电平换流器(8)的操作的控制装置(44)，其中，所述控制装置(44)布置成以这样的 方式控制所述电力半导体开关：总是发射单极输出电压(Ua)，并且能够在所述双子模块 (18)的输入/输出端子(42, 43)之间传输双极电流。 13 .根据权利要求12所述的模块化多电平换流器，其中，所述控制装置(44)布置成检测 所述DC电压中间电路中的短路，并且接着关断双子模块(18)的所有电力半导体开关(T1, T4, T6, T7)，以便通过所述双子模块(18)中的并联电流路径传导短路电流，其中，每个电 流路径具有所述双子模块(18)的两个串联连接的二极管(D2, D5)或续流二极管(D4, D7)。 | [DE EP3211784B1]: Die vorliegende Erfindung betrifft ein Doppel-Submodul für einen modularen Mehrpunktstromrichter und einen modularen Mehrpunktstromrichter mit einer Reihenschaltung derartiger Doppel-Submodule. Stromrichter zur Umwandlung von Gleichstrom in Wechselstrom und umgekehrt werden für viele Anwendungen, wie bspw. zur Kopplung elektrischer Netze mit drehzahlvariablen Antrieben, zum Energieaustausch zwischen zwei elektrischen Netzen und dgl. verwendet. Hierzu sind Stromrichter in unterschiedlichen Schaltungstopologien und Konfigurationen bekannt. Für kleinere und mittlere Leistungen sind konventionelle Stromrichter in Zweipunkttechnik bekannt, die einfache und robuste Lösungen bieten und weit verbreitet sind. Mit fortwährender Entwicklung von Leistungshalbleiterschaltern und Anwendungsmöglichkeiten von Leistungselektronik werden stets neuere Stromrichtertopologien für immer höhere Leistungs- und Spannungsbereiche gewünscht und entwickelt. Im Mittel- und Hochspannungsbereich werden häufig sog. Mehrpunktstromrichter eingesetzt, um mehrere Spannungsstufen zu erzeugen und die Spannungen auf höhere Niveaus bis in Bereiche der Hochspannungsgleichstromübertragung (HGÜ) zu erhöhen, wobei eine hinreichende Spannungsqualität bei hoher Stufenzahl zu erreichen ist. Eine zunehmend verbreitete Stromrichtertopologie stellt der modulare Mehrpunktstromrichter (Modular Multilevel Converter, MMC bzw. M2C) dar. Dieser Stromrichter weist Phasenzweige bzw. -module auf, die aus zwei in Reihe miteinander verbundenen Stromrichterzweigen bestehen, wobei jeder Stromrichterzweig aus einer Anzahl gleichartiger Zellen (Submodulen) aufgebaut ist. Jedes Submodul ist durch eine Brückenschaltung mit ansteuerbaren Leistungshalbleiterschaltern und einem internen Kondensator zur Zwischenspeicherung elektrischer Energie gebildet. Die Brückenschaltung kann eine Halbbrücke mit zwei in Reihe verbundenen ansteuerbaren Leistungshalbleiterschaltern oder auch eine H- bzw. Vollbrücke sein, die zwei parallele Brückenzweige aufweist, in denen jeweils zwei Leistungshalbleiterschalter in Reihe zueinander angeordnet sind. Zu jedem ansteuerbaren Schalter ist eine Freilaufdiode antiparallel geschaltet. Durch die modulare Bauweise ist der Stromrichter für unterschiedliche Leistungen und Anwendungen individuell skalierbar. Die Spannungen und Ströme auf der Wechselspannungs(AC)-Seite und der Gleichspannungs(DC)-Seite können hochdynamisch und weitgehend entkoppelt voneinander gesteuert und geregelt werden. Ein derartiger modularer Mehrpunktstromrichter ist bspw. aus der DE 101 03 031 A1 bekannt, wobei die Submodule nach Art einer Halbbrücke ausgebildet sind. Jedes Submodul weist also lediglich zwei in Reihe zueinander geschaltete Leistungshalbleiterschalter, die so mit einem Kondensator als Energiespeicher des jeweiligen Submoduls verschaltet sind, dass eine unipolare Spannung, entweder die positive Kondensatorspannung oder eine Nullspannung, an den beiden Anschlussklemmen des Submoduls abfällt. Diese Schaltung ist relativ kostengünstig und zeichnet sich durch geringe Leitungsverluste aus. Es sind auch modulare Mehrpunktstromrichter mit Submodulen in Form von Voll- oder H-Brücken bekannt. Die Verwendung von Voll- bzw. H-Brücken ermöglicht eine Invertierung der an dem Kondensator abfallenden Spannung an den Submodulklemmen. Erkauft wird dies aber mit einer höheren Anzahl von Leistungshalbleiterschaltern und dadurch einem erhöhten Schaltungsaufwand und erhöhten Kosten für den Stromrichter insgesamt. Außerdem sind bei solchen vollbrückenbasierten Submodulen stets zwei Schalter stromdurchflossen, wodurch die Leitungsverluste gegenüber halbbrückenbasierten Submodulen deutlich erhöht sind. Für Anwendungen im Mittel- und Hochspannungsbereich können derartige Leitungsverluste inakzeptabel sein. Ein wesentlicher Aspekt ist auch die Robustheit des Stromrichters im Falle eines Kurzschlusses im Gleichspannungszwischenkreis. Tritt in dem Gleichspannungszwischenkreis ein Kurzschluss auf, der durch ein Wechselspannungsnetz gespeist wird, können sehr hohe Kurzschlussströme durch die Stromrichterzweige fließen. Bei der Verwendung von Halbbrücken als Submodule fließen diese Kurzschlussströme durch die Freilaufdioden, die zu den jeweiligen Leistungshalbleiterschaltern antiparallel geschaltet sind. Die Freilaufdioden müssen folglich relativ stark dimensioniert sein, um derartige transiente Kurzschlussströme auszuhalten, bevor diese erkannt werden und der Stromrichter durch Öffnung des Leistungsschalters auf der Wechselstromseite oder durch Trennung eines DC-Schalters von dem Gleichspannungszwischenkreis getrennt wird. Insofern müssen auch relativ hohe Grenzlastintegral-Anforderungen an die verwendeten Dioden gestellt werden. Das Grenzlastintegral, auch als i2t-Wert bezeichnet, ist ein Kriterium für die Kurzzeitüberlastbarkeit eines Halbleiterbauelementes, bspw. einer Diode. Es gibt den zulässigen Höchstwert an, der innerhalb einer bestimmten Zeitdauer anstehen darf, ohne dass es zur Überschreitung der zulässigen Sperrschicht-Temperatur und somit zur Zerstörung des Bauteils kommt. Das Grenzlastintegral wird durch Integration des Quadratwerts des Stroms über die Zeit für eine bestimmte Zeitdauer bestimmt. Das Grenzlastintegral der verwendeten Dioden muss über dem entsprechenden Grenzlastintegral einer Sicherung liegen, die zum Abschalten des Stromrichters im Kurzschlussfalle verwendet wird. Es ist bekannt, spezielle Kurzschlussschutzeinrichtungen für die Dioden bzw. Freilaufdioden in den Submodulen von modularen Mehrpunktstromrichtern vorzusehen. Bspw. sieht die WO 2008/110129 A1 Thyristoren vor, die parallel zu den Freilaufdioden der Halbbrücken in den Submodulen angeordnet und im Kurzschlussfalle gezündet werden, um einen Teil des durch die jeweilige Freilaufdiode fließenden Kurzschlussstroms zu übernehmen. Dies erhöht aber die Komplexität und die Kosten der Submodulschaltung und für deren Betrieb. Angesichts der unterschiedlichen Einsatzmöglichkeiten und Anforderungen werden stets neuere Konfigurationen von Submodulen für modulare Mehrpunktstromrichter mit dem Ziel entwickelt, die Anzahl der Zellen, die Anzahl der Leistungshalbleiterschalter und die Leitungsverluste zu reduzieren und die Robustheit des Stromrichters im Kurzschlussfalle zu erhöhen. Eine Übersicht von modularen Mehrpunktstromrichtern mit unterschiedlichen Submodulkonfigurationen, einschließlich Vollbrücken-, gekreuzten Konfigurationen, gemischten Zellen, asymmetrischen Zellen, etc., kann bspw. in Alireza Nami, et al.: "Modular Multilevel Converters for HVDC Applications: Review on Converter Cells and Functionalities", in IEEE Transactions on Power Electronics, Vol. 30, No. 1, Januar 2015, Seiten 18-36 gefunden werden. Die Verwendung von Vollbrücken führt zu einer relativ hohen Anzahl von Leistungshalbleiterschaltern und erhöhten Leitungsverlusten im Betrieb. EP 2 432 109 A2 beschreibt ein Submodul in der Konfiguration einer asymmetrischen H-Brückenschaltung und einen modularen Mehrpunktstromrichter mit derartigen Submodulen. Das Submodul weist eine erste Serienschaltung bestehend aus einem ersten steuerbaren Leistungshalbleiterbauelement und einer ersten Diode und eine zweite Serienschaltung bestehend aus einer zweiten Diode und einem zweiten steuerbaren Leistungshalbleiterbauelement auf. Die erste Serienschaltung, die zweite Serienschaltung und ein Kondensator sind zueinander parallel geschaltet. Der Verbindungspunkt des ersten Leistungshalbleiterbauelements mit der ersten Diode bildet einen ersten Ausgangsanschluss, und der Verbindungspunkt der zweiten Diode mit dem zweiten Leistungshalbleiterbauelement bildet einen zweiten Ausgangsanschluss des Submoduls. Der modulare Mehrpunktstromrichter weist pro Phasenzweig mehrere derartige Submodule auf, die über deren erste und zweite Ausgangsanschlüsse in Reihe miteinander verbunden sind. Ein zweiter Ausgangsanschluss eines ersten Submoduls in der Reihenschaltung der Submodule ist mit dem Pluspol einer Zwischenkreisgleichspannung verbunden, während ein erster Ausgangsanschluss eines letzten Submoduls in der Reihenschaltung der Submodule mit dem Minuspol der Zwischenkreisgleichspannung verbunden ist und der Verbindungspunkt zwischen den innersten Submodulen in jeder Reihe zu einem Wechselspannungs-Phasenanschluss des Stromrichters herausgeführt ist. Kalle Ilves, et al.: "A Submodule Implementation for Parallel Connection of Capacitors in Modular Multilevel Converters", in Power Electronics and Applications (EPE), 2013 15th European Conference on, Seiten 1-10 , beschreibt ein Doppel-Submodul, das zwei parallel verbundene Vollbrücken aufweist. Es sind zwei Vollbrückenschaltungen über deren jeweilige Wechselspannungsanschlüsse miteinander verbunden, während ein erster Gleichspannungsanschluss einer ersten Vollbrücke und ein zweiter Gleichspannungsanschluss der zweiten Vollbrücke die beiden Gleichspannungsklemmen des Doppel-Submoduls bilden. Das Doppel-Submodul kann vorteilhafterweise zur direkten AC-AC-Umwandlung verwendet werden. Es weist aber doppelt so viele Leistungshalbleiterschalter wie zwei in Reihe verbundene halbbrückenbasierte Submodule auf. Bei Doppelsubmodulen, die durch bestimmte Schaltzustände eine Parallelschaltung beider Zwischenkreiskondensatoren herbeiführen, können voneinander abweichende Spannungen der Kondensatoren zu teilweise großen Ausgleichströmen und zu dementsprechend höheren Verlusten innerhalb der Submodule führen. Es besteht weiterhin ein Bedarf nach neuen Submodulkonfigurationen für modulare Mehrpunktstromrichter, die die Vorteile der halbbrückenbasierten Submodule, einschließlich einer geringen Anzahl von Leistungshalbleiterschaltern und geringen Leitungsverlusten, bieten, während sie gleichzeitig eine hohe Kurzschlussfestigkeit ermöglichen. Weiterhin wäre es von Vorteil, einen mechanischen Grundaufbau für mehrere Sub-Modulvarianten verwenden zu können. Bisher erfordern bspw. halbbrückenbasierte Submodule einen anderen mechanischen Grundaufbau als vollbrückenbasierte Submodule. Es ist deshalb eine Aufgabe der Erfindung, ein Submodul zur Verwendung in einem modularen Mehrpunktstromrichter zu schaffen, das eine ähnliche Spannungs- und Stromcharakteristik wie halbbrückenbasierte Submodule aufweist, relativ unaufwendig und kostengünstig aufgebaut ist, insbesondere eine geringe Anzahl von Leistungshalbleiterschaltern benötigt, und sich durch geringe Leitungsverluste im Betrieb auszeichnet. Vorzugsweise kann das Submodul mit einem mechanischen Grundaufbau anderer bestehender Submodularten eingesetzt werden. Eine weitere Aufgabe der Erfindung ist es, einen modularen Mehrpunktstromrichter mit einer Anzahl derartiger Submodule zu schaffen, der bei einfachem Aufbau mit relativ geringen Kosten implementiert und betrieben werden kann. Diese Aufgabe wird durch ein Doppel-Submodul mit den Merkmalen des unabhängigen Anspruchs 1 und durch einen modularen Mehrpunktstromrichter mit den Merkmalen des unabhängigen Anspruchs 10 gelöst. Besonders vorteilhafte Ausführungsformen der Erfindung sind Gegenstand der Unteransprüche. Gemäß einem Aspekt der Erfindung ist ein Doppel-Submodul für einen modularen Mehrpunktstromrichter geschaffen, wobei das Doppel-Submodul zwei miteinander verbundene Submodule aufweist. Jedes Submodul weist eine asymmetrische H-Brückenschaltung mit zwei parallelen Brückenzweigen, die zwischen einem ersten und einem zweiten Polanschluss des Submoduls angeschlossen sind, und einen Kondensator auf. Jeder Brückenzweig ist durch eine Reihenschaltung aus einem Leistungshalbleiterschalter und einer Diode gebildet, wobei dem Leistungshalbleiterschalter eine antiparallel geschaltete Freilaufdiode zugeordnet ist. Der Kondensator ist parallel zu der asymmetrischen H-Brückenschaltung zwischen dem ersten und dem zweiten Polanschluss des Submoduls angeschlossen. Ein Verbindungspunkt zwischen einem Leistungshalbleiterschalter und einer Diode jedes Brückenzweigs eines der Submodule ist mit jeweils einem Verbindungspunkt zwischen einem Leistungshalbleiterschalter und einer Diode eines Brückenzweigs des anderen Submoduls direkt verbunden, um das Doppel-Submodul zu bilden. Somit sind erfindungsgemäß zwei asymmetrische H-Brückenschaltungen über ihre Wechselspannungs(AC)-Anschlüsse parallel miteinander verbunden, um das Doppel-Submodul zu bilden. Das Doppel-Submodul weist die gleiche Anzahl von Leistungshalbleiterschaltern wie zwei in Reihe verbundene Halbbrücken-Submodule auf, die das Doppel-Submodul funktionsmäßig ersetzen kann. Das Doppel-Submodul weist auch eine Spannungs- und Stromcharakteristik auf, die denjenigen von Halbbrücken-Submodulen entsprechen. Es kann eine unipolare Ausgangsspannung erzeugen und einen bipolaren Strom führen. Im Betrieb kann sichergestellt werden, dass stets maximal ein Leistungshalbleiterschalter pro Brücke des Doppel-Submoduls in dem Leitungspfad enthalten ist, so dass auch die Leitungsverluste maximal denjenigen von Submodulen auf Halbbrückenbasis entsprechen. Es kann auch in manchen Schaltzuständen der Leistungshalbleiterschalter erreicht werden, dass zwei Halbleiter je Submodul im Strompfad parallel den Strom führen, so dass in diesen Schaltzuständen in vorteilhafter Weise eine Verringerung der Leitungsverluste im Vergleich zu Submodulen auf Basis von Halbbrücken, bei denen der gesamte Strom durch eine einzige Freilaufdiode fließt, bewirkt werden kann. Diese Schaltzustände bei dem Doppel-Submodul verbessern auch die Kurzschlussfestigkeit eines Stromrichters, weil das Grenzlastintegral der Freilaufdioden in den parallelen Strompfaden gemeinsam genutzt werden kann. Im Vergleich zu einem Doppel-Submodul auf Vollbrückenbasis sind die Anzahl von Leistungshalbleiterschaltern in der Schaltung und die Leitungsverluste wenigstens um den Faktor 2 reduziert. Das Doppel-Submodul weist einen einfachen und kostengünstigen Aufbau auf. Seine Konfiguration schafft auch eine Basis dafür, dass bestehende mechanische Grundaufbauten, die z.B. für Submodule auf Basis von Vollbrücken oder asymmetrischen Vollbrücken verwendet werden, ohne große Modifikationen auch für das Doppel-Submodul genutzt werden können. In Ausführungsformen kann ein erster, z.B. negativerer Polanschluss eines der Submodule eine erste Ein-/Ausgangsklemme des Doppel-Submoduls bilden, während ein zweiter, bspw. positiverer Polanschluss des anderen Submoduls eine zweite Ein-/Ausgangsklemme des Doppel-Submoduls bilden kann. Die Kondensatoren der Brückenschaltungen können unipolare Kondensatoren sein. Bei Ansteuerung der Leistungshalbleiterschalter kann eine Spannung zwischen der ersten und der zweiten Ein-/Ausgangsklemme erzeugt werden oder anfallen, die entweder eine Null-Spannung, eine Spannung, die der positiven Spannung eines der Kondensatoren entspricht, oder eine Spannung ist, die der Summe der positiven Spannungen der Kondensatoren entspricht. Wie bereits erwähnt, kann das Doppel-Submodul derart eingerichtet sein, dass bei der Übertragung eines Stroms zwischen der ersten und der zweiten Ein-/Ausgangsklemme des Doppel-Submoduls in jede beliebige Richtung in jedem Submodul maximal nur ein einziger Leistungshalbleiter stromdurchflossen ist. Vorzugsweise ist das Doppel-Submodul ferner dazu eingerichtet, in manchen Schaltzuständen, insbesondere wenn alle Leistungshalbleiterschalter ausgeschaltet sind, einen Strom zwischen der ersten und der zweiten Ein-/Ausgangsklemme des Doppel-Submoduls durch zwei parallele Strompfade zu übertragen, wobei jeder Strompfad zwei der Dioden bzw. Freilaufdioden, nämlich eine Diode bzw. Freilaufdiode in der ersten asymmetrischen H-Brückenschaltung und eine weitere in der zweiten asymmetrischen H-Brückenschaltung, enthält. Dieser Schaltzustand des Doppel-Submoduls kann auch im Falle eines Kurzschlusses im Gleichspannungszwischenkreis genutzt werden, wobei die Strombelastung dann auf die beiden parallelen Strompfade und die zugehörigen Dioden aufgeteilt wird. Die momentane transiente Kurzschlussstromstärke pro Diode ist reduziert, und die Grenzlastintegral (i2t)-Anforderungen an jede Diode bzw. Freilaufdiode können reduziert werden. In einer bevorzugten Ausführungsform sind alle Dioden und Freilaufdioden jedes Submoduls in Durchlassrichtung von dem zweiten zu dem ersten Polanschluss jedes Submoduls ausgerichtet. In anderen Worten sind alle Dioden und Freilaufdioden in Durchlassrichtung von der ersten zu der zweiten Ein-/Ausgangsklemme des Doppel-Submoduls ausgerichtet. Ferner sind die asymmetrischen H-Brückenzweige vorzugsweise derart gestaltet, dass die Dioden in den Brückenzweigen eines jeden Submoduls mit unterschiedlichen Anschlüssen des Submoduls direkt verbunden sind. D.h., die Dioden sind in jeder asymmetrischen H-Brückenschaltung diagonal zueinander angeordnet, so dass die Kathode einer Diode mit dem Pluspol des Submoduls verbunden ist, während die Anode der anderen Diode mit dem Minuspol des Submoduls verbunden ist. Außerdem sind in der bevorzugten Ausführungsform die Submodule vorzugsweise derart miteinander elektrisch verbunden, dass stets eine Anode einer Diode in einem Brückenzweig eines der Submodule mit einer Kathode einer Diode in einem Brückenzweig des anderen Submoduls direkt verbunden ist. Anders gesagt, ist in dem Fall, dass die ansteuerbaren Leistungshalbleiterschalter des Doppel-Submoduls vorzugsweise durch IGBTs gebildet sind, ein Kollektor eines Leistungshalbleiterschalters in einem Brückenzweig eines der Submodule mit einem Emitter eines Leistungshalbleiterschalters in einem Brückenzweig des anderen Submoduls direkt verbunden. Es ist verständlich, dass auch andere Bauarten von ansteuerbaren Leistungshalbleiterschaltern, wie bspw. IGCTs, MOSFETs, GTOs oder dgl., verwendet werden können. Gemäß einem weiteren Aspekt der Erfindung ist ein modularer Mehrpunktstromrichter zur Umwandlung einer Wechselspannung in eine Gleichspannung oder umgekehrt geschaffen. Der modulare Mehrpunktstromrichter weist wenigstens einen Phasenzweig auf, der einen Wechselspannungsanschluss und wenigstens einen mit einem Gleichspannungszwischenkreis verbundenen Gleichspannungsanschluss aufweist, wobei zwischen jedem Gleichspannungsanschluss und jedem Wechselspannungsanschluss ein Stromrichterzweig ausgebildet ist und wobei in jedem der Stromrichterzweige wenigstens ein erfindungsgemäßes Doppel-Submodul nach einer beliebigen der vorstehend beschriebenen Ausführungsformen angeordnet ist. Die Vorteile des Doppel-Submoduls, insbesondere der einfache und kostengünstige Aufbau, die Möglichkeit, bestehende mechanische Grundaufbauten von Submodulen auf Basis von Vollbrücken oder asymmetrischen Vollbrücken auch für das Doppel-Submodul einsetzen zu können, die geringe Anzahl von Leistungshalbleiterschaltern in der Schaltung, die geringe Anzahl von in Reihe geschalteten, stromdurchflossenen Leistungshalbleiterschaltern im Leitungspfad im Betrieb und die damit verbundenen geringen Leitungsverluste, die Möglichkeit, den Strom und insbesondere einen Kurzschlussstrom durch zwei parallele Strompfade mit jeweiligen Dioden bzw. Freilaufdioden zu führen und dadurch die Robustheit des Doppel-Submoduls in Bezug auf seine Kurzschlussfestigkeit zu erhöhen bzw. die i2t-Anforderungen an die Dioden und Freilaufdioden zu reduzieren, kommen auch dem modularen Mehrpunktstromrichter zugute. Der modulare Mehrpunktstromrichter kann eine beliebige Anzahl von Phasenzweigen aufweisen, die der gewünschten Anzahl von Phasen entspricht. Im Allgemeinen sind drei Phasenzweige vorgesehen. Je nach Anwendung kann auch ein einziger Phasenzweig ausreichen, oder es können zwei oder mehr als drei Phasen benötigt sein. Der modulare Mehrpunktstromrichter weist vorzugsweise einen ersten Gleichspannungsanschluss, der mit einem ersten, z.B. positiven Pol des Gleichspannungszwischenkreises verbunden sein kann, und einen zweiten Gleichspannungsanschluss auf, der mit einem zweiten, z.B. negativen oder negativeren Pol des Gleichspannungszwischenkreises verbunden sein kann. In jedem Stromrichterzweig des Stromrichters ist vorzugsweise die gleiche Anzahl von Doppel-Submodulen, vorzugsweise jeweils zwei oder mehrere in Reihe verbundene Doppel-Submodule, angeordnet. Prinzipiell können sich aber die Stromrichterzweige hinsichtlich der Anzahl der Doppel-Submodule voneinander unterscheiden. Es kann eine Steuereinrichtung zur Steuerung des Betriebs des modularen Mehrpunktstromrichters vorgesehen sein, die dazu eingerichtet ist, die Leistungshalbleiterschalter nach einem vorgegebenen Muster derart anzusteuern, dass eine ein- oder mehrphasige Wechselspannung an einem Wechselspannungsanschluss des Stromrichters in eine Gleichspannung an dem Gleichspannungszwischenkreis oder umgekehrt umgewandelt wird. Insbesondere kann die Steuereinrichtung die Leistungshalbleiterschalter derart ansteuern, dass stets eine unipolare Klemmenspannung über den Doppel-Submodulen abfällt und ein bipolarer Strom durch jeden Stromrichterzweig übertragen werden kann. Der modulare Mehrpunktstromrichter ist so für viele unterschiedliche Anwendungen, wie z.B. zur Hochspannungsgleichstrom(HGÜ)-Leistungsübertragung, für große Leistungsantriebe, wie bspw. für Pumpspeicherkraftwerke, für Mittelspannungsantriebe, für Umrichteranlagen zur Bahnstromversorgung, zur Mittelspannungsgleichstromübertragung (MGÜ), bspw. für Photovoltaik- und Windkraftanlagen, und dgl. geeignet. Die Doppel-Submodule gemäß der Erfindung können die üblicherweise in modularen Mehrpunktstromrichtern verwendeten halbbrückenbasierten Submodule bei weiter reduzierten Leitungsverlusten, verbesserter Kurzschlussfestigkeit und reduzierten i2t-Anforderungen an die Halbleiterbauelemente ersetzen. Vorteilhafterweise kann der modulare mechanische Grundaufbau, der z.B. für vollbrückenbasierte Submodule verwendet wird, prinzipiell relativ einfach auch für das Doppel-Submodul genutzt werden. In einer bevorzugten Ausführungsform kann die Steuereinrichtung dazu eingerichtet sein, einen Kurzschluss in dem Gleichspannungszwischenkreis zu erkennen und daraufhin alle Leistungshalbleiterschalter aller Doppel-Submodule in dem Kurzschlusspfad auszuschalten, um einen Kurzschlussstrom über parallele Strompfade in jedem Doppel-Submodul zu führen, wobei jeder Strompfad zwei in Reihe verbundene Dioden des Doppel-Submoduls aufweist. Die Belastung der Dioden mit dem Kurzschlussstrom ist um Faktor 2 reduziert, und die i2t-Auslegung der Dioden kann entsprechend, im Idealfall bis auf ein Viertel reduziert werden. Kurzschlussschutzeinrichtungen für die Dioden bzw. Freilaufdioden werden aufgrund der erfindungsgemäßen Topologie nicht benötigt. Weitere vorteilhafte Einzelheiten von Ausführungsformen der Erfindung ergeben sich aus den Unteransprüchen, der Zeichnung sowie der zugehörigen Beschreibung. Die Erfindung ist nachstehend anhand einer Zeichnung näher beschrieben, die beispielhafte, keinesfalls beschränkende Ausführungsformen der Erfindung zeigt, wobei gleiche Bezugszeichen in allen Figuren verwendet werden, um gleiche Elemente zu bezeichnen. Es zeigen: Fig. 1 ein beispielhaftes System mit einem modularen Mehrpunktstromrichter zur Kopplung eines elektrischen Energieversorgungsnetzes, einer elektrischen Maschine oder einer anderen Wechselspannungsquelle mit einem anderen Netz oder einer Last zur Verdeutlichung einer beispielhaften Anwendung der Erfindung, in Form eines vereinfachten Blockdiagramms;Fig. 2 einen Schaltplan eines auf asymmetrischen H-Brückenschaltungen basierenden Doppel-Submoduls, das in dem modularen Mehrpunktstromrichter nach Fig. 1 gemäß der Erfindung verwendet werden kann;Fig. 3 eine Tabelle, die bevorzugt verwendete Schaltzustände des Doppel-Submoduls nach Fig. 2 mit den resultierenden Ausgangsspannungen veranschaulicht;Fig. 4 eine Darstellung der Ausgangsspannungscharakteristik Ua[pU] normiert, bezogen auf die maximal erreichbare Ausgangsspannung, für das Doppel-Submodul nach Fig. 2;Fig. 5 einen Schaltplan des Doppel-Submoduls nach Fig. 2 unter Veranschaulichung eines Stromflusses in eine erste Richtung bei bestimmten Schaltzuständen des Doppel-Submoduls;Fig. 6 einen Schaltplan des Doppel-Submoduls nach Fig. 2 unter Veranschaulichung von Schaltzuständen mit einer gegenüber Fig. 5 entgegengesetzten Stromflussrichtung;Fig. 7 einen Schaltplan des Doppel-Submoduls nach Fig. 2 unter Veranschaulichung eines weiteren Schaltzustands des Doppel-Submoduls und der resultierenden Strompfade; undFig. 8 eine beispielhafte Strom-Spannungs-Kennlinie im Durchlassbereich einer Diode zur Verwendung in der Schaltungsanordnung des Doppel-Submoduls nach Fig. 2 zur Veranschaulichung einer Reduktion von Leitungsverlusten durch die Schaffung paralleler Strompfade. Es wird nun auf Ausführungsformen der Erfindung Bezug genommen, die in den Zeichnungen veranschaulicht sind. Es sollte verständlich sein, dass die in den Zeichnungen veranschaulichten Ausführungsformen lediglich beispielhaft sind und die Erfindung als solche nicht beschränken. Vielmehr sind die Ausführungsformen lediglich dazu gedacht, mögliche Ausführungsformen zu erläutern und den Fachmann zu befähigen, die Erfindung auszuführen. Es sollte ferner verständlich sein, dass in dem Bemühen, eine konzise Beschreibung möglicher Ausführungsformen zu liefern, gegebenenfalls nicht alle von dem Umfang der Erfindung umfassten Einzelheiten angegeben sein können. In Fig. 1 ist in einer stark vereinfachten Darstellung ein System 1 veranschaulicht, das bspw. ein Hoch- oder Mittelspannungsgleichstrom-Verteilungssystem zur elektrischen Energieübertragung bei hoher bzw. mittlerer Gleichspannung darstellen kann. Ein solches System könnte bspw. zur Kopplung von Gleichspannungsanwendungen an Wechselstromnetze wie Photovoltaik- oder Sammelschienensysteme mit Gleichspannung bzw. Gleichspannungsnetze verwendet werden. Ferner, kann ein solches System auch als sog. Back-to-Back System ausgeführt sein, bei dem die Gleichspannungsseite 6 mit einem elektrischen Stromrichter ähnlich dem Umrichter 4 direkt verbunden sein kann. Eine solche Anordnung ist vorzugsweise für eine Kopplung von Anwendungen oder elektrischen Netzen mit Wechselspannung mit einem Wechselspannungsnetz, wie bspw. für Pumpspeicherkraftwerke unter Verwendung von Generatoren, Windkraftanlagen oder zum Antrieb elektrischer Maschinen, wie Pumpen und Kompressoren, als auch zur Kopplung elektrischer Wechselspannungsnetze einsetzbar. Zur Übertragung von elektrischer Energie können die Stromrichter auf der Gleichspannungsseite 6 auch indirekt über eine Gleichspannungsübertragungseinrichtung verbunden sein. Das System 1 umfasst eine hier bspw. dreiphasige Wechselspannungsquelle 2, die z.B. ein elektrisches Energieversorgungsnetz, eine elektrische Wechselstrom(AC)-Maschine, ein AC-Generator, eine Windkraftanlage oder dgl. sein kann. An die Wechselspannungsquelle 2 ist mit seiner Wechselspannungsseite 3 ein elektrischer Umrichter 4 angeschlossen, dessen Gleichspannungsseite 6 bspw. über eine hier nicht näher dargestellte Gleichstromübertragungseinrichtung mit einem anderen elektrischen Energieversorgungsnetz oder elektrischem Stromrichter ähnlich dem Umrichter 4 verbunden sein kann. Der Anschluss des Umrichters 4 an die Wechselspannungsquelle 2 kann optional über einen Transformator 7 erfolgen. Darüber hinaus ist es ebenfalls denkbar, dass zwei oder mehrere Gleichspannungsnetze mit unterschiedlicher Spannung durch Stromrichter ähnlich dem Umrichter 4 über einen Transformator 7, der im Mittelfrequenzbereich betrieben wird, gekoppelt werden können. Diese Ausführung ermöglicht eine galvanisch getrennte Kopplung von Gleichspannungsnetzen, wobei ein Transformator 7, durch den Betrieb im Mittelfrequenzbereich, so ausgeführt sein kann, dass er ein erheblich geringeres Bauvolumen bzw. einer erheblich reduzierte Baugröße besitzt. Der Umrichter 4 weist wenigstens einen ersten Stromrichter 8 auf, der hier als Gleichrichter betrieben sein kann, um eine Wechselspannung Uac der Wechselspannungsquelle 2 in eine ausgangsseitige Gleichspannung Udc zu wandeln. Optional könnte der Umrichter 4 einen hier nicht dargestellten weiteren Stromrichter aufweisen, der die Spannung Udc in eine passende Wechselspannung wandelt. Der Stromrichter 8 könnte umgekehrt als Wechselrichter eingesetzt werden, um die Gleichspannung Udc in eine Wechselspannung zur Einspeisung in das Wechselspannungsnetz 2 umzuwandeln. Es versteht sich, dass sich die Funktion des bzw. der Stromrichter umkehrt, wenn der Energiefluss zu dem Energieversorgungsnetz oder der Spannungssenke 2 hin erfolgt. Wie aus Fig. 1 ersichtlich, weist der Stromrichter hier sechs Stromrichterzweige 9a-9f auf, von denen jeweils zwei, ein oberer und ein unterer 9a, 9b bzw. 9c, 9d bzw. 9e, 9f einen jeweiligen Phasenzweig 11a, 11b bzw. 11c bilden. Jeder Phasenzweig 11a, 11b, 11c erstreckt sich zwischen einer positiven Stromschiene bzw. einem positiven Gleichspannungsanschluss ("+") 12 des Stromrichters 8 und einer negativen Stromschiene bzw. einem negativen Gleichspannungsanschluss ("-") 13. Wie ferner aus Fig. 1 ersichtlich, weist jeder Stromrichterzweig hier eine Reihenschaltung aus mehreren in Reihe geschalteten Stromrichter-Submodulen oder modularen Schaltern 14 auf. Die steuerbare Gleichspannung Udc an den Gleichspannungsanschlüssen 12, 13 des Stromrichters 8 kann über die Schaltzustände der einzelnen Stromrichter-Submodule 14 dynamisch verändert werden. Die Anzahl der Stromrichter-Submodule 14 bestimmt dabei die verfügbare Anzahl von Stromrichter-Schaltzuständen, die eine feine Spannungsstufung und eine Spannungsform hoher Güte sowie hohe Spannungsniveaus bis in den Bereich der Hochspannungs-Gleichstrom-Übertragungs(HGÜ) ermöglichen. Bei dem Stromrichter 8 handelt es sich somit um einen modularen MultiLevel- oder Mehrpunktstromrichter, der auch als MMC oder M2C bezeichnet wird. In der Technik sind unterschiedliche Konfigurationen für die Submodule 14 bekannt, die sich für unterschiedliche Anwendungen eignen. Bspw. werden vorwiegend sog. Halbbrücken verwendet, die im Wesentlichen eine Reihenschaltung zweier Leistungshalbleiterschalter mit jeweils antiparallel geschalteter Freilaufdiode darstellen, wobei zu der Reihenschaltung ein Kondensator als Energiespeicher parallelgeschaltet ist. Es sind auch Submodulkonfigurationen in Form von Voll- oder H-Brückenschaltungen, asymmetrischen H-Brückenschaltungen oder gemischte Konfigurationen bekannt. Eine erfindungsgemäße Konfiguration eines Submoduls 14 zur Verwendung in dem Stromrichter 8 ist nachstehend im Zusammenhang mit Figur 2 näher erläutert. In den Stromrichterzweigen 9a-9f können jeweils kreisstrombegrenzende Induktivitäten 16 vorgesehen sein, die eine Entkopplung der Stromrichterzweige voneinander unterstützen. An dem Verbindungspunkt zwischen den zugehörigen Stromrichterzweigen 9a, 9b bzw. 9c, 9d bzw. 9e, 9f sind die jeweiligen Wechselspannungsanschlüsse 17a, 17b, 17c des Stromrichters 8 herausgeführt, die mit der Wechselspannungsquelle 2 verbunden sind. Die gleichspannungsseitigen Anschlüsse der ersten obersten Submodule 14 des Stromrichters 8 sind miteinander und mit der positiven Stromschiene 12 verbunden. Ähnlich sind die gleichspannungsseitigen Anschlüsse der letzten, untersten Submodule 14 miteinander und mit dem negativen Gleichspannungsanschluss 13 verbunden. Zwischen den Stromschienen 12, 13 liegt die Gleichspannung Udc des Gleichspannungszwischenkreises an, die eine Hochspannung von bspw. über 100 kV sein kann. Fig. 2 zeigt in Form eines vereinfachten Schaltplans eine Topologie eines erfindungsgemäßen Doppel-Submoduls oder modularen Schalters 18, wie es bzw. er in dem modularen Mehrpunktstromrichter 8 nach Fig. 1 verwendet werden kann. Es sollte beachtet werden, dass das Doppel-Submodul 18 anstelle von zwei in Reihe geschalteten Halb-, Voll- oder H-Brücken oder sonstigen zwei Submodulen eingesetzt werden kann. Insofern kann gegebenenfalls für jeden Stromrichterzweig 9a-f nur die halbe Anzahl der Doppel-Submodule 18 gemäß der Erfindung im Vergleich zu der Anzahl herkömmlicher Submodule 14 erforderlich sein. Bezugnehmend auf Fig. 2 weist das Doppel-Submodul 18 im Wesentlichen eine Parallelschaltung aus zwei Submodulen 19, 21 auf. Insbesondere weist ein erstes, in Fig. 2 unteres Submodul 19 eine Brückenschaltung 22 und einen zu der Brückenschaltung 22 parallel geschalteten Kondensator C1, 23 auf. Die Brückenschaltung 22 ist hier als sog. asymmetrische H-Brücke mit zwei parallelen Brückenzweigen 24, 26 ausgebildet, die zwischen einem ersten und einem zweiten Gleichspannungsknoten bzw. Polanschluss 27, 28 parallel zueinander angeschlossen sind. Der erste Brücke
[EN US2021111629A1]: MODULAR MULTI-LEVEL DC/DC CONVERTER WITH CURRENT-SHAPING [FR WO2020000091A1]: CONVERTISSEUR C.C.-C.C. MULTINIVEAU MODULAIRE À MISE EN FORME DU COURANT | [EN US2021111629A1]: Embodiments are directed to a modular multi-level DC/DC power electronic converter for transferring power from or between a higher-voltage DC network and a lower-voltage DC network. The power electronic converter features a series connection of low-voltage voltage source modules (VSM) and a current source module (CSM). The series connection of the sub-module elements forms a string. The higher-voltage DC network is interfaced to the converter by connecting across the outer terminals of the string. The lower-voltage DC network is interfaced to the converter through the CSM. [FR WO2020000091A1]: Des modes de réalisation concernent un convertisseur électronique de puissance c.c.-c.c. multiniveau modulaire permettant de transférer de l'énergie à partir d'un réseau c.c. de tension supérieure vers un réseau c.c. de tension inférieure ou entre ceux-ci. Le convertisseur électronique de puissance comprend une connexion en série de modules de source de tension (VSM) basse tension et un module de source de courant (CSM). La connexion en série des éléments de sous-module forme une chaîne. Le réseau c.c. de tension supérieure est en interface avec le convertisseur par connexion par le biais des bornes externes de la chaîne. Le réseau c.c. de tension inférieure est en interface avec le convertisseur par l'intermédiaire du CSM. | WO2020000091A1 | 2020-01-02 | CA2019050880W | 2019-06-25 | US201862689614P, 2018-06-25 US201962824048P, 2019-03-26 | WO2020000091A1: 2020-01-02 US2021111629A1: 2021-04-15 | GOVERNING COUNCIL UNIV TORONTO GRAY PHILIPPE LEHN PETER WALDEMAR | GRAY PHILIPPE LEHN PETER WALDEMAR | H02M3/28: I H02M1/08: I H02M1/12: I H02M3/335: I H02M3/158: I H02M3/157: I | H02M1/15: I H02M3/158: I H02M3/33569: I H02M3/33584: I H02M3/33592: I H02M1/08: I H02M1/12: I H02M3/28: I H02M3/335: I H02M1/009: A H02M1/0095: A H02M7/4835: I Y02B70/10: A H02M3/157: I H02M3/1584: I H02M3/072: A H02M3/1586: A | US9318968B2 |  | [EN US2021111629A1]: 1. A converter circuit for transferring power between a higher-voltage DC network and a lower-voltage DC network; the converter circuit comprising: two or more voltage source modules (VSMs);a current source module (CSM) having one or more inductors, two or more switches, the two or more voltage source modules (VSMs), the CSM connected as a series connected string, wherein the series connected string is coupled to the higher-voltage DC network; wherein at least two AC side terminals of the CSM are connected in series with the two or more VSMs, and two or three DC side terminals of the CSM are coupled to a lower-voltage network; anda controller that is configured to control one or more states of operation of one or more switches within the CSM or the two or more VSMs of the series connected string to change a direction of a current in the two or more VSMs such that a direction of power flow to the two or more VSMs is reversed during a switching period. 2. The converter circuit of claim 1, wherein the controller controls one or more switches of the two or more switches of the CSM or one or more switches of a VSM of the two or more VSMs of the series connected string such that the current in the two or more VSMs is equal to a current in an inductor of the one or more inductors of the CSM for a first portion of the switching period and equal to a negative of the current in the inductor of the one or more inductors of the CSM for a second portion of the switching period. 3. The converter circuit of 1, wherein: power is delivered to the at least two AC-side terminals of the CSM for a first portion of the switching period when the direction of the series connected string current is positive and for a second portion of the switching period when the direction of a current of the series connected string is negative; orpower is delivered from the at least two AC-side terminals of the CSM for the first portion of the switching period when the direction of the string current is positive and for a second portion of the switching period when the direction of the current of the series connected string is negative. 4. The converter circuit of claim 1, wherein the one or more states of operation of the one or more states within the CSM can be changed between: a first CSM state, defined by a first CSM switch conducting current and a second CSM switch precluding current conduction; anda second CSM state, defined by the first CSM switch precluding current conduction and the second CSM switch is conducting current; andwherein when the direction of the current in a VSM of the two or more VSMs is positive in the first CSM state, the direction of the current is negative in the second CSM state; andwherein when the direction of the current in a VSM of the two or more VSMs is negative in the first CSM state, the direction of the current is positive in the second CSM state. 5. The converter circuit of claim 1, wherein the CSM is configured to shape a current into the series connected string through a control protocol provided by the controller to at least one of the one or more switches within the CSM or the two or more VSMs. 6. The converter circuit of claim 1, wherein in response to the controller controlling the one or more switches to change the direction of the current into the series connected string, a commutation or free-wheeling state first occurs where a loop is formed wherein the current in the series connected string is equal to a loop current such that the one or more inductors of the CSM do not limit changes in the current of the series connected string and an inductance in the loop includes a leakage inductance of the loop. 7. The converter circuit of claim 1, further comprising: a filtering circuit including at least one capacitor across the series connected string;wherein the filtering circuit is configured to divert a portion of the AC current component of the current in the two or more VSMs from entering the higher voltage DC network. 8. The converter circuit of claim 1, wherein the CSM is coupled to the lower-voltage DC network through an intermediary isolation stage, the intermediary isolation stage providing galvanic isolation between the lower-voltage DC network and the higher-voltage DC network. 9. The converter circuit of claim 1, wherein the two or more VSMs are paralleled such that a high-voltage (HV) loop current can be shared between multiple voltage source sub-module strings. 10. The converter circuit of claim 1, wherein the series connected string comprises four or more VSMs, and is configured with at least one VSM of the four or more VSMs connected to a first AC terminal of the CSM and at least one VSM of the four or more VSMs connected to a second AC terminal of the CSM. 11. The converter circuit of claim 1, wherein at least one of the two or more VSMs are configured to conduct bidirectional current and insert unipolar voltages. 12. The converter circuit of claim 1, wherein at least one of the two or more VSMs are configured to conduct bidirectional current and insert bipolar voltages. 13. The converter circuit of claim 1, wherein the CSM has two switches and two inductors and is configured such that both inductors can simultaneously either deliver current to or receive current from the lower-voltage DC network, yielding an amplified current to or from the lower-voltage DC network, respectively. 14. The converter circuit of claim 1, wherein the CSM has four switches and one inductor, wherein the CSM is configured such that the inductor either delivers current to or receives current from the lower-voltage DC network. 15. A method for transferring power between a higher-voltage DC network and a lower-voltage DC network; the method comprising: providing a converter circuit comprising: two or more voltage source modules (VSMs);a current source module (CSM) having one or more inductors, and having two or more switches, the two or more voltage source modules (VSMs) and the current source module (CSM) connected as a series connected string, the series connected string coupled to the higher-voltage DC network;two AC side terminals of the CSM connected in series with two or more VSMs;two or three DC side terminals of the CSM coupled to a lower-voltage network; andgenerating a control command to control one or more states of one or more switches within the CSM and the two or more VSMs such that a current into the series connected string is equal to a current in an inductor of the one or more inductors of the CSM for a first portion of each period and equal to a negative of the current in the inductor of the one or more inductors of the CSM for a second portion of each period. 17. The method of claim 15, wherein the CSM is configured to shape the current into the series connected string, through applying a control protocol provided by the controller to one or more switches of the one or more switches within the string modules. 18. The method of claim 15, wherein after a change of the direction of the current in the series connected string, a commutation or free-wheeling state occurs where a loop is formed; wherein the current in the series connected string is equal to a loop current and accordingly, there is no inductor of the CSM limiting a change in the current in the series connected string and an inductance in the loop is only a leakage inductance of the loop. 19. The method of claim 15, wherein a filtering circuit interfaces the higher-voltage DC network and the series connected string of sub-module elements, reducing harmonic currents of the higher-voltage DC network; wherein the filtering circuit is configured to divert a portion of the AC current component of the current in the two or more VSMs from entering the higher voltage DC network. 20. The method of claim 15, wherein the CSM is coupled to the lower-voltage DC network through an intermediary isolation stage, the isolation stage providing galvanic isolation between the lower-voltage DC network and the higher-voltage DC network. 21. The method of claim 15, wherein the two or more VSMs are paralleled in multiple voltage source sub-module strings such that by paralleling the voltage source sub-module elements, a high-voltage (HV) loop current can be shared between the multiple voltage source sub-module strings. 22. The method of claim 15, wherein the series connected string comprises four or more VSMs, and is configured with at least one VSM of the four or more VSMs connected to a first AC terminal of the CSM and at least one VSM of the four or more VSMs connected to a second AC terminal of the CSM. 23. The method of claim 15, wherein at least one of the two or more voltage source modules are configured to conduct bidirectional current and insert unipolar voltages. 24. The method of claim 15, wherein at least one of the two or more voltage source modules are configured to conduct bidirectional current and insert bipolar voltages. 25. The method of claim 15, wherein the CSM has two switches and two inductors and is configured such that both inductors can simultaneously either deliver current to or receive current from the lower-voltage DC network, yielding an amplified current to or from the lower-voltage DC network, respectively. 26. The method of claim 15, wherein the CSM has four switches and an inductor, wherein the CSM is configured such that the inductor either delivers current to or receives current from the lower-voltage DC network. 27. A non-transitory machine readable media, storing machine interpretable instructions, which when executed, cause a processor to perform a method comprising: generating a control command to control one or more states of one or more switches within: two or more voltage source modules (VSMs);a current source module (CSM) having one or more inductors, and having two or more switches, the two or more voltage source modules (VSMs) and the current source module (CSM) connected as a series connected string, the series connected string coupled to the higher-voltage DC network;wherein two AC side terminals of the CSM are connected in series with two or more VSMs; andtwo or three DC side terminals of the CSM are coupled to a lower-voltage network; andwherein a current into the series connected string is equal to a current in one of the one or more inductors of the CSM for a first portion of each period and equal to a negative of the current in an inductor of the one or more inductors of the CSM for a second portion of each period. 28. The converter circuit of claim 1, wherein the controller is configured to maintain a DC voltage across the two or more VSMs that is equal to the DC voltage of the higher voltage DC network. 29. The converter circuit of claim 1, wherein the controller is configured to change the switching state of at least two VSMs of the two or more VSMs each fundamental AC period, in accordance with a logic state machine that sequentially switches the VSMs such that after an integer number of fundamental AC periods, each VSM capacitor has been inserted for an equal amount of time. 30. The converter circuit of claim 1, wherein the controller is configured to switch only a subset of the two or more VSMs every fundamental AC period. 31. The converter circuit of claim 1, further comprising: a transformer within the CSM, the transformer having at least one primary winding and at least one secondary winding, the at least one primary winding electrically in series with the two or more VSMs, the at least one secondary winding coupled to the lower voltage dc network through a network of switches and inductive elements, and wherein the at least one primary and at least one secondary windings are isolated from each other. 32. The converter circuit of claim 31, wherein: the transformer within the CSM has at least two primary windings, each primary winding connected as a series string with at least two or more VSMs; andwherein the controller is configured to cause a DC component of a current through the two or more primary windings to sum to zero. 33. The converter circuit of claim 31, wherein the transformer has at least two primary windings, the converter circuit further comprising: an input filter with at least two capacitors connected in series;a mid-point of the at least two capacitors electrically bonded to the at least two primary windings of the CSM transformer;wherein, the at least two primary windings have an equal number of turns and are wound in opposing directions around the transformer core. | [EN US2021111629A1]: CROSS REFERENCE This application is a continuation in part of, and claims all benefit to, including priority to, PCT Application No. PCT/CA2019/050880, filed on 25 Jun. 2019, entitled “MODULAR MULTI-LEVEL DC/DC CONVERTER WITH CURRENT-SHAPING”. PCT/CA2019/050880 is a non-provisional of, U.S. Provisional Application No. 62/689,614 dated 25 Jun. 2018 and entitled “HYBRID MULTI-MODULAR DC/DC POWER CONVERSION MECHANISM”, and U.S. Provisional Application No. 62/824,048 dated 26 Mar. 2019 and entitled “MODULAR MULTI-LEVEL DC/DC CONVERTER WITH CURRENT-SHAPING”. All of these applications are incorporated herein by reference in their entirety. FIELD The disclosure generally relates to power electronics for grid applications. More specifically, the disclosure relates to converters for the interconnection of DC networks at differing voltage levels. INTRODUCTION Advantages of DC over AC include lower line losses, reduced conductor requirements as well as enhanced controllability, for instance. In addition, DC power transmission offers the possibility for lower number of power conversion stages from generation to load enabling improved overall system efficiencies, reliability and costs. DC power transmission is competitive with respect to AC power transmission currently for transferring bulk power from remote locations and/or offshore wind farms, for instance. It is also a competitive solution in specific distribution applications such as DC powered data centres, for instance. A commonly proposed approach to interface a LVDC and a HVDC or MVDC network involves use of a dual-active bridge with a multi-modular converter (MMC) front-end at the high-voltage side and a two-level voltage source converter at the low-voltage side. The MMC for this application typically consists of 4 or 6 strings of voltage sub-modules (VSMs), a transformer and an arm inductor for each string of VSMs. Each VSM string is typically rated for the full high-side voltage. In addition, the transformer and arm inductors are typically rated for the full high-side voltage. While this approach may be effective in higher power application, the cost and complexity limit its potential for use in lower power applications such as for HVDC to LVDC or MVDC to LVDC tap applications, for instance. SUMMARY A converter topology which enables high step-down ratio power exchange between DC networks at differing voltage levels in a more cost-efficient manner is desirable. A number of variant and additional alternate embodiments are described, along with a number of simulation results established for a number of different operating cases and modes. Embodiments described herein are directed to a new power-electronic converter for exchanging power between a higher-voltage DC network and a lower-voltage DC network. An improved circuit architecture is described that, in accordance with some embodiments, allows for improved DC/DC step down and/or step up power conversion. Accordingly, DC power distribution is more practically feasible if DC power can both be distributed at a higher voltage levels and either consumed and/or generated at lower voltage levels. There are two main variations described in this application. In a first main variation, the power electronic converter is able to transfer power from a higher voltage dc network to a lower voltage dc network all while maintaining capacitor charge balance of the VSM cell capacitors. If charge balance of the VSM cell capacitors were not maintained, the cell capacitor voltages would either continually rise and therefore overcharge or otherwise the cell capacitor voltages would collapse. The power electronic converter is able to maintain charge balance of the VSM cell capacitors through its use of a current source module (CSM). Through the use of a CSM, the converter is able to change the direction of the current into the VSM cell capacitors through changing the state of the CSM. The CSM is able to essentially force a current to flow down or up the VSMs, which is described in further detail in various embodiments. It is through a controlled switching action that the converter is able to force current from inductive elements upwards or downwards through the VSM strings. This ability to change the direction of the current through switch action enables the current to be flipped rapidly and in some cases nearly instantly. Accordingly, this allows the system to change the power flow into each individual VSM rapidly and balance the power so that the cell capacitors do not charge or discharge over a longer period interval of time so that it maintains charge balance over time. This ability to change the direction of the string current nearly instantly enables the cell capacitor voltages to achieve charge balance over a short time in some embodiments. Therefore, this allows the cell capacitors to be realized with very low cell capacitances. This cell capacitance can be potentially reduced, for example, by up to a 100× factor if this power electronic is run at high frequencies compared to other approaches. As the cell capacitance is proportional to the energy in a cell capacitor, the cell capacitors can be made physically small and thus the volume of the converter can be reduced significantly and therefore this power electronic circuit has the ability to achieve much greater power densities. The VSMs in the power electronic circuit set the voltage appearing across the input terminals of the CSM. The VSMs, in effect, step-down the higher voltage dc network voltage and in this way, a much lower voltage is appearing across the CSM input terminals. When transitioning between different CSM states, only a fraction of the total number of VSM switches are switched. This is advantageous as it results in reduced switching losses in the VSMs compared to if all VSM switches were to be switched. In the second main variation, in selected CSM configurations, the topology is configured such that zero DC (or substantially near zero) voltage appears across this input to the CSM module, yielding a special configuration that makes integration of transformer isolation within the CSM itself possible. This allows galvanic transformer isolation to be introduced using fewer switching devices, reducing complexity, part count and cost. Typically, DC current within a transformer leads to a DC magnetic flux superimposed on the AC flux needed for power transfer. This leads to the need for a larger transformer core. Transformer size reduction is achieved through a process of DC flux cancellation in variant embodiments, which ensures zero net DC flux within the magnetic core of the transformer. Through elimination of DC flux in the transformer, a lower peak flux level is achieved requiring less ferromagnetic material for the transformer core. Additionally, through controller control action, in variant embodiments of the second main variation, the converter does not need to measure the cell capacitor voltages. In this way, the converter is able to achieve self-balancing and therefore is much simpler than approaches that require the cell capacitor voltages to be measured. The circuit architectures for implementing the above variations can be described as a circuit topology, and can includes a system established using electronic circuitry and devices which interoperate with one another to, in concert, provide the improved step down or step up power conversion. The circuitry can include energy storage elements, power electronics components (e.g., capacitors, inductors), and switches (e.g., transistors). The switches are controlled through the operation of a switch controller circuit, which may control the operation of the switches based on a switching pattern provided through, for example, machine interpretable instruction sets stored on non-transitory machine readable media for execution by a processor of the switch controller circuit. The switching pattern, for example, can be generated using pulse-width modulation and function generators. Embodiments are directed to several different variant topologies which interconnect VSM(s) and CSM(s), and control approaches in respect of controlling the circuit topologies. In some embodiments, devices, control methods, non-transitory computer readable media are described for DC conversion. As described herein, the circuit topologies may be utilized to reduce a need for AC transformers or AC transformation networks for household power distribution (or power delivery back to the grid), potentially reducing unnecessary conversion losses, and allowing for physically smaller and/or lighter power conversion components to be utilized. For example, where power generation provides a DC source, rather than changing the power to AC for transmission and then back to DC at the DC consuming device (DC consuming device being at a household, for instance), DC power may be directly stepped up to a higher-voltage DC for transmission and then stepped down to a lower-voltage DC at the DC consuming device. Regarding unnecessary conversion losses, when loads and generators are DC-based, an AC/DC converter is required both at the load and at the generator so that both can be interfaced with the grid. Therefore, there are two AC/DC stages between the actual generation and load with both stages having to process the full load power. Examples of DC based loads are cell phones or computers. Examples of DC based generators include solar PV. By replacing this AC grid with a DC grid, an AC/DC converter is not required at the load and generator. Instead, the load and generator could be connected with a single DC/DC conversion stage, in some cases. By removing one of the conversion stages it is possible to realize higher overall efficiencies as the power is only processed by one conversion stage. Also, unlike in the traditional AC grid approach, a transformer is not functionally necessary for voltage conversion. A 50/60 Hz transformer is a source of significant volume and weight which is avoided by the circuit topologies described in some of the embodiments herein. As illustrated in some embodiments, a transformer can also be integrated into some embodiments converter circuit of the circuit architecture but this transformer is not tied to a specific grid frequency (i.e. 50/60 Hz) and therefore can be designed for much higher AC frequencies (for example, 10 kHz). The transformer volume and weight can be constrained by the AC frequency and therefore for some embodiments a transformer can be integrated but at significantly reduced transformer size, volume and magnetic material compared to that of a traditional 50/60 Hz transformer. This capability is realized through a string of power electronic sub-modules that comprise of a mixture of voltage source sub-module elements and a current source sub-module element. In some embodiments, an optional galvanic isolation stage can be added between the lower-voltage DC network and the current source sub-module element. Additionally, in some embodiments an optional grounding circuit can be added to the mid-point of the current source sub-module element. Galvanic isolation is primarily important for safety reasons. With galvanic isolation, one can have a separate ground on secondary side of the transformer. This limits the voltage seen on the secondary side of the transformer to safe levels. Many grid codes would require galvanic isolation. It also provides other benefits. The transformer also gives another degree of design freedom which could be very important. By changing the relative ratio of the number of turns on the primary winding of the transformer with respect to the turns on the secondary winding of the transformer one can reduce the current that has to be conducted by our VSMs even though the system is delivering the same output power to the same output voltage. This flexibility enables one to employ this converter for a much wider range of conversion ratios. Without the transformer the approach may be limited to 10:1 conversion ratio but with the transformer, one does not have this limitation. For example, a ratio could be 40:1, etc. In a non-limiting example, a module represents a physical device or unit. A power electronic sub-module or module represents a physical device or unit that contains one or multiple power semiconductor switches. A voltage source sub-module represents a physical device or unit that has at least two external electrical terminals, contains one or multiple power semiconductor switches and an energy storage device that holds a relatively constant voltage. Examples of energy storage devices with this feature include a capacitor or battery. A current source sub-module represents a physical device or unit, containing one or multiple power semiconductor switches, has at least two external electrical terminals and contains an energy storage device that holds a relatively constant current. An example of an energy storage device with this feature includes an inductor. The voltage source sub-modules (VSMs) are controlled to act as a variable voltage source with steps defined by the state of charge of the individual VSM cell capacitors. In this mechanism, power inductors are separated from the string by CSM switching elements. Switching of the CSM switching elements can therefore direct the power inductor current either to the positive or negative terminal of the high voltage DC network. This is referred to as “current shaping”. Through this separation of the power inductors, the string inductance is minimized, enabling a nearly square-wave current at a high-frequency to propagate down the series string of voltage source sub-module elements enabling the energy transfer mechanism. The CSM shapes this current propagating down the series string of VSM elements. The separation of the inductor, in accordance with an example embodiment, is the following, if the inductor is not separated from the string of power electronic sub-modules then the inductor is in series with the string of power electronic sub-modules. Therefore, regardless of the string switch states, the current through the string is equal to the inductor current. Instead, in the mechanism of example embodiments described herein, the power inductor or power inductors are separated from the string and therefore for certain string switch states the current through the string is not equal to the inductor current. This enables advantages such as a string current that can be quickly changed during parts of a switching period and for other parts of the switching period equal to a relatively constant inductor current, in some embodiments. As described further, switching protocols and control mechanisms are also disclosed that aid in achieving the advantages described herein. The CSM can feature two power inductors in an example embodiment (although not all embodiments are thus limited to having two power inductors). The lower-voltage DC network current is shared between these two power inductors. This sharing of the current is advantageous as only a fraction of the lower-voltage DC network current is conducted by the series string of VSMs enabling improved efficiencies and reduced rating requirements of the VSM cells, for instance. In this converter, near continuous power can be exchanged between the DC networks irrespective of the direction of the current propagating down the series string of sub-modules. Examples of the higher-voltage DC side networks include a medium-voltage (MVDC) or high-voltage DC grid (HVDC). Examples of lower-voltage DC side networks include a residential home, an industrial plant, a microgrid or an energy storage system. A summary of some of the key features of the power-electronic converter include high-step down ratio power exchange, delivery of near constant power, optional grounding circuit, optional galvanic isolation, bidirectional power transfer capability and near square-wave string currents at a high-frequency made possible by separating the power inductors with the CSM. In a first aspect, a converter circuit for transferring power between a higher-voltage DC network and a lower-voltage DC network is provided; the converter circuit comprising: one or more voltage source modules (VSMs); a current source module (CSM), the one or more voltage source modules (VSMs) and the current source module (CSM) connected as a series connected string, the series connected string coupled to the higher-voltage DC network; two AC side terminals of the CSM connected in series with the one or more VSMS; two or three DC side terminals of the CSM coupled to a lower-voltage network; a CSM consisting of one or more inductors; and a controller configured to control one or more states of one or more switches within the string modules such that a current into the series connected string is equal to a current in one of the inductors of the CSM for a fraction of each period and equal to a negative of the current in one of the inductors of the CSM for a fraction of each period. The positive and negative intervals can be changed, and accordingly, in this variation, the negative interval comes before the positive interval. Fractions of a period can include, for example, a proportion of a switching period selected from approximately 1%, 5%, 10%, 25%, 50%, 75%, or 100%. The fractions of each period do not necessarily have to be the same (e.g., different fractions allow for different control methods), and the fractions of the period allow a current to reverse in a switching period. In another aspect, neither of the two AC terminals of the CSM are electrically bonded to either of the DC terminals of the CSM. In another aspect, the string comprises two or more VSMs, and is configured with at least one VSM of the two or more VSMs connected to each of the two AC terminals of the CSM. In another aspect, the CSM comprises two switches and two inductors, wherein the CSM is configured such that both inductors can simultaneously either deliver current to or receive current from the lower-voltage DC network, yielding an amplified current to or from the lower-voltage DC network, respectively; wherein for a set of CSM switch states, the current into the series connected string is equal to the current in a first CSM inductor; and wherein for an alternate set of CSM switch states, the current into the series connected string is equal to the negative of a current of a second CSM inductor. During the positive current interval, the string current magnitude is equal to the first inductor. During the negative current interval, the string current magnitude is equal to the second inductor. In another aspect, the CSM comprises four switches and one inductor, wherein the CSM is configured such that the inductor either delivers current to or receives current from the lower-voltage DC network; wherein for a set of CSM switch states, the current into the series connected string is equal to the current in the CSM inductor; and for an alternate set of CSM switch states, the current into the series connected string is equal to the negative of the current in the CSM inductor. In another aspect, the two or more VSMs are of half-bridge type each containing a positive and negative external terminal; wherein, either the positive and negative external terminals of the VSM are electrically bonded to the midpoint and the negative terminal of the VSM cell capacitor, respectively; or the positive and negative external terminals are electrically bonded to the positive terminal of the VSM cell capacitor and the midpoint of the VSM, respectively. This feature can be specific to the half-bridge submodule of some embodiments, and there are other ways to connect this half-bridge submodule. The VSM module can be the upper most module in the substring. In another aspect, the positive external terminal of the first VSM of the first VSM stack is electrically bonded to a positive terminal of the higher-voltage DC network; and the negative external terminal of the last VSM of the second VSM stack is electrically bonded to a negative terminal of the higher-voltage DC network. In another aspect, the negative external terminal of the last VSM of the first VSM stack is electrically bonded to a first AC terminal of the CSM; and the positive external terminal of the first VSM of the second VSM stack is electrically bonded to a second AC terminal of the CSM. In another aspect, when there is only one VSM in the first VSM stack the first and last VSM are the same VSM in that stack. In another aspect, when there is only one VSM in the second VSM stack the first and last VSM are the same VSM in that stack. In another aspect, there are two or more VSMs in the first VSM stack and/or the second VSM stack, the negative external terminal of all the VSMs excluding the last VSM of the stack are electrically bonded to the positive terminal of the adjacent VSM in the sequence (i.e. the negative external terminal of the first VSM is electrically bonded to the positive external terminal of the second VSM in the stack). In another aspect, wherein the CSM is configured to shape the current into the series connected string, through a control protocol provided by the controller to one or more switches of the one or more switches that reside within the string modules. In particular, the control protocol can control any of the VSM switches. It may switch multiple VSM switches at the same instant. In an alternate variation, the CSM switches are indirectly controlled by control of the VSM string switches. For instance, when the CSM switches are diodes. In another aspect, after the controller acts to change the direction of the current into the series string a commutation or free-wheeling state first occurs where a loop is formed wherein the current in the series connected string is equal to a loop current and accordingly, there is no inductor of the CSM limiting a change in the current into the series connected string and an inductance in the loop is only a leakage inductance of the loop. In a variation, it is also possible to add an external leakage inductance and actually this may be preferable in some embodiments. In another aspect, the voltage source modules (VSM) are configured to operate in concert as a variable voltage source with steps defined by the state of charge of individual VSM cell capacitors. In another aspect, the voltage source modules are configured to conduct bi-directional current and insert unipolar voltages. An example implementation is a VSM of half-bridge type. It can only insert a positive voltage or a zero voltage. In another aspect, the voltage source modules are of half-bridge type. In another aspect, the voltage source modules are configured to conduct bi-directional current and insert bipolar voltages. In another aspect, the voltage source modules are of full-bridge type. In another aspect, the voltage source modules are of different type. In another aspect, the voltage source modules are of the same type. In another aspect, the switches of the VSMs consist of one or more switches in series and/or parallel to increase the voltage blocking and/or current conduction capabilities of the voltage sub-module, respectively. In another aspect, the converter circuit is configured for uni-directional power transfer. In another aspect, the converter circuit is configured for bi-directional power transfer. In another aspect, the switches of the current source sub-module consist of one or more switches in series and/or parallel to increase the voltage blocking and/or current conduction capabilities of the current source module, respectively. In another aspect, the CSM switches feature positive current conduction and reverse voltage blocking capabilities such as diodes. In another aspect, the CSM switches feature positive current conduction and bipolar voltage blocking capabilities such as MOSFETs with series diodes or GTOs. In another aspect, the power inductor or power inductors of the converter circuit are separated from the series string of sub-module elements by the current source module. In another aspect, current into the series connection of one or multiple voltage source modules can be quickly changed due to the low commutation loop inductance enabling higher switching frequencies. In another aspect, the switching frequency can be adapted to reduce capacitive and inductive energy storage requirements of the VSMs and the CSM, respectively. In another aspect, an isolation stage interfaces the CSM to the lower-voltage DC network. The isolation stage consisting of (i) one or more transformers; (ii) a secondary-side AC/DC power conversion stage between the one or more transformers and the lower-voltage DC network; and (iii) a primary-side DC/AC power conversion stage between the CSM and the one or more transformers. In another aspect, the primary-side DC/AC power conversion stage consists of two switches. In another aspect, the secondary-side AC/DC power conversion stage is of single-phase converter type. In another aspect, the switches of the secondary-side AC/DC power conversion stage feature positive current conduction and reverse-voltage blocking capability such as diodes. In another aspect, the switches of the secondary-side AC/DC power conversion stage feature bidirectional current conduction and positive voltage blocking capability such as MOSETs or IGBTs with anti-parallel diodes. In another aspect, the primary-side DC/AC power conversion stage switches are controllable and feature positive current conduction and positive voltage blocking capability such as MOSFETs or IGBTs. In another aspect, the primary-side DC/AC power conversion stage switches are controllable and feature positive current conduction and bipolar voltage blocking capability such as MOSFETs with series diodes or IGBTs with series diodes. In another aspect, the isolation stage features a two-winding transformer. In another aspect, the isolation stage features a center-tapped winding transformer. In another aspect, the isolation stage switches are made up of 1 or more switches in parallel and/or series to increase the current conduction and/or voltage blocking capability, respectively. In another aspect, a grounding circuit is electrically connected between the two switches of the CSM. In another aspect, a series choke is added in series with the series string of sub-module elements reducing the di/dt in the high-voltage (HV) loop. In another aspect, a filtering circuit interfaces the higher-voltage DC network and the series string of sub-module elements reducing the harmonic currents into the higher-voltage DC network. In another aspect, the converter circuit is incorporated into electronic components coupled to a residential home. In another aspect, the converter circuit is incorporated into electronic components coupled to an industrial plant. In another aspect, the converter circuit is incorporated into electronic components coupled to a microgrid. In another aspect, the converter circuit is incorporated into electronic components coupled to an energy storage system. In another aspect, the converter circuit is incorporated into electronic components coupled to a DC network which may be a grid, a load or generator or a combination of component/s of these types. In another aspect, a switching controller for operating the circuit of is provided, for transferring power between a higher-voltage DC network and a lower-voltage DC network; the converter circuit comprising a series connection of voltage source modules (VSM) and a current source module, across the terminals of the higher-voltage DC network; wherein the lower voltage network is interfaced to the converter circuit through the CSM; the method comprising: In another aspect, the switching controller controls the direction of the main loop current by applying bipolar voltages to the input terminals of the CSM. In another aspect, the switching controller controls the direction of the main loop current by sending gating signals to the CSM switches. In another aspect, the switching controller regulates the lower voltage DC network voltage. In another aspect, the switching controller maintains energy balance of the string of voltage source submodules by controlling the total sum of VSM cell capacitor voltages. In another aspect, the switching controller maintains energy balance between the individual voltage source submodules by distributing the gating signals to the VSM cells based on their relative states of charge. In another aspect, the switching controller regulates the difference of the two CSM inductor currents. In another aspect, the switching controller acts to minimize the difference between the two CSM inductor currents reducing the rms current conducted by the string of VSMs. In another aspect, the switching controller acts to minimize the difference between the two CSM inductor currents, reducing (i) the rms current conducted by the string of VSMs and (ii) the DC current flowing through the primary-side transformer windings. In another aspect, the switching controller sends gating signals to the CSM switches to control the direction of power being exchanged between the CSM and the higher-voltage DC network. In another aspect, the upper and lower voltage source modules (VSM) strings are configured to operate in concert to minimize the DC voltage component at the mid-point of the two switches of the CSM. In another aspect, the upper and lower voltage source modules (VSM) strings are configured to operate in concert to minimize the DC voltage component at the input terminals of the CSM. In another aspect, the primary-side DC/AC isolation stage switches are controlled such that power is transferred between the CSM and the lower voltage DC network without saturating the transformer. In another aspect, the secondary-side AC/DC isolation stage switches are controlled in concert with the primary-side DC/AC isolation stage switches to control the power being exchanged between the CSM and the lower-voltage DC network. In another aspect, a method for operating a circuit described in various embodiments herein, including control of a switching controller is provided. A non-transitory machine readable media, storing machine interpretable instructions, which when executed, cause a controller processor to perform steps of a method for modular multi-level DC/DC conversion with current-shaping, according to various embodiments herein. In another aspect, the disclosure relates to a power electronic circuit consisting of a cascaded string of voltage source submodules and a current source submodule (CSM), electrically in series, for interconnecting a higher and a lower DC voltage network. The current source submodules consist of one or more inductors, and two or more switches in some embodiments of the converter circuit. The current source submodules have one or more inductors, two or more switches and one or more transformers in some embodiments of the converter circuit. The voltage source submodules each consist of two or more switches and a DC voltage source in some embodiments of the converter circuit. In a non-limiting example, the DC voltage source may include a capacitor, a battery, a super capacitor or a PV array. One or more controllers are configured to control one or more states of the one or more switches within the submodules such that a linear combination of the CSM inductor currents are injected into the one or more VSM strings during a first portion of a fundamental AC period and the string current is positive and in a second portion of a fundamental AC period a different linear combination of the CSM inductor currents are injected into the one or more VSM strings. Some embodiments of the converter circuit include one or more controllers that are configured to control one or more states of the one or more switches within the submodules such the string current and is equal to a linear combination of the CSM inductor currents and the CSM transformer currents during a first portion of a fundamental AC period and in a second portion of a fundamental AC period the VSM string currents are equal to different linear combination of the CSM inductor currents and
[ZH CN110868093B]: 一种高压输出的多电平逆变电路 [EN CN110868093B]: A high-voltage output multi-level inverter circuit | [ZH CN110868093B]: 本发明实施例涉及一种高压输出的多电平逆变电路，包括低压直流电源、至少五个半桥单元、至少四个电容单元和输出端，半桥单元包括两个串联连接的开关元件；五个半桥单元分别为第一半桥单元、第二半桥单元、第三半桥单元、第四半桥单元和第五半桥单元；四个电容单元分别为第一电容单元、第二电容单元、第三电容单元和第四电容单元。该高压输出的多电平逆变电路将一个低压直流电源输出的电压通过五个半桥单元上开关元件的导通或截止转换成多电平交流电的电压的高压交流电从输出端输出，使得采用一个电源输入实现了多电平交流电的输出，并且该高压输出的多电平逆变电路的电路结构简单。 [EN CN110868093B]: The embodiment of the invention relates to a high-voltage output multi-level inverter circuit which comprises a low-voltage direct-current power supply, at least five half-bridge units, at least fourcapacitor units and an output end. Each half-bridge unit comprises two switching elements which are connected in series; the five half-bridge units are respectively a first half-bridge unit, a secondhalf-bridge unit, a third half-bridge unit, a fourth half-bridge unit and a fifth half-bridge unit; the four capacitor units are respectively a first capacitor unit, a second capacitor unit, a third capacitor unit and a fourth capacitor unit. According to the high-voltage output multi-level inverter circuit, voltage outputted by a low-voltage direct-current power supply is converted into high-voltage alternating current of voltage of multi-level alternating current through connection or disconnection of the switching elements on the five half-bridge units, and the high-voltage alternating current is outputted from the output end so that the output of the multi-level alternating current is realized by adopting one power supply input, and the circuit structure of the high-voltage output multi-level inverter circuit is simple. | CN110868093B | 2020-03-06 2021-08-27 | CN201911193235A | 2019-11-28 2019-11-28 | CN201911193235A, 2019-11-28 CN201911193235A, 2019-11-28 | CN110868093B: 2021-08-27 | UNIV GUANGDONG TECHNOLOGY 广东工业大学 | YE YUANMAO YI YONG WANG XIAOLIN | H02M7/483: I H02M7/5387: I | H02M7/483: I H02M7/53871: I H02M7/4835: I | CN2130007Y JP2009017622A CN104362877A CN105071679A JP2016093073A CN106972748A CN108566108A CN109842312A CN110138250A |  | [ZH CN110868093B]: 1 .一种高压输出的多电平逆变电路，其特征在于，包括低压直流电源、至少五个半桥单 元、至少四个电容单元和输出端； 所述半桥单元包括两个串联连接的开关元件，且两个所述开关元件连接的节点为第一 串联节点； 每个所述电容单元包括电容器和与所述电容器串联连接的二极管，且所述电容器与所 述二极管连接的节点为第二串联节点； 其中，五个所述半桥单元分别为第一半桥单元、第二半桥单元、第三半桥单元、第四半 桥单元和第五半桥单元；四个所述电容单元分别为第一电容单元、第二电容单元、第三电容 单元和第四电容单元； 所述第一半桥单元的第一串联节点与所述第一电容单元连接，所述第一电容单元还与 所述低压直流电源的负极连接； 所述第二半桥单元的第一串联节点与所述第二电容单元连接，所述第二电容单元还与 所述低压直流电源的正极连接； 所述第三半桥单元的第一串联节点分别与所述第三电容单元和所述第四电容单元连 接，所述第三电容单元还与所述第一电容单元连接，所述第四电容单元还与所述第二电容 单元连接； 所述输出端的第一端与所述第四半桥单元的第一串联节点连接，所述输出端的第二端 与所述第五半桥单元的第一串联节点连接； 所述第四半桥单元的第一端与所述第四电容单元的第二串联节点连接，所述第四半桥 单元的第二端与所述第三电容单元的第二串联节点连接； 所述第一半桥单元包括第一开关元件和第二开关元件；所述第二半桥单元包括第三开 关元件和第四开关元件；所述第三半桥单元包括第五开关元件和第六开关元件；所述第四 半桥单元包括第七开关元件和第八开关元件；所述第五半桥单元包括第九开关元件和第十 开关元件； 所述第一电容单元包括第一电容器和第一二极管;所述第二电容单元包括第二电容器 和第二二极管；所述第三电容单元包括第三电容器和第三二极管；所述第四电容单元包括 第四电容器和第四二极管;其中， 所述第一开关元件的第一端、所述第三开关元件的第一端和所述第一二极管的阴极分 别与所述低压直流电源的负极连接； 所述第二开关元件的第二端、所述第四开关元件的第二端和所述第二二极管的阳极分 别与所述低压直流电源的正极连接； 所述第一开关元件的第二端和所述第二开关元件的第一端分别与所述第一电容器的 第二端连接； 所述第三开关元件的第二端和所述第四开关元件的第一端分别与所述第二电容器的 第一端连接； 所述第一电容器的第一端、所述第一二极管的阳极、所述第五开关元件的第一端和所 述第三二极管的阴极分别与所述第九开关元件的第一端连接； 所述第二电容器的第二端、所述第二二极管的阴极、所述第六开关元件的第二端和所 述第四二极管的阳极分别与所述第十开关元件的第二端连接； 所述第五开关元件的第二端和所述第六开关元件的第一端分别与所述第三电容器的 第二端和所述第四电容器的第一端连接； 所述第三电容器的第二端和所述第三二极管的阳极分别与所述第七开关元件的第一 端连接； 所述第四电容器的第二端和所述第四二极管的阴极分别与所述第八开关元件的第二 端连接； 所述第七开关元件的第二端与所述第八开关元件的第一端分别与所述输出端的第一 端连接，所述第九开关元件的第二端与所述第十开关元件的第一端分别与所述输出端的第 二端连接 若开通所述第一开关元件、所述第四开关元件、所述第五开关元件、所述第八开关元件 和所述第十开关元件，其他的所述开关元件全部关断，所述第一电容器和所述第二电容器 分别与所述低压直流电源串联，所述低压直流电源通过所述第四二极管给所述第四电容器 充电，所述输出端输出的电压为0； 若开通所述第一开关元件、所述第四开关元件、所述第六开关元件、所述第七开关元件 和所述第九开关元件，其他的所述开关元件全部关断，所述第一电容器和所述第二电容器 分别与所述低压直流电源串联，所述低压直流电源通过所述第三二极管给所述第三电容器 充电，所述输出端输出的电压为0。 2 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，所述低压直流电源 输出的电压为Vdc，若开通所述第一开关元件和所述第三开关元件，并且开通所述第五开关 元件、所述第八开关元件和所述第十开关元件;或者并且开通所述第六开关元件、所述第七 开关元件和所述第九开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为 Vdc或Xc； 若开通所述第二开关元件和所述第四开关元件，并且开通所述第五开关元件、所述第 八开关元件和所述第十开关元件;或者并且开通所述第六开关元件、所述第七开关元件和 所述第九开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为Vdc或-Vdc。 3 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，所述低压直流电源 输出的电压为Vdc，若开通所述第二开关元件和所述第三开关元件，并且开通所述第五开关 元件、所述第八开关元件和所述第十开关元件;或者并且开通所述第六开关元件、所述第七 开关元件和所述第九开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为 2Vde或「2Vdc； 若开通所述第一开关元件和所述第四开关元件，并且开通所述第五开关元件、所述第 八开关元件和所述第九开关元件;或者并且开通所述第六开关元件、所述第七开关元件和 所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为3Vde或-3Vdc； 若开通所述第二开关元件和所述第三开关元件，并且开通所述第六开关元件、所述第 八开关元件和所述第九开关元件;或者并且开通所述第五开关元件、所述第七开关元件和 所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为4Vde或-4Vdc。 4 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，所述低压直流电源 输出的电压为Vdc，若开通所述第一开关元件和所述第三开关元件，并且开通所述第六开关 元件、所述第八开关元件和所述第九开关元件;或者并且开通所述第五开关元件、所述第七 开关元件和所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为 5Vdc或-5V dc 若开通所述第二开关元件和所述第四开关元件，并且开通所述第六开关元件、所述第 八开关元件和所述第九开关元件;或者并且开通所述第五开关元件、所述第七开关元件和 所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为5Vde或-5Vdc。 5 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，所述低压直流电源 输出的电压为Vdc，若开通所述第一开关元件和所述第四开关元件，并且开通所述第六开关 元件、所述第八开关元件和所述第九开关元件;或者并且开通所述第五开关元件、所述第七 开关元件和所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为 6Vde或一 6V dc 6 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，两个所述开关元件 形成一对互补导通的所述半桥单元。 7 .根据权利要求1所述的高压输出的多电平逆变电路，其特征在于，五个所述半桥单元 中的开关元件均选用N沟道MOSFET或P沟道MOSFET或IGBT器件，其中： 当所述开关元件均选用N沟道MOSFET时，所述N沟道MOSFET的源极作为所述开关元件的 第一端，所述N沟道MOSFET的漏极作为所述开关元件的第二端，所述N沟道MOSFET的栅极作 为所述开关元件的控制端； 当所述开关元件均选用P沟道MOSFET时，所述P沟道MOSFET的漏极作为所述开关元件的 第一端，所述P沟道MOSFET的源极为所述开关元件的第二端，所述P沟道MOSFET的栅极作为 所述开关元件的控制端； 当所述开关元件均选用IGBT器件时，所述IGBT器件的发射极作为所述开关元件的第一 端，所述IGBT器件的集电极作为所述开关元件的第二端，所述IGBT器件的基极作为所述开 关元件的控制端。 8 .根据权利要求7所述的高压输出的多电平逆变电路，其特征在于，各所述开关元件的 控制端均与控制器连接，所述控制器用于控制各所述开关元件的导通或关断，以实现多电 平交流电的输出。 [EN CN110868093B]: 1 A high-voltage output multi-level inverter circuit, characterized by comprising a low-voltage DC power supply, at least five half-bridge units, at least four capacitor units and an output terminal; the half-bridge unit includes two switches connected in series The node connecting the two switching elements is a first series node; each of the capacitance units includes a capacitor and a diode connected in series with the capacitor, and the node connecting the capacitor and the diode is a second A series connection node; wherein the five half-bridge units are respectively a first half-bridge unit, a second half-bridge unit, a third half-bridge unit, a fourth half-bridge unit, and a fifth half-bridge unit; four of the capacitor units Are a first capacitor unit, a second capacitor unit, a third capacitor unit, and a fourth capacitor unit; the first series node of the first half-bridge unit is connected to the first capacitor unit, and the first capacitor unit is also Connected to the negative electrode of the low-voltage DC power supply; the first series node of the second half-bridge unit is connected to the second capacitor unit, and the second capacitor unit is also connected to the positive electrode of the low-voltage DC power supply; The first series node of the third half-bridge unit is respectively connected to the third capacitor unit and the fourth capacitor unit, the third capacitor unit is also connected to the first capacitor unit, and the fourth capacitor unit is further Connected to the second capacitor unit; the first end of the output end is connected to the first series node of the fourth half-bridge unit, and the second end of the output end is connected to the first series connection of the fifth half-bridge unit Node connection The first end of the fourth half-bridge unit is connected to the second series node of the fourth capacitor unit, and the second end of the fourth half-bridge unit is connected to the second series node of the third capacitor unit; The first half-bridge unit includes a first switching element and a second switching element; the second half-bridge unit includes a third switching element and a fourth switching element; the third half-bridge unit includes a fifth switching element and a second switching element. Six switching elements; the fourth half-bridge unit includes a seventh switching element and an eighth switching element; the fifth half-bridge unit includes a ninth switching element and a tenth switching element; the first capacitor unit includes a first capacitor And the first diode; the second capacitor unit includes a second capacitor and a second diode; the third capacitor unit includes a third capacitor and a third diode; the fourth capacitor unit includes a fourth A capacitor and a fourth diode; wherein the first end of the first switching element, the first end of the third switching element, and the cathode of the first diode are respectively connected to the cathode of the low-voltage DC power supply Connected; the second end of the second switching element, the second end of the fourth switching element, and the anode of the second diode are respectively connected to the anode of the low-voltage DC power supply; the first switching element The second end of the second switching element and the first end of the second switching element are respectively connected to the second end of the first capacitor; the second end of the third switching element and the first end of the fourth switching element are respectively connected Connected to the first end of the second capacitor; The first terminal of the first capacitor, the anode of the first diode, the first terminal of the fifth switching element, and the cathode of the third diode are respectively connected to the first terminal of the ninth switching element. One end is connected; the second end of the second capacitor, the cathode of the second diode, the second end of the sixth switching element and the anode of the fourth diode are respectively connected to the tenth The second end of the switching element is connected; The second end of the fifth switching element and the first end of the sixth switching element are respectively connected to the second end of the third capacitor and the first end of the fourth capacitor; The second terminal and the anode of the third diode are respectively connected to the first terminal of the seventh switching element; the second terminal of the fourth capacitor and the cathode of the fourth diode are respectively connected to the The second end of the eighth switch element is connected; the second end of the seventh switch element and the first end of the eighth switch element are respectively connected to the first end of the output end, and the second end of the ninth switch element The two ends and the first end of the tenth switching element are respectively connected to the second end of the output end. If the first switching element, the fourth switching element, the fifth switching element, and the eighth switching element are turned on, The switching element and the tenth switching element, the other switching elements are all turned off, the first capacitor and the second capacitor are respectively connected in series with the low-voltage DC power supply, and the low-voltage DC power supply passes through the fourth The diode charges the fourth capacitor, and the output voltage of the output terminal is 0; if the first switching element, the fourth switching element, the sixth switching element, and the seventh switching element are turned on And the ninth switching element, all the other switching elements are turned off, the first capacitor and the second capacitor are respectively connected in series with the low-voltage DC power supply, and the low-voltage DC power supply passes through the third two poles. The third capacitor is charged by the tube, and the voltage output from the output terminal is zero. 2 The high-voltage output multi-level inverter circuit according to claim 1, wherein the output voltage of the low-voltage DC power supply is Vdc, If the first switching element and the third switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on, The seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the voltage output by the output terminal is Vdc or Xc; if the second switching element and the fourth switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on The switching element, the seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is VdcOr -Vdc。 3 The high-voltage output multi-level inverter circuit according to claim 1, wherein the output voltage of the low-voltage DC power supply is Vdc, If the second switching element and the third switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on, The seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the voltage output by the output terminal is 2Vde or "2Vdc; if the first switching element and the fourth switching element are turned on, and the fifth switching element, the eighth switching element, and the ninth switching element are turned on; or the sixth switching element is turned on , The seventh switching element and the tenth switching element, all other switching elements are turned off, and the output voltage of the output terminal is 3VdeOr -3Vdc; If the second switching element and the third switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switching element is turned on, The seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the output voltage at the output terminal is 4VdeOr -4Vdc。 4 The high-voltage output multi-level inverter circuit according to claim 1, wherein the output voltage of the low-voltage DC power supply is Vdc, If the first switching element and the third switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switching element is turned on, The seventh The switching element and the tenth switching element, the other switching elements are all turned off, and the voltage output by the output terminal is 5Vdc or -5V dc if the second switching element and the fourth switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the first switching element is turned on Five switching elements, the seventh switching element, and the tenth switching element, all other switching elements are turned off, and the output voltage of the output terminal is 5VdeOr -5Vdc。 5 The high-voltage output multi-level inverter circuit according to claim 1, wherein the output voltage of the low-voltage DC power supply is Vdc, If the first switching element and the fourth switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switching element is turned on, The seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the voltage output by the output terminal is 6Vde or one 6V dc 6 The high-voltage output multi-level inverter circuit according to claim 1, wherein the two switching elements form a pair of complementary conduction half-bridge units. 7 The multi-level inverter circuit with high voltage output according to claim 1, wherein the switching elements in the five half-bridge units are all selected as N-channel MOSFET or P-channel MOSFET or IGBT device, wherein: When the switching elements are all N-channel MOSFETs, the source of the N-channel MOSFET serves as the first end of the switching element, and the drain of the N-channel MOSFET serves as the second end of the switching element , The gate of the N-channel MOSFET is used as the control terminal of the switching element; when the switching elements are all P-channel MOSFETs, the drain of the P-channel MOSFET is used as the first terminal of the switching element , The source of the P-channel MOSFET is the second end of the switching element, and the gate of the P-channel MOSFET serves as the control end of the switching element; when the switching elements are all IGBT devices, the The emitter of the IGBT device serves as the first terminal of the switching element, the collector of the IGBT device serves as the second terminal of the switching element, and the base of the IGBT device serves as the control terminal of the switching element. 8 The high-voltage output multi-level inverter circuit according to claim 7, wherein the control terminal of each of the switching elements is connected to a controller, and the controller is used to control the conduction of each of the switching elements. Or turn it off to achieve multi-level AC output. | [ZH CN110868093B]: 一种高压输出的多电平逆变电路 技术领域 [0001]本发明涉及电力电子逆变电路技术领域，尤其涉及一种高压输出的多电平逆变电 路。 背景技术 [0002]随着社会的发展，人们对不可再生资源的需求越来越多，不可以再生资源是可以 被使用完的，由此石油、煤炭等化石不可再生能源被人们使用，变得越来越少。因此，目前能 源危机和能源污染步步逼近，获取新型能源已经变得十分迫切，以风能和太阳能为代表的 分布式发电技术以及以电池和超级电容为代表的分布式储能技术越来越受到世界各国的 高度重视。这些新兴能源和新技术的发展和应用高度依赖于电力电子逆变装置的性能。现 有电力电子逆变装置大部分是采用两电平逆变电路实现的，而两电平逆变电路本身具有谐 波含量高和效率低等缺陷。 [0003]随着电力电子技术的高速发展，目前的电力电子逆变装置大部分是采用多电平逆 变电路实现电源的转换，多电平逆变电路的优点包括输出电压谐波含量少、器件电压应力 低、电磁干扰少和效率较高等。而典型的多电平逆变电路包括二极管钳位型、电容钳位型和 H桥级联型。其中二极管钳位型和电容钳位型在多电平逆变电路中存在电路钳位复杂且不 具备自主升压的问题，而H桥级联型的多电平逆变电路需要多个独立的直流电源，使得多电 平逆变电路电路复杂。 [0004]因此，针对上述情况，如何设计出电路结构简单、输入电源数量少且具备自主升压 能力的多电平逆变电路成为本领域技术人员亟待解决的重要技术问题。 发明内容 [0005]本发明实施例提供了一种高压输出的多电平逆变电路，用于解决现有多电平逆变 电路的需要多个输入直流电源且不会自动升压的技术问题。 [0006]为了实现上述目的，本发明实施例提供如下技术方案： [0007] 一种高压输出的多电平逆变电路，包括低压直流电源、至少五个半桥单元、至少四 个电容单元和输出端； [0008]所述半桥单元包括两个串联连接的开关元件，且两个所述开关元件连接的节点为 第一串联节点； [0009]每个所述电容单元包括电容器和与所述电容器串联连接的二极管，且所述电容器 与所述二极管连接的节点为第二串联节点； [0010]其中，五个所述半桥单元分别为第一半桥单元、第二半桥单元、第三半桥单元、第 四半桥单元和第五半桥单元；四个所述电容单元分别为第一电容单元、第二电容单元、第三 电容单元和第四电容单元； [0011]所述第一半桥单元的第一串联节点与所述第一电容单元连接，所述第一电容单元 还与所述低压直流电源的负极连接； [0012]所述第二半桥单元的第一串联节点与所述第二电容单元连接，所述第二电容单元 还与所述低压直流电源的正极连接； [0013]所述第三半桥单元的第一串联节点分别与所述第三电容单元和所述第四电容单 元连接，所述第三电容单元还与所述第一电容单元连接，所述第四电容单元还与所述第二 电容单元连接； [0014]所述输出端的第一端与所述第四半桥单元的第一串联节点连接，所述输出端的第 二端与所述第五半桥单元的第一串联节点连接； [0015]所述第四半桥单元的第一端与所述第四电容单元的第二串联节点连接，所述第四 半桥单元的第二端与所述第三电容单元的第二串联节点连接。 [0016]优选地，所述第一半桥单元包括第一开关元件和第二开关元件;所述第二半桥单 元包括第三开关元件和第四开关元件;所述第三半桥单元包括第五开关元件和第六开关元 件；所述第四半桥单元包括第七开关元件和第八开关元件；所述第五半桥单元包括第九开 关元件和第十开关元件； [0017]所述第一电容单元包括第一电容器和第一二极管;所述第二电容单元包括第二电 容器和第二二极管；所述第三电容单元包括第三电容器和第三二极管；所述第四电容单元 包括第四电容器和第四二极管;其中， [0018]所述第一开关元件的第一端、所述第三开关元件的第一端和所述第一二极管的阴 极分别与所述低压直流电源的负极连接； [0019]所述第二开关元件的第二端、所述第四开关元件的第二端和所述第二二极管的阳 极分别与所述低压直流电源的正极连接； [0020]所述第一开关元件的第二端和所述第二开关元件的第一端分别与所述第一电容 器的第二端连接； [0021]所述第三开关元件的第二端和所述第四开关元件的第一端分别与所述第二电容 器的第一端连接； [0022]所述第一电容器的第一端、所述第一二极管的阳极、所述第五开关元件的第一端 和所述第三二极管的阴极分别与所述第九开关元件的第一端连接； [0023]所述第二电容器的第二端、所述第二二极管的阴极、所述第六开关元件的第二端 和所述第四二极管的阳极分别与所述第十开关元件的第二端连接； [0024]所述第五开关元件的第二端和所述第六开关元件的第一端分别与所述第三电容 器的第二端和所述第四电容器的第一端连接； [0025]所述第三电容器的第二端和所述第三二极管的阳极分别与所述第七开关元件的 第一端连接； [0026]所述第四电容器的第二端和所述第四二极管的阴极分别与所述第八开关元件的 第二端连接； [0027]所述第七开关元件的第二端与所述第八开关元件的第一端分别与所述输出端的 第一端连接，所述第九开关元件的第二端与所述第十开关元件的第一端分别与所述输出端 的第二端连接。 [0028] 优选地，若开通所述第一开关元件、所述第四开关元件、所述第五开关元件、所述 第八开关元件和所述第十开关元件，其他的所述开关元件全部关断，所述第一电容器和所 述第二电容器分别与所述低压直流电源串联，所述低压直流电源通过所述第四二极管给所 述第四电容器充电，所述输出端输出的电压为0; [0029] 若开通所述第一开关元件、所述第四开关元件、所述第六开关元件、所述第七开关 元件和所述第九开关元件，其他的所述开关元件全部关断，所述第一电容器和所述第二电 容器分别与所述低压直流电源串联，所述低压直流电源通过所述第三二极管给所述第三电 容器充电，所述输出端输出的电压为0。 [0030] 优选地，所述低压直流电源输出的电压为Vdc，若开通所述第一开关元件和所述第 三开关元件，并且开通所述第五开关元件、所述第八开关元件和所述第十开关元件；或者并 且开通所述第六开关元件、所述第七开关元件和所述第九开关元件，其他的所述开关元件 全部关断，所述输出端输出的电压为Vdc或- Vdc ； [0031] 若开通所述第二开关元件和所述第四开关元件，并且开通所述第五开关元件、所 述第八开关元件和所述第十开关元件;或者并且开通者所述第六开关元件、所述第七开关 元件和所述第九开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为丫n或「 Vdc。 [0032] 优选地，所述低压直流电源输出的电压为Vdc，若开通所述第二开关元件和所述第 三开关元件，并且开通所述第五开关元件、所述第八开关元件和所述第十开关元件；或者并 且开通所述第六开关元件、所述第七开关元件和所述第九开关元件，其他的所述开关元件 全部关断，所述输出端输出的电压为2Vde或- 2 Vde ； [0033] 若开通所述第一开关元件和所述第四开关元件，并且开通所述第五开关元件、所 述第八开关元件和所述第九开关元件;或者并且开通所述第六开关元件、所述第七开关元 件和所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为3Vde或3Vdc； [0034] 若开通所述第二开关元件和所述第三开关元件，并且开通所述第六开关元件、所 述第八开关元件和所述第九开关元件；或者并且开通所述第五开关元件、所述第七开关元 件和所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为4Vde或4Vdc。 [0035] 优选地,所述低压直流电源输出的电压为Vdc，若开通所述第一开关元件和所述第 三开关元件,并且开通所述第六开关元件、所述第八开关元件和所述第九开关元件;或者并 且开通所述第五开关元件、所述第七开关元件和所述第十开关元件，其他的所述开关元件 全部关断，所述输出端输出的电压为5Vde或- 5 Vde ； [0036] 若开通所述第二开关元件和所述第四开关元件，并且开通所述第六开关元件、所 述第八开关元件和所述第九开关元件；或者并且开通所述第五开关元件、所述第七开关元 件和所述第十开关元件，其他的所述开关元件全部关断，所述输出端输出的电压为5Vde或5Vdc。 [0037] 优选地,所述低压直流电源输出的电压为Vdc，若开通所述第一开关元件和所述第 四开关元件，并且开通所述第六开关元件、所述第八开关元件和所述第九开关元件;或者并 且开通所述第五开关元件、所述第七开关元件和所述第十开关元件，其他的所述开关元件 全部关断，所述输出端输出的电压为6Vde或-6Vdc。 [0038]优选地，两个所述开关元件形成一对互补导通的所述半桥单元。 [0039] 优选地，五个所述半桥单元中的开关元件均选用N沟道MOSFET或P沟道MOSFET或 IGBT器件，其中： [0040]当各所述开关元件均选用N沟道MOSFET时，所述N沟道MOSFET的源极作为各所述开 关元件的第一端，所述N沟道MOSFET的漏极作为各所述开关元件的第二端，所述N沟道 MOSFET的栅极作为各所述开关元件的控制端； [0041]当各所述开关元件均选用P沟道MOSFET时，所述P沟道MOSFET的漏极作为各所述开 关元件的第一端，所述P沟道MOSFET的源极作为各所述开关元件的第二端，所述P沟道 MOSFET的栅极作为各所述开关元件的控制端； [0042]当各所述开关元件均选用IGBT器件时，所述IGBT器件的发射极作为各所述开关元 件的第一端，所述IGBT器件的集电极作为各所述开关元件的第二端，所述IGBT器件的基极 作为各所述开关元件的控制端。 [0043] 优选地，各所述开关元件的控制端均与控制器连接，所述控制器用于控制各所述 开关元件的导通或关断，以实现多电平交流电的输出。 [0044]从以上技术方案可以看出，本发明实施例具有以下优点：该高压输出的多电平逆 变电路将一个低压直流电源输出的电压通过五个半桥单元上开关元件的导通或截止转换 成多电平交流电的电压的高压交流电从输出端输出，使得采用一个电源输入实现了多电平 交流电的输出，并且该高压输出的多电平逆变电路的电路结构简单，解决了现有多电平逆 变电路的需要多个输入直流电源且不会自动升压的技术问题。 附图说明 [0045]为了更清楚地说明本发明实施例或现有技术中的技术方案，下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本 发明的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可 以根据这些附图获得其它的附图。 [0046]图1为本发明实施例所述的高压输出的多电平逆变电路的框架示意图。 [0047]图2为本发明实施例所述的高压输出的多电平逆变电路的电路图。 [0048]图3为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为0的电 路图。 [0049]图4为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为输入电 压的电路图。 [0050]图5为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负输入 电压的电路图。 [0051]图6为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为两倍输 入电压的电路图。 [0052]图7为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负两倍 输入电压的电路图。 [0053]图8为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为三倍输 入电压的电路图。 [0054]图9为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负三倍 输入电压的电路图。 [0055]图10为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为四倍 输入电压的电路图。 [0056]图11为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负四 倍输入电压的电路图。 [0057]图12为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为五倍 输入电压的电路图。 [0058]图13为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负五 倍输入电压的电路图。 [0059]图14为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为六倍 输入电压的电路图。 [0060]图15为本发明实施例所述的高压输出的多电平逆变电路输出端输出电压为负六 倍输入电压的电路图。 [0061]图16为本发明实施例所述的高压输出的多电平逆变电路的开关逻辑表。 具体实施方式 [0062]为使得本发明的发明目的、特征、优点能够更加的明显和易懂，下面将结合本发明 实施例中的附图，对本发明实施例中的技术方案进行清楚、完整地描述，显然，下面所描述 的实施例仅仅是本发明一部分实施例，而非全部的实施例。基于本发明中的实施例，本领域 普通技术人员在没有做出创造性劳动前提下所获得的所有其它实施例，都属于本发明保护 的范围。 [0063]本申请实施例提供了一种高压输出的多电平逆变电路，用于解决现有多电平逆变 电路的需要多个输入直流电源且不会自动升压的技术问题。 [0064]如图1所示，图1为本发明实施例所述的高压输出的多电平逆变电路的框架示意 图。 [0065] 本发明实施例提供了一种高压输出的多电平逆变电路，包括低压直流电源V、至少 五个半桥单元、至少四个电容单元和输出端Uo；半桥单元包括两个串联连接的开关元件，且 两个开关元件连接的节点为第一串联节点;每个电容单元包括电容器和与电容器串联连接 的二极管，且电容器与二极管连接的节点为第二串联节点。其中，五个半桥单元分别为第一 半桥单元11、第二半桥单元12、第三半桥单元13、第四半桥单元14和第五半桥单元15；四个 电容单元分别为第一电容单元21、第二电容单元22、第三电容单元23和第四电容单元24。 [0066]第一半桥单元11的第一串联节点与第一电容单元21连接，第一电容单元21还与低 压直流电源V的负极连接;第二半桥单元12的第一串联节点与第二电容单元22连接，第二电 容单元22还与低压直流电源V的正极连接;第三半桥单元13的第一串联节点分别与第三电 容单元23和第四电容单元24连接，第三电容单元23还与第一电容单元21连接，第四电容单 元24还与第二电容单元22连接;输出端Uo的第一端与第四半桥单元24的第一串联节点连 接，输出端Uo的第二端与第五半桥单元15的第一串联节点连接;第四半桥单元14的第一端 与第四电容单元24的第二串联节点连接，第四半桥单元14的第二端与第三电容单元23的第 二串联节点连接。 [0067] 需要说明的是，电容器可以优选选用电解电容器。开关元件可以为IGBT器件，也可 以为MOSFET元件。其中，输出端Uo用于与负载连接。低压直流电源V输出的电压为Vdc。具体 地，五个半桥单元中的开关元件均可以选用N沟道MOSFET，也可以选用P沟道MOSFET，也可以 选用IGBT器件，当开关元件均选用N沟道MOSFET时，N沟道MOSFET的源极作为开关元件的第 一端，N沟道MOSFET的漏极作为开关元件的第二端，N沟道MOSFET的栅极作为开关元件的控 制端；当开关元件均选用P沟道MOSFET时，P沟道MOSFET的漏极作为开关元件的第一端，P沟 道MOSFET的源极作为开关元件的第二端，P沟道MOSFET的栅极作为开关元件的控制端；当开 关元件均选用IGBT器件时，IGBT器件的发射极作为开关元件的第一端，IGBT器件的集电极 作为开关元件的第二端，IGBT器件的基极作为开关元件的控制端。各开关元件的控制端均 与控制器连接，控制器用于控制各开关元件的导通或关断，以实现多电平交流电的输出。 [0068]本发明实施例中的高压输出的多电平逆变电路将一个低压直流电源输出的电压 通过五个半桥单元上开关元件的导通或截止转换成多电平交流电的电压的高压交流电从 输出端输出，使得采用一个电源输入实现了多电平交流电的输出，并且该高压输出的多电 平逆变电路的电路结构简单，解决了现有多电平逆变电路的需要多个输入直流电源且不会 自动升压的技术问题。 [0069]需要说明的是，多电平交流电的电压是指输出电压不但极性可以在正负之间变 化，而且输出电压可以按阶梯的形式逐个电平递增然后递减，使得输出电压波形逼近正弦 波形。 [0070]如图2所示，图2为本发明实施例所述的高压输出的多电平逆变电路的电路图。 [0071]本发明实施例提供的高压输出的多电平逆变电路中，第一半桥单元11包括第一开 关元件S1和第二开关元件S2；第二半桥单元12包括第三开关元件S3和第四开关元件S4；第 三半桥单元13包括第五开关元件S5和第六开关元件S6；第四半桥单元14包括第七开关元件 S7和第八开关元件S8；第五半桥单元15包括第九开关元件S9和第十开关元件S10。第一电容 单元21包括第一电容器C1和第一二极管D1；第二电容单元22包括第二电容器C2和第二二极 管D2 ；第三电容单元23包括第三电容器C3和第三二极管D3 ；第四电容单元24包括第四电容 器C4和第四二极管D4。 [0072]第一开关元件S1的第一端、第三开关元件S3的第一端和第一二极管D1的阴极分别 与低压直流电源V的负极连接;第二开关元件S2的第二端、第四开关元件S4的第二端和第二 二极管D2的阳极分别与低压直流电源V的正极连接;第一开关元件S1的第二端和第二开关 元件S2的第一端分别与第一电容器C1的第二端连接;第三开关元件S3的第二端和第四开关 元件S4的第一端分别与第二电容器C2的第一端连接;第一电容器C1的第一端、第一二极管 D1的阳极、第五开关元件S5的第一端和第三二极管D3的阴极分别与第九开关元件S9的第一 端连接;第二电容器C2的第二端、第二二极管D2的阴极、第六开关元件S6的第二端和第四二 极管D4的阳极分别与第十开关元件D10的第二端连接;第五开关元件S5的第二端和第六开 关元件S6的第一端分别与第三电容器C3的第二端和第四电容器C4的第一端连接;第三电容 器C3的第二端和第三二极管D3的阳极分别与第七开关元件S7的第一端连接;第四电容器C4 的第二端和第四二极管D4的阴极分别与第八开关元件S8的第二端连接;第七开关元件S7的 第二端与第八开关元件S8的第一端分别与输出端Uo的第一端连接，第九开关元件S9的第二 端与第十开关元件S10的第一端分别与输出端Uo的第二端连接。 [0073]需要说明的是，第一开关元元件S1与第二开关元件S2构成一对互补导通的半桥单 元，第三开关元件S3与第四开关元件S4构成一对互补导通的半桥单元，第五开关元件S5与 第六开关元件S6构成一对互补导通的半桥单元，第七开关元件S7与第八开关元件58构成一 对互补导通的半桥单元，第八开开关元件S9与第十开关元件S10构成一对互补导通的半桥 单元。第一电容器C1与第二电容器C2的电容值一样且它们的额定电压都等于低压直流电源 的电压值Vdc，第三电容器C3与第四电容器C4的电容值一样且它们的额定电压都等于低压直 流电源电压值Vdc的三倍，即是第三电容器C3与第四电容器C4的额定电压值为3Vde。该高压 输出的多电平逆变电路通过第一半桥单元11、第二半桥单元12、第三半桥单元13、第四半桥 单元14和第五半桥单元15上均导通任意一个开关元件，使得输出端Uo输出交流电压，该高 压输出的多电平逆变电路在工作过程中输出多电平交流电时，整个电路是在各种不同状态 间有序切换的第一半桥单元11、第二半桥单元12、第三半桥单元13、第四半桥单元14和第五 半桥单元15上均导通任意一个开关元件，实现一个低压直流电源的电压Vdc转换成含有0、土 Vdc、±2Vde、±3Vde、±4Vdc、±5Vde和土6Vde共13中不同电平的高压交流电在输出端端U。输 出。 [0074]如图3所示，图3为本发明实施例所述的高压输出的多电平逆变电路输出端输出电 压为0的电路图。 [0075]本发明实施例的一个实施例中，开通第一开关元件S1、第四开关元件S4、第五开关 元件S5、第八开关元件S8和第十开关元件S10,其他的开关元件全部关断，第一电容器C1和 第二电容器C2分别与低压直流电源V串联，低压直流电源V通过第四二极管D2给第四电容器 C4充电，输出端Uo输出的电压为0。开通第一开关元件S1、第四开关元件S4、第六开关元件 S6、第七开关元件S7和第九开关元件S9,其他的开关元件全部关断，第一电容器C1和第二电 容器C2分别与低压直流电源V串联，低压直流电源V通过第三二极管D3给第三电容器C3充 电，输出端Uo输出的电压为0。 [0076]需要说明的是，开通第一开关元件S1、第四开关元件S4、第五开关元件S5、第八开 关元件S8和第十开关元件S10,其他的开关元件全部关断，第一电容器C1和第二电容器C2分 别与低压直流电源V串联，低压直流电源V通过第四二极管D4给第四电容器C4充电，同时，由 于第四二极管D4、第八开关元件S8和和第十开关元件S10导通，输出端Uo输出的电压为0。开 通第一开关元件S1、第四开关元件S4、第六开关元件S6、第七开关元件S7和第九开关元件 S9,其他的开关元件全部关断，第一电容器C1和第二电容器C2分别与低压直流电源V串联， 低压直流电源V通过第三二极管D3给第三电容器C3充电，同时，由于第三二极管D3、第七开 关元件S7和和第九开关元件S9导通，输出端Uo输出的电压为0。 [0077]如图4和图5所示，图4为本发明实施例所述的高压输出的多电平逆变电路输出端 输出电压为输入电压的电路图，图5为本发明实施例所述的高压输出的多电平逆变电路输 出端输出电压为负输入电压的电路图。 [0078]本发明实施例的一个实施例中，低压直流电源V输出的电压为Vdc，若开通第一开关 元件S1和第三开关元件S3,并且开通第五开关元件S5、第八开关元件S8和第十开关元件 S10；或者并且开通第六开关元件S6、第七开关元件S7和第九开关元件S9，其他的开关元件 全部关断，输出端Uo输出的电压为Vdc或- Vdc ； [0079] 若开通第二开关元件S2和第四开关元件S4,并且开通第五开关元件S5、第八开关 元件S8和第十开关元件S10；或者并且开通者第六开关元件S6、第七开关元件S7和第九开关 元件S9，其他的开关元件全部关断，输出端Uo输出的电压为Vdc或-Vdc。 [0080]需要说明的是，低压直流电源V输出的电压为Vdc，如图4所示，若开通第一开关元件 S1、第三开关元件S3、第五开关元件S5、第八开关元件S8和第十开关元件S10，其他的开关元 件全部关断，低压直流电源V通过第二二极管D2给第二电容器C2充电，第一电容器C1和第二 电容器C2通过第一开关元件S1和第三开关元件S3串联后再通过第五开关元件S5与第四电 容器C4反向串联连接，并通过第八开关元件S8和第十开关元件S10从输出端Uo输出的电压/ 电平为+Vdc；若开通第二开关元件S2、第四开关元件S4、第五开关元件S5、第八开关元件S8和 第十开关元件S10，其他的开关元件全部关断，低压直流电源V通过第一二极管D1给第一电 容器C1充电，第一电容器C1和第二电容器C2通过第二开关元件S2和第四开关元件S4串联后 再通过第五开关元件S5与第四电容器C4反向串联连接，并通过第八开关元件S8和第十开关 元件S10从输出端Uo输出的电压/电平为+Vdc。如图5所示，若开通第一开关元件S1、第三开关 元件S3、第六开关元件S6、第七开关元件S7和第九开关元件S9,其他的开关元件全部关断， 低压直流电源V通过第二二极管D2给第二电容器C2充电，第一电容器C1和第二电容器C2通 过第一开关元件S1和第三开关元件S3串联后再通过第六开关元件S6与第三电容器C3反向 串联连接，并通过第七开关元件S7和第九开关元件S9从输出端Uo输出的电压/电平为-Vdc； 若开通第二开关元件S2、第四开关元件S4、第六开关元件S6、第七开关元件S7和第九开关元 件S9,其他的开关元件全部关断，低压直流电源V通过第一二极管D1给第一电容器C1充电， 第一电容器C1和第二电容器C2通过第二开关元件S2和第四开关元件S4串联后再通过第六 开关元件S6与第三电容器C3反向串联连接，并通过第七开关元件S7和第九开关元件S9从输 出端Uo输出的电压/电平为-Vdc。 [0081]如图6和图7所示，图6为本发明实施例所述的高压输出的多电平逆变电路输出端 输出电压为两倍输入电压的电路图，图7为本发明实施例所述的高压输出的多电平逆变电 路输出端输出电压为负两倍输入电压的电路图。 [0082]本发明实施例的一个实施例中，低压直流电源V输出的电压为Vdc，若开通第二开关 元件S2和第三开关元件S3,并且开通第五开关元件S5、第八开关元件S8和第十开关元件 S10；或者并且开通第六开关元件S6、第七开关元件S7和第九开关元件S9，其他的开关元件 全部关断，输出端Uo输出的电压/电平为2 Vde或-2 Vde。 [0083]需要说明的是，低压直流电源V输出的电压为Vdc，如图6所示，若开通第二开关元件 S2、第三开关元件S3、第五开关元件S5、第八开关元件S8和第十开关元件S10,其他的开关元 件全部关断，低压直流电源V通过第一二极管D1和第二二极管D2分别给第一电容器C1和第 二电容器C2充电，同时通过第五开关元件S5与第四电容器C4反向串联连接，还通过第八开 关元件S8和第十开关元件S10从输出端Uo输出的电压/电平为2Vde。如图7所示，若开通第二 开关元件S2、第三开关元件S3、第六开关元件S6、第七开关元件S7和第九开关元件S9,其他 的开关元件全部关断，低压直流电源V通过第一二极管D1和第二二极管D2分别给第一电容 器C1和第二电容器C2充电，同时通过第六开关元件S5与第三电容器C3反向串联连接，还通 过第七开关元件S7和第九开关元件S9从输出端Uo输出的电压/电平为-2Vdc。 [0084]如图8和图9所示，图8为本发明实施例所述的高压输出的多电平逆变电路输出端 输出电压为三倍输入电压的电路图，图9为本发明实施例所述的高压输出的多电平逆变电 路输出端输出电压为负三倍输入电压的电路图。 [0085]本发明实施例的一个实施例中，若开通第一开关元件S1和第四开关元件S4,并且 开通第五开关元件S5、第八开关元件S8和第九开关元件S9；或者并且开通第六开关元件S6、 第七开关元件S7和第十开关元件S10，其他的开关元件全部关断，输出端Uo输出的电压/电 平为或-3Vd0。 [0086]需要说明的是，低压直流电源V输出的电压为Vdc，如图8所示，若开通第一开关元件 S1、第四开关元件S4、第五开关元件S5、第八开关元件S8和第九开关元件S9,其他的开关元 件全部关断，第一电容器C1和第二电容器C2分别与低压直流电源V串联后通过第四二极管 D4给第四电容器C4充电，同时第四电容器C4通过第五开关元件S5、第八开关元件S8和第九 开关元件S9从输出端Uo输出的电压/电平为3Vde。如图9所示，若开通第一开关元件S1、第四 开关元件S4、第六开关元件S6、第七开关元件S7和第十开关元件S10，其他的开关元件全部 关断，第一电容器C1和第二电容器C2分别与低压直流电源V串联后通过第三二极管D3给第 三电容器C3充电，同时第三电容器C3通过第六开关元件S6、第七开关元件S7和第十开关元 件S10从输出端Uo输出的电压/电平为-3Vdc。 [0087]如图10和图11所示，图10为本发明实施例所述的高压输出的多电平逆变电路输出 端输出电压为四倍输入电压的电路图，图11为本发明实施例所述的高压输出的多电平逆变 电路输出端输出电压为负四倍输入电压的电路图。 [0088]本发明实施例的一个实施例中，若开通第二开关元件S2和第三开关元件S3,并且 开通第六开关元件S6、第八开关元件S8和第九开关元件S9；或者并且开通第五开关元件S5、 第七开关元件S7和第十开关元件S10,其他的开关元件全部关断，输出端V输出的电压/电平 为4Vde或©dc。 [0089]需要说明的是，低压直流电源V输出的电压为Vdc,如图10所示，若开通第二开关元 件S2、第三开关元件S3、第六开关元件S6、第八开关元件S8和第九开关元件S9,其他的开关 元件全部关断，低压直流电源V通过第一二极管D1和第二二极管D2分别给第一电容器C1和 第二电容器C2充电，同时还通过第六开关元件S6与第四电容器C4串联后通过第八开关元件 S8和第九开关元件S9从输出端Uo输出的电压/电平为4Vde。如图11所示，若开通第二开关元 件S2、第三开关元件S3、第五开关元件S5、第七开关元件S7和第十开关元件S10,其他的开关 元件全部关断，低压直流电源V通过第一二极管D1和第二二极管D2分别给第一电容器C1和 第二电容器C2充电，同时通过第五开关元件S5与第三电容器C3串联后通过第七开关元件S7 和第十开关元件S10从输出端Uo输出的电压/电平为-4Vdc。 [0090]如图12和图13所示，图12为本发明实施例所述的高压输出的多电平逆变电路输出 端输出电压为五倍输入电压的电路图，图13为本发明实施例所述的高压输出的多电平逆变 电路输出端输出电压为负五倍输入电压的电路图。 [0091]本发明实施例的一个实施例中，低压直流电源输出的电压为Vdc，若开通第一开关 元件S1和第三开关元件S3,并且开通第六开关元件S6、第八开关元件S8和第九开关元件S9； 或者并且开通第五开关元件S5、第七开关元件S7和第十开关元件S10,其他的开关元件全部 关断，输出端Uo输出的电压为5Vde或-5Vdc；若开通第二开关元件S2和第四开关元件S4,并且 开通第六开关元件S6、第八开关元件S8和所述第九开关元件S9；或者并且开通第五开关元 件S5、第七开关元件S7和第十开关元件S10,其他的开关元件全部关断，输出端Uo输出的电 压为5Vdc或-5Vd0。 [0092]需要说明的是，如图12所示，若开通第一开关元件S1、第三开关元件S3、第六开关 元件S6、第八开关元件S8和第九开关元件S9，其他的开关元件全部关断，低压直流电源V通 过第二二极管D2给第二电容器C2充电，第一电容器C1和第二电容器C2通过第一开关元件S1 和第三开关元件S3串联后再通过第六开关元件S6与第四电容器C4串联连接后并通过第八 开关元件S8和第九开关元件S9从输出端Uo输出的电压为5Vdc；若开通第二开关元件S2、第四 开关元件S4、第六开关元件S6、第八开关元件S8和第九开关元件S9,其他的开关元件全部关 断，低压直流电源V通过第一二极管D1给第一电容器C1充电，第一电容器C1和第二电容器C2 通过第二开关元件S2和第四开关元件S4串联后再通过第六开关元件S6与第四电容器C4串 联连接后并通过第八开关元件S8和第九开关元件S9从输出端Uo输出的电压为5Vde。如图13 所示，若开通第一开关元件S1、第三开关元件S3、第五开关元件S5、第七开关元件S7和第十 开关元件S10,其他的开关元件全部关断，低压直流电源V通过第二二极管D2给第二电容器 C2充电，第一电容器C1和第二电容器C2通过第一开关元件S1和第三开关元件S3串联后再通 过第五开关元件S5与第三电容器C3串联连接后并通过第七开关元件S7和第十开关元件S10 从输出端Uo输出的电压为-5Vdc；若开通第二开关元件S2、第四开关元件S4、第五开关元件 S5、第七开关元件S7和第十开关元件S10，其他的开关元件全部关断，低压直流电源V通过第 一二极管D1给第一电容器C1充电，第一电容器C1和第二电容器C2通过第二开关元件S2和第 四开关元件S4串联后再通过第五开关元件S5与第三电容器C3串联连接后并通过第七开关 元件S7和第十开关元件S10从输出端Uo输出的电压为-5Vdc。 [0093]如图14和图15所示，图14为本发明实施例所述的高压输出的多电平逆变电路输出 端输出电压为六倍输入电压的电路图，图15为本发明实施例所述的高压输出的多电平逆变 电路输出端输出电压为负六倍输入电压的电路图。 [0094]本发明实施例的一个实施例中，低压直流电源输出的电压为Vdc，若开通第一开关 元件S1和第四开关元件S4,并且开通第六开关元件S6、第八开关元件S8和第九开关元件S9； 或者并且开通第五开关元件S5、第七开关元件S7和第十开关元件S10,其他的开关元件全部 关断，输出端Uo输出的电压为6 Vde或- 6 Vde。 [0095]需要说明的是，如图14所示，若开通第一开关元件S1、第四开关元件S4、第六开关 元件S6、第八开关元件S8和第九开关元件S9,其他的开关元件全部关断，第一电容器C1和第 二电容器C2分别与低压直流电源V串联后通过第三二极管D3给第三电容器C3充电，并第三 电容器C3与第四电容器C4串联后通过第八开关元件S8和第九开关元件S9从输出端Uo输出 的电压为6Vde。如图15所示，若开通第一开关元件S1、第四开关元件S4、第五开关元件S5、第 七开关元件S7和第十开关元件S10,其他的开关元件全部关断，第一电容器C1和第二电容器 C2分别与低压直流电源V串联后通过第四二极管D4给第四电容器C4充电，并第三电容器C3 与第四电容器C4串联后通过第七开关元件S7和第十开关元件S10从输出端Uo输出的电压 为-6% [0096]该高压输出的多电平逆变电路通过控制第一至第十开关元件的合理导通和关断， 可将一个低压直流电源V的电压Vdc转换成含有0、土Vdc、±2Vdc、±3Vdc、±4Vdc、士5Vdec和土 6Vde共13中不同电平的高压交流电输出。如表1所示， [0097] 表1为高压输出的多电平逆变电路的开关逻辑表 CN 110868093 Β [0098] 开关状态（1—导通；0—关断） 4命出Uo S1 S2 S3 S4 S5 S6 S7 S8 S9 S10 1 0 0 1 0 1 0 1 1 0 +6Vdc 1 0 1 0 0 1 0 1 1 0 +5Vdc 0 1 0 1 0 1 0 1 1 0 0 1 1 0 0 1 0 1 1 0 +4Vdc 1 0 0 1 1 0 0 1 1 0 +3Vdc 0 1 1 0 1 0 0 1 0 1 +2Vdc 0 1 0 1 1 0 0 1 0 1 +Vdc 1 0 1 0 1 0 0 1 0 1 1 0 0 1 1 0 0 1 0 1 0 1 0 0 1 0 1 1 0 1 0 1 0 1 0 0 1 1 0 1 0 -Vdc 0 1 0 1 0 1 1 0 1 0 0 1 1 0 0 1 1 0 1 0 -2Vdc 1 0 0 1 0 1 1 0 0 1 -3Vdc 0 1 1 0 1 0 1 0 0 1 -4Vdc 0 1 0 1 1 0 1 0 0 1 -5Vdc 1 0 1 0 1 0 1 0 0 1 1 0 0 1 1 0 1 0 0 1 -6Vdc [0099]参考表1,该高压输出的多电平逆变电路的输出电压可以从-6Vdc、-5Vde逐级增加 到+6Vdj然后再逐级减小到-6Vdc，再往返增减实现多电平交流电的输出，因此，低压直流电 源的输出电压为丫公，通过该高压输出的多电平逆变电路输出交流电的幅值为6Vde 实现了 多电平交流电的输出。 [0100]所属领域的技术人员可以清楚地了解到,为描述的方便和简洁，上述描述的系统, 装置和单元的具体工作过程，可以参考前述方法实施例中的对应过程,在此不再赘述。 [0101]在本申请所提供的几个实施例中，应该理解至U，所揭露的系统，装置和方法，可以 通过其它的方式实现。例如，以上所描述的装置实施例仅仅是示意性的，例如，所述单元的 划分，仅仅为一种逻辑功能划分，实际实现时可以有另外的划分方式,例如多个单元或组件 可以结合或者可以集成到另一个系统，或一些特征可以忽略，或不执行。另一点，所显示或 讨论的相互之间的耦合或直接耦合或通信连接可以是通过一些接口，装置或单元的间接耦 合或通信连接，可以是电性，机械或其它的形式。 [0102]所述作为分离部件说明的单元可以是或者也可以不是物理上分开的，作为单元显 示的部件可以是或者也可以不是物理单元，即可以位于一个地方，或者也可以分布到多个 网络单元上。可以根据实际的需要选择其中的部分或者全部单元来实现本实施例方案的目 的。 [0103]另外，在本发明各个实施例中的各功能单元可以集成在一个处理单元中，也可以 是各个单元单独物理存在，也可以两个或两个以上单元集成在一个单元中。上述集成的单 元既可以采用硬件的形式实现，也可以采用软件功能单元的形式实现。 [0104]所述集成的单元如果以软件功能单元的形式实现并作为独立的产品销售或使用 时，可以存储在一个计算机可读取存储介质中。基于这样的理解，本发明的技术方案本质上 或者说对现有技术做出贡献的部分或者该技术方案的全部或部分可以以软件产品的形式 体现出来，该计算机软件产品存储在一个存储介质中，包括若干指令用以使得一台计算机 设备(可以是个人计算机，服务器，或者网络设备等)执行本发明各个实施例所述方法的全 部或部分步骤。而前述的存储介质包括：U盘、移动硬盘、只读存储器(ROM，Read - Only Memory)、随机存取存储器(RAM，Random Access Memory)、磁碟或者光盘等各种可以存储程 序代码的介质。 [0105]以上所述，以上实施例仅用以说明本发明的技术方案，而非对其限制;尽管参照前 述实施例对本发明进行了详细的说明，本领域的普通技术人员应当理解:其依然可以对前 述各实施例所记载的技术方案进行修改，或者对其中部分技术特征进行等同替换;而这些 修改或者替换，并不使相应技术方案的本质脱离本发明各实施例技术方案的精神和范围。 [EN CN110868093B]: A high-voltage output multi-level inverter circuit technical field [0001] The present invention relates to the technical field of power electronic inverter circuits, and in particular to a multi-level inverter circuit with high voltage output. Background technique [0002] With the development of society, people have more and more demand for non-renewable resources. Non-renewable resources can be used up. As a result, fossil non-renewable energy sources such as petroleum and coal are used by people and become more and more popular. Less. Therefore, the current energy crisis and energy pollution are approaching, and access to new energy sources has become very urgent. Distributed power generation technologies represented by wind and solar energy, and distributed energy storage technologies represented by batteries and super capacitors are becoming more and more popular. All countries in the world attach great importance to it. The development and application of these emerging energy and new technologies are highly dependent on the performance of power electronic inverter devices. Most of the existing power electronic inverter devices are realized by using a two-level inverter circuit, and the two-level inverter circuit itself has defects such as high harmonic content and low efficiency. [0003] With the rapid development of power electronic technology, most of the current power electronic inverter devices adopt multi-level inverter circuits to achieve power conversion. The advantages of multi-level inverter circuits include low output voltage harmonic content, The device has low voltage stress, less electromagnetic interference and higher efficiency. The typical multi-level inverter circuit includes diode clamp type, capacitor clamp type and H-bridge cascade type. Among them, the diode clamp type and the capacitor clamp type have the problem of complicated circuit clamping and no autonomous boost in the multi-level inverter circuit, while the H-bridge cascaded multi-level inverter circuit requires multiple independent The DC power supply makes the multi-level inverter circuit complicated. [0004] Therefore, in view of the above situation, how to design a multi-level inverter circuit with a simple circuit structure, a small number of input power sources, and an autonomous boost capability has become an important technical problem to be solved by those skilled in the art. Summary of the invention [0005] The embodiment of the present invention provides a high-voltage output multi-level inverter circuit, which is used to solve the technical problem that the existing multi-level inverter circuit requires multiple input DC power sources and does not automatically boost the voltage. [0006] In order to achieve the foregoing objectives, the embodiments of the present invention provide the following technical solutions: [0007] A high-voltage output multi-level inverter circuit includes a low-voltage DC power supply, at least five half-bridge units, at least four capacitor units, and an output terminal; [0008] The half-bridge unit includes two switching elements connected in series, and the node where the two switching elements are connected is a first series node; [0009] Each of the capacitance units includes a capacitor and a diode connected in series with the capacitor, and a node connected to the capacitor and the diode is a second series node; [0010] Wherein, the five half-bridge units are respectively a first half-bridge unit, a second half-bridge unit, a third half-bridge unit, a fourth half-bridge unit, and a fifth half-bridge unit; and four of the capacitor units They are a first capacitor unit, a second capacitor unit, a third capacitor unit, and a fourth capacitor unit; [0011] The first series node of the first half-bridge unit is connected to the first capacitor unit, and the first capacitor unit is also connected to the negative electrode of the low-voltage DC power supply; [0012] The first series node of the second half-bridge unit is connected to the second capacitor unit, and the second capacitor unit is also connected to the positive pole of the low-voltage DC power supply; [0013] The first series node of the third half-bridge unit is connected to the third capacitor unit and the fourth capacitor unit, and the third capacitor unit is also connected to the first capacitor unit. The fourth capacitor unit is also connected to the second capacitor unit; [0014] The first end of the output end is connected to the first series node of the fourth half-bridge unit, and the second end of the output end is connected to the first series node of the fifth half-bridge unit; [0015] The first end of the fourth half-bridge unit is connected to the second series node of the fourth capacitor unit, and the second end of the fourth half-bridge unit is connected to the second series node of the third capacitor unit. Node connection. [0016] Preferably, the first half-bridge unit includes a first switching element and a second switching element; the second half-bridge unit includes a third switching element and a fourth switching element; the third half-bridge unit includes A fifth switching element and a sixth switching element; the fourth half-bridge unit includes a seventh switching element and an eighth switching element; the fifth half-bridge unit includes a ninth switching element and a tenth switching element; [0017] The first capacitor unit includes a first capacitor and a first diode; the second capacitor unit includes a second capacitor and a second diode; the third capacitor unit includes a third capacitor and a third capacitor. Diode; the fourth capacitor unit includes a fourth capacitor and a fourth diode; wherein, [0018] The first end of the first switching element, the first end of the third switching element, and the cathode of the first diode are respectively connected to the negative electrode of the low-voltage DC power supply; [0019] The second end of the second switching element, the second end of the fourth switching element, and the anode of the second diode are respectively connected to the anode of the low-voltage DC power supply; [0020] The second end of the first switching element and the first end of the second switching element are respectively connected to the second end of the first capacitor; [0021] The second end of the third switching element and the first end of the fourth switching element are respectively connected to the first end of the second capacitor; [0022] The first terminal of the first capacitor, the anode of the first diode, the first terminal of the fifth switching element, and the cathode of the third diode are respectively connected to the ninth switch The first end of the component is connected; [0023] The second terminal of the second capacitor, the cathode of the second diode, the second terminal of the sixth switching element, and the anode of the fourth diode are respectively connected to the tenth switch The second end of the component is connected; [0024] The second end of the fifth switching element and the first end of the sixth switching element are respectively connected to the second end of the third capacitor and the first end of the fourth capacitor; [0025] The second end of the third capacitor and the anode of the third diode are respectively connected to the first end of the seventh switching element; [0026] The second end of the fourth capacitor and the cathode of the fourth diode are respectively connected to the second end of the eighth switching element; [0027] The second end of the seventh switching element and the first end of the eighth switching element are respectively connected to the first end of the output end, and the second end of the ninth switching element is connected to the tenth end of the output end. The first end of the switching element is respectively connected to the second end of the output end. [0028] Preferably, if the first switching element, the fourth switching element, the fifth switching element, the eighth switching element, and the tenth switching element are turned on, all other switching elements are Turn off, the first capacitor and all The second capacitors are respectively connected in series with the low-voltage DC power supply, the low-voltage DC power supply charges the fourth capacitor through the fourth diode, and the output voltage of the output terminal is 0; [0029] If the first switching element, the fourth switching element, the sixth switching element, the seventh switching element, and the ninth switching element are turned on, all other switching elements are turned off, The first capacitor and the second capacitor are respectively connected in series with the low-voltage DC power supply, the low-voltage DC power supply charges the third capacitor through the third diode, and the output voltage of the output terminal is 0 . [0030] Preferably, the voltage output by the low-voltage DC power supply is Vdc, If the first switching element and the third switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on, The seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is VdcOr-Vdc ； [0031] If the second switching element and the fourth switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on The switching element, the seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the output voltage at the output terminal is Yn or " Vdc. [0032] Preferably, the voltage output by the low-voltage DC power supply is Vdc, If the second switching element and the third switching element are turned on, and the fifth switching element, the eighth switching element, and the tenth switching element are turned on; or the sixth switching element is turned on, The seventh switching element, the ninth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is 2VdeOr-2 Vde ； [0033] If the first switching element and the fourth switching element are turned on, and the fifth switching element, the eighth switching element, and the ninth switching element are turned on; or the sixth switch is turned on Element, the seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the output voltage at the output terminal is 3Vdeor3Vdc; [0034] If the second switching element and the third switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switch is turned on Element, the seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the output voltage at the output terminal is 4Vdeor4Vdc. [0035] Preferably, the voltage output by the low-voltage DC power supply is Vdc, If the first switching element and the third switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switching element is turned on, The seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is 5VdeOr-5 Vde ； [0036] If the second switching element and the fourth switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switch is turned on Element, the seventh switching element, and the tenth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is 5VdeOr 5Vdc。 [0037] Preferably, the voltage output by the low-voltage DC power supply is Vdc, If the first switching element and the fourth switching element are turned on, and the sixth switching element, the eighth switching element, and the ninth switching element are turned on; or the fifth switching element is turned on, The seventh switching element, the tenth switching element, and the other switching elements are all turned off, and the output voltage of the output terminal is 6VdeOr -6Vdc。 [0038] Preferably, the two switching elements form a pair of complementary conduction half-bridge units. [0039] Preferably, the switching elements in the five half-bridge units are all N-channel MOSFETs, P-channel MOSFETs or IGBT devices, wherein: [0040] When each of the switching elements is selected as an N-channel MOSFET, the source of the N-channel MOSFET is used as the first end of each of the switching elements, and the drain of the N-channel MOSFET is used as the first end of each of the switching elements. The second end of the switching element, the gate of the N-channel MOSFET serves as the control end of each of the switching elements; [0041] When each of the switching elements is a P-channel MOSFET, the drain of the P-channel MOSFET is used as the first end of each of the switching elements, and the source of the P-channel MOSFET is used as the first end of each of the switching elements. The second end of the switching element, the gate of the P-channel MOSFET serves as the control end of each of the switching elements; [0042] When each of the switching elements is an IGBT device, the emitter of the IGBT device is used as the first end of each of the switching elements, and the collector of the IGBT device is used as the second end of each of the switching elements. , The base of the IGBT device serves as the control terminal of each of the switching elements. [0043] Preferably, the control terminals of each of the switching elements are connected to a controller, and the controller is used to control the on or off of each of the switching elements, so as to realize the output of multi-level alternating current. [0044] It can be seen from the above technical solutions that the embodiment of the present invention has the following advantages: the high-voltage output multi-level inverter circuit pass
[ZH CN113193760A]: 一种带储能装置的电力电子变压器 [EN CN113193760A]: Power electronic transformer with energy storage device | [ZH CN113193760A]: 本发明涉及一种带储能装置的电力电子变压器。该电力电子变压器包括：电力电子变压器高压侧接10kV配电网，电力电子变压器低压侧接400V等级配电网，三相10kV交流电压通过A相电路、B相电路和C相电路进行分压与隔离变换，将高压交流电变换为直流电，均连接直流母线P和N，直流母线P和N电性连接储能型Quasi‑Z源逆变器将直流电变换为三相400V等级交流电接低压配电网。本发明提出的电力电子变压器减少了高频变压器与子模块数量，提高了电力电子变压器的功率密度，能有效地抑制电力电子变压器给上级配电网带来的谐波，在保证电能质量的情况下，维持低压配电网稳定，还能参与上级配电网的电压/频率调节，并具有一定的惯性与阻尼。 [EN CN113193760A]: The invention relates to a power electronic transformer with an energy storage device. The power electronic transformer includes: the high-voltage side of the power electronic transformer is connected to the 10kV distribution network, and the low-voltage side of the power electronic transformer is connected to the 400V-level distribution network. Isolation conversion, converts high-voltage AC power to DC power, both are connected to DC buses P and N, and DC buses P and N are electrically connected to energy storage type QuasiZ source inverters to convert DC power into three-phase 400V AC power to low-voltage power distribution network . The power electronic transformer proposed in the present invention reduces the number of high-frequency transformers and sub-modules, improves the power density of the power electronic transformer, can effectively suppress the harmonics brought by the power electronic transformer to the upper-level distribution network, and guarantees the quality of power It maintains the stability of the low-voltage distribution network, and can also participate in the voltage/frequency adjustment of the superior distribution network, and has a certain inertia and damping. | CN109067195A | 2018-12-21 | CN201811185378A | 2018-10-11 | CN201811185378A, 2018-10-11 | CN109067195A: 2018-12-21 CN113193760A: 2021-07-30 | UNIV NORTH CHINA WATER RESOURCES & ELECTRIC POWER 华北水利水电大学 | WANG JIDONG WANG YANHENG WANG MENGDI ZHU LENGXUE LI JIFANG LI YUANQIAN YANG LONGTUAN | H02M5/458: I H02J3/00: I H02J3/01: I H02M3/335: I H02M7/537: I | H02J3/00: I H02J3/01: I H02M3/33584: I H02M5/458: I H02M7/537: I Y02E40/40: A | CN101795081A CN101917017A CN102185533A CN204707045U CN207354062U CN207459728U |  | [ZH CN113193760A]: 1 .一种带储能装置的电力电子变压器，其特征在于，所述电力电子变压器的高压侧接 10kV配电网，所述电力电子变压器的低压侧接400V等级配电网;所述电力电子变压器包括: A相电路、B相电路、C相电路和储能型Quasi”源逆变器； 所述A相电路的末端x和所述B相电路的末端y均与所述C相电路的末端z电性连接成公 共点o； 所述A相电路、所述B相电路和所述C相电路均用于将三相10kV交流电压进行分压与隔 离变换，得到直流电，并输入直流母线线； 所述储能型Quasi-Z源逆变器与所述直流母线P和N电性连接;所述储能型Quasi-Z源逆 变器用于将10kV交流电降为400V等级交流电；所述储能型Quasi-Z源逆变器还用于将连接 在电容C3的分布式直流电变换为三相400V等级交流电，并输入低压配电网；所述储能型 Quasi-Z源逆变器还用于将直流负载联接在蓄电池B1处，对直流负载进行供电。 2 .根据权利要求1所述的一种带储能装置的电力电子变压器，其特征在于，所述A相电 路的结构与所述B相电路的结构和所述C相电路的结构均相同。 3 .根据权利要求2所述的一种带储能装置的电力电子变压器，其特征在于，所述A相电 路包括输入级和隔离变换级； 所述输入级包括:9个级联的H桥联接模块； 所述隔离变换级包括:3个级联的单元模块。 4 .根据权利要求3所述的一种带储能装置的电力电子变压器，其特征在于，所述单元模 块：3个原边多绕组和一个副边单绕组。 5 .根据权利要求3所述的一种带储能装置的电力电子变压器，其特征在于，所述H桥联 接模块包括：四个全控型开关器件SAi，SAi+1，SAi+2，SAi+3和电容CAm； 所述全控型开关器件SAi的集电极与所述全控型开关器件SAi + 1的集电极相连并均连 接在所述电容CAm的一端； 所述全控型开关器件SAi+2的发射极与所述全控型开关器件SAi+3的发射极相连并均 连接在所述电容CAm的另一端； 所述全控型开关器件SAi的发射极与所述全控型开关器件SAi+2的集电极连接作为一 个接线端子;所述全控型开关器件SAi+1的发射极与所述全控型开关器件SAi+3的集电极连 接作为一个接线端子。 6 .根据权利要求1所述的一种带储能装置的电力电子变压器，其特征在于，所述储能型 Quasi -Z源逆变器包括:电感工、全控型开关器件S7和电容C2； 所述电感工的一端连接直流母线P，所述电感工的另一端连接全控型开关器件S7的发射 极，所述全控型开关器件S7的集电极串联电感L2和电容C2后连接所述全控型开关器件S7的 发射极，所述全控型开关器件S7的集电极并联电容4和蓄电池81后连接直流母线N，在所述 电感L2和所述电容C2之间连接全控型开关器件SrS3和S5的集电极，所述直流母线N连接全控 型开关器件S4、S6和S2的发射极，所述全控型开关器件5］的发射极和所述全控型开关器件S4 的集电极连接作为输出端a，所述全控型开关器件S3的发射极和所述全控型开关器件S6的集 电极连接作为输出端b，所述全控型开关器件S5的发射极和所述全控型开关器件邑的集电极 连接作为输出端c。 [EN CN113193760A]: 1 A power electronic transformer with an energy storage device, wherein the high-voltage side of the power electronic transformer is connected to a 10kV distribution network, and the low-voltage side of the power electronic transformer is connected to a 400V-level distribution network; the power electronic transformer Including: A-phase circuit, B-phase circuit, C-phase circuit and energy storage type Quasi" source inverter; the end x of the A-phase circuit and the end y of the B-phase circuit are all connected with the end of the C-phase circuit z is electrically connected to a common point o; the A-phase circuit, the B-phase circuit, and the C-phase circuit are all used to divide and isolate the three-phase 10kV AC voltage to obtain DC power and input it to the DC bus bar The energy storage type Quasi-Z source inverter is electrically connected to the DC buses P and N; the energy storage type Quasi-Z source inverter is used to reduce 10kV AC power to 400V AC power; The energy type Quasi-Z source inverter is also used to connect the capacitor C3The distributed DC power is converted into three-phase 400V AC power and input into the low-voltage power distribution network; the energy storage type Quasi-Z source inverter is also used to connect the DC load to the battery B1 to supply power to the DC load. 2 The power electronic transformer with energy storage device according to claim 1, wherein the structure of the A-phase circuit is the same as the structure of the B-phase circuit and the structure of the C-phase circuit. 3 The power electronic transformer with energy storage device according to claim 2, wherein the A-phase circuit includes an input stage and an isolation conversion stage; the input stage includes: 9 cascaded H-bridge connections Module; The isolation conversion stage includes: 3 cascaded unit modules. 4 The power electronic transformer with energy storage device according to claim 3, wherein the unit module: 3 primary side multi-windings and one secondary side single winding. 5 The power electronic transformer with energy storage device according to claim 3, characterized in that the H-bridge connection module comprises: four fully-controlled switching devices SAi, SAi+1, SAi+2, SAi+ 3 and a capacitor CAm; the collector of the fully-controlled switching device SAi is connected to the collector of the fully-controlled switching device SAi+1 and both are connected to one end of the capacitor CAm; the fully-controlled switching device SAi The emitter of +2 is connected to the emitter of the fully-controlled switching device SAi+3 and both are connected to the other end of the capacitor CAm; the emitter of the fully-controlled switching device SAi is connected to the fully-controlled switch The collector of the device SAi+2 is connected as a terminal; the emitter of the fully-controlled switching device SAi+1 is connected with the collector of the fully-controlled switching device SAi+3 as a terminal. 6 The power electronic transformer with energy storage device according to claim 1, wherein the energy storage type Quasi-Z source inverter comprises: an inductance and a fully controlled switching device S7And capacitance C2; One end of the inductor is connected to the DC bus P, and the other end of the inductor is connected to the fully-controlled switching device S7The emitter of the fully controlled switching device S7The collector series inductance L2And capacitance C2Then connect the emitter of the fully-controlled switching device S7, the collector parallel capacitor 4 of the fully-controlled switching device S7 and the battery 81 are connected to the DC bus N, and the inductance L2And the capacitance C2Fully-controlled switching device SrS is connected between3And S5The collector of the DC bus N is connected to the fully-controlled switching device S4, S6And S2The emitter of the fully-controlled switching device 5] and the fully-controlled switching device S4 The collector is connected as the output terminal a, and the fully-controlled switching device S3The emitter and the fully controlled switching device S6The collector is connected as the output terminal b, and the fully-controlled switching device S5The emitter of and the collector of the fully-controlled switching device are connected as an output terminal c. | [ZH CN113193760A]: 一种带储能装置的电力电子变压器 技术领域 [0001]本发明涉及电气工程技术领域，特别是涉及一种带储能装置的电力电子变压器。 背景技术 [0002]电力电子变压器是一种将电力电子器件和高频变压器相结合、通过电力电子变流 技术实现电能变换的变压器，除具有电压转换、电气隔离、能量传递等基本功能外，还具有 可控性高，可以实现对波形、潮流、电能质量控制以及自动保护控制等优点，是配电网理想 的配电设备。在电力机车牵引用的车载变流器系统、智能电网/能源互联网和分布式可再生 能源发电并网系统中得到广泛的应用。 [0003]常规电力电子变压器输出端采用常规逆变器，为防止同一逆变桥臂上下开关管同 时导通造成逆变器损坏，往往在桥臂开关管的开关信号中加入死区时间，这反而使输出交 流电压波形发生畸变。另外，拓扑不具有模块化结构，且随着电平数的增加，使电路拓扑变 得极其复杂，所以，就需要一种带储能装置的电力电子变压器。 发明内容 [0004]本发明的目的是提供一种带储能装置的电力电子变压器，用以解决现有技术中存 在的问题。 [0005]为实现上述目的，本发明提供了如下方案： [0006] 一种带储能装置的电力电子变压器，所述电力电子变压器的高压侧接10kV配电 网，所述电力电子变压器的低压侧接400V等级配电网；所述电力电子变压器包括:A相电路、 B相电路、C相电路和储能型Quasi”源逆变器； [0007]所述A相电路的末端x和所述B相电路的末端y均与所述C相电路的末端z电性连接 成公共点o； [0008] 所述A相电路、所述B相电路和所述C相电路均用于将三相10kV交流电压进行分压 与隔离变换，得到直流电，并输入直流母线线； [0009] 所述储能型Quasi-Z源逆变器与所述直流母线P和N电性连接;所述储能型Quasi-Z 源逆变器用于将10kV交流电降为400V等级交流电；所述储能型Quasi-Z源逆变器还用于将 连接在电容C3的分布式直流电变换为三相400V等级交流电，并输入低压配电网；所述储能 型Quasi-Z源逆变器还用于将直流负载联接在蓄电池B1处，对直流负载进行供电。 [0010]可选地，所述A相电路的结构与所述B相电路的结构和所述C相电路的结构均相同。 [0011]可选地，所述A相电路包括输入级和隔离变换级； [0012]所述输入级包括：9个级联的H桥联接模块； [0013]所述隔离变换级包括：3个级联的单元模块。 [0014] 可选地，所述单元模块：3个原边多绕组和一个副边单绕组。 [0015] 可选地，所述H桥联接模块包括：四个全控型开关器件SAi，SAi + 1，SAi+2，SAi+3和 电容CAm； [0016]所述全控型开关器件SAi的集电极与所述全控型开关器件SAi + 1的集电极相连并 均连接在所述电容CAm的一端； [0017] 所述全控型开关器件SAi+2的发射极与所述全控型开关器件SAi+3的发射极相连 并均连接在所述电容CAm的另一端； [0018]所述全控型开关器件SAi的发射极与所述全控型开关器件SAi+2的集电极连接作 为一个接线端子;所述全控型开关器件SAi+1的发射极与所述全控型开关器件SAi+3的集电 极连接作为一个接线端子。 [0019] 可选地，所述储能型Quasi源逆变器包括:电感工、全控型开关器件S7和电容C2； [0020] 所述电感工的一端连接直流母线P，所述电感工的另一端连接全控型开关器件S7的 发射极，所述全控型开关器件S7的集电极串联电感l2和电容c2后连接所述全控型开关器件 S7的发射极，所述全控型开关器件S7的集电极并联电容C/口蓄电池瓦后连接直流母线N，在 所述电感12和所述电容C2之间连接全控型开关器件SrS3和S5的集电极，所述直流母线N连接 全控型开关器件S4、S^K2的发射极，所述全控型开关器件5]的发射极和所述全控型开关器 件S4的集电极连接作为输出端a，所述全控型开关器件S3的发射极和所述全控型开关器件S6 的集电极连接作为输出端b，所述全控型开关器件S5的发射极和所述全控型开关器件S2的集 电极连接作为输出端c。 [0021]根据本发明提供的具体实施例，本发明公开了以下技术效果： [0022]本发明所提供的一种带储能装置的电力电子变压器，具有高压侧高电压、小电流 与低压侧低电压、大电流的特点，减少了变压器与子模块数量，提高了电力电子变压器的功 率密度。 [0023] 本发明在电能变换以及能量波动过程中，上级配电网侧并网点电流THD足够小，能 有效地抑制电力电子变压器给上级配电网带来的谐波。 [0024]本发明所提出的电力电子变压器具有良好的功率跟踪性能，在保证电能质量的情 况下，维持低压配电网稳定，还能参与上级配电网的电压/频率调节，并具有一定的惯性与 阻尼。 [0025] 本发明所提出的电力电子变压器可方便地实现光伏电池板、蓄电池等分布式直流 电源并网，还能给直流负载提供相应的直流电源用于充电或驱动直流电动机等。 附图说明 [0026]为了更清楚地说明本发明实施例或现有技术中的技术方案，下面将对实施例中所 需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本发明的一些实施 例，对于本领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可以根据这些附图 获得其他的附图。 [0027]图1为本发明所提供的一种带储能装置的电力电子变压器结构示意图； [0028]图2为本发明实施例提供的一种带储能装置的电力电子变压器的每相电路图； [0029]图3为本发明实施例提供的一种带储能装置的电力电子变压器的H桥联接模块的 结构示意图。 具体实施方式 [0030]下面将结合本发明实施例中的附图，对本发明实施例中的技术方案进行清楚、完 整地描述，显然，所描述的实施例仅仅是本发明一部分实施例，而不是全部的实施例。基于 本发明中的实施例，本领域普通技术人员在没有做出创造性劳动前提下所获得的所有其他 实施例，都属于本发明保护的范围。 [0031]本发明的目的是提供一种带储能装置的电力电子变压器，在维持低压配电网稳定 的同时还能实现对上级配电网的友好支撑，针对高渗透率分布式电源发电的间歇性和功率 波动性引起的配电网电压/频率不稳定问题。 [0032]本发明提出的电力电子变压器可通过直流接口获得功率缓冲，从而在PET维持低 压配电网功率消耗的同时，还具有参与上级配电网电压/频率调节的能力。 [0033]本发明专利针对现有技术中存在的缺点，在隔离变换级中，高频变压器采用固定 数目的原边多绕组与副边单绕组耦合的单元模块级联而成，结构简单，便于扩展。输出端采 用独特的阻抗网络从而允许同一桥臂上下开关管同时导通，使其具备一定的升降压功能。 由于直通状态为Z源逆变器的工作常态，因此在换流过程中无需插入死区时间。 [0034]为使本发明的上述目的、特征和优点能够更加明显易懂，下面结合附图和具体实 施方式对本发明作进一步详细的说明。 [0035]参照图1，本发明提供了一种带储能装置的电力电子变压器，包括:A相电路、B相电 路、C相电路和储能型Quasi”源逆变器，电力电子变压器高压侧接10kV配电网，接线端子为 A、B、C，所述A相电路的末端x和所述B相电路的末端y均与所述C相电路的末端z电性连接成 公共点o,所述电力电子变压器低压侧接400V等级配电网，接线端子为a、b、c； [0036] 三相10kV交流电压通过所述A相电路、所述B相电路和所述C相电路进行分压与隔 离变换，将高压交流电变换为直流电，均连接直流母线P和N，所述直流母线P和N电性连接储 能型Quasi”源逆变器将直流电变换为三相400V等级交流电接低压配电网。 [0037] 所述储能型Quasi-Z源逆变器包括：电感工、全控型开关器件S7和电容C2,所述电感 L的一端连接直流母线p，所述电感^的另一端连接全控型开关器件s7的发射极，所述全控 型开关器件s7的集电极串联电感l2和电容c2后连接所述全控型开关器件s7的发射极，所述 全控型开关器件S7的集电极并联电容4和蓄电池81后连接直流母线N，在所述电感L2和所述 电容C2之间连接全控型开关器件SrS3和S5的集电极，所述直流母线N连接全控型开关器件 S4、S6和52的发射极，所述全控型开关器件5]的发射极和所述全控型开关器件s4的集电极连 接作为输出端a，所述全控型开关器件S3的发射极和所述全控型开关器件S6的集电极连接 作为输出端b，所述全控型开关器件S5的发射极和所述全控型开关器件S2的集电极连接作为 输出端c。 [0038]这种独特的结构允许同一桥臂上的开关管瞬时直通,提高了系统的安全性和可靠 性;此外，通过引入直通量灵活地控制系统的升降压功能，因而也克服了传统电压型逆变器 只能降压的缺点；进一步，相比传统的单级式、两级式逆变器，以单级功率变换形式实现了 升降压与逆变功能。另外，由于电感L1的作用，使得流入到输出级的电流连续恒定，而且由 于分压作用，电容C2上的电压要小，器件承受的电压应力小。 [0039]参照图2,所述A相电路包括输入级和隔离变换级,所述输入级采用级联H桥多电平 拓扑，由9个H桥联接模块级联组成，从而降低分担到每个开关管上的的电压； [0040]所述隔离变换级采用多主动桥拓扑，控制能量双向流动，由3个单元模块级联组 成，所述单元模块由3个原边多绕组和一个副边单绕组耦合而成，前级分别与H桥联接模块 的直流电容相连，后级并联组成直流母线，正极接P直流母线，负极接N直流母线;所述A相电 路结构与所述B相电路结构和所述C相电路结构均相同，每一相由多个单元模块组合而成， 结构简单，便于扩展。 [0041] 参照图3,所述H桥联接模块包括四个全控型开关器件SAi，SAi + 1，SAi+2，SAi+3和 电容CAm，所述全控型开关器件SAi的集电极与所述全控型开关器件SAi+1的集电极相连并 均连接在所述电容CAm的一端，所述全控型开关器件SAi+2的发射极与所述全控型开关器件 SAi+3的发射极相连并均连接在所述电容CAm的另一端,所述全控型开关器件SAi的发射极 与所述全控型开关器件SAi+2的集电极连接作为一个接线端子,所述全控型开关器件SAi+1 的发射极与所述全控型开关器件SAi+3的集电极连接作为一个接线端子;将高压工频交流 转换为数量为9的悬浮直流，级联多电平结构使得输入级功率器件能以较小的电压应力和 开关频率应用于高压大功率。 [0042]综上所述,本发明提出的电力电子变压器具有高压侧高电压、小电流与低压侧低 电压、大电流的特点，减少了变压器与子模块数量，提高了电力电子变压器的功率密度;本 发明在电能变换以及能量波动过程中，上级配电网侧并网点电流THD足够小，能有效地抑制 电力电子变压器给上级配电网带来的谐波;本发明所提出的电力电子变压器具有良好的功 率跟踪性能，在保证电能质量的情况下，维持低压配电网稳定，还能参与上级配电网的电 压/频率调节，并具有一定的惯性与阻尼。 [0043]本中各个实施例采用递进的方式描述,每个实施例重点说明的都是与其他 实施例的不同之处，各个实施例之间相同相似部分互相参见即可。 [0044] 本文中应用了具体个例对本发明的原理及实施方式进行了阐述，以上实施例的说 明只是用于帮助理解本发明的方法及其核心思想；同时,对于本领域的一般技术人员，依据 本发明的思想，在具体实施方式及应用范围上均会有改变之处。综上所述，本内容不 应理解为对本发明的限制。 [EN CN113193760A]: Technical field of power electronic transformer with energy storage device [0001] The present invention relates to the technical field of electrical engineering, in particular to a power electronic transformer with an energy storage device. Background technique [0002] A power electronic transformer is a transformer that combines power electronic devices and high-frequency transformers to achieve electrical energy conversion through power electronic conversion technology. In addition to basic functions such as voltage conversion, electrical isolation, and energy transfer, it also has It has high controllability and can realize the advantages of waveform, power flow, power quality control and automatic protection control. It is an ideal power distribution equipment for the distribution network. It is widely used in the on-board converter system for electric locomotive traction, smart grid/energy Internet and distributed renewable energy power generation and grid-connected systems. [0003] Conventional inverters are used at the output of conventional power electronic transformers. In order to prevent the upper and lower switching tubes of the same inverter bridge arm from being turned on at the same time and causing damage to the inverter, dead time is often added to the switching signals of the bridge arm switching tubes. Instead, the output AC voltage waveform is distorted. In addition, the topology does not have a modular structure, and as the number of levels increases, the circuit topology becomes extremely complicated. Therefore, a power electronic transformer with an energy storage device is needed. Summary of the invention [0004] The purpose of the present invention is to provide a power electronic transformer with an energy storage device to solve the problems existing in the prior art. [0005] In order to achieve the above objective, the present invention provides the following solutions: [0006] A power electronic transformer with an energy storage device, the high-voltage side of the power electronic transformer is connected to a 10kV distribution network, and the low-voltage side of the power electronic transformer is connected to a 400V-level distribution network; the power electronic transformer includes: A-phase circuit, B-phase circuit, C-phase circuit and energy storage type Quasi" source inverter; [0007] The end x of the A-phase circuit and the end y of the B-phase circuit are electrically connected to the end z of the C-phase circuit to form a common point o; [0008] The A-phase circuit, the B-phase circuit, and the C-phase circuit are all used to divide and isolate a three-phase 10kV AC voltage to obtain a direct current, and input the direct current bus bar; [0009] The energy storage type Quasi-Z source inverter is electrically connected to the DC buses P and N; the energy storage type Quasi-Z source inverter is used to reduce 10kV AC power to 400V AC power; The energy storage type Quasi-Z source inverter is also used to connect the capacitor C3The distributed DC power is converted into three-phase 400V AC power and input into the low-voltage power distribution network; the energy storage type Quasi-Z source inverter is also used to connect the DC load to the battery B1 to supply power to the DC load. [0010] Optionally, the structure of the A-phase circuit is the same as the structure of the B-phase circuit and the structure of the C-phase circuit. [0011] Optionally, the A-phase circuit includes an input stage and an isolation conversion stage; [0012] The input stage includes: 9 cascaded H-bridge connection modules; [0013] The isolation conversion stage includes: 3 cascaded unit modules. [0014] Optionally, the unit module: 3 primary side multi-windings and one secondary side single winding. [0015] Optionally, the H-bridge connection module includes: four fully-controlled switching devices SAi, SAi+1, SAi+2, SAi+3 and a capacitor CAm; [0016] The collector of the fully-controlled switching device SAi is connected to the collector of the fully-controlled switching device SAi+1 and both are connected to one end of the capacitor CAm; [0017] The emitter of the fully-controlled switching device SAi+2 is connected to the emitter of the fully-controlled switching device SAi+3 and both are connected to the other end of the capacitor CAm; [0018] The emitter of the fully-controlled switching device SAi is connected to the collector of the fully-controlled switching device SAi+2 as a terminal; the emitter of the fully-controlled switching device SAi+1 is connected to the The collector of the fully-controlled switching device SAi+3 is connected as a terminal. [0019] Optionally, the energy storage type Quasi source inverter includes: an inductor, a fully controlled switching device S7And capacitance C2[0020] One end of the inductor is connected to the DC bus P, and the other end of the inductor is connected to the fully controlled switching device S7The emitter of the fully controlled switching device S7The collector series inductance l2And capacitance c2Then connect the full-control switching device S7The emitter of the fully controlled switching device S7The collector parallel capacitor C/ port battery watts is connected to the DC bus N, in the inductance 12And the capacitance C2Fully-controlled switching device SrS is connected between3And S5The collector of the DC bus N is connected to the fully-controlled switching device S4, S^K2The emitter of the fully-controlled switching device 5] and the fully-controlled switching device S4The collector is connected as the output terminal a, and the fully-controlled switching device S3The emitter and the fully controlled switching device S6 The collector is connected as the output terminal b, and the fully-controlled switching device S5The emitter and the fully controlled switching device S2The collector is connected as the output terminal c. [0021] According to the specific embodiments provided by the present invention, the present invention discloses the following technical effects: [0022] A power electronic transformer with energy storage device provided by the present invention has the characteristics of high voltage and small current on the high voltage side and low voltage and large current on the low voltage side, reducing the number of transformers and submodules, and improving power electronics The power density of the transformer. [0023] In the process of electric energy conversion and energy fluctuations of the present invention, the upper-level distribution network side grid-connected point current THD is sufficiently small, which can effectively suppress the harmonics brought by the power electronic transformer to the upper-level distribution network. [0024] The power electronic transformer proposed by the present invention has good power tracking performance. Under the condition of ensuring power quality, it maintains the stability of the low-voltage distribution network, and can also participate in the voltage/frequency adjustment of the upper-level distribution network, and has certain Inertia and damping. [0025] The power electronic transformer proposed by the present invention can conveniently realize the grid connection of distributed DC power sources such as photovoltaic panels and storage batteries, and can also provide corresponding DC power sources to DC loads for charging or driving DC motors. Description of the drawings [0026] In order to more clearly explain the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the drawings that need to be used in the embodiments. Obviously, the drawings in the following description are merely present For some embodiments of the invention, for those of ordinary skill in the art, other drawings may be obtained based on these drawings without creative labor. [0027] FIG. 1 is a schematic diagram of the structure of a power electronic transformer with an energy storage device provided by the present invention; [0028] FIG. 2 is a circuit diagram of each phase of a power electronic transformer with an energy storage device provided by an embodiment of the present invention; [0029] FIG. 3 is a schematic structural diagram of an H-bridge connection module of a power electronic transformer with an energy storage device according to an embodiment of the present invention. Detailed ways [0030] The following will clearly and completely describe the technical solutions in the embodiments of the present invention with reference to the accompanying drawings in the embodiments of the present invention. Obviously, the described embodiments are only a part of the embodiments of the present invention, rather than all implementations. example. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0031] The purpose of the present invention is to provide a power electronic transformer with energy storage device, while maintaining the stability of the low-voltage distribution network, but also to achieve friendly support for the superior distribution network, for high-permeability distributed power generation Voltage/frequency instability of the distribution network caused by intermittent and power fluctuations. [0032] The power electronic transformer proposed by the present invention can obtain power buffer through a DC interface, so that while PET maintains the power consumption of the low-voltage distribution network, it also has the ability to participate in the voltage/frequency adjustment of the upper-level distribution network. [0033] The patent of the present invention is aimed at the shortcomings in the prior art. In the isolation conversion stage, the high-frequency transformer is formed by cascading a fixed number of primary side multi-windings and secondary single-winding coupled unit modules. The structure is simple and convenient. Extension. The output end adopts a unique impedance network to allow the upper and lower switch tubes of the same bridge arm to be turned on at the same time, so that it has a certain buck-boost function. Since the through state is the normal working state of the Z-source inverter, there is no need to insert a dead time during the commutation process. [0034] In order to make the above objectives, features and advantages of the present invention more obvious and easy to understand, the present invention will be further described in detail below in conjunction with the accompanying drawings and specific embodiments. [0035] Referring to FIG. 1, the present invention provides a power electronic transformer with energy storage device, including: A-phase circuit, B-phase circuit, C-phase circuit and energy storage type Quasi" source inverter, high-voltage power electronic transformer Side connected to the 10kV power distribution network, the connection terminals are A, B, C, the end x of the A-phase circuit and the end y of the B-phase circuit are electrically connected to the end z of the C-phase circuit to form a common point o , The low-voltage side of the power electronic transformer is connected to a 400V power distribution network, and the connection terminals are a, b, and c; [0036] The three-phase 10kV AC voltage is divided and isolated through the A-phase circuit, the B-phase circuit, and the C-phase circuit to convert high-voltage AC power into DC power, both of which are connected to DC buses P and N, The DC bus P and N are electrically connected to the energy storage type Quasi" source inverter to convert the DC power into a three-phase 400V AC power to connect to the low-voltage power distribution network. [0037] The energy storage type Quasi-Z source inverter includes: an inductor, a fully controlled switching device S7And capacitance C2, One end of the inductor L is connected to the DC bus p, and the other end of the inductor L is connected to the fully-controlled switching device s7The emitter of the fully controlled switching device s7The collector series inductance l2And capacitance c2Then connect the full-control switching device s7The emitter of the fully controlled switching device S7The collector parallel capacitor 4 and the battery 81 are connected to the DC bus N, and the inductance L2And the capacitance C2Fully-controlled switching device SrS is connected between3And S5The collector of the DC bus N is connected to a fully-controlled switching device S4, S6And 52The emitter of the fully-controlled switching device 5] and the fully-controlled switching device s4The collector is connected as the output terminal a, and the fully-controlled switching device S3The emitter of the fully-controlled switching device S6 is connected as the output terminal b, and the fully-controlled switching device S5The emitter and the fully controlled switching device S2The collector is connected as the output terminal c. [0038] This unique structure allows the switch tubes on the same bridge arm to be directly connected instantaneously, which improves the safety and reliability of the system; in addition, the buck-boost function of the system is flexibly controlled by introducing direct flux, thus overcoming the traditional The voltage-type inverter can only step down the shortcomings; further, compared with the traditional single-stage and two-stage inverters, it realizes the functions of step-down and inversion in the form of single-stage power conversion. In addition, due to the effect of the inductor L1, the current flowing into the output stage is continuously constant, and due to the partial pressure, the capacitor C2The voltage on the device should be small, and the voltage stress on the device should be small. [0039] Referring to FIG. 2, the A-phase circuit includes an input stage and an isolation conversion stage. The input stage adopts a cascaded H-bridge multilevel topology and is composed of 9 H-bridge connection modules cascaded, thereby reducing the burden to each The voltage on each switch tube; [0040] The isolation conversion stage adopts a multi-active bridge topology to control the bidirectional flow of energy, and is composed of three unit modules cascaded. The unit modules are coupled by three primary side multi-windings and a secondary side single winding. The stages are respectively connected to the DC capacitors of the H-bridge connection module, the latter stages are connected in parallel to form a DC bus, the positive pole is connected to the P DC bus, and the negative pole is connected to the N DC bus; the A-phase circuit structure, the B-phase circuit structure and the C-phase circuit The structure is the same, each phase is composed of multiple unit modules, and the structure is simple and easy to expand. [0041] Referring to FIG. 3, the H-bridge connection module includes four fully-controlled switching devices SAi, SAi+1, SAi+2, SAi+3 and a capacitor CAm. The collector of the fully-controlled switching device SAi is connected to The collector of the fully-controlled switching device SAi+1 is connected to one end of the capacitor CAm, and the emitter of the fully-controlled switching device SAi+2 is connected to the emitter of the fully-controlled switching device SAi+3. The emitter is connected and both connected to the other end of the capacitor CAm, the emitter of the fully-controlled switching device SAi is connected to the collector of the fully-controlled switching device SAi+2 as a connecting terminal, and the fully-controlled The emitter of the SAi+1 type switching device is connected with the collector of the full control type switching device SAi+3 as a terminal; the high-voltage power frequency AC is converted into a floating DC with a number of 9, and the cascaded multi-level structure makes Input-level power devices can be applied to high-voltage and high-power with less voltage stress and switching frequency. [0042] In summary, the power electronic transformer proposed by the present invention has the characteristics of high voltage and small current on the high voltage side and low voltage and large current on the low voltage side, reducing the number of transformers and sub-modules, and improving the power density of the power electronic transformer In the process of electric energy conversion and energy fluctuations of the present invention, the upper-level distribution network side grid-connected point current THD is sufficiently small, which can effectively suppress the harmonics brought by the power electronic transformer to the upper-level distribution network; the power electronic transformer proposed by the present invention It has good power tracking performance, maintains the stability of the low-voltage distribution network under the condition of ensuring the power quality, and can also participate in the voltage/frequency adjustment of the upper-level distribution network, and has a certain inertia and damping. [0043] The various embodiments in this disclosure are described in a progressive manner, and each embodiment focuses on the differences from other embodiments, and the same or similar parts between the various embodiments can be referred to each other. [0044] In this article, specific examples are used to describe the principles and implementations of the present invention. The descriptions of the above embodiments are only used to help understand the methods and core ideas of the present invention; at the same time, for those of ordinary skill in the art, According to the idea of the present invention, there will be changes in the specific implementation and the scope of application. In summary, this content should not be construed as a limitation to the present invention.
[ZH CN109687498B]: 换流站双极并联运行线路倒闸系统及方法 [EN CN109687498A]: Convertor station bipolar parallel running line switching system and method | [ZH CN109687498B]: 本发明提供了一种换流站双极并联运行线路倒闸系统及方法，包括：交流电源AC的输出端连接负极换流站M1和正极换流站M2；负极换流站M1的上桥臂出线经负极接地极电抗L1、第一隔离开关S1接地；正极换流站M2的下桥臂出线经正极接地极电抗L2接地；负极换流站M1的下桥臂出线上设有第二隔离开关S2；第三隔离开关S3的一端连接负极换流站M1的上桥臂出线，另一端连接负极换流站M1的下桥臂出线；第四隔离开关S4的一端连接正极换流站M2的上桥臂出线，另一端连接负极换流站M1的上桥臂出线。本发明可以实现换流站双极并联运行线路融冰，且融冰成本低。 [EN CN109687498B]: The invention provides a convertor station bipolar parallel running line switching system and method. According to the system, an output end of an alternating current (AC) power supply is connected toa negative pole convertor station M1 and a positive pole convertor station M2; an upper bridge arm outgoing line of the negative pole convertor station M1 is earthed through a negative earthing polereactor L1 and a first isolating switch S1; a lower bridge arm outgoing line of the positive pole convertor station M2 is earthed through a positive earthing pole reactor L2; a lower bridge arm outgoing line of the negative pole convertor station M1 is provided with a second isolating switch S2; one end of a third isolating switch S3 is connected with the upper bridge arm outgoing line of the negative pole convertor station M1, and the other end of the third isolating switch S3 is connected with the lower bridge arm outgoing line of the negative pole convertor station M1; one end of a fourth isolating switch S4 is connected with the upper bridge arm outgoing line of the positive pole convertor station M2, and the other end of the fourth isolating switch S4 is connected with the upper bridge arm outgoing line of the negative pole convertor station M1. By means of the bipolar parallel running line switching system and method, deicing of a convertor station bipolar parallel running line is achieved, and the deicing cost is low. | CN109687498A | 2021-03-02 2019-04-26 | CN201811517758A | 2018-12-12 2018-12-12 | CN201811517758A, 2018-12-12 CN201811517758A, 2018-12-12 | CN109687498B: 2021-03-02 | 国网冀北电力有限公司电力科学研究院 华北电力大学 国家电网有限公司 华北电力科学研究院有限责任公司 ELECTRIC POWER RES INST STATE GRID JIBEI ELECTRIC POWER CO LTD UNIV NORTH CHINA ELECTRIC POWER STATE GRID CORP CHINA NORTH CN ELEC POWER RES INST | FAN SHUOCHAO LU YI ZHAO CHENGYONG XIA JIAHANG ZHANG XU GAO YANFENG WANG XIN XUE WENXIANG CAI WEI WANG SHUYUAN ZHANG JIFEI WANG HUI SU BIN | H02J3/36: I H02G7/16: I | H02G7/16: I H02J3/36: I Y02E60/60: A | US2012313581A1 CN103107725A CN103219738A CN103532162A CN105977894A CN107546698A CN105720818A CN106058908A CN106532757A CN107743672A |  | [ZH CN109687498B]: 1.一种换流站双极并联运行线路倒闸系统，其特征在于，包括:交流电源(AC)、负极换 流站(M1)、正极换流站(M2)、第一隔离开关(S1)、第二隔离开关(S2)、第三隔离开关(S3)、第四 隔离开关(S4)、负极接地极电抗(L1)和正极接地极电抗(L2)，其中， 交流电源(AC)的输出端连接负极换流站(M1)和正极换流站(M2)； 负极换流站(M1)的上桥臂出线经负极接地极电抗(L1)、第一隔离开关(S1)接地； 正极换流站(M2)的下桥臂出线经正极接地极电抗(L2)接地； 负极换流站(M1)的下桥臂出线上设有第二隔离开关(S2)； 第三隔离开关(S3)的一端连接负极换流站(M1)的上桥臂出线，另一端连接负极换流站 (M1)的下桥臂出线； 第四隔离开关(S4)的一端连接正极换流站(M2)的上桥臂出线，另一端连接负极换流站 (M1)的上桥臂出线； 其中，在负极换流站(M1)的输出有功功率值稳定到零后，且所述第一隔离开关(S1)和第 二隔离开关(S2)两端的电压和流经所述第一隔离开关(S1)和第二隔离开关(S2)的电流为零 时，所述第一隔离开关(S1)和第二隔离开关(S2)断开，用于保证负极换流站(M1)和正极换流 站(M2)的内部无冲击电流。 2 .如权利要求1所述的换流站双极并联运行线路倒闸系统，其特征在于，负极换流站 (M1)包括3个相单元(X)；正极换流站(M2)包括3个相单元(X)； 每一相单元(X)包括上桥臂(Q)和下桥臂(W)； 上桥臂(Q)包括串联的一个桥臂电抗(Larm)、一个桥臂电阻(Rarm)和多个模块化多电平 换流器子模块； 下桥臂(W)包括串联的一个桥臂电抗(Larm)、一个桥臂电阻(Rarm)和多个模块化多电平 换流器子模块。 3 .如权利要求2所述的换流站双极并联运行线路倒闸系统，其特征在于，模块化多电平 换流器子模块包括:第一IGBT开关管(T1)、第二IGBT开关管(T2)、第一二极管(D1)、第二二极 管(D2)和电容(C1)，其中， 第一IGBT开关管(T1)的发射极(E)为模块化多电平换流器子模块的电流输入端，与第二 IGBT开关管(T2)的集电极(C)连接； 第二IGBT开关管(T2)的发射极(E)为模块化多电平换流器子模块的电流输出端； 第一二极管(D1)的正极连接第一IGBT开关管(T1)的发射极(E)，第一二极管(D1)的负极 连接第一IGBT开关管(T1)的集电极(C)； 第二二极管(D2)的正极连接第二IGBT开关管(T2)的发射极(E)，第二二极管(D2)的负极 连接第二IGBT开关管(T2)的集电极(C)； 电容(C1)的一端连接第一IGBT开关管(T1)的集电极(C)，另一端连接第二IGBT开关管 (T2)的发射极(E)。 4 .如权利要求1所述的换流站双极并联运行线路倒闸系统，其特征在于，还包括第一变 压器漏电抗(LT1)和第二变压器漏电抗(LT2)，其中， 交流电源(AC)的输出端通过第一变压器漏电抗(Lt1)连接负极换流站(M1)； 交流电源(AC)的输出端通过第二变压器漏电抗(LT2)连接正极换流站(M2)。 5 .如权利要求1所述的换流站双极并联运行线路倒闸系统，其特征在于，还包括第一直 流断路器(DCCB1)、第二直流断路器(DCCB2)、第一直流侧平波电抗器(Ldci)和第二直流侧平 波电抗器(LdC2)，其中， 负极换流站(M1)的下桥臂出线经第一直流断路器(DCCB1)连接第一直流侧平波电抗器 (Ldc1)，第一直流侧平波电抗器(Ldc1)连接输电线路； 正极换流站(M2)的上桥臂出线经第二直流断路器(DCCB2)连接第二直流侧平波电抗器 (Ldc2)，第二直流侧平波电抗器(Ldc2)连接输电线路。 6 .一种换流站双极并联运行线路倒闸方法，其特征在于，该方法应用于权利要求1至5 任一所述的换流站双极并联运行线路倒闸系统，包括： 将负极换流站(M1)的输出有功功率值降为零，断开第一隔离开关(S1)和第二隔离开关 (S2)； 若负极换流站(M1)和正极换流站(M2)的内部无冲击电流，闭合第三隔离开关(S3)； 将负极换流站(M1)的控制方式切换为定直流电压控制，调整负极换流站(M1)的上桥臂 出线对地电压的值为正极换流站(M2)的上桥臂出线对地电压的值； 闭合第四隔离开关(S4)，切换负极换流站(M1)的控制方式为定有功功率控制，将负极换 流站(M1)的输出有功功率值提升至正常运行时的有功功率值。 [EN CN109687498B]: 1. A bipolar parallel operation line switching system for converter stations, which is characterized by comprising: alternating current power (AC), negative converter station (M1), positive converter station (M2), first isolating switch (S1) ), the second isolating switch (S2), the third isolating switch (S3), the fourth isolating switch (S4), the negative grounding electrode reactance (L1) and the positive grounding reactance (L2), among which the alternating current power supply (AC) The output end is connected to the negative converter station (M1) and the positive converter station (M2); the upper bridge arm of the negative converter station (M1) is grounded through the negative grounding reactance (L1) and the first isolating switch (S1); The outlet of the lower bridge arm of the converter station (M2) is grounded via the positive grounding reactance (L2); the outlet of the lower bridge arm of the negative converter station (M1) is equipped with a second isolating switch (S2); the third isolating switch (S3) One end of) is connected to the upper arm outlet of the negative converter station (M1), and the other end is connected to the lower arm outlet of the negative converter station (M1); one end of the fourth isolating switch (S4) is connected to the positive converter station (M2) The upper bridge arm of the outlet is connected to the upper bridge arm of the negative converter station (M1); wherein, after the output active power value of the negative converter station (M1) stabilizes to zero, and the first isolating switch ( S1) and the voltage across the second isolating switch (S2) and the current flowing through the first isolating switch (S1) and the second isolating switch (S2) are zero At this time, the first isolating switch (S1) and the second isolating switch (S2) are disconnected to ensure that there is no inrush current inside the negative converter station (M1) and the positive converter station (M2). 2 The bipolar parallel operation line switching system of a converter station according to claim 1, wherein the negative converter station (M1) includes three phase units (X); the positive converter station (M2) includes three Phase unit (X); Each phase unit (X) includes an upper bridge arm (Q) and a lower bridge arm (W); the upper bridge arm (Q) includes a bridge arm reactance (Larm) and a bridge arm resistance ( Rarm) and multiple modular multi-level converter sub-modules; the lower bridge arm (W) includes a bridge arm reactance (Larm), a bridge arm resistance (Rarm) and multiple modular multi-level converters connected in seriesUtensilmodule. 3 The bipolar parallel operation line switching system of a converter station according to claim 2, wherein the modular multilevel converter sub-module includes: a first IGBT switch tube (T1), a second IGBT switch tube (T2), the first diode (D1), the second diode (D2) and the capacitor (C1), where the emitter (E) of the first IGBT switch tube (T1) is a modular multi-level converter The current input terminal of the converter sub-module is connected to the collector (C) of the second IGBT switch tube (T2); the emitter (E) of the second IGBT switch tube (T2) is a modular multilevel converter sub-module The current output terminal of the module; the anode of the first diode (D1) is connected to the emitter (E) of the first IGBT switch tube (T1), and the cathode of the first diode (D1) is connected to the first IGBT switch tube (T1) ) Collector (C); the anode of the second diode (D2) is connected to the emitter (E) of the second IGBT switch tube (T2), and the cathode of the second diode (D2) is connected to the second IGBT switch tube The collector (C) of (T2); one end of the capacitor (C1) is connected to the collector (C) of the first IGBT switch tube (T1), and the other end is connected to the emitter (E) of the second IGBT switch tube (T2). 4 The bipolar parallel operation line switching system of a converter station according to claim 1, further comprising a first transformer leakage reactance (LT1) and a second transformer leakage reactance (LT2), wherein the AC power supply (AC The output terminal of) is connected to the negative converter station (M1) through the first transformer leakage reactance (Lt1); the output terminal of the alternating current power source (AC) is connected to the positive converter station (M2) through the second transformer leakage reactance (LT2). 5 The bipolar parallel operation line switching system of a converter station as claimed in claim 1, characterized in that it further comprises a first straight line Current circuit breaker (DCCB1), second DC circuit breaker (DCCB2), first DC side smoothing reactor (Ldci), and second DC side smoothing reactor (LdC2), among which, the negative converter station (M1) The outgoing line of the lower bridge arm is connected to the first DC side smoothing reactor (Ldc1) through the first DC circuit breaker (DCCB1), and the first DC side smoothing reactor (Ldc1) is connected to the transmission line; the positive converter station ( The outgoing line of the upper bridge arm of M2) is connected to the second DC side smoothing reactor (Ldc2) through the second DC circuit breaker (DCCB2), and the second DC side smoothing reactor (Ldc2) is connected to the transmission line. 6 A switching method for a bipolar parallel operation line of a converter station, characterized in that the method is applied to the bipolar parallel operation line switching system of a converter station according to any one of claims 1 to 5, comprising: changing the negative pole The output active power value of the current station (M1) drops to zero, disconnect the first isolating switch (S1) and the second isolating switch (S2); if the inside of the negative converter station (M1) and the positive converter station (M2) Without inrush current, close the third isolating switch (S3); switch the control mode of the negative converter station (M1) to constant DC voltage control, and adjust the voltage value of the upper bridge arm of the negative converter station (M1) to ground The value of the voltage to the ground of the upper bridge arm of the positive converter station (M2); close the fourth isolating switch (S4), switch the control mode of the negative converter station (M1) to constant active power control, and set the negative converter station ( The output active power value of M1) is increased to the active power value during normal operation. | [ZH CN109687498B]: 换流站双极并联运行线路倒闸系统及方法 技术领域 [0001]本发明涉及电力系统线路融冰技术领域，尤其涉及换流站双极并联运行线路倒闸 实现线路融冰的系统及方法。 背景技术 [0002]冰雪灾害会使架空线覆冰过重，使得线路机械和电气性能的急剧下降，这将导致 输电杆塔倒塌、供电中断等危害，严重威胁电网的安全可靠运行，并造成巨大的经济损失。 因此，十分有必要对覆冰的输电线路的进行融冰。 [0003]目前，输电线路除冰的方法主要包括热力融冰、机械除冰、自然被动除冰等方法， 其中热力融冰具有操作简便、易实施等优点，是高压直流输电工程中常用的融冰方法，双极 并联融冰是热力融冰法的一种，MMC（Modular Multilevel Converter，模块化多电平换流 器）换流站在进行双极并联融冰时，常采用内部安装断路器的方式，但该方式成本较高。 发明内容 [0004]本发明实施例提供一种换流站双极并联运行线路倒闸系统，用以实现换流站双极 并联运行线路融冰，且融冰成本低，该系统包括:交流电源AC、负极换流站M1、正极换流站M2、 第一隔离开关S1、第二隔离开关S2、第三隔离开关S3、第四隔离开关S4、负极接地极电抗L1和 正极接地极电抗L2,其中， [0005] 交流电源AC的输出端连接负极换流站M1和正极换流站M2； [0006]负极换流站M1的上桥臂出线经负极接地极电抗L1、第一隔离开关S1接地； [0007] 正极换流站M2的下桥臂出线经正极接地极电抗L2接地； [0008]负极换流站M1的下桥臂出线上设有第二隔离开关S2； [0009]第三隔离开关S3的一端连接负极换流站M1的上桥臂出线，另一端连接负极换流站 M1的下桥臂出线； [0010]第四隔离开关S4的一端连接正极换流站M2的上桥臂出线，另一端连接负极换流站 M1的上桥臂出线。 [0011]本发明实施例提供一种换流站双极并联运行线路倒闸方法，该方法应用于上述换 流站双极并联运行线路倒闸系统，用以实现换流站双极并联运行线路融冰，且融冰成本低， 包括: [0012] 将负极换流站M1的输出有功功率值降为零，断开第一隔离开关S1和第二隔离开关 S2； [0013]若负极换流站M1和正极换流站M2的内部无冲击电流，闭合第三隔离开关S3； [0014]将负极换流站M1的控制方式切换为定直流电压控制，调整负极换流站M1的上桥臂 出线对地电压的值为正极换流站M2的上桥臂出线对地电压的值； [0015]闭合第四隔离开关S4，切换负极换流站M1的控制方式为定有功功率控制，将负极换 流站M1的输出有功功率值提升至正常运行时的有功功率值。 [0016]在本发明实施例中，将负极换流站Mi的输出有功功率值降为零，断开第一隔离开 关Si和第二隔离开关S2；若负极换流站Mi和正极换流站M2的内部无冲击电流，闭合第三隔离 开关S3；将负极换流站Mi的控制方式切换为定直流电压控制，调整负极换流站Mi的上桥臂出 线对地电压的值为正极换流站M2的上桥臂出线对地电压的值;闭合第四隔离开关S4,切换负 极换流站Mi的控制方式为定有功功率控制，将负极换流站Mi的输出有功功率值提升至正常 运行时的有功功率值，此时正极换流站M2的上桥臂出线电流增加，实现对覆冰电路的融冰。 本发明实施例中采用四个隔离开关进行融冰的方法，与现有技术中采用断路器进行融冰的 方法相比，降低了融冰的成本。 附图说明 [0017]为了更清楚地说明本发明实施例或现有技术中的技术方案，下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本 发明的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动的前提下，还可以 根据这些附图获得其他的附图。在附图中： [0018]图i为本发明实施例中换流站双极并联运行线路倒闸系统的电路图； [0019]图2为本发明实施例提出的换流站双极并联运行线路倒闸方法的流程图； [0020]图3为采用换流站双极并联运行线路倒闸方法时的仿真结果图。 具体实施方式 [0021]为使本发明实施例的目的、技术方案和优点更加清楚明白，下面结合附图对本发 明实施例做进一步详细说明。在此，本发明的示意性实施例及其说明用于解释本发明，但并 不作为对本发明的限定。 [0022]图i为本发明实施例中换流站双极并联运行线路倒闸系统的电路图，如图i所示， 该系统包括:交流电源AC、负极换流站Mi、正极换流站M2、第一隔离开关Si、第二隔离开关S2、 第三隔离开关S3、第四隔离开关S4、负极接地极电抗Li和正极接地极电抗L2,其中， [0023] 交流电源AC的输出端连接负极换流站Mi和正极换流站M2； [0024]负极换流站Mi的上桥臂出线经负极接地极电抗Li、第一隔离开关Si接地； [0025] 正极换流站M2的下桥臂出线经正极接地极电抗L2接地； [0026]负极换流站Mi的下桥臂出线上设有第二隔离开关S2； [0027]第三隔离开关S3的一端连接负极换流站Mi的上桥臂出线，另一端连接负极换流站 Mi的下桥臂出线； [0028]第四隔离开关S4的一端连接正极换流站M2的上桥臂出线，另一端连接负极换流站 Mi的上桥臂出线。 [0029] 在一实施例中，负极换流站Mi可以包括3个相单元X；正极换流站M2包括3个相单元 X； [0030] 每一相单元X包括上桥臂Q和下桥臂W； [0031]上桥臂Q包括串联的一个桥臂电抗Larm、一个桥臂电阻Rarm和多个模块化多电平换 流器子模块； [0032]下桥臂W包括串联的一个桥臂电抗Larm、一个桥臂电阻Rarm和多个模块化多电平换 流器子模块。 [0033]在一实施例中，模块化多电平换流器子模块可以包括：第一IGBT开关管T1、第二 IGBT开关管T2、第一二极管D1、第二二极管D2和电容Ci,其中， [0034]第一IGBT开关管Ti的发射极E为模块化多电平换流器子模块的电流输入端，与第 二IGBT开关管T2的集电极C连接； [0035]第二IGBT开关管T2的发射极E为模块化多电平换流器子模块的电流输出端； [0036]第一二极管Di的正极连接第一IGBT开关管Ti的发射极E,第一二极管Di的负极连接 第一IGBT开关管Ti的集电极C； [0037]第二二极管D2的正极连接第二IGBT开关管T2的发射极E,第二二极管D2的负极连接 第二IGBT开关管T2的集电极C； [0038]电容Ci的一端连接第一IGBT开关管Ti的集电极C,另一端连接第二IGBT开关管T2的 发射极E。 [0039] 在一实施例中，该系统还可以包括第一变压器漏电抗Lti和第二变压器漏电抗Lt2, 其中, [0040] 交流电源AC的输出端通过第一变压器漏电抗Lti连接负极换流站Mi； [0041] 交流电源AC的输出端通过第二变压器漏电抗Lt2连接正极换流站M2。 [0042] 在一实施例中，该系统还可以包括:第一直流断路器DCCBi、第二直流断路器DCCB2、 第一直流侧平波电抗器LdCi和第二直流侧平波电抗器LdC2,其中， [0043] 负极换流站Mi的下桥臂出线经第一直流断路器DCCBi连接第一直流侧平波电抗器 Ldci,第一直流侧平波电抗器Ldci连接输电线路； [0044] 正极换流站M2的上桥臂出线经第二直流断路器DCCB2连接第二直流侧平波电抗器 LdC2,第二直流侧平波电抗器LdC2连接输电线路。 [0045]图2为本发明实施例提出的换流站双极并联运行线路倒闸方法的流程图，如图2所 示，该方法应用于上述换流站双极并联运行线路倒闸系统，包括： [0046]步骤20i,将负极换流站Mi的输出有功功率值降为零，断开第一隔离开关Si和第二 隔离开关S2； [0047]步骤202，若负极换流站Mi和正极换流站M2的内部无冲击电流，闭合第三隔离开关 S3； [0048] 步骤203,将负极换流站Mi的控制方式切换为定直流电压控制，调整负极换流站Mi 的上桥臂出线对地电压的值为正极换流站M2的上桥臂出线对地电压的值； [0049]步骤204，闭合第四隔离开关S4,切换负极换流站Mi的控制方式为定有功功率控制, 将负极换流站Mi的输出有功功率值提升至正常运行时的有功功率值。 [0050]具体实施时，在步骤20i中，将负极换流站Mi的输出有功功率值降为零，等待该输 出有功功率稳定到零后，第一隔离开关Si和第二隔离开关S2两端的电压和流过这两个隔离 开关的电流基本为零，此时断开第一隔离开关Si和第二隔离开关S2； [0051] 在步骤202中，若负极换流站Mi和正极换流站M2的内部无冲击电流，闭合第三隔离 开关S3,使得负极换流站Mi的下桥臂出线对地电压的值Udclnn为零，而正极换流站M2的上桥臂 出线对地电压的值达到额定电压值左右； [0052] 在步骤203中，将负极换流站Mi的控制方式切换为定直流电压控制，调整负极换流 站Mi的上桥臂出线对地电压的值为正极换流站M2的上桥臂出线对地电压的值，其中，定直流 电压控制的控制目标是将负极换流站Mi中的模块化多电平换流器子模块的直流电压控制 在其额定值附近。 [0053]在步骤204中，闭合第四隔离开关S4,切换负极换流站Mi的控制方式为定有功功率 控制，将负极换流站Mi的输出有功功率值提升至正常运行时的有功功率值，即实现了双极 并联运行，此时正极换流站M2的上桥臂出现电流增加，实现对覆冰电路的融冰。 [0054]如图2所示，在本发明实施例中，将负极换流站Mi的输出有功功率值提升至正常运 行时的有功功率值，此时正极换流站M2的上桥臂出线电流增加，实现对覆冰电路的融冰。本 发明实施例中采用四个隔离开关进行融冰的方法，与现有技术中采用断路器进行融冰的方 法相比，四个隔离开关的成本低于断路器的成本，从而降低了融冰的成本。 [0055]下面给出一具体实施例，说明本发明实施例中的换流站双极并联运行线路倒闸方 法的具体应用。 [0056]本实施例以康宝换流站为例，图3为采用换流站双极并联运行线路倒闸方法时的 仿真结果图，结合图3,在第2s时，将负极换流站Mi的输出有功功率值降为零，此时负极换流 站的上桥臂出线电流Ii开始下降到零值;在第2.5时，断开第一隔离开关Si和第二隔离开关 S2,之后负极换流站Mi和正极换流站M2的内部无冲击电流，且负极换流站Mi的上桥臂出线对 地电压Udclnp和负极换流站Mi的下桥臂出线对地电压Udclnn开始上升;在第2.7s时，闭合第三 隔离开关S3,使得负极换流站Mi的下桥臂出线对地电压的值Udclnn为零，而正极换流站M2的上 桥臂出线对地电压的值达到额定电压值左右；在第2.8s时，将负极换流站Mi的控制方式切 换为定直流电压控制，调整负极换流站Mi的上桥臂出线对地电压Udclnp的值为正极换流站M2 的上桥臂出线对地电压的值;在第3.3s时，闭合第四隔离开关S4；在第3.4s时，切换负极换 流站Mi的控制方式为定有功功率控制；在第3.4s之后,将负极换流站Mi的输出有功功率值提 升至正常运行时的有功功率值，从图3中可以看到，正极换流站M2的上桥臂出线电流I2从第 3.7s之后开始增加，从而可以实现对覆冰电路的融冰。 [0057]综上所述，在本发明实施例中，将负极换流站Mi的输出有功功率值降为零，断开第 一隔离开关Si和第二隔离开关S2；若负极换流站Mi和正极换流站M2的内部无冲击电流，闭合 第三隔离开关S3；将负极换流站Mi的控制方式切换为定直流电压控制，调整负极换流站Mi的 上桥臂出线对地电压的值为正极换流站M2的上桥臂出线对地电压的值；闭合第四隔离开关 S4,切换负极换流站Mi的控制方式为定有功功率控制，将负极换流站Mi的输出有功功率值提 升至正常运行时的有功功率值，此时正极换流站M2的上桥臂出线电流增加，实现对覆冰电 路的融冰。本发明实施例中采用四个隔离开关进行融冰的方法，与现有技术中采用断路器 进行融冰的方法相比，四个隔离开关的成本低于断路器的成本，从而降低了融冰的成本。 [0058]以上所述的具体实施例，对本发明的目的、技术方案和有益效果进行了进一步详 细说明，所应理解的是，以上所述仅为本发明的具体实施例而已，并不用于限定本发明的保 护范围，凡在本发明的精神和原则之内，所做的任何修改、等同替换、改进等，均应包含在本 发明的保护范围之内。 [EN CN109687498B]: Technical field of switching system and method for bipolar parallel operation line of converter station [0001] The present invention relates to the technical field of line ice melting in power systems, and in particular to a system and method for realizing line ice melting by switching the bipolar parallel operation line of a converter station. Background technique [0002] Ice and snow disasters will cause excessive ice coating on overhead lines, resulting in a sharp decline in the mechanical and electrical performance of the lines, which will lead to the collapse of power transmission towers, power supply interruption and other hazards, severely threaten the safe and reliable operation of the power grid, and cause huge economic losses . Therefore, it is very necessary to melt ice on ice-coated transmission lines. [0003] At present, deicing methods for power transmission lines mainly include thermal deicing, mechanical deicing, and natural passive deicing. Among them, thermal deicing has the advantages of simple operation and easy implementation, and is a commonly used melting in high-voltage direct current transmission projects. The ice method, bipolar parallel ice melting is a thermal ice melting method. When the MMC (Modular Multilevel Converter) converter station performs bipolar parallel ice melting, internal circuit breakers are often used. Method, but the cost of this method is higher. Summary of the invention [0004] The embodiment of the present invention provides a bipolar parallel operation line switching system of a converter station, which is used to realize the ice melting of the bipolar parallel operation line of the converter station, and the ice melting cost is low. The system includes: AC power supply, AC, The negative converter station M1, the positive converter station M2, the first isolating switch S1, the second isolating switch S2, the third isolating switch S3, the fourth isolating switch S4, the negative grounding electrode reactance L1 and the positive grounding electrode reactance L2, of which, [0005] The output end of the AC power supply AC is connected to the negative converter station M1 and the positive converter station M2; [0006] The outgoing line of the upper bridge arm of the negative converter station M1 is grounded through the negative grounding electrode reactance L1 and the first isolating switch S1; [0007] The outgoing line of the lower bridge arm of the positive converter station M2 is grounded via the positive grounding electrode reactance L2; [0008] A second isolating switch S2 is provided on the outgoing line of the lower bridge arm of the negative converter station M1; [0009] One end of the third isolating switch S3 is connected to the outlet of the upper bridge arm of the negative converter station M1, and the other end is connected to the outlet of the lower bridge arm of the negative converter station M1; [0010] One end of the fourth isolation switch S4 is connected to the upper bridge arm outlet of the positive converter station M2, and the other end is connected to the upper bridge arm outlet of the negative converter station M1. [0011] The embodiment of the present invention provides a method for switching the bipolar parallel operation line of a converter station, which is applied to the above-mentioned bipolar parallel operation line switching system of a converter station to realize the bipolar parallel operation line of the converter station Melting ice, and the cost of melting ice is low, including: [0012] The output active power value of the negative converter station M1 is reduced to zero, and the first isolating switch S1 and the second isolating switch are disconnected S2; [0013] If there is no inrush current inside the negative converter station M1 and the positive converter station M2, close the third isolating switch S3; [0014] Switch the control mode of the negative converter station M1 to constant DC voltage control, and adjust the voltage of the upper bridge arm of the negative converter station M1 to the ground voltage of the upper bridge arm of the positive converter station M2. value; [0015] The fourth isolation switch S4 is closed, and the control mode of the negative converter station M1 is switched to constant active power control, and the output active power value of the negative converter station M1 is increased to the active power value during normal operation. [0016] In the embodiment of the present invention, the output active power value of the negative converter station Mi is reduced to zero, and the first isolating switch Si and the second isolating switch S2 are disconnected; if the negative converter station Mi and the positive converter station There is no inrush current inside M2, close the third isolating switch S3; switch the control mode of the negative converter station Mi to constant DC voltage control, and adjust the voltage of the upper bridge arm of the negative converter station Mi to ground voltage to the positive converter The value of the ground voltage of the upper bridge arm of station M2; close the fourth isolating switch S4, switch the control mode of the negative converter station Mi to constant active power control, and increase the output active power value of the negative converter station Mi to normal operation At this time, the current of the upper bridge arm of the positive converter station M2 increases to realize the ice melting of the ice-coated circuit. The method of using four isolating switches to melt ice in the embodiment of the present invention reduces the cost of ice melting compared with the method of using a circuit breaker to melt ice in the prior art. Description of the drawings [0017] In order to more clearly describe the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the drawings that need to be used in the description of the embodiments or the prior art. Obviously, in the following description The drawings are merely some embodiments of the present invention. For those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative work. In the attached picture: [0018] Figure i is a circuit diagram of a bipolar parallel operation line switching system of a converter station in an embodiment of the present invention; [0019] FIG. 2 is a flowchart of a method for switching off a line in a bipolar parallel operation of a converter station according to an embodiment of the present invention; [0020] FIG. 3 is a diagram of the simulation results when the bipolar parallel operation line switching method of the converter station is adopted. detailed description [0021] In order to make the objectives, technical solutions, and advantages of the embodiments of the present invention clearer, the following describes the embodiments of the present invention in further detail with reference to the accompanying drawings. Here, the exemplary embodiments of the present invention and the description thereof are used to explain the present invention, but not as a limitation to the present invention. [0022] Figure i is a circuit diagram of the bipolar parallel operation line switching system of a converter station in an embodiment of the present invention. As shown in Figure i, the system includes: AC power supply AC, negative converter station Mi, positive converter station M2 , The first isolating switch Si, the second isolating switch S2, the third isolating switch S3, the fourth isolating switch S4, the negative grounding electrode reactance Li and the positive grounding electrode reactance L2, where [0023] the output terminal of the AC power supply AC is connected to the negative electrode Converter station Mi and positive converter station M2; [0024] The outgoing line of the upper bridge arm of the negative converter station Mi is grounded via the negative grounding electrode reactance Li and the first isolating switch Si; [0025] The outgoing line of the lower bridge arm of the positive converter station M2 is grounded via the positive grounding electrode reactance L2; [0026] A second isolating switch S2 is provided on the outgoing line of the lower bridge arm of the negative converter station Mi; [0027] One end of the third isolating switch S3 is connected to the outlet of the upper bridge arm of the negative converter station Mi, and the other end is connected to the outlet of the lower bridge arm of the negative converter station Mi; [0028] One end of the fourth isolation switch S4 is connected to the upper bridge arm outlet of the positive converter station M2, and the other end is connected to the upper bridge arm outlet of the negative converter station Mi. [0029] In an embodiment, the negative converter station Mi may include three phase units X; the positive converter station M2 includes three phase units X; [0030] Each phase unit X includes an upper bridge arm Q and a lower bridge arm W; [0031] The upper bridge arm Q includes a bridge arm reactance Larm, a bridge arm resistance Ram and a plurality of modular multi-level converter sub-modules connected in series; [0032] The lower bridge arm W includes a bridge arm reactance Larm, a bridge arm resistance Larm and multiple modular multilevel converters connected in series. Streamer sub-module. [0033] In an embodiment, the modular multi-level converter sub-module may include: a first IGBT switch tube T1, a second IGBT switch tube T2, a first diode D1, a second diode D2, and Capacitance Ci, where, [0034] The emitter E of the first IGBT switch tube Ti is the current input end of the modular multilevel converter sub-module, and is connected to the collector C of the second IGBT switch tube T2; [0035] The emitter E of the second IGBT switch tube T2 is the current output end of the modular multi-level converter sub-module; [0036] The anode of the first diode Di is connected to the emitter E of the first IGBT switch tube Ti, and the cathode of the first diode Di is connected to the collector C of the first IGBT switch tube Ti; [0037] The anode of the second diode D2 is connected to the emitter E of the second IGBT switch tube T2, and the cathode of the second diode D2 is connected to the collector C of the second IGBT switch tube T2; [0038] One end of the capacitor Ci is connected to the collector C of the first IGBT switch tube Ti, and the other end is connected to the emitter E of the second IGBT switch tube T2. [0039] In an embodiment, the system may further include a first transformer leakage reactance Lti and a second transformer leakage reactance Lt2, where, [0040] The output end of the AC power supply AC is connected to the negative converter station Mi through the first transformer leakage reactance Lti; [0041] The output end of the AC power source AC is connected to the positive converter station M2 through the second transformer leakage reactance Lt2. [0042] In an embodiment, the system may further include: a first DC circuit breaker DCCBi, a second DC circuit breaker DCCB2, a first DC side smoothing reactor LdCi, and a second DC side smoothing reactor LdC2 ,among them, [0043] The outgoing line of the lower bridge arm of the negative converter station Mi is connected to the first DC side smoothing reactor via the first DC circuit breaker DCCBi Ldci, the first DC side smoothing reactor Ldci is connected to the transmission line; [0044] The upper bridge arm outgoing line of the positive converter station M2 is connected to the second DC side smoothing reactor via the second DC circuit breaker DCCB2 LdC2, the second DC side smoothing reactor LdC2 is connected to the transmission line. [0045] FIG. 2 is a flowchart of a method for switching a line in a bipolar parallel operation of a converter station according to an embodiment of the present invention. As shown in FIG. 2, the method is applied to the above-mentioned switching system of a line in the bipolar parallel operation of a converter station, include: [0046] Step 20i, the output active power value of the negative converter station Mi is reduced to zero, and the first isolating switch Si and the second isolating switch S2 are disconnected; [0047] Step 202, if there is no inrush current inside the negative converter station Mi and the positive converter station M2, close the third isolating switch S3; [0048] Step 203: Switch the control mode of the negative converter station Mi to constant DC voltage control, and adjust the voltage of the upper bridge arm of the negative converter station Mi to the ground voltage to the value of the upper bridge arm outlet pair of the positive converter station M2 The value of ground voltage; [0049] Step 204, close the fourth isolation switch S4, switch the control mode of the negative converter station Mi to constant active power control, and increase the output active power value of the negative converter station Mi to the active power value during normal operation. [0050] In specific implementation, in step 20i, the output active power value of the negative converter station Mi is reduced to zero, and after waiting for the output active power to stabilize to zero, the two ends of the first isolating switch Si and the second isolating switch S2 The voltage and the current flowing through the two isolation switches are basically zero, and the first isolation switch Si and the second isolation switch S2 are disconnected at this time; [0051] In step 202, if there is no inrush current inside the negative converter station Mi and the positive converter station M2, the third isolating switch S3 is closed, so that the voltage Udclnn of the lower bridge arm of the negative converter station Mi to ground is Udclnn Is zero, and the value of the ground voltage of the upper bridge arm of the positive converter station M2 reaches about the rated voltage; [0052] In step 203, the control mode of the negative converter station Mi is switched to constant DC voltage control, and the negative commutation is adjusted. The value of the outgoing line-to-ground voltage of the upper bridge arm of station Mi is the value of the outgoing line-to-ground voltage value of the upper bridge arm of the positive converter station M2. The control objective of the constant DC voltage control is to increase the modularity of the negative converter station Mi. The DC voltage of the level converter sub-module is controlled near its rated value. [0053] In step 204, the fourth isolating switch S4 is closed, the control mode of switching the negative converter station Mi is constant active power control, and the output active power value of the negative converter station Mi is increased to the active power value during normal operation. , That is, bipolar parallel operation is realized. At this time, the current increases in the upper bridge arm of the positive converter station M2, which realizes the ice melting of the ice-coated circuit. [0054] As shown in FIG. 2, in the embodiment of the present invention, the output active power value of the negative converter station Mi is increased to the active power value during normal operation. At this time, the outgoing current of the upper bridge arm of the positive converter station M2 Increased to realize the melting of ice on the icing circuit. In the embodiment of the present invention, the method of using four isolating switches to melt ice is compared with the method of using a circuit breaker to melt ice in the prior art. The cost of the four isolating switches is lower than that of the circuit breaker, thereby reducing ice melting. the cost of. [0055] A specific embodiment is given below to illustrate the specific application of the switching method for the bipolar parallel operation line of the converter station in the embodiment of the present invention. [0056] This embodiment takes the Kangbao converter station as an example. FIG. 3 is a simulation result diagram when the bipolar parallel operation line switching method of the converter station is adopted. In combination with FIG. 3, in the second second, the negative pole converter station Mi The output active power value drops to zero. At this time, the outgoing current Ii of the upper bridge arm of the negative converter station begins to drop to zero; at 2.5th, the first isolating switch Si and the second isolating switch S2 are disconnected, and then the negative commutation There is no inrush current inside the station Mi and the positive converter station M2, and the voltage Udclnp of the upper leg of the negative converter station Mi and the voltage Udclnn of the lower leg of the negative converter station Mi start to rise; in section 2.7 At s, the third isolating switch S3 is closed, so that the value Udclnn of the outgoing line to ground of the lower leg of the negative converter station Mi is zero, and the value of the outgoing voltage to ground of the upper leg of the positive converter station M2 reaches the rated voltage value Left and right; at 2.8s, switch the control mode of the negative converter station Mi to constant DC voltage control, and adjust the voltage Udclnp of the upper bridge arm of the negative converter station Mi to the upper bridge of the positive converter station M2 The value of the voltage of the arm outgoing line to ground; in the 3.3s, the fourth isolating switch S4 is closed; in the 3.4s, the control mode of the negative converter station Mi is switched to constant active power control; after the 3.4s, the negative The output active power value of the converter station Mi is increased to the active power value during normal operation. It can be seen from Figure 3 that the outgoing current I2 of the upper bridge arm of the positive converter station M2 is from the first It starts to increase after 3.7s, so that the ice can be melted on the icing circuit. [0057] In summary, in the embodiment of the present invention, the output active power value of the negative converter station Mi is reduced to zero, and the first isolating switch Si and the second isolating switch S2 are disconnected; if the negative converter station Mi There is no impulse current inside the positive converter station M2, close the third isolating switch S3; switch the control mode of the negative converter station Mi to constant DC voltage control, and adjust the voltage of the upper bridge arm of the negative converter station Mi to ground The value is the value of the voltage to the ground of the upper bridge arm of the positive converter station M2; close the fourth isolating switch S4, switch the control mode of the negative converter station Mi to constant active power control, and change the output active power of the negative converter station Mi The value is increased to the active power value during normal operation. At this time, the outgoing current of the upper bridge arm of the positive converter station M2 increases to realize the ice melting of the ice-coated circuit. In the embodiment of the present invention, the method of using four isolating switches to melt ice is compared with the method of using a circuit breaker to melt ice in the prior art. The cost of the four isolating switches is lower than that of the circuit breaker, thereby reducing ice melting. the cost of. [0058] The specific embodiments described above further describe the purpose, technical solutions and beneficial effects of the present invention in further detail. It should be understood that the above descriptions are only specific embodiments of the present invention and are not intended to limit The protection scope of the present invention, any modification, equivalent replacement, improvement, etc., made within the spirit and principle of the present invention shall be included in the protection scope of the present invention.
[EN US10978948B2]: Interleaved multi-channel, multi-level, multi-quadrant DC-DC converters [FR WO2015108613A1]: CONVERTISSEURS CC-CC À PLUSIEURS CANAUX, À PLUSIEURS NIVEAUX, À PLUSIEURS QUADRANTS ENTRELACÉS | [EN US10978948B2]: Direct-current-to-direct-current (DC-DC) power converters that include two or more multi-quadrant, multi-level, DC-DC, switching converter subcircuits, connected in parallel at respective input and output sides, so as to provide a multi-channel, multi-quadrant, multi-level configuration, are disclosed. The DC-DC power converters further include a control circuit configured to control the switching converter subcircuits so that corresponding switching semiconductors in each of the switching converter subcircuits are switched in an interleaved manner. In some embodiments, each of the switching converter subcircuits is a three-level, neutral-point-clamped, four-quadrant DC-DC converter circuit. In other embodiments, each of the switching converter subcircuits is a three-level, neutral-point-clamped, two-quadrant DC-DC converter circuit. In any of these embodiments, a filter capacitor may be connected between across a pair of output terminals at the output sides of the switching converter subcircuits. [FR WO2015108613A1]: L'invention concerne des convertisseurs de courant continu en courant continu (CC-CC) qui comprennent au moins deux sous-circuits de convertisseur de commutation CC-CC à plusieurs quadrants et à plusieurs niveaux raccordés en parallèle aux côtés d'entrée et de sortie respectifs de sorte à donner une configuration à plusieurs canaux, à plusieurs quadrants et à plusieurs niveaux. Les convertisseurs CC-CC comprennent en outre un circuit de commande configuré pour commander les sous-circuits de convertisseur de commutation de telle sorte que des semi-conducteurs de commutation correspondants dans chaque sous-circuit de convertisseur de commutation soient commutés de manière entrelacée. Selon certains modes de réalisation, chaque sous-circuit de convertisseur de commutation est un circuit de convertisseur CC-CC clampé par le neutre à trois niveaux et à quatre quadrants. Selon d'autres modes de réalisation, chaque sous-circuit de convertisseur de commutation est un circuit de convertisseur CC-CC clampé par le neutre à trois niveaux et à deux quadrants. Selon l'un quelconque de ces modes de réalisation, un condensateur de filtrage peut être raccordé entre une paire de bornes de sortie au niveau des côtés de sortie des sous-circuits de convertisseur de commutation. | WO2015108613A1 | 2015-07-23 | US2014065702W | 2014-11-14 | US201461927776P, 2014-01-15 | WO2015108613A1: 2015-07-23 US10978948B2: 2021-04-13 | ABB TECHNOLOGY AG DU YU AELOIZA EDDY BURGOS ROLANDO ABB INC ABB SCHWEIZ AG | DU YU AELOIZA EDDY BURGOS ROLANDO BURGUS ROLANDO | H02M7/487: I H02M1/00: N H02M3/158: N H02M3/158: I H02M1/08: I H02M1/14: I | H02M3/1584: I H02M7/487: I H02M1/0064: A H02M1/0074: A H02M3/1586: A H02M1/08: I H02M1/14: I H02M3/158: I H02M1/0009: A | US2013003424A1 US2011187369A1 EP2677650A1 US4384321A US2009066307A1 WO0217469A1 US5784269A US6545450B1 US2008304300A1 US2009196764A1 US2013099767A1 US2016211749A1 | US10886851B1 US10886851 10886851 FR3043285A1 FR3043285 3043285 CN108604862A CN108604862 108604862 US10749442B2 US10749442 10749442 DE102016200473A1 DE102016200473 102016200473 US10181802B2 US10181802 10181802 CN110875683A CN110875683 110875683 CN112039348A CN112039348 112039348 WO2021050163A1 WO2021050163 2021/050163 WO2021/050163A1 WO2019066929A1 WO2019066929 2019/066929 WO2019/066929A1 US10186950B2 US10186950 10186950 US2018234008A1 US2018234008 20180234008 US10348209B2 US10348209 10348209 US10439516B2 US10439516 10439516 US2018159441A1 US2018159441 20180159441 US20180159441A1 US10833603B2 US10833603 10833603 US10924031B2 US10924031 10924031 US10848067B2 US10848067 10848067 US2018136678A1 US2018136678 20180136678 US9680395B2 US9680395 09680395 US09680395B2 US2016118910A1 US2016118910 20160118910 US20160118910A1 US9985524B2 US9985524 09985524 US09985524B2 US2016211749A1 US2016211749 20160211749 US9906183B1 US9906183 09906183 US2019058411A1 US2019058411 20190058411 US20190058411A1 US10601339B2 US10601339 10601339 US10886852B2 US10886852 10886852 US10050531B1 US10050531 10050531 WO2020041602A1 WO2020041602 2020/041602 WO2020/041602A1 US10944335B2 US10944335 10944335 US9800175B2 US9800175 09800175 US09800175B2 US2017012554A1 US2017012554 20170012554 US20170012554A1 US10536099B2 US10536099 10536099 WO2020263290A1 WO2020263290 2020/263290 WO2020/263290A1 US2019052177A1 US2019052177 20190052177 US20190052177A1 US2017201170A1 US2017201170 20170201170 US2019363644A1 US2019363644 US20190363644A1 CN108075653A CN108075653 108075653 EP3352353A1 EP3352353 3352353 US11108230B2 US11108230 11108230 US9878635B1 US9878635 09878635 US09878635B1 US10447174B1 US10447174 10447174 | [EN US10978948B2]: 1. A direct-current-to-direct-current (DC-DC) power converter, comprising: two or more multi-quadrant, multi-level, DC-DC, switching converter subcircuits, each switching converter subcircuit including a switching assembly including a plurality of phases, the switching converter subcircuits connected in parallel at respective input and output sides, each of the respective input sides being connected to a common DC input voltage source including three or more DC voltage levels, so as to provide a multi-channel, multi-quadrant, multi-level configuration; anda control circuit configured to selectively control one or more switching semiconductor devices of the switching assembly in each phase of the switching converter subcircuits by transmitting one control signal of a plurality of control signals to each phase of each switching converter subcircuit,wherein each control signal of the plurality of control signals includes a duty cycle such that each phase of each of the switching converter subcircuit operates using the duty cycle in an interleaved manner to reduce at least one of input side ripple current and output side ripple current. 2. The DC-DC power converter of claim 1, wherein each of the switching converter subcircuits comprises a three-level, neutral-point-clamped, four-quadrant DC-DC converter circuit. 3. The DC-DC power converter of claim 1, wherein each of the switching converter subcircuits comprises a three-level, neutral-point-clamped, two-quadrant DC-DC converter circuit. 4. The DC-DC power converter of claim 1, wherein the the plurality of control signals of the switching converter subcircuits is separated by a phase angle of 2π/N, where N denotes a number of the two or more multi-quadrant, multi-level, DC-DC, switching converter subcircuits. 5. The DC-DC power converter of claim 1 wherein the plurality of control signals provides interleaved operation of the two or more switching converter subcircuits connected in parallel to provide an increased effective switching frequency relative to a switching frequency applied to a single one of the switching converter subcircuits. 6. The DC-DC power converter of claim 1 wherein the plurality of control signals provides interleaved operation of the two or more switching converter subcircuits connected in parallel to effectively increase at least one of input current ripple frequency and output current ripple frequency. 7. The DC-DC power converter of claim 1, wherein each of the switching converter subcircuits comprises: the switching assembly having a first side and a second side, the first side having three or more terminals configured for connecting to a multi-level DC interface and the second side having a pair of terminals configured for coupling to a two-level DC interface; andan inductor assembly comprising first and second inductors and connected to the switching assembly so that each terminal of the pair terminals on the second side of the switching is connected to a corresponding first end of a different one of the first and second inductors. 8. The DC-DC power converter of claim 7, further comprising a filter capacitor connected across a pair of output terminals at the output sides of the switching converter subcircuits. 9. The DC-DC power converter of claim 1, wherein each of the switching converter subcircuits comprises: the switching assembly having a first side and a second side, the first side having three or more terminals configured for connecting to a multi-level DC interface and the second side having first and second terminals configured for coupling to a two-level DC interface; andfirst and second inductors coupled to one another, each having a first and second end, wherein the first end of the first inductor is connected to the first terminal of the switching assembly and the first end of the second inductor is connected to the second terminal of the switching assembly. 10. The DC-DC power converter of claim 9, wherein a coupling coefficient between the first and second inductors is about 0.5. 11. The DC-DC power converter of claim 9, wherein a coupling coefficient between the first and second inductors is between about 0.3 and about 0.7. 12. The DC-DC power converter of claim 9, wherein the first and second inductors are coupled to one another and to one or more additional inductors via a common core structure. 13. The DC-DC power converter of claim 9, wherein the first and second inductors comprise well-coupled windings of a transformer. 14. The DC-DC power converter of claim 9, wherein each of the switching converter subcircuits is a separate, self-contained module. 15. A direct-current-to-direct-current (DC-DC) power converter, comprising: two or more DC-DC, switching converter subcircuits, connected in parallel at respective input and output sides; anda control circuit configured to selectively control each of the switching converter subcircuits;wherein each of the switching converter subcircuits comprises:a switching assembly including a first phase and a second phase each coupled between a first side and a second side, the first phase including two semiconductor devices coupled at a first output terminal, the second phase including two semiconductor devices coupled at a second output terminal, the first side having three or more terminals configured for connecting to a first DC interface including three or more DC voltage levels providing a multi-level converter topology; andfirst and second inductors magnetically coupled to one another, each having a first and second end, wherein the first end of the first inductor is connected to the first output terminal, the second end of the first inductor is connected to a positive DC bus, the first end of the second inductor is connected to the second output terminal, and the second end of the second inductor is coupled to a negative DC bus. 16. The DC-DC power converter of claim 15, wherein a coupling coefficient between the first and second inductors is about 0.5. 17. The DC-DC power converter of claim 15, wherein a coupling coefficient between the first and second inductors is between about 0.3 and about 0.7. 18. The DC-DC power converter of claim 15, wherein the first and second inductors are coupled to one another and to one or more additional inductors via a common core structure. 19. The DC-DC power converter of claim 15, wherein each of the switching converter subcircuits is a separate, self-contained module. | [EN US10978948B2]: U.S. GOVERNMENT RIGHTS This invention was made with Government support under ARPA-E Cooperative Agreement DE-AR0000141 awarded by the Department of Energy (DOE). The Government has certain rights in this invention. TECHNICAL FIELD The present disclosure relates to DC-to-DC converters for use in electric distribution systems. BACKGROUND In the electric power industry, direct-current (DC) distribution systems, DC energy sources such as photovoltaic (PV) panels and fuel cells, and DC-based energy storage systems are of increasing systems. In each of these technology areas, improved DC-DC converters, with the capability to handle high voltages and high currents are needed. SUMMARY Embodiments of the present invention are based on the parallel connection and interleaving of multiple multi-level, multi-quadrant, DC-DC converters. Because these converter systems can provide bidirectional current flow and/or bipolar output voltages, they can be used to couple a DC grid or an AC-DC converter output to a wide range of DC loads and energy sources, such as passive loads in a DC distribution system, DC energy sources such as photovoltaic (PV) panels and fuel cells, DC energy storage systems such as batteries and super capacitors with two-quadrant current flow, superconducting magnetic energy storage (SEMS) coils with two-quadrant voltage polarity, and active loads such as DC motors with four-quadrant operation. Example embodiments of the present invention include a direct-current-to-direct-current (DC-DC) power converter that includes two or more multi-quadrant, multi-level, DC-DC, switching converter subcircuits, connected in parallel at respective input and output sides, so as to provide a multi-channel, multi-quadrant, multi-level configuration. The DC-DC power converter further includes a control circuit configured to control the switching converter subcircuits so that corresponding switching semiconductors in each of the switching converter subcircuits are switched in an interleaved manner. In some embodiments, each of the switching converter subcircuits includes a switching assembly having a first side and a second side, the first side having three or more terminals configured for connecting to a multi-level DC interface and the second side having a pair of terminals configured for coupling to a two-level DC interface, as well as an inductor assembly including first and second inductors and connected to the switching assembly so that that each terminal on the second side of the switching is connected to a corresponding first end of a different one of the first and second inductors. In some embodiments, each of the switching converter subcircuits is a three-level, neutral-point-clamped, four-quadrant DC-DC converter circuit. In other embodiments, each of the switching converter subcircuits is a three-level, neutral-point-clamped, two-quadrant DC-DC converter circuit. In any of these embodiments, a filter capacitor may be connected between across a pair of output terminals at the output sides of the switching converter subcircuits. In several embodiments, each of the switching converter subcircuits includes a switching assembly having a first side and a second side, the first side having three or more terminals configured for connecting to a multi-level DC interface and the second side having first and second terminals configured for coupling to a two-level DC interface, as well as a coupled inductor pair, comprising first and second inductors, each having a first and second end, where the first end of the first inductor is connected to the first terminal of the switching assembly and the first end of the second inductor is connected to the second terminal of the switching assembly. In some of these embodiments, the coupled inductor pair in each switching converter subcircuit has a coupling coefficient of about 0.5. In some of these embodiments, the coupled inductor pair can be implemented by two un-coupled inductors in series to a transformer with two well-coupled windings. In some of these embodiments, all the inductors can be coupled to a common core structure instead of coupled pairs. Those skilled in the art will recognize still further embodiments, as well as additional features and advantages of several of these embodiments, upon reading the following detailed description and upon viewing the accompanying drawings. BRIEF DESCRIPTION OF THE DRAWINGS The components in the figures are not necessarily to scale, instead emphasis being placed upon illustrating the principles of the invention. Moreover, in the figures, like reference numerals designate corresponding parts. In the drawings: FIG. 1 is a schematic diagram illustrating an example interleaved, multi-channel, multi-level, multi-quadrant, DC-DC converter, according to some embodiments of the present invention. FIG. 2 is a schematic diagram of an interleaved synchronous buck converter. FIG. 3 is a schematic diagram of an interleaved boost converter. FIG. 4 is a schematic diagram illustrating an interleaved bidirectional half-bridge converter. FIG. 5 illustrates an interleaved three-level buck converter. FIG. 6 is a schematic diagram of an interleaved three-level boost converter. FIG. 7 shows an interleaved, three-level, four-quadrant, DC-DC converter (voltage source type load with filter capacitor), according to some embodiments of the present invention. FIG. 8 shows an interleaved, three-level, four-quadrant, DC-DC converter (current source type load without filter capacitor), according to other embodiments of the present invention. FIG. 9 illustrates an example interleaved, three-level, voltage-two-quadrant, DC-DC converter. FIG. 10 shows an example interleaved, three-level, current-two-quadrant, DC-DC converter. FIG. 11 is a block diagram illustrating components of an example control circuit. FIG. 12 is a schematic diagram illustrating an interleaved, multi-channel, multi-level, DC-DC converter with coupled inductors. FIG. 13 shows an interleaved synchronous buck converter with inverse coupling. FIG. 14 illustrates an interleaved synchronous buck converter with direct coupling. FIG. 15 illustrates inductor coupling in pairs between phases A and B in each channel of an example embodiment. FIG. 16 shows a modularized DC-DC converter with coupled inductor pairs between phases A and B of another example embodiment. FIG. 17 shows a comparison of the sizes and losses for coupled and inductor pairs in a design example. FIG. 18 illustrates inductor coupling between channels in a multi-channel converter in another embodiment for the coupled inductors. FIG. 19 shows an interleaved 3-level, four-quadrant DC-DC converter with coupled inductor pairs between channels. FIGS. 20 and 21 illustrate a comparison of the inductor ripple current for two coupled inductor pair arrangements. FIG. 22 illustrates an example of peak-to-peak amplitude reduction and frequency multiplication of the total channel input current corresponding to the topology shown in FIG. 16 with 3 channels, 0.2 duty cycle, and 1800 A output current, resulting in smaller input filter capacitors. FIG. 23 illustrates an example of peak-to-peak amplitude reduction and frequency multiplication of the converter output voltage corresponding to the topology shown in FIG. 16 with a SMES coil (no filter capacitor), 3-channel modules, 0.278 duty cycle, 1800 V input and 500 V output voltage, resulting in reduced dv/dt on load or smaller output filter capacitors if needed. DETAILED DESCRIPTION In the claims and discussion that follow, terms such as “first”, “second”, and the like, are used to differentiate between several similar elements, regions, sections, etc., and are not intended to imply a particular order or priority unless the context clearly indicates otherwise. Furthermore, as used herein, the terms “having”, “containing”, “including”, “comprising” and the like are open-ended terms that indicate the presence of stated elements or features but that do not preclude additional elements or features. Likewise, the use of the singular articles “a”, “an” and “the” are not intended to preclude the presence of additional ones of the referenced item. Like terms refer to like elements throughout the description. DC-DC converters with the capability to handle high voltage and high currents are needed for such applications as coupling a DC grid or an AC-DC converter output to any of a wide range of DC loads and energy sources, such as a passive load in a DC distribution system, a DC energy source such as a photovoltaic (PV) panel or fuel cell array, a DC energy storage device such as batteries and super capacitors with two-quadrant current flow, superconducting magnetic energy storage (SEMS) coils with two-quadrant voltage polarity, and an active load such as DC motors with four-quadrant operation. As discussed in further detail below, previously used circuits do not provide the combination of high-voltage handling, high-current handling, and multi-quadrant operation that are required to satisfy this wide variety of applications. Embodiments of the present invention are based on the parallel connection and interleaving of multiple multi-level, multi-quadrant, DC-DC converters. Because these converter systems can provide bidirectional current flow and/or bipolar output voltages, the same circuit configuration can be used to couple a DC grid or a DC rectifier output to any of the loads or energy sources mentioned above. The DC-DC converters described in detail below combine multi-level, multi-quadrant converter subcircuits, in an interleaved fashion, to provide high-efficiency, high-power conversion systems while maintaining relatively low levels of voltage and current stresses on individual switching devices. The interleaving of these subcircuits reduces the magnitude of current ripple in DC-link capacitors and increases the effective switching frequency of the converter system, so that output voltage and/or current ripples, as well as capacitor sizes and costs, are reduced. The design of the converter systems is modular, allowing for easy scalability of the converters and the reduction of manufacturing and maintenance costs. An example power converter 100 according to this approach is pictured in FIG. 1, and includes a DC-link multi-level capacitor assembly 110, a multi-level, multi-quadrant, switch assembly 120 in each of several converter subcircuits 150, or “channels,” and an inductor assembly 130 in each converter subcircuit 150. The converter subcircuits are connected in parallel between the multi-level capacitor assembly 110 and a load or source with filter 160. Each switch assembly 120 is configured in a multi-level structure, such that the voltage rating of the power converter system 100 is increased. The switch assembly 120 contains a combination of actively controlled switches, such as MOSFETs, IGBTs, BJTs, Thyristors/SCRs, GTOs, IGCTs, etc., or a combination of active switches with passive switches, such as PiN diodes, schottky diodes, etc. The DC-link capacitor assembly 110 is configured to provide multiple voltage levels and has multiple corresponding terminals that are connected to the corresponding multi-level switch assembly structure. The inductor assembly 130 is used to reduce the circulating current among the different switch assemblies, as well as to limit the ripple current in each switch assembly 120 to a reasonable level. The inductors in the inductor assembly 130 can be either independent or coupled with each other. Since the power converter system 100 can provide bidirectional current flow, and/or bipolar the output voltage, the same circuit configuration can be applied to a wide range of DC loads and energy sources, for example, passive loads in DC distribution system, DC energy sources such as photovoltaic (PV) panels and fuel cells, all kinds of batteries and super capacitors with two-quadrant current flow, superconducting magnetic energy storage (SMES) coil with two-quadrant voltage polarity, and DC motors with four-quadrant operation. In the illustrated configuration, the several multi-level DC-DC converter subcircuits 150 are connected in parallel, which improves the current-handling capacity of the power converter 100 over that of a single converter subcircuit 150. The subcircuits, each of which includes one or more semiconductor switching devices, can also be operated in an interleaved fashion, to reduce both the input and the output current ripple, and the output voltage ripple if no filter capacitors are used. This means that the control signals (e.g., gate signals) for corresponding switches in each channel are shifted by some phase angle, e.g. 2π/N, where N is the number of converter channels, such that the input/output ripple current is reduced when the converter channels operate in coordination with one another. This interleaved operation also serves to increase the effective switching frequency, compared to the switching frequency applied to a single one of the subcircuits. The effect of this is to increase the ripple frequency, therefore allowing a reduction in the DC-link capacitor size and simplification and/or size reduction of the output filter. The converter configuration illustrated in FIG. 1 can be used to obtain several features and advantages. These features and advantages include high current capacity, high voltage capacity, small capacitor and inductor size, and higher switching frequencies, as well as higher power density. The illustrated converter configuration can also be readily realized with a modular and scalable structure, to reduce the converter system cost. The multi-channel configuration of the DC-DC converters increases the current rating of the converter system, via the use of paralleled channels. At the same time, the parallel structure of the converter enables the modular design of switch assemblies 120 and inductor assemblies 130, as well as the scalability of the current rating for different applications. The converter subcircuits 150 as a whole can be designed and manufactured in a modular manner, which simplifies the manufacturing and sourcing process and reduces the converter system cost. The current rating of the converter can be easily scaled by selecting the number of modular converter channels. The multi-level structure used in each channel allows high DC-link (input side) voltage, despite a wide voltage range and/or low voltage level of the load/source (output side). Employing the multi-level structure in each channel also reduces the voltage stress of inductors. In addition, much lower inductance is needed due to lower voltage stress, compared to the inductance that would be needed for a single-channel converter having the same voltage-handling and current-handling capabilities. The reduced inductor size helps to decrease the physical size of the inductor assembly. Likewise, lower voltage stress of the switches allows the use of faster power semiconductor devices with lower voltage ratings, and further allows switching at higher frequencies while still maintaining high power conversion efficiency. This helps to further improve the power density of the DC-DC converter system. Interleaving of multiple channels of DC-DC converters also reduces both the input and output current ripple significantly and, at the same time, increases the ripple frequency by a factor of N, where N is the number of interleaved channels. As a result, relatively small DC-link capacitors can be used in the input side, and a smaller filter can be used in the output side load/source. Interleaving technology has been previously proposed for basic DC-DC converters, including buck, boost, flyback, Ćuk, and single-ended primary-inductor (SEPIC) converters. It has been shown that the amplitude of the input/output current ripple of N (≥2) parallel interleaved modules is always less than or equal to that of the individual modules for these basic DC-DC converters, if the phase shift between the control signals applied among the modules is 2π/N. Interleaving of basic buck converters is widely used for low-voltage high-current applications. FIG. 2 illustrates an interleaved, two-channel, synchronous buck converter suitable for use in a computer CPU voltage-regulation module (VRM) application. In the illustrated circuit, low-side diodes have been replaced by MOSFETs working in synchronous rectification mode to improve the power conversion efficiency relative to a conventional buck converter where the low-side switch is a diode. Interleaved synchronous buck converters are also used in point-of-load applications such as mobile telephone. The use of coupled inductors to improve both the steady state and dynamic performance of voltage-regulating buck converters has also been described. Interleaving of basic multi-channel boost converters, as shown in FIG. 3, has also been used. Important applications of interleaved boost converters include fuel-cell electric vehicles, and photovoltaic power conversion chains. Coupled inductors may be used in interleaved boost converters to improve the converter performance, e.g., by increasing power density and reducing current ripple. An interleaved bi-directional half-bridge converter is shown in FIG. 4. Major applications are for battery or supercapacitor energy storage systems, and motor drives with regenerative braking. Stand-alone multi-level AC-DC rectifiers, DC-AC inverters, and DC-DC converters have been widely used. It should be appreciated that the term “multi-level converter” is a term of art that indicates that a voltage output is synthesized or an input voltage is sourced from three or more levels of DC capacitor voltages. Previously described three-level DC-DC converter configurations include a current-two-quadrant bidirectional DC-DC converter for ultracapacitor energy storage system, as well as a voltage-two-quadrant three-level DC-DC converter for superconducting magnetic energy storage (SMES) system. Three-level neutral point clamping inverter and five-level AC-DC rectifiers have also been described, as have multi-level AC-DC converters for power electronic transformer applications and for motor drive applications. An interleaved, one-quadrant, three-level, buck converter is shown in FIG. 5, while an interleaved, one-quadrant, three-level boost converter is shown in FIG. 6. An interleaved (two channel) three-level (DC-AC) inverter has also been disclosed, for use in hardware-in-loop simulation system for HVDC circuit breakers. In prior converter circuits, interleaving has only been used for basic DC-DC converters or two-level DC-DC converters, or one-quadrant three-level buck or boost converter. Multi-level, multi-quadrant, interleaved DC-DC converters have not previously been disclosed. FIG. 7 illustrates details of one embodiment of a DC-DC power converter having interleaved, multi-quadrant, multi-level, DC-DC switching converter subcircuits. Converter 700A includes a DC-link three-level capacitor assembly 710, a three-level, four-quadrant, switch assembly 720 in each of several converter subcircuits 750, and an inductor assembly 730 in each converter subcircuit 750. The converter subcircuits are connected in parallel between the multi-level capacitor assembly 710 and a load or source with filter 760. More particularly, the power converter 700A shown in FIG. 7 uses three-level, NPC (neutral-point-clamped), four-quadrant, DC-DC converter. Because the H-bridge configuration is used for each of the converter subcircuits 750 and active power semiconductor devices are used for the H-bridge, the converter 700A can process either bi-directional current (e.g., for a battery application), bipolar voltage output (e.g., for an SMES application), or both of them, i.e., as four-quadrant operation (e.g., for DC motors). Note that converter 700A includes a small filter capacitor 765, connected to the output, to configure the converter as a voltage source for the different types of loads or sources, which may include a resistive load, PV panels, fuel cells, batteries, super capacitors, SMES coil, DC motors, etc. FIG. 8 illustrates a variant of the power converter circuit shown in FIG. 7. Power converter 700B again includes three-level, NPC (neutral-point-clamped), interleaved, four-quadrant DC-DC converter subcircuits 750. In this case, however, there is no filter capacitor at the output. Rather, the outputs of the converter subcircuits 750 are connected directly to the source/load 770, which may be an SMES coil or DC motor, for example, thus making the output a current source. In another variant, illustrated in FIG. 9, the interleaved converter subcircuits 950 each include a three-level, voltage-two-quadrant, DC-DC converter 920. This configuration can be employed for SMES applications, where support for bipolar output voltages is required. Because the H-bridge configuration is used for each of the converter channels, a bi-polar voltage output can be obtained to charge and discharge the SMES coil. Only one-third of the power semiconductor devices in the H-bridge converter are active devices, in this configuration, while the rest are diodes, so the converter output current is uni-directional. Still another variation is shown in FIG. 10. In this case, the interleaved converter subcircuits 1050 each include a three-level current-two-quadrant DC-DC converter 1020. This configuration can be employed for battery-based energy-storage applications, for example. Since the output voltage polarity is unidirectional, an H-bridge or full-bridge configuration is not required, and a three-level half-bridge configuration is used. With active switches in the half-bridge, bi-directional current can be obtained to charge and discharge the battery 1060, which is shown with a filter capacitor 765 in FIG. 10. Connected to the switching elements in the circuits of FIGS. 1, 7, 8, 9, and 10, but not illustrated in those figures, are control circuits configured to drive control inputs of the active switching elements in the converter subcircuits. The control circuit providing these control signals can be an appropriately programmed microcontroller or Field-Programmable Gate Array (FPGA), or the like; an example of such a control circuit 1100 is shown in FIG. 11, which includes a microprocessor 1110, memory 1120, and digital/analog hardware circuit 1130. In the illustrated control circuit 1100, hardware circuit 1130 outputs a set of control voltages g1, g2, . . . , each of which corresponds to one or more switching elements in one of the step-down converter circuits described above. In the illustrated circuit, feedback from the converters is provided via the “VOLTAGE SENSE LINE(S),” to allow for controlling of the DC output from the corresponding converters, and “CURRENT SENSE LINE(S)” to allow balancing and control of the channel currents. Hardware 1130 thus may include one or more analog-to-digital (A/D) converters, in some embodiments, to convert the analog signals on the one or more voltage sense lines to digital signals suitable for use by microprocessor 1110. Of course, variants of the circuit illustrated in FIG. 11 may employ a microcontroller device that incorporates not only a processor element but that also includes one or more A/D converters, in which case A/D converters need not be provided in separate hardware. Microprocessor 1110 is configured, using program instructions stored in memory 1120, to pulse-width modulate the control inputs of the active switching elements of the converter subcircuits, according to known techniques applicable to the particular subconverter switching converter. Memory circuit 1120 may comprise one or several memory devices and/or memory types, such as flash memory or other non-volatile memory, random-access memory (RAM), read-only memory (ROM), etc. It will be appreciated that the control circuit shown in FIG. 11 is but one example of a circuit that can be adapted to control the power converter circuits disclosed herein. Other control circuits, including those that rely in whole or in part on analog feedback and control are also possible. In any case, the control circuit is configured so that the control inputs for the separate converter subcircuits are controlled such that corresponding switching semiconductors in each of the switching converter subcircuits are switched in an interleaved manner. For example, if there are three converter subcircuits connected in parallel, the control signals to the respective subcircuits should generally be 120 degrees out of phase with one another, with respect to the switching frequency, to balance the current-handling loads across the subcircuits. More generally, the control signals for each subcircuit should be separated by a phase angle of 2π/N, where N is the number of channels/subcircuits. It should be understood that the present invention is not limited to the particular circuit configurations illustrated in FIGS. 7, 8, 9, 10, and 11. Instead, these configurations should be understood to be examples of power converters that include two or more multi-quadrant, multi-level, DC-DC, switching converter subcircuits, connected in parallel at respective input and output sides, so as to provide a multi-channel, multi-quadrant, multi-level configuration, where the switching converter subcircuits are switched in an interleaved manner. While several of the pictured converter circuits include several multi-level, neutral-point-clamped converters, for example, other subcircuit topologies may be used instead, such as athe active neural-point-claimed topology, topologies using flying capacitors, etc. There is a wide range of applications for the multi-channel, multi-level, multi-quadrant, DC-DC converters described. A general application of these circuits is to connect a high current load or source, having a relatively low voltage, to a DC-link side that has a relatively high voltage rating, and to control the DC rating load or DC source. The DC-link side could be a DC grid system, or the DC terminals of an inverter or rectifier. One principle application is with superconducting magnetic energy storage (SMES) system. The interleaved multi-channel and multi-level DC-DC converter system connect the SMES coil to a grid-tied inverter. In this application, the SMES coil is used as the energy storage device for the grid to smooth the power fluctuations. The current rating of the high power and high energy SMES coil can be thousands of amperes. The voltage polarity of the coil is bidirectional, due to the charging and discharging operation, and the coil voltage varies in a very wide range for different power absorbed or injected to the grid. On the other hand, DC link of high power inverters has a higher voltage rating than that of SMES coil, and is constant. A multi-level, multi-channel, multi-quadrant DC-DC converter as disclosed herein can accommodate the large voltage difference between the DC link and the SMES coil, and also controls the voltage applied to the coil. In addition, the required current rating of the inverter is significantly reduced due to high AC and DC-link voltage such that conventional voltage source converter (VSC) can be used for this application. Multiple channels of DC-DC converters increase the current rating of the converter, whereas a single DC-DC converter cannot handle the SMES coil current with thousands of amperes. Interleaving technology reduces the current ripple amplitude significantly in both the input DC-link side and the output load/source side, which results in much smaller DC-link capacitor size and output filter size. Another principle application for the circuits disclosed herein is the PV farm. In addition to wind energy, solar energy is another important renewable energy source. Photovoltaic (PV) panel is the device to capture solar energy. One of the major issues for today's PV system is high capital cost. A large-scale solar farm, with thousands of PV panels, helps to reduce the specific cost of the system, but requires high-power central converters. The multi-channel, multi-level, multi-quadrant, DC-DC converters described above can be used to connect the large PV farm to the grid through an inverter. Such a converter can implement maximal power point tracking (MPPT) control, and reduces the ripple current of the panels, thus minimizing the size of the passive components. The modular design of these converters simplifies the manufacturers' product line and reduces both the manufacture and maintenance cost. Similarly to PV farm applications with unidirectional current and unipolar voltage source, the circuits can be used in fuel cell systems because the interleaved multi-quadrant, multi-channel and multi-level DC-DC converters can also operate in one quadrant. The fuel cell system can benefit from the low current ripple of the converter due to interleaving, which is important to extend the lifetime of fuel cells. The DC-DC converter systems can also be used for DC load with unidirectional current and unipolar voltage. Applications include electrochemical processes such as electrodialysis, electrolysis, and industrial processes where high DC current is required. Another important application for these circuits is the battery energy storage system (BESS) (and super capacitors as well), where voltage is unipolar but bidirectional current is required to charge and discharge the battery. The low battery pack voltage can be boosted up to the high DC-link voltage level by the DC-DC converter, and the charging and discharging of batteries is controlled by the converter. The large battery voltage variation due to the state-of-charge change is also tolerated by the DC-DC converter. The low ripple current helps to extend the battery lifetime. The BESS is used both in grid applications and in plug-in electric vehicle (PEV) applications. The DC-DC converters can also be used as fast chargers for electric vehicles, and for vehicle-to-grid (V2G) applications to support the distribution grid power quality. Still another principle application is the DC motor drive, where four-quadrant operation of the DC motors is satisfied. The DC-DC converter systems with H-bridge configuration in each channel enable bidirectional current flow and bidirectional voltage polarity for DC motors, such that they can rotate in both directions and the brake energy can be regenerated and captured through the DC-DC converter. Interleaving of the DC-DC converter channels can allow high motor current rating and in the meanwhile reduce the filter size. Multi-level converters allow the motor to be connected to medium-voltage level DC-grid through the DC-DC converter. Accordingly, the disclosed interleaved, multi-channel, multi-level, and multi-quadrant DC-DC converters can be used in DC grid system to manage various DC loads and sources, and to connect different DC grids and control the power flow. As detailed above, interleaved multi-level converters are good solutions for high power DC-DC conversion with high voltage rating, large and scalable current rating, and modular structure. Capacitor size can be significantly reduced by interleaving. However, the total energy storage requirement in inductors does not benefit from the interleaving. Phase inductors are required to control the current ripple in each converter channel and to mitigate the circulating current. With proper design, coupled inductors can be used to achieve similar current ripple amplitude but with smaller volume than that of uncoupled inductors. This is due to the cancelation of DC magnetic flux with coupled windings. The power loss of the coupled inductors is also lower than that with the uncoupled case. One analysis shows a 24% volume reduction and a 17% power loss reduction, making the converter more compact and efficient. Also, less core and copper materials are used, which helps reduce the cost of the coupled inductors. FIG. 12 shows a generalized structure of an interleaved, multi-channel, multi-level DC-DC converter 1200, including a coupled inductor assem
[EN EP3005519B1]: A MULTI MODULAR CONVERTER ARRANGEMENT FOR POWER COMPENSATION AND A METHOD FOR CONTROLLING A POWER CONVERTER [FR EP3005519B1]: AGENCEMENT DE CONVERTISSEUR MULIT MODULAIRE POUR UNE COMPENSATION DE PUISSANCE ET PROCÉDÉ POUR COMMANDER UN CONVERTISSEUR DE PUISSANCE [ZH CN105393423B]: 用于功率补偿的变换器装置以及用于控制功率变换器的方法 [DE EP3005519B1]: MULTI MODULAREWANDLERANORDNUNG FÜR LEISTUNGSKOMPENSATION UND VERFAHREN ZUR STEUERUNG EINES STROMWANDLERS [ES MX351604B]: UNA DISPOSICIÓN DE CONVERTIDOR PARA COMPENSACIÓN DE POTENCIA Y UN MÉTODO PARA CONTROLAR UN CONVERTIDOR DE POTENCIA. [PT BR112015030204A2]: disposição de conversor para compensação de potência e método para controlar um conversor de potência | [EN EP3005519B1]: A converter arrangement (1) and a method of controlling a three-phase converter arrangement connected to a transmission grid is provided. The converter arrangement (1) comprises three phase legs (10, 20, 30) and an energy transfer circuit (40). The method comprises providing a varying respective output phase (A, B, C) voltage to the transmission grid by selecting (206) energy storage elements (12A-n, 21A-n, 31A-n, 44) of both the phase legs (10, 20, 30) and the energy transfer circuit (40) and connecting (210) the selected energy storage elements (12A-n, 21A-n, 31A-n, 44) to the transmission grid output (15, 25, 35). The method further comprises selecting (208) energy storage elements (12A-n, 21A-n, 31A-n, 44) for performing a transfer of energy between the energy storage elements (12A-n, 21A-n, 31A-n, 44) during the control period. [FR EP3005519B1]: L'invention porte sur un agencement de convertisseur (1) et un procédé de commande d'un agencement de convertisseur à trois phases connecté à un réseau de transmission. L'agencement de convertisseur (1) comprend trois branches de phase (10, 20, 30) et un circuit de transfert d'énergie (40). Le procédé comprend la fourniture d'une tension de phase de sortie respective variante (A, B, C) au réseau de transmission par sélection (206) d'éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) des branches de phase (10, 20, 30) et du circuit de transfert d'énergie (40) et connexion (210) des éléments de stockage d'énergie sélectionnés (12A-n, 21A-n, 31A-n, 44) à la sortie de réseau de transmission (15, 25, 35). Le procédé comprend en outre la sélection (208) d'éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) pour réaliser un transfert d'énergie entre les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) durant la période de commande. [ZH CN105393423B]: 提供了种变换器装置(1)和种控制连接到输电网的三相变换器装置。变换器装置(1)包括三个相腿(10、20、30)和能量传输电路(40)。方法包括通过选择(206)相腿(10、20、30)和能量传输电路(40)的能量存储元件(12A‑n、21A‑n、31A‑n、44)提供变化的相应的输出相(A、B、C)电压至输电网，以及将所选择的能量存储元件(12A‑n、21A‑n、31A‑n、44)连接至输电网输出(15、25、35)。方法进步包括选择(208)在控制周期期间用于执行能量存储元件(12A‑n、21A‑n、31A‑n、44)之间的能量传输的能量存储元件(12A‑n、21A‑n、31A‑n、44)。 [ES MX351604B]: Se proporciona una disposición de convertidor (1) y un método para controlar una disposición trifásica de convertidor conectada a una red de transmisión. La disposición de convertidor (1) comprende tres patas de fase (10, 20, 30) y un circuito de transferencia de energía (40). El método comprende proporcionar un voltaje de fase de salida (A, 3, C) variante respectivo a la red de transmisión al seleccionar (206) elementos de almacenamiento de energía (12A-n, 22A-n, 32A-n, 44) tanto de las patas de fase (10, 20, 30) como del circuito de transferencia de energía (40) y conectar (210) los elementos de almacenamiento de energía (12A-n, 22A-n, 32A-n, 44 seleccionados a la salida (15, 25, 35) de la red de transmisión. El método de más comprende seleccionar (208) elementos de almacenamiento de energía (12A-n, 22A-n, 32A-n, 44) para llevar a cabo una transferencia de energía entre los elementos de almacenamiento de energía (12A-n, 22A-n, 32A-n, 44) durante el periodo de control. [PT BR112015030204A2]: resumo patente de invenção: "disposição de conversor para compensação de potência e método para controlar um conversor de potência". trata-se de uma disposição de conversor (1) e um método para controlar uma disposição de conversor de três fases conectada a uma rede de transmissão. a disposição de conversor (1) compreende três pernas de fase (10, 20, 30) e um circuito de transferência de energia (40). o método compreende fornecer uma respectiva tensão de fase de saída variante (a, b, c) para a rede de transmissão selecionando-se (206) elementos de armazenamento de energia (12a-n, 21a-n, 31a-n, 44) tanto das pernas de fase (10, 20, 30) quanto do circuito de transferência de energia (40) e conectar (210) os elementos de armazenamento de energia selecionados (12a-n, 21a-n, 31a-n, 44) à saída de rede de transmissão (15, 25, 35). o método compreende adicionalmente selecionar (208) elementos de armazenamento de energia (12a-n, 21a-n, 31a-n, 44) para realizar uma transferência de energia entre os elementos de armazenamento de energia (12a-n, 21a-n, 31a-n, 44) durante o período de controle. | WO2014194968A1 | 2014-12-11 | EP2013061843W | 2013-06-07 | EP2013061843W, 2013-06-07 | WO2014194968A1: 2014-12-11 AU2013391740B2: 2017-01-05 CA2914653C: 2018-10-30 CN105393423B: 2018-05-04 EP3005519B1: 2020-11-11 MX351604B: 2017-10-20 US9876358B2: 2018-01-23 BR112015030204A2: 2017-07-25 | ABB TECHNOLOGY LTD ABB TECHNOLOGY AG ABB技术有限公司 ABB POWER GRIDS SWITZERLAND AG ABB SCHWEIZ AG | DIJKHUIZEN FRANS NAMI ALIREZA ZELAYA DE LA PARRA HECTOR TOWNSEND CHRISTOPHER PARRA HECTOR ZELAYA DE LA ALIREZA NAMI FRANS DIJKHUIZEN HECTOR ZELAYA DE LA PARRA CHRISTOPHER TOWNSEND | H02J3/32: I H02J3/18: I H02M7/49: I H02M7/483: N | H02J3/1857: I H02M7/483: I H02M1/0095: I H02M7/4835: A Y02E40/20: A H02J3/18: I H02J3/32: I | DE19535552A1 WO02063758A1 WO2008086760A1 DE10103031A1 US5642275A CN1933274A CN101584109A CN202076951U CN102301579A US5673189A US2010060235A1 US2012161858A1 CN101345422A CN101574935A CN101588073A | WO2017223267A1 WO2017223267 2017/223267 WO2016119820A1 WO2016119820 2016/119820 WO2016/119820A1 WO2018215071A1 WO2018215071 2018/215071 WO2018/215071A1 EP3251205A1 EP3251205 3251205 CN109195831A CN109195831 109195831 US9948117B2 US9948117 09948117 US2017104362A1 US2017104362 20170104362 US9935491B2 US9935491 09935491 US2016211667A1 US2016211667 20160211667 | [EN EP3005519B1]: A method for controlling a three-phase converter arrangement (1) connected to a transmission network, which converter arrangement (1) comprises three phase branches (10, 20, 30) and a power transfer circuit (40), each phase branch comprising a plurality of switching cells (11A-n, 21A-n, 31A-n) arranged in series, each switching cell (11A-n, 21A-n, 31A-n) comprising a storage element d 'energy (12A-n, 22A-n, 32A-n) selectively connectable to the respective phase branch (10, 20, 30), the energy transfer circuit (40) comprising at least one energy storage element (44) selectively connectable to each of the phase branches (10, 20, 30), the method comprising the step of providing a respective variable output phase voltage (A, B, C) to the transmission network by the selection (206) of elements energy storage (12A-n, 21A-n, 31A-n, 44) and branching (210) of the selected energy storage elements (12A-n, 21A-n, 31A-n, 44) to the output (15, 25, 35) for a number of successive control periods as a function of a voltage reference signal, the selection (206) being made for each control period to provide adjustment of the output phase voltages (A, B, C) for each control period, the selection (206) for each phase voltage (A, B, C) being performed among the energy storage elements (12A-n, 21A-n, 31A-n) of the corresponding phase branch (10, 20, 30) and said at least one energy storage element ( 44) of the energy transfer circuit (40), the method being characterized in thatit also includes the step of selecting (208) energy storage elements (12A-n, 21A-n, 31A-n, 44) to effect energy transfer in each phase branch (10, 20, 30) between the storage elements energy (12A-n, 21A-n, 31A-n, 44) during the control period, the selection (208) to effect the energy transfer being made for each phase branch (10, 20, 30) among the energy storage elements (12A-n, 21A-n, 31A-n, 44) of this phase branch (10, 20, 30) and the energy transfer circuit (40), and connect (210) the energy storage elements (12A-n, 21A-n, 31A-n , 44) selected (206) to provide phase voltage adjustment, and energy storage elements (12A-n, 21A-n, 31A-n, 44) selected (208) to effect energy transfer , on the exit (15, 25, 35). A method for controlling a converter arrangement according to claim 1, further comprising the step of monitoring (203, 204) the voltage level of each energy storage element (12A-n, 21A-n, 31A-n, 44), the selection (208) of the energy storage elements (12A-n, 21A-n, 31A-n, 44) for energy transfer being based on their voltage levels. A method for controlling a converter arrangement according to claim 2, wherein the selection (206) made to provide the output phase voltages is based on the monitored voltage levels. A method for controlling a converter arrangement according to claim 2 or 3, wherein selecting (208) energy storage elements (12A-n, 21A-n, 31A-n, 44) for energy transfer in each phase branch (10, 20, 30) includes the adaptation of the energy storage elements (12A-n, 21A-n, 31A-n, 44) according to their voltage levels to provide a zero voltage contribution for the control period to the output phase voltage from the energy storage elements (12A-n, 21A-n, 31A-n, 44) which are selected for energy transfer. A method for controlling a converter arrangement according to claim 4, wherein said adapting comprises the step of selecting a fraction of the control period for switching on at least one of the selected energy storage elements, so that the voltage contributions of the energy storage elements are equalized. A method for controlling a converter arrangement according to claim 5, wherein said fraction of the control period is equal to the fraction of the desired voltage level in relation to the voltage level of said at least one of the selected energy storage elements. . A method for controlling a converter arrangement according to any one of claims 1 to 6, wherein the selection (208) to effect the energy transfer is made from among the energy storage elements (12A-n, 21A-n , 31A-n, 44) which are not selected to provide the respective output phase voltages (A, B, C) during the control period. A method for controlling a converter arrangement according to any one of claims 1 to 7, further comprising the step of receiving a voltage reference signal indicating an output voltage level for each phase (A, B, C) for each control period, the selection (206) for providing the output phase voltages being based on the voltage reference signal. A method for controlling a converter arrangement according to claim 8, which converter arrangement (1) comprises an energy storage circuit (40) comprising a plurality of energy storage elements (44), the method also comprising: 'step of restricting (202) the possibility of selecting at least one of the energy storage elements (44) of the energy storage device (40) for at least one phase (A, B, C) during the control period when selecting (206) energy storage elements (12A-n, 21A-n, 31A-n, 44) to provide each output phase voltage and when selecting (208) energy storage elements (12A-n, 21A-n, 31A-n, 44) for energy transfer. Converter arrangement (1) for a three-phase transmission network (A, B, C) comprising three phase branches (10, 20, 30), each phase branch (10, 20, 30) comprising a plurality of cells of switch (11A-n, 21A-n, 31A-n) connected in series, each switch cell (11A-n, 21A-n, 31A-n) including an energy storage element (12A-n, 22A- not, 32A-n) and semiconductor switches (14A-n) arranged to selectively connect the energy storage elements (12A-n, 22A-n, 32A-n) to phase (A, B, C) respective CA transport network, the converter (1) being designed to supply a voltage to each phase (A, B, C) of the transmission network at a respective reference voltage level during successive control periods, the applied voltage being supplied by combining a number of energy storage elements (11A-n, 21A-n, 31A-n, 44) during each control period to synthesize each phase voltage to give it the level of respective reference voltage, the voltage reference specifying an individual voltage level for each phase during each of the control periods, also comprising an energy transfer circuit (40) comprising at least one energy storage element (44) and comprising first (41), second (42) and third (43) phase connections, each being connected to a respective phase branch of the three phase branches (10, 20, 30), and the converter arrangement (1) being configured to selectively connect each of the three phase branches (10, 20, 30) to the transfer circuit d 'energy (40), for each phase (A, B, C), said converter arrangement (1) being adapted to select from among the energy storage elements (11A-n, 21A-n, 31A-n, 44) of the energy transfer circuit (40) and of the branch phase (10, 20, 30) when supplying phase voltages, characterized in thatthe converter arrangement (1) is also designed to transfer energy between the energy storage elements (12A-n, 22A-n, 32A-n) of each phase branch (10, 20, 30) and said at least one energy storage element (44) of the energy transfer circuit (40) during the control periods, with the energy storage elements (12An, 22A-n, 32A-n, 44 ) which remain after the selection to supply the phase voltage, the transfer comprising the step of making an adaptation among these remaining energy storage elements, and branching the energy storage elements in selected directions, so that the energy transfer provides a full voltage output to each phase (A, B, C) at a substantially zero voltage level during the selected control periods. A converter arrangement (1) according to claim 10, wherein each phase branch (10, 20, 30) comprises a first end and a second end, the second end being opposite the first end, and comprising a connection (15, 25, 35) to the network at the first end and a connection (16, 26, 36) to the energy transfer circuit (40) at the second end. A converter arrangement (1) according to claim 10 or 11, wherein the power transfer circuit (40) comprises a capacitor (44) and three sets of two switches (61A, 61B, 61C), each set of switches being connected to the capacitor (44) and to a respective phase branch (10, 20, 30) and arranged to selectively connect the respective phase branch to the capacitor. A converter arrangement (1) according to claim 10 or 11, wherein the power transfer circuit (44) comprises three H-bridge switching cells (65A, 65B, 65C), each connected to a respective phase branch. phase branches (10, 20, 30), and in which the capacitors (66A, 66B, 66C) of the three H-bridge switching cells (65A, 65B, 65C) are interconnected by means of a continuous link (64A , 64B) on both sides of the capacitors (66A, 66B, 66C). Converter arrangement (1) according to claim 10 or 11, the energy transfer circuit (44) being arranged in a delta configuration comprising three delta connections (67AB, 67BC, 67AC) between the phase branches (10, 20, 30). A converter arrangement (1) according to claim 14, each delta connection (67AB, 67BC, 67AC) comprising at least one energy storage element and switching means for the selective connection of the energy storage element to the delta connection, each delta connection (67AB, 67BC, 67AC) comprising in particular energy storage elements, and the switching means being arranged in the form of an H bridge (69AB, 69BC, 69AC). A converter arrangement (1) according to claim 10 or 11, wherein the energy storage elements and the switching means of the energy transfer circuit (40) are arranged according to an M2LC converter topology (48). Converter arrangement according to claim 10 or 11, the phase connection of each phase branch (10, 20, 30) comprising a transformer (17), each phase branch (10, 20, 30) being connected directly to a first winding of the transformer (17), each phase branch being connected at its other end to the first winding of the transformer (17) via the energy transfer circuit (40), the second winding of the transformer being arranged for connection to the transport network. A converter arrangement according to claim 10 or 11, wherein each phase branch (10, 20, 30) consists of a first sub-branch (10A, 20A, 30A) and a second sub-branch (10B, 20B, 30B), the energy transfer circuit (40, 40B) being connected to a respective end of the second sub-branches (10B, 20B, 30B), the converter arrangement (1, 1A, 1B) also containing a second energy transfer circuit (40A) connected to a respective end of the first sub-branches (10A, 20A, 30A), each sub-branch (10A, 20A, 30A, 10B, 20B, 30B) being connected via the respective power transfer circuit (40, 40A, 40B) to a first winding of a respective transformer (17A1, 17B1, 17C1, 17A2, 17B2, 17C2) which provides a phase connection for each sub-branch (10A, 20A, 30A, 10B, 20B, 30B), the second winding of the two sub-branch transformers (17A1, 17B1, 17C1, 17A2, 17B2, 17C2) of each phase branch (10, 20, 30) being connected in series and forming a connection for one phase (A, B , C) respective transport network. [ZH CN105393423B]: 1.一种用于控制连接到输电网的三相变换器装置(1)的方法，所述变换器装置(1)包括 三个相腿（10、20、30)和能量传输电路(40)，每个相腿包括串联布置的多个开关单元（11八-n、21A-n、31A_n)，每个开关单兀(llA-n、21A_n、31 A-n)包括能够选择性地连接到相应相腿 (10、20、30)的能量存储元件（12A-n、22A-n、32A-n)，所述能量传输电路(40)包括能够选择 性地连接到所述相腿(10、20、30)的每一个的至少一个能量存储元件(44)，所述方法包括基 于电压参考信号，针对多个连续的控制周期，通过对能量存储元件（12A-n、22A-n、32A-n、 44)进行选择(206)并连接(210)所选择的所述能量存储元件（12A-n、22A-n、32A-n、44)至输 出（15、25、35)，来提供变化的相应输出相(A、B、C)电压至所述输电网，其中 针对每个控制周期来执行对能量存储元件（12A-n、22A-n、32A-n、44)的选择(206)，以 针对每个控制周期提供所述输出相(A、B、C)电压的调整，以及在相应的相腿（10、20、30)的 能量存储元件（12A-n、22A-n、32A-n)和所述能量传输电路(40)的所述至少一个能量存储元 件(44)之间，作出针对每个相(A、B、C)电压的对所述能量存储元件（12A-n、22A-n、32A-n、 44)的选择(206)，所述方法进一步包括： 在所述控制周期期间选择（208)在每个相腿（10、20、30)中在所述能量存储元件（12八_ n、22A-n、32A-n、44)之间用于执行能量传输的能量存储元件（12A-n、22A-n、32A-n、44)，在 所述相腿（10、20、30)和所述能量传输电路(40)的能量存储元件（12A-n、22A-n、32A-n、44) 之间，针对每个相腿（10、20、30)作出对用于执行所述能量传输的能量存储元件的选择 (208)，将所选择（206)的用于提供所述输出相(A、B、C)电压的调整的所述能量存储元件 (12A-n、22A-n、32A-n、44)，以及所选择(208)的用于执行所述能量传输的所述能量存储元 件（12A-n、22A_n、32A-n、44)连接(210)至所述输出（15、25、35)。 2. 根据权利要求1所述的用于控制变换器装置的方法，进一步包括监测(203、204)每个 能量存储元件（12A-n、22A-n、32A_n、44)的电压电平，其中用于所述能量传输的能量存储元 件(12A-n、22A-n、32A-n、44)的所述选择(208)是基于所述能量存储元件的电压电平的。 3. 根据权利要求2所述的用于控制变换器装置的方法，其中用于提供所述输出相电压 的所述选择(206)是基于监测的所述电压电平的。 4. 根据权利要求2所述的用于控制变换器装置的方法，其中用于在每个相腿（1〇、20、 30)中的能量传输的能量存储元件（12A-n、22A-n、32A-n、44)的所述选择(208)包括基于所 述能量存储元件的电压电平来匹配所述能量存储元件（12A-n、22A-n、32A-n、44)，以针对所 述控制周期提供零电压贡献至来自被选择用于所述能量传输的所述能量存储元件（IM-n、 22A-n、32A_n、44)的所述输出相电压。 5. 根据权利要求4所述的用于控制变换器装置的方法，其中所述匹配包括选择所述控 制周期的部分用于所选择的所述能量存储元件的至少一个能量存储元件的连接，使得所述 能量存储元件的所述电压贡献是相等的。 6. 根据权利要求5所述的用于控制变换器装置的方法，其中所述控制周期的所述部分 等于与所选择的所述能量存储元件的所述至少一个能量存储元件的所述电压电平有关的 期望的电压电平的部分。 7. 根据权利要求1-6的任一项所述的用于控制变换器装置的方法，其中在那些未被选 择的能量存储元件（12A-n、22A-n、32A_n、44)之中作出用于执行所述能量传输的所述选择 (208)，以在所述控制周期期间提供相应的输出相(A、B、C)电压。 8. 根据权利要求1 -6的任一项所述的用于控制变换器装置的方法，进一步包括接收指 示对于每个所述控制周期用于每相(A、B、C)的输出电压电平的电压参考信号，用于提供所 述输出相电压的所述选择(206)是基于所述电压参考信号的。 9. 根据权利要求8所述的用于控制变换器装置的方法，所述变换器装置(1)包括含有多 个能量存储元件(44)的能量存储电路，所述方法进一步包括在选择(206)用于提供每个输 出相电压的能量存储元件（12A-n、22A-n、32A-n、44)和在选择(208)用于能量传输的能量存 储元件（12A-n、22A_n、32A-n、44)时，限制（202)在所述控制周期期间选择用于至少一•个相 (A、B、C)的所述能量存储电路的所述能量存储元件(44)的至少一个的可能性。 10. —种用于三相(A、B、C)输电网的变换器装置（1)，所述变换器装置（1)包括三个相腿 (10、20、30)，每个相腿（10、20、30)包括串联连接的多个开关单元（llA-n、21A-n、31A-n)，每 个开关单元（11A-n、21A-n、31A_n)包括能量存储元件（12A-n、22A-n、32A-n)和半导体开关 (14A-n)，所述半导体开关（14A-n)被布置为选择性地连接所述能量存储元件（12A-n、22A-n、32A_n)至AC输电网的相应相(A、B、C)， 所述变换器装置（1)适用于在针对连续的控制周期以相应的参考电压电平提供电压至 所述输电网的每相(A、B、C)，其中所应用的所述电压在每个控制周期期间通过组合多个能 量存储元件（12A-n、22A-n、32A-n、44)而被提供，以合成在所述相应的参考电压电平处的每 个相电压， 所述参考电压电平指定在所述控制周期的每个控制周期期间用于每相的单个电压电 平， 所述变换器装置（1)进一步包括能量传输电路(40)，所述能量传输电路(40)包括至少 一个能量存储元件(44)并且包括第一相连接(41)、第二相连接(42)和第三相连接(4¾，每 一个相连接被连接到所述三个相腿（1〇、2〇、30)的相应的一个相腿，并且所述变换器装置 (1)被配置为选择性地将所述三个相腿(1〇、2〇、3〇)的每一个相腿连接至所述能量传输电路 (40)， 对于每相(A、B、C)，所述变换器装置（1)适用于当提供所述相电压时，在所述能量传输 电路(40)和所述相腿（10、20、30)的所述能量存储元件（12A-n、22A-n、32A-n、44)之间进行 选择，其特征在于， 所述变换器装置（1)进一步适用于在所述控制周期期间，在每个相腿（1〇、2〇、3〇)的H邑 量存储元件(12A-n、22A_n、32A-n)和所述能量传输电路(4〇)的所述至少一个能量存储元件 (44)之间传输能量，所述能量存储元件（12A-n、22A-n、32A-n、44)是在用以提供所述相电压 的选择之后剩余的能量存储元件（12A-n、22A_n、32A_n、44)，所述传输包括执行在所述剩余 的能量存储元件之间的匹配，并以选择的方向连接所述能量存储元件，使得所述能量传输 针对所选择的控制周期以实质上零电压电平提供总电压输出至每相(A、B、C)。 11. 根据权利要求10所述的变换器装置（1)，其中每个相腿（10、20、30)包括第一端和第 二端，所述第二端与所述第一端相对，并且包括在所述第一端处的网络连接（15、25、35)和 在所述第二端处的到所述能量传输电路(4〇)的连接(16、26、36)。 12. 根据权利要求10或11所述的变换器装置（1)，其中所述能量传输电路(40)包括一个 电容器(44)和三组双开关(61A、61B、61C)，每组开关连接到所述电容器(44)和相应的相腿 (10、20、30)并被布置为选择性地将所述相应的相腿连接至所述电容器。 13. 根据权利要求1〇或11所述的变换器装置（1)，其中所述能量传输电路(40)包括三个 H桥开关单元(65A、65B、65C)，每一个H桥开关单元连接到所述相腿（1〇、2〇、3〇)的相应的一 个相腿，并且其中所述三个H桥开关单元(65A、65B、65C)的电容器(66A、66B、66C)是通过所 述电容器(66A、66B、66C)两侧的DC链(64A、6细互联的。 14. 根据权利要求1〇或11所述的变换器装置（1)，所述能量传输电路(40)被布置在三角 形配置中，所述三角形配置包括所述相腿（1〇、2〇、30)之间的三个三角形连接(67AB、e7BC、 67AC) 〇 15. 根据权利要求14所述的变换器装置（1)，每个三角形连接(67AB、67BC、67AC)包括至 少一个能量存储元件和用于选择性地将所述能量存储元件连接至所述三角形连接的开关 装置。 16. 根据权利要求15所述的变换器装置（1)，每个三角形连接(67AB、67BC、67AC)包括能 量存储元件和被布置在H桥(69AB、69BC、69AC)中的所述开关装置。 17. 根据权利要求10或11所述的变换器装置（1)，其中所述能量存储元件和所述能量传 输电路(40)的开关装置被布置在M2LC变换器拓扑(48)中。 18. 根据权利要求10或11所述的变换器装置(1)，每个相腿（10、20、30)的所述相连接包 括变压器（17)，每个相腿（10、20、30)直接连接到所述变压器（17)的第一绕组，每个相腿在 所述每个相腿的另一端通过所述能量传输电路(40)连接到所述变压器（17)的所述第一绕 组，所述变压器的第二绕组被布置用于连接到所述输电网。 19. 根据权利要求10或11所述的变换器装置(1)，其中每个相腿（10、20、30)由第一分腿 (10A、20A、30A)和第二分腿(10B、20B、30B)组成，其中所述能量传输电路连接到所述第二分 腿（10B、20B、3〇B)的一个相应端，所述变换器装置进一步包括连接到所述第一分腿（10A、 20A、30A)的相应端的第二能量传输电路(40A)，每个分腿（10八、2(^、3(^、108、2(«、308)通过 相应的所述能量传输电路(40、40A、40B)连接到为每个分腿（10A、20A、30A、10B、20B、30B：^¦ 供相连接的相应的变压器(17A1、17B1、17C1、17A2、17B2、17C2)的第一绕组，每个相腿（1〇、 20、30)的两个分腿变压器（17A1、17B1、17C1、17A2、17B2、17C2)的第二绕组串联连接并形成 用于所述输电网的相应相(A、B、C)的连接。 [DE EP3005519B1]: Verfahren zum Steuern einer dreiphasigen Wandleranordnung (1), die mit einem Übertragungsnetz verbunden ist, wobei die Wandleranordnung (1) drei Phasenzweige (10, 20, 30) und einen Energieübertragungskreis (40) umfasst, wobei jeder Phasenzweig eine Vielzahl von Schaltzellen (11A-n, 21An, 31A-n) umfasst, die in Reihe geschaltet sind, wobei jede Schaltzelle (11A-n, 21A-n, 31A-n) ein Energiespeicherelement (12A-n, 22A-n, 32A-n) umfasst, das selektiv an den entsprechenden Phasenzweig (10, 20, 30) anschließbar ist, wobei der Energieübertragungskreis (40) mindestens ein Energiespeicherelement (44) umfasst, das selektiv an Jeden der Phasenzweige (10, 20, 30) anschließbar ist, wobei das Verfahren umfasst: Bereitstellen einer variierenden Spannung einer entsprechenden Ausgangsphase (A, B, C) für das Übertragungsnetz, indem Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) ausgewählt werden (206); und Verbinden (210) der ausgewählten Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) mit dem Ausgang (15, 25, 35) für eine Anzahl von aufeinanderfolgenden Steuerzeiträumen auf der Grundlage eines Spannungsbezugssignals, wobei das Auswählen (206) für jeden Steuerzeitraum ausgeführt wird, um eine Anpassung der Spannungen der Ausgangsphasen (A, B, C) für jeden Steuerzeitraum bereitzustellen, und wobei das Auswählen (206) für jede Spannung der Phase (A, B, C) aus den Energiespeicherelementen (12A-n, 21A-n, 31A-n) des entsprechenden Phasenzweigs (10, 20, 30) und dem mindestens einen Energiespeicherelement (44) des Energieübertragungskreises (40) erfolgt, wobei das Verfahren dadurch gekennzeichnet ist, dass es außerdem umfasst: Auswählen (208) von Energiespeicherelementen (12An, 21A-n, 31A-n, 44) zum Ausführen einer Energieübertragung in jedem Phasenzweig (10, 20, 30) zwischen den Energiespeicherelementen (12A-n, 21A-n, 31A-n, 44) während des Steuerzeitraums, wobei das Auswählen (208) zum Ausführen der Energieübertragung für jeden Phasenzweig (10, 20, 30) aus den Energiespeicherelementen (12A-n, 21A-n, 31A-n, 44) dieses Phasenzweigs (10, 20, 30) und des Energieübertragungskreises (40) erfolgt; und Verbinden (210) der Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44), die zum Bereitstellen einer Anpassung der Phasenspannungen ausgewählt werden (206), und der Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44), die zum Ausführen einer Energieübertragung ausgewählt werden (208), mit dem Ausgang (15, 25, 35). Verfahren zum Steuern einer Wandleranordnung nach Anspruch 1, das außerdem ein Überwachen (203, 204) des Spannungspegels von jedem Energiespeicherelement (12A-n, 21A-n, 31A-n, 44) beinhaltet, wobei das Auswählen (208) der Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) für die Energieübertragung auf ihren Spannungspegeln beruht. Verfahren zum Steuern einer Wandleranordnung nach Anspruch 2, wobei das Auswählen (206) zum Bereitstellen der Ausgangsphasenspannungen auf den überwachten Spannungspegeln beruht. Verfahren zum Steuern einer Wandleranordnung nach Anspruch 2 oder 3, wobei das Auswählen (208) der Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) für die Energieübertragung in jedem Phasenzweig (10, 20, 30) aufweist: Abgleichen der Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) auf der Grundlage ihrer Spannungspegel, um einen Nullspannungsbeitrag für den Steuerzeitraum zu der Ausgangsphasenspannung von den Energiespeicherelementen (12A-n, 21A-n, 31A-n, 44) bereitzustellen, die für die Energieübertragung ausgewählt werden. Verfahren zum Steuern einer Wandleranordnung nach Anspruch 4, wobei das Abgleichen ein Auswählen eines Bruchteils des Steuerzeitraums für die Verbindung mindestens eines der ausgewählten Energiespeicherelemente aufweist, sodass der Spannungsbeitrag der Energiespeicherelemente ausgeglichen wird. Verfahren zum Steuern einer Wandleranordnung nach Anspruch 5, wobei der Bruchteil des Steuerzeitraums gleich dem Bruchteil des gewünschten Spannungspegels in Bezug auf den Spannungspegel des mindestens Einen der ausgewählten Energiespeicherelemente ist. Verfahren zum Steuern einer Wandleranordnung nach einem der Ansprüche 1 bis 6, wobei das Auswählen (208) zum Ausführen der Energieübertragung aus jenen Energiespeicherelementen (12A-n, 21A-n, 31A-n, 44) erfolgt, die nicht ausgewählt werden, um die entsprechenden Spannungen der Ausgangsphasen (A, B, C) während des Steuerzeitraums bereitzustellen. Verfahren zum Steuern einer Wandleranordnung nach einem der Ansprüche 1 bis 7, das außerdem ein Empfangen eines Spannungsbezugssignals aufweist, das einen Ausgangsspannungspegel für jede Phase (A, B, C) für jeden Steuerzeitraum anzeigt, wobei das Auswählen (206) zum Bereitstellen der Ausgangsphasenspannungen auf dem Spannungsbezugssignal beruht. Verfahren zum Steuern einer Wandleranordnung nach Anspruch 8, wobei die Wandleranordnung (1) einen Energiespeicherschaltkreis (40) umfasst, der eine Vielzahl von Energiespeicherelementen (44) umfasst, wobei das Verfahren außerdem ein Einschränken (202) der Möglichkeit des Auswählens mindestens Eines der Energiespeicherelemente (44) des Energiespeichers (40) für mindestens eine Phase (A, B, C) während des Steuerzeitraums aufweist, wenn Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) zum Bereitstellen jeder Ausgangsphasenspannung ausgewählt werden (206) und wenn Energiespeicherelemente (12A-n, 21A-n, 31A-n, 44) für eine Energieübertragung ausgewählt werden (208). Wandleranordnung (1) für ein dreiphasiges (A, B, C) Übertragungsnetz, das drei Phasenzweige (10, 20, 30) umfasst, wobei jeder Phasenzweig (10, 20, 30) eine Vielzahl von Schaltzellen (11A-n, 21A-n, 31A-n) umfasst, die in Reihe geschaltet sind, wobei jede Schaltzelle (11A-n, 21A-n, 31A-n) ein Energiespeicherelement (12A-n, 22A-n, 32A-n) und Halbleiterschalter (14A-n) umfasst, die ausgelegt sind, um die Energiespeicherelemente (12A-n, 22A-n, 32A-n) selektiv mit den entsprechenden Phasen (A, B, C) des AC-Übertragungsnetzes zu verbinden, wobei der Wandler (1) geeignet ist zum Bereitstellen einer Spannung für jede Phase (A, B, C) des Übertragungsnetzes mit einem jeweiligen Referenzspannungspegel für aufeinanderfolgende Steuerzeiträume, wobei die angelegte Spannung bereitgestellt wird, indem eine Anzahl von Energiespeicherelementen (11A-n, 21A-n, 31A-n, 44) während jedes Steuerzeitraums kombiniert werden, um jede Phasenspannung auf dem jeweiligen Referenzspannungspegel zu synthetisieren, wobei die Spannungsreferenz einen einzigen Spannungspegel für jede Phase während jedes Steuerzeitraums festlegt, wobei die Wandleranordnung außerdem einen Energieübertragungskreis (40) umfasst, der mindestens ein Energiespeicherelement (44) umfasst und eine erste (41), eine zweite (42) und eine dritte (43) Phasenverbindung umfasst, die jeweils mit einem Entsprechenden der drei Phasenzweige (10, 20, 30) verbunden sind, und wobei die Wandleranordnung (1) konfiguriert ist zum selektiven Verbinden Jedes der drei Phasenzweige (10, 20, 30) mit dem Energieübertragungskreis (40), wobei die Wandleranordnung (1) für jede Phase (A, B, C) geeignet ist zum Auswählen aus den Energiespeicherelementen (11A-n, 21A-n, 31A-n, 44) des Energieübertragungskreises (40) und des Phasenzweigs (10, 20, 30), wenn die Phasenspannungen bereitgestellt werden, dadurch gekennzeichnet, dass die Wandleranordnung (1) außerdem geeignet ist zum Übertragen von Energie zwischen den Energiespeicherelementen (12A-n, 22A-n, 32A-n) von jedem Phasenzweig (10, 20, 30) und dem mindestens einen Energiespeicherelement (44) des Energieübertragungskreises (40) während der Steuerzeiträume, wobei nach der Auswahl zum Bereitstellen der Phasenspannung mit Energiespeicherelemente (12A-n, 22A-n, 32A-n, 44) verbleiben, wobei das Übertragen ein Ausführen eines Abgleichens zwischen diesen verbliebenen Energiespeicherelementen und ein Verbinden der Energiespeicherelemente in ausgewählte Richtungen aufweist, sodass die Energieübertragung einen Gesamtspannungsausgang zu jeder Phase (A, B, C) auf einem im Wesentlichen Nullspannungspegel für die ausgewählten Steuerzeiträume bereitstellt. Wandleranordnung (1) nach Anspruch 10, wobei jeder Phasenzweig (10, 20, 30) ein erstes Ende und ein zweites Ende umfasst, wobei sich das zweite Ende entgegengesetzt zu dem ersten Ende befindet, und wobei die Wandleranordnung eine Netzverbindung (15, 25, 35) an dem ersten Ende und eine Verbindung (16, 26, 36) mit dem Energieübertragungskreis (40) an dem zweiten Ende umfasst. Wandleranordnung (1) nach Anspruch 10 oder 11, wobei der Energieübertragungskreis (40) einen Kondensator (44) und drei Gruppen von je zwei Schaltern (61A, 61B, 61C) umfasst, wobei jede Schaltergruppe mit dem Kondensator (44) und einem entsprechenden Phasenzweig (10, 20, 30) verbunden ist und ausgelegt ist zum selektiven Verbinden des jeweiligen Phasenzweigs mit dem Kondensator. Wandleranordnung (1) nach Anspruch 10 oder 11, wobei der Energieübertragungskreis (44) mindestens drei H-Brückenschaltzellen (65A, 65B, 65C) umfasst, die jeweils mit einem Entsprechenden der Phasenzweige (10, 20, 30) verbunden sind, und wobei die Kondensatoren (66A, 66B, 66C) der drei H-Brückenschaltzellen (65A, 65B, 65C) mithilfe einer DC-Verschaltung (64A, 64B) auf beiden Seiten der Kondensatoren (66A, 66B, 66C) miteinander verbunden sind. Wandleranordnung (1) nach Anspruch 10 oder 11, wobei der Energieübertragungskreis (44) in einer Delta-Konfiguration ausgelegt ist, die drei Delta-Verbindungen (67AB, 67BC, 67AC) zwischen den Phasenzweigen (10, 20, 30) umfasst. Wandleranordnung (1) nach Anspruch 14, wobei jede Delta-Verbindung (67AB, 67BC, 67AC) mindestens ein Energiespeicherelement und ein Schaltelement zum selektiven Verbinden des Energiespeicherelements mit der Delta-Verbindung umfasst, wobei insbesondere jede Delta-Verbindung (67AB, 67BC, 67AC) Energiespeicherelemente umfasst und wobei das Schaltelement in einer H-Brücke (69AB, 69BC, 69AC) angeordnet ist. Wandleranordnung (1) nach Anspruch 10 oder 11, wobei die Energiespeicherelemente und das Schaltelement des Energieübertragungskreises (40) in einer M2LC-Wandlertopologie (48) ausgelegt sind. Wandleranordnung nach Anspruch 10 oder 11, wobei die Phasenverbindung von jedem Phasenzweig (10, 20, 30) einen Transformator (17) umfasst, wobei jeder Phasenzweig (10, 20, 30) direkt mit einer ersten Wicklung des Transformators (17) verbunden ist, wobei jeder Phasenzweig an seinem anderen Ende über den Energieübertragungskreis (40) mit der ersten Wicklung des Transformators (17) verbunden ist, wobei die zweite Wicklung des Transformators für eine Verbindung mit dem Übertragungsnetz ausgelegt ist. Wandleranordnung nach Anspruch 10 oder 11, wobei jeder Phasenzweig (10, 20, 30) aus einem ersten (10A, 20A, 30A) und einem zweiten Teilzweig (10B, 20B, 30B) besteht, wobei der Energieübertragungskreis (40, 40B) mit einem entsprechenden Ende des zweiten Teilzweigs (10B, 20B, 30B) verbunden ist, wobei die Wandleranordnung (1, 1A, 1B) außerdem einen zweiten Energieübertragungskreis (40A) aufweist, der mit einem entsprechenden Ende der ersten Teilzweige (10A, 20A, 30A) verbunden ist, wobei jeder Teilzweig (10A, 20A, 30A, 10B, 20B, 30B) über den entsprechenden Energieübertragungskreis (40, 40A, 40B) mit einer ersten Wicklung eines entsprechenden Transformators (17A1, 17B1, 17C1, 17A2, 17B2, 17C2) verbunden ist, der eine Phasenverbindung für jeden Teilzweig (10A, 20A, 30A, 10B, 20B, 30B) bereitstellt, wobei die zweite Wicklung der Zwei-Teilzweig-Transformatoren (17A1, 17B1, 17C1, 17A2, 17B2, 17C2) von jedem Phasenzweig (10, 20, 30) in Reihe geschaltet ist und eine Verbindung für eine entsprechende Phase (A, B, C) des Übertragungsnetzes bildet. [FR EP3005519B1]: Procédé pour commander un agencement de convertisseur triphasé (1) relié à un réseau de transport, lequel agencement de convertisseur (1) comprend trois branches de phase (10, 20, 30) et un circuit de transfert d'énergie (40), chaque branche de phase comprenant une pluralité de cellules de commutation (11A-n, 21A-n, 31A-n) agencées en série, chaque cellule de commutation (11A-n, 21A-n, 31A-n) comprenant un élément de stockage d'énergie (12A-n, 22A-n, 32A-n) pouvant être branché sélectivement sur la branche de phase (10, 20, 30) respective, le circuit de transfert d'énergie (40) comprenant au moins un élément de stockage d'énergie (44) pouvant être branché sélectivement sur chacune des branches de phase (10, 20, 30), le procédé comprenant l'étape consistant à fournir une tension de phase de sortie (A, B, C) respective variable au réseau de transport par la sélection (206) d'éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) et le branchement (210) des éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) sélectionnés sur la sortie (15, 25, 35) pendant un certain nombre de périodes de commande successives en fonction d'un signal de référence de tension, la sélection (206) étant effectuée pour chaque période de commande pour assurer un réglage des tensions de phase de sortie (A, B, C) pour chaque période de commande, la sélection (206) pour chaque tension de phase (A, B, C) étant effectuée parmi les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n) de la branche de phase (10, 20, 30) correspondante et ledit au moins un élément de stockage d'énergie (44) du circuit de transfert d'énergie (40), le procédé étant caractérisé en ce qu'il comprend également l'étape consistant à sélectionner (208) des éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) pour effectuer un transfert d'énergie dans chaque branche de phase (10, 20, 30) entre les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) durant la période de commande, la sélection (208) pour effectuer le transfert d'énergie étant faite pour chaque branche de phase (10, 20, 30) parmi les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) de cette branche de phase (10, 20, 30) et le circuit de transfert d'énergie (40), et brancher (210) les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) sélectionnés (206) pour assurer un réglage des tensions de phase, et les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) sélectionnés (208) pour effectuer un transfert d'énergie, sur la sortie (15, 25, 35). Procédé pour commander un agencement de convertisseur selon la revendication 1, comprenant également l'étape consistant à surveiller (203, 204) le niveau de tension de chaque élément de stockage d'énergie (12A-n, 21A-n, 31A-n, 44), la sélection (208) des éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) pour le transfert d'énergie étant basée sur leurs niveaux de tension. Procédé pour commander un agencement de convertisseur selon la revendication 2, dans lequel la sélection (206) effectuée pour fournir les tensions de phase de sortie est basée sur les niveaux de tension surveillés. Procédé pour commander un agencement de convertisseur selon la revendication 2 ou 3, dans lequel la sélection (208) d'éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) pour le transfert d'énergie dans chaque branche de phase (10, 20, 30) comprend l'adaptation des éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) en fonction de leurs niveaux de tension pour fournir une contribution de tension nulle pour la période de commande à la tension de phase de sortie à partir des éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) qui sont sélectionnés pour le transfert d'énergie. Procédé pour commander un agencement de convertisseur selon la revendication 4, dans lequel ladite adaptation comprend l'étape consistant à sélectionner une fraction de la période de commande pour le branchement d'au moins un des éléments de stockage d'énergie sélectionnés, afin que les contributions de tension des éléments de stockage d'énergie soient égalisées. Procédé pour commander un agencement de convertisseur selon la revendication 5, dans lequel ladite fraction de la période de commande est égale à la fraction du niveau de tension souhaité en rapport avec le niveau de tension dudit au moins un des éléments de stockage d'énergie sélectionnés. Procédé pour commander un agencement de convertisseur selon l'une quelconque des revendications 1 à 6, dans lequel la sélection (208) pour effectuer le transfert d'énergie est faite parmi les éléments de stockage d'énergie (12A-n, 21A-n, 31A-n, 44) qui ne sont pas sélectionnés pour fournir les tensions de phase de sortie (A, B, C) respectives durant la période de commande. Procédé pour commander un agencement de convertisseur selon l'une quelconque des revendications 1 à 7, comprenant également l'étape consis | [EN EP3005519B1]: TECHNICAL FIELD The invention relates to power converters used in electrical power systems, which power converters include series connected switching cells having semiconductor switches and energy storage elements, such as capacitors. Especially, the invention relates to power converters used for power compensation in three phase AC transmission networks. BACKGROUND The invention relates to the field of voltage source converters, such as multilevel converters. Voltage source converters (VSC) have changed power transmission and distribution and using power electronics including semiconductor switching elements that can be turned off, such as IGBTs (Insulated Gate Bipolar Transistors) have found great use for DC transmission, reactive power compensation, control of active as well as reactive power, being able to create AC voltage out of DC voltage by means of switching control, and for converting AC to DC etcetera. The multilevel converter technique, employing switching cells having respective energy storage elements for providing many voltage levels, wherein each voltage level being individually switched, can be used to compensate for example for reactive power in AC transmission networks. Often, the energy storage elements used consists of capacitors but may also be batteries. The chain link H-bridge is a successful topology in the market and it is provided by several manufacturers. The H-bridge cells can be comparably simple and are suitable for being provided as modules, which helps to keep the costs of the construction down. Since the number of modules or switching cells is proportional to the AC voltage the system is easily scalable. Several variants of the chain-link topology exist, such as wye- or delta-connected H-bridge, and wye-connected M2LC. Figure 9 is a simplified example of a multilevel H-bridge converter according to the prior art, which converter is wye connected. The multilevel converter arrangement comprising three phase legs 10, 20, 30, each having a connection 15, 25, 35, respectively, adapted for connecting the converter arrangement to a respective phase A, B, C of a three-phase AC power transmissions grid, which transmission grid connection 15, 25, 35 is provided at a first end of each phase leg 10, 20, 30. A coil 13, 23, 33 is arranged at the transmission grid connections to smoothen the wave forms created by the converter. At the second end of each phase leg 10, 20, 30, the phase legs 10, 20, 30 are interconnected in the wye connection. Each phase leg 10, 20, 30 comprises a number of series connected switching cells 11A-n, 21A-n, and 31A-n. Each switching cell 11A-n, 21A-n, and 31A-n comprises an energy storage element 12A-n, 22A-n, 32A-n in the form of a capacitor. Each switching cell 11A-n, 21A-n, and 31A-n of the phase legs 10, 20, 30 are provided as modules of the same type as every other switching cell 11A-n, 21A-n, 31A-n; having the same bridge topology, the same type of capacitor and the same type of semiconductor switches. The multilevel converter also includes a controller 50 arranged for monitoring currents and voltages and controlling switching of the switching cells 11A-n, 21A-n, 31A-n. The controller 50 is provided to control the switching cells 11A-n, 21A-n, 31A-n to adjust the active and reactive power in a transmission line or grid. The controller 50 controls the switching cells 11A-n, 21A-n, 31A-n for control periods at a switching frequency that is substantially higher than the transmission grid frequency. Each phase voltage is adjusted for each control period, wherein the phase voltage is adjusted in accordance with a voltage reference signal that the converter receives as input from an outer controller provided in the transmission grid. The phase legs 10, 20, 30 may become unbalanced such that the voltages of some, or all, of the capacitors (energy storage elements 12A-n, 21A-n and 31A-n) deviate from the desired nominal cell voltages. German Patent Application DE 101 03 031 A1 discloses such a modular multi level converter. In the document it is explicitly mentioned that it is possible to balance the cell voltages by a control routine, which causes switching of the individual switches without any extra circuits. Document DE 195 35 552 discloses an energy transfer circuit for a three phase full bridge inverter. Cost and losses for such and similar converters are related to the total silicon area used in the converter. The silicon area is dependent on the voltage and current rating. A problem that may arise is that voltages over individual energy storage elements become too large or too low. Also, the total voltage available in the cells of a phase leg may for example become too low. For normal operation of the converter in industrial applications the designer must take into account the unbalance in the three-phase load. Unbalanced loads produce negative sequence currents that need to be compensated by the converter. To counteract the effect of these currents the total number of series connected cells will have too be large enough to compensate for the unbalanced condition due to the zero sequence voltage that needs to be injected. This has lead to the need for over-rated converters, wherein a number of extra switching cells has to be included in the phase legs for redundancy. Using more switching cells is disadvantageous since the extra switching cells add to the costs of the converters and add losses during use of the converters. SUMMARY Generally, all terms used in the claims are to be interpreted according to their ordinary meaning in the technical field, unless explicitly defined otherwise herein. All references to "a/an/the element, apparatus, component, means, step, etc." are to be interpreted openly as referring to at least one instance of the element, apparatus, component, means, step, etc., unless explicitly stated otherwise. The steps of any method disclosed herein do not have to be performed in the exact order disclosed, unless explicitly stated. It is an object of the invention to overcome the drawbacks of the prior art. For this purpose the invention provides a method for controlling a three-phase converter arrangement connected to a transmission grid according to claim 1 and a converter arrangement according to claim 10. The converter arrangement comprises three phase legs and an energy transfer circuit. Each phase leg comprising a plurality of switching cells arranged in series, and each switching cell comprises an energy storage element that is being selectively connectable to the respective phase leg. The energy transfer circuit comprises at least one energy storage element that is selectively connectable to each one of the phase legs. The method comprises providing a varying respective output phase voltage to the transmission grid by selecting energy storage elements and connecting the selected energy storage elements to the output for a number of successive control periods on the basis of a voltage reference signal, wherein the selecting is performed for each control period to provide an adjustment of the output phase voltages for each control period, and the selecting for each phase voltage being made among the energy storage elements of the corresponding phase leg and the at least one energy storage element of the energy transfer circuit. The method further comprises selecting energy storage elements for performing a transfer of energy in each phase leg between the energy storage elements during the control period, wherein the selection for performing the energy transfer for each phase leg is made among the energy storage elements of that phase leg and of the energy transfer circuit. Especially, the selection of energy storage element for the energy transfer in a specific phase leg is made among those energy storage elements not selected for providing the output phase voltage. Preferably, each phase leg has an output connected to the transmission grid in one end, and preferably each phase leg has a connection to the energy transfer circuit at the opposite end. Preferably, the switching cells are arranged in series between the first and the second end. In an embodiment the method further includes monitoring the voltage levels of each energy storage elements and the selecting of energy storage elements for the energy transfer being based on their voltage levels. In an embodiment the selecting for providing the output phase voltages being based on the monitored voltage levels. In an embodiment the selecting of energy storage elements for energy transfer in each phase leg includes matching the energy storage elements on the basis of their voltage levels to provide a zero voltage contribution during the control period to the outputted phase voltage from the energy storage elements that are selected for the energy transfer. In an embodiment, said matching includes selecting a fraction of the control period for the connection of at least one of the selected energy storage elements so that the voltage levels are equalized. In an embodiment, said fraction of the control period is equal to the fraction of the desired voltage level in relation to the voltage level of the at least one of the selected energy storage elements. Thus if for example 95% of the voltage of an energy storage element, e.g. a capacitor, is desired (i.e. needed for providing a zero total contribution to the phase voltage), the connection period for the capacitor is selected to be 95% of the control period. In an embodiment the selection for performing the energy transfer is made among those energy storage elements that are not selected to provide the respective output phase voltages during the control period. In an embodiment, the method further includes receiving a voltage reference signal indicating an output voltage level for each phase for each the control period, the selecting for providing the output phase voltages being based on the voltage reference signal. In an embodiment the converter arrangement comprises an energy storage circuit comprises a plurality of energy storage elements, and the method further includes restricting the possibility to select at least one of the energy storage elements of the energy storage for at least one phase during the control period when selecting energy storage elements for providing each output phase voltage and when selecting energy storage elements for energy transfer. Preferably, a selection of which energy storage elements of the energy transfer circuit that should be available during the control period for each phase leg is performed for each respective phase leg. Preferably also, when restricting the use of one or more energy storage elements, the phase leg having the lowest phase voltage during the control period, i.e. having the lowest phase voltage as provided in the voltage reference signal of the control period, is restricted to use fewer energy storage elements of the energy transfer circuit than the other phase legs. Thus, the number of available energy storage elements varies for the phase legs. Such a restriction makes it possible to provide converters having a limited number of energy storage elements in the energy transfer circuit, and thus provides an economic advantage compared to circuits dimensioned to provide the maximum phase voltage for every phase in every control period. The invention also provides a converter arrangement for a three-phase transmission grid comprising three phase legs. Each phase leg comprising a plurality of switching cells connected in series, each switching cell comprising an energy storage element and semiconductor switches arranged to selectively connect the energy storage elements to the respective phase of the AC transmission grid. The converter is adapted to provide a voltage to each phase of the transmission grid at a respective reference voltage level for successive control periods, wherein the voltage applied being provided by combining a number of energy storage elements during each control period to synthesize each phase voltage at the respective reference voltage level. The voltage reference specifies a single voltage level for each phase during each of the control periods. Especially the converter arrangement further comprises an energy transfer circuit comprising at least one energy storage element and comprising a first, a second and a third phase connection, each being connected to a respective one of the three phase legs. The energy transfer circuit is arranged to selectively transfer electrical energy between each of the three phase legs and the energy storage. For each phase, the converter is adapted to select among the energy storage elements of the energy transfer circuit as well as those of the phase leg when providing the phase voltages. The converter is further adapted to transfer energy between energy storage elements of each phase leg and the at least one energy storage element of the energy transfer circuit during selected control periods, which energy storage elements are selected among those energy storage elements that remain after the selection of energy storage element to provide the respective phase voltage. The transfer includes performing a matching among the remaining energy storage elements, and connecting the energy storage elements in selected directions, so that the energy storage elements selected for the energy transfer provides a total voltage output to each phase at an essentially zero voltage level for the selected control periods. Preferably, each switching cell comprises an energy storage element, preferably a capacitor, arranged with the switches in a bridge configuration, such as an H-bridge or half H-bridge. In an embodiment, each phase leg comprises a first end and a second end, the second end being opposite to the first end, and comprising a grid connection at the first end and a connection to the energy transfer circuit at the second end. In an embodiment, the energy transfer circuit comprises one capacitor and three sets of two switches, each set of switches being connected to the capacitor and a respective phase leg, and arranged to selectively connect the respective phase leg to the capacitor. In an embodiment, the energy transfer circuit comprises three H-bridge switching cells, each one connected to a respective one of the phase legs, and wherein the capacitors of the three H-bridge switching cells are interconnected by means of a DC link on both sides. Especially, one DC link interconnecting the low voltage side of the capacitors and one DC link interconnecting the high voltage side of the capacitors. In an embodiment, each side of the capacitor of each switching cell are connected to a corresponding side of the capacitors of the other switching cells. In an embodiment, the energy transfer circuit is arranged in a delta configuration comprising three delta connections between each pair of the phase legs. In an embodiment each delta connection comprises at least one energy storage element and switching means for selectively connecting the energy storage element to the delta connection. Especially each delta connection comprises energy storage elements and the switching means being arranged in an H-bridge. In an embodiment, the energy transfer circuit comprises an M2LC converter topology.In an embodiment, the phase connection of each phase leg comprises a transformer, each phase leg connected directly to a first winding of the transformer, each phase leg connected at its other end to the first winding of the transformer via the energy transfer circuit, the second winding of the transformer being arranged for connection to the transmission grid. In an embodiment, each phase leg consists of a first and a second sub-leg, wherein the energy transfer circuit is connected to one respective end of the second sub-legs, the converter arrangement further includes a second energy transfer circuit connected to a respective end of the first sub-legs, each sub-leg being connected via the respective energy transfer circuit to a first winding of a respective transformer that provides a phase connection for each sub-leg, the second winding of the two sub-leg transformers of each phase leg being serially connected and forms a connection for a respective phase of the transmission grid. BRIEF DESCRIPTION OF THE DRAWINGS The invention is now described, by way of example, with reference to the accompanying drawings, in which: Fig 1 illustrates a converter arrangement in accordance with the invention;Fig 2 illustrates a method of controlling a converter arrangement of the invention;Fig 3 illustrates an embodiment of a converter topology according to the invention;Fig 4 illustrates an embodiment of a converter topology according to the invention;Fig 5 illustrates an embodiment of a converter topology according to the invention;Fig 6 illustrates an embodiment of a converter topology according to the invention;Fig 7 illustrates an embodiment of a converter topology according to the invention;Fig 8 illustrates an embodiment of a converter topology according to the invention;Fig 9 illustrates a converter arrangement according to the prior art. DETAILED DESCRIPTION The invention will now be described more fully hereinafter with reference to the accompanying drawings, in which certain embodiments of the invention are shown. This invention may, however, be embodied in many different forms and should not be construed as limited to the embodiments set forth herein; rather, these embodiments are provided by way of example so that this disclosure will be thorough and complete, and will fully convey the scope of the invention to those skilled in the art. Like numbers refer to like elements throughout the description. Figure 1 illustrates a multilevel converter arrangement 1 comprising three phase legs 10, 20, 30, each having a connection 15, 25, 35, respectively, adapted for connecting the converter arrangement 1 to a respective phase A, B, C of a three-phase AC power transmissions grid, which transmission grid connection 15, 25, 35 is provided at a first end of each phase leg 10, 20, 30. Each phase leg 10, 20, 30 comprises a number of series connected switching cells 11A-n, 21A-n, and 31A-n, respectively. There are an equal number of switching cells 11A-n, 21A-n, and 31A-n in all phase legs 10, 20, 30. Each switching cell 11A-n, 21A-n, and 31A-n comprises an energy storage element in the form of a capacitor 12A-n, 22A-n, 32A-n. Preferably, each one of the capacitors 12A-n, 22A-n, 32A-n have the same capacitance value, and are provided for the same voltage level. Even though capacitors of the same type having the same capacitance is a preferred embodiment. Other preferred embodiments are envisioned and may be provided in correspondence with the invention. In one other preferred embodiment capacitors with different capacitances are used. In one other preferred embodiment, battery cells are used instead of capacitors. In one preferred embodiment some switching cells include battery cells and the others include capacitors. Each capacitor i2A-n, 22A-n, 32A-n is preferably, however not illustrated in figure 1, arranged in an H-bridge configuration, of four semiconductor switches, such as IGBTs, each in anti-parallel connection with a diode, see figure 3-8. Alternatively each capacitor may preferably be arranged in a half bridge configuration. Each switching cell 11A-n, 21A-n, and 31A-n of the phase legs 10, 20, 30 are provided as modules of the same type as every other switching cell 11A-n, 21A-n, and 31A-n; having the same bridge topology, the same type of capacitor and the same type of semiconductor switches. At the second end of each phase leg 10, 20, 30, opposite the grid connections 15, 25, and 35, each phase leg 10, 20, 30 is connected to an energy transfer circuit 40 arranged for exchanging energy between the phase legs. Each phase leg 10, 20, 30 comprises, at the second end, a respective connection 16, 26, 36 to the energy transfer circuit 30, which energy transfer circuit 40 has a corresponding respective connection terminal 41, 42, 43 to each one of the phase legs 10, 20, 30.The energy transfer circuit 40 comprises at least one energy storing element, such as a capacitor 44, and switches, or switching means, (not illustrated) by means of which the at least one energy storage element can be electrically connected to each phase leg 10, 20, 30. The energy transfer circuit 40 is arranged to selectively connect the three phase legs 10, 20, 30 electrically to transfer electrical energy to and from each phase 10, 20, 30. It is noted that the energy transfer circuit 40 comprises at least one energy storage element 44 being common to the phase legs 10, 20, 30, whereas each phase leg 10, 20, 30 comprises energy storage elements 12A-n, 22A-n, 32A-n being dedicated only to that respective phase. The phase legs 10, 20, 30 are electrically separated from each other along the line of series connected switching cells 11A-n, 21A-n, 31A-n and each leg 10, 20, 30 has a connection at the respective second end to the common energy transfer circuit to provide an energy transfer between the phase legs 10, 20, 30. The converter arrangement 1 also comprises a controller 50 that is operatively connected to each phase leg 10, 20, 30 and to the energy transfer circuit 40, as illustrated by the dotted lines. The controller 50 is adapted to obtain measurements of the currents in each phase leg 10, 20, 30 by means of current measuring means 18, 28, 38 arranged in each phase leg 10, 20, 30 at each respective grid connections 15, 25, 35. The current measuring means 18, 28, 38 can suitably be provided by means of current transformers. The controller 50 is adapted to obtain voltage measurements of each energy storage element, the capacitors 12A-n, 22A-n, 32A-n, of the switching cells 11A-n, 21A-n, 31A-n and obtain voltage measurements of the energy storage elements 44 of the energy transfer circuit 40, for example by means of voltage meters or voltage transformers (not illustrated) and the controller 50 is further operatively connected to each switching cell 11A-n, 21A-n, 31A-n in every phase leg 10, 20, 30 and each switch of the energy transfer circuit 40 and is adapted to control the switching of each switching cell 11A-n, 21A-n, 31A-n and the switches of the energy transfer circuit 40 so that each phase leg 10, 20, 30 together with energy storage elements 44 of the energy transfer circuit provide the desired phase voltage to the transmission grid. The controller 50 is configured to employ pulse width modulation to control the switches of the switching cells of each phase leg 10, 20, 30 and the switches of the energy transfer circuit 40. The controller 50 is for example provided to control the switching cells to adjust the active and/or reactive power in a transmission line or grid, and is adapted to receive a voltage reference signal to provide such compensation. The voltage reference signal is provided by an external controller that controls an outer control loop of the converter arrangement 1, and the voltage reference signal is based on grid measurements, such as measurements of the phase voltages and currents of a transmission line from current and voltage measuring means arranged at the transmission line. The voltage reference signal provides a single voltage level for each phase to be provided during one control period. The controller 50 is further adapted to provide a desired energy transfer by controlling the switching of the switching cells 11A-n, 21A-n, 31A-n and the energy transfer circuit 40 so that unbalanced capacitor voltages in the phase legs 10, 20, 30 are rebalanced. The controller 50 is adapted to effectuate such energy transfer without affecting the phase voltages provided to the transmission grid. In this way, the controller 50 is adapted to control both the phase voltages and the energy transfer between the phase legs 10, 20, 30. For each control period, one single reference voltage level for each phase is used, and one single process of energy transfer is employed. For each phase A, B, C, the controller 50 is adapted to select energy storage elements or capacitors i2A-n, 22A-n, 32A-n, 44 of the phase leg 10, 20, 30 and the energy transfer circuit 40, for each control period, and provide the desired phase voltages by controlling the corresponding switches of the cells and the energy transfer circuit, so that the desired phase voltages are provided in accordance with the voltage reference signal. The controller 50 is adapted to control the connection of some energy storage elements, or first set of energy storage elements, selected from the energy storage elements, e.g. the capacitor12A-n, 22A-n, 33A-n, of each phase leg and the at least one energy storage element 44 of the energy transfer circuit 40, to provide the desired voltage for each phase A, B, C. The controller 50 is also adapted to control, for each and every control period, the connection of some other energy storage elements, or second set of energy storage elements, selected from the remaining energy storage elements i2A-n, 22A-n, 33A-n of each phase leg and the at least one energy storage element 44 of the energy transfer circuit 40 to effectuate a power transfer within each phase leg 10, 20, 30 and to effectuate an energy transfer between the switching cells of each phase leg 10, 20, 30 and the energy transfer circuit 40, i.e. to especially effectuate an energy transfer between the capacitors i2A-n, 21A-n, 31A-n of each phase leg 10, 20, 30 and the capacitor, or capacitors, 44 of the energy storage circuit 40 that have not been selected for providing the respective phase voltage level of the control period. Figure 2 illustrates a method performed by a converter for providing phase voltages to a transmission grid and transferring energy between at least one phase leg 10, 20, 30 of the converter and an energy transfer circuit 40 connected to the phase legs 10, 20, 30. The controller 50 is adapted to control a converter arrangement to perform the method. For this purpose, the controller 50 is provided with means for performing the method steps, which means 51-55 can be implemented as a combination of software and hardware, especially as computer program, memory and processor, which computer program when executed by means of the processor and memory perform the method steps. The controller 50 is therefore provided with means 51 for monitoring voltages, means 52 for monitoring the phase currents, means 53 for selecting energy storage elements to provide the phase voltages, means 54 for selecting energy storage elements to provide the energy transfer and means 55 for executing the switching of the switching cells and the switches of the energy transfer circuit. Switching is provided at a switching frequency sufficiently high to provide a varying voltage of the grid frequency, in most transmission grids being 50Hz or 60 Hz. The effective switching may for example be 2.5 kHz, and for each control period the switching provides the outputted phase voltages at each respective reference voltage level by means of the switching cells selected for that control, or switching, period. The method starts with receiving a voltage reference level 201 to be provided to each phase A, B, C from each respective phase leg 10, 20, 30 by means of the switching cells 11A-n, 21A-n, 31A-n of each respective phase leg 10, 20, 30, and the at least one common energy storage element, capacitor 44, of the energy transfer circuit 40. The method continues with the step of establishing the voltage level 203 of each switching cell 11A-n, 21A-n, 31A-n. In step 204 the controller establish the voltage level for each of the at least one energy storage elements 44 of the energy transfer circuit 40. Suitably, the respective voltage level of every energy storage element nA-n, 21A-n, 31A-n, 44 is established in steps 203 and 204. The method continues with monitoring the currents 205 in each phase leg 10, 20, 30, and determines the direction of the power flow during the control period for each of the phase legs 10, 20, 30. Thus, the direction of the phase currents are used to choose in which direction the energy storage elements 12A-n, 22, A-n, 32A-n of the switching cells nA-n, 21A-n, 31A-n and the energy storage element or elements 44 of the transfer circuit 40 shall be connected so that the power is added to a capacitor if the voltage of the capacitor is below the nominal voltage and, vice versa, so that power is removed from the capacitor if the voltage of the capacitor is above the nominal voltages. Thus, by the monitoring of step 205 the direction in which each energy storage element shall be connected during the control period can be determined based on the direction of the phase current. The method further includes selecting energy storage elements i2A-n, 22A-n, 32A-n, 44, step 206, from each phase leg 10, 20, 30 and from the energy transfer circuit 40, to provide the reference voltage levels of the phases A, B, C. Suitably, a minimum number of switching cells is selected, i.e. a minimum number of cells to provide the voltage reference level. The selection is preferably based on the voltage levels of the energy storage elements i2A-n, 22A-n, 32A-n, 44 as established in steps 203 and 204, and the reference voltage levels obtained in step 201. Preferably also, energy storage elements are selected on the basis of the direction of the power flow in the phase leg during the control period, such that energy storage elements having the highest voltage levels are selected for control periods where power is supplied from the respective phase leg 10, 20, 30 to the transmission grid, and energy storage elements having the lowest voltage levels are selected for control periods during which power is received in the respective phase leg 10, 20, 30 from the transmission grid. Also, to obtain the desired phase voltages one of the energy storage elements are suitably only selected for being connected at a fraction of the control period, which fraction corresponds to the fraction of desired voltage contribution of thet energy storage element and the actual voltage level of that energy storage element. To exemplify a switching strategy, a reference voltage of 170 Volts may be provided by switching in a first cell having a capacitor voltage of 100 Volts for the whole switching period and switching in a second cell having a capacitor voltage of 100 Volts for 70% of the switching period. If the voltage levels deviate from a nominal voltage of 100 Volts, the switching is adjusted. Thus, to provide a voltage of 170 Volts, a first switching cell having a capacitor voltage of 98 volts can be switched in for the full switching period together with switching in a cell having a capacitor voltage level of 97.5 Volts for 74 % of the switching period to add up the required 170 Volts (since 98*1+97.5*0.74 is approximately 170 Volts). Thus, from measured capacitor voltages of the switching cells, a number of the switching cells of each phase leg are selected to synthesize the reference voltage of each phase. The method continues with selecting, step 208, the switching cells 11A-n, 21A-n, 31A-n to be used for transfer of energy between each phase leg 10, 20, 30 and the energy transfer circuit 40. The selection 208 is based on the established voltage levels of the energy storing elements i2A-n, 22A-n, 32An, of the at least one energy storage element 44 and the direction of the phase currents or phase power flow. In step 208 the selection is made from remaining energy storage elements 12A-n, 22A-n, 32A-n, 44, i.e. among those energy storage elements that have not been selected, in step 206, for providing the phase voltages. Preferably, out of the remaining switching cells 11A-n, 21A-n, 31A-n of each phase leg 10, 20, 30 and switches of the energy transfer circuit 40, those switching cells that are used for the remaining energy storage elements i2A-n, 22A-n, 32A-n, 44 having voltage levels that deviate the most from the nominal voltage levels should be selected. In an embodiment, the controller 50 is adapted to select those energy storage elements that have the largest deviation primarily, so that these storage elements have the largest likelihood of being subjected to the energy transf
[EN US2021184467A1]: LOW VOLTAGE, LOW FREQUENCY, MULTI LEVEL POWER CONVERTER [FR EP3403322A4]: CONVERTISSEUR DE PUISSANCE MULTINIVEAUX À BASSE TENSION ET BASSE FRÉQUENCE [ZH CN108702106A]: 低压低频多电平电源转换器 [DE EP3403322A4]: SPANNUNGSARMER, NIEDERFREQUENTER, MEHRSTUFIGER LEISTUNGSWANDLER [JA JP2019502355A]: 低電圧、低周波数、マルチレベル電力変換器 | [EN US2021184467A1]: A low voltage, low frequency multi-level power converter capable of power conversion is disclosed. The power converter may include a low voltage, low frequency circuit that includes a plurality of phase-shifting inverters in series; a plurality of low voltage source inputs, and a plurality of phase-shifting inverters in series. Each of the plurality of phase-shifting inverters may be configured to receive at least one of the plurality of low voltage source inputs; and generate at least one square wave output. A semi-sine wave output may be derived from the generated at least one square wave output. [FR EP3403322A4]: L'invention concerne un convertisseur de puissance multiniveaux à basse tension et basse fréquence pouvant accomplir une conversion de puissance. Le convertisseur de puissance peut comprendre: un circuit basse tension et basse fréquence comprenant une pluralité d'onduleurs à déphasage raccordés en série; une pluralité d'entrées de source basse tension, et une pluralité d'onduleurs à déphasage raccordés en série. Chacun de la pluralité d'onduleurs à déphasage peut être configuré pour recevoir au moins l'une de la pluralité d'entrées de source basse tension; et générer au moins une sortie d'onde carrée. Une sortie d'onde semi-sinusoïdale peut être dérivée desdits au moins une sortie d'onde carrée. [ZH CN108702106A]: 本发明公开了种能够进行电源转换的低压低频多电平电源转换器。所述电源转换器可以包括低压低频电路，所述低压低频电路包括串联的多个相移逆变器；多个低压源输入和串联的多个相移逆变器。所述多个相移逆变器中的每者可以被配置为接收多个低压源输入中的至少个，并生成至少个方波输出。可以从所生成的至少个方波输出导出半正弦波输出。 [JA JP2019502355A]: 電力変換が可能な低電圧、低周波マルチレベル電力変換器が開示される。この電力変換器は、直列の複数の位相インバータ、即ち、複数の低電圧源入力と、直列の複数の位相インバータとを含む。複数の位相シフトインバータの各々は、複数の低電圧源入力のうちの少なくとも1つを受信するように構成されてもよく、少なくとも1つの方形波出力を生成する。生成された少なくとも１つの方形波出力からほぼ完全な正弦波出力を出力することができる。【選択図】図１Ａ | WO2017124107A1 | 2017-07-20 | US2017013811W | 2017-01-17 | US201662278832P, 2016-01-14 US201662291333P, 2016-02-04 | WO2017124107A1: 2017-07-20 US10431989B2: 2019-10-01 US10873187B2: 2020-12-22 CN108702106A: 2018-10-23 EP3403322A4: 2018-11-21 JP2019502355A: 2019-01-24 US2021184467A1: 2021-06-17 | JABIL CIRCUIT INC RAFSANJAN SALMAN TALEBI ECKERSON DAVID MICHAEL JABIL INC ジャビル インク | RAFSANJAN SALMAN ECKERSON DAVID RAFSANJAN SALMAN TALEBI ECKERSON DAVID MICHAEL | H02M7/49: I H02M3/158: I H02S40/32: I H02J3/38: I H02J7/00: I H02M1/12: I H02M7/5387: I H02M1/00: I G05F1/67: I H02M1/00: N H02M3/158: N | H02M3/1582: A H02M7/49: I H02S40/32: I H02M1/007: A Y02E10/56: A H02J3/385: I H02J3/387: I H02J3/38: I H02J7/00: I H02M1/12: I H02M7/5387: I | US2015200603A1 JP2009064809A JP2013172616A US8842454B2 US2013181531A1 US2015021998A1 US2017229874A1 DE102008032813A1 CN103828217A CN205265555U WO2010003941A2 WO2013030236A2 WO2009073868A1 | EP3633816A1 EP3633816 3633816 US10873187B2 US10873187 10873187 NL2021570B1 NL2021570B 2021570 US2019379208A1 US2019379208 US20190379208A1 WO2020192863A1 WO2020192863 2020/192863 WO2020/192863A1 CN112019075A CN112019075 112019075 CN112019076A CN112019076 112019076 CN111541391A CN111541391 111541391 | [EN US2021184467A1]: 1. A low voltage, low frequency multi-level power converter capable of power conversion, comprising: a low voltage, low frequency circuit, comprising: a plurality of low voltage source inputs;a plurality of phase-shifting inverters in series, each of the plurality of phase-shifting inverters being configured to:receive at least one of the plurality of low voltage source inputs, andgenerate at least one square wave output; anda semi-sine wave output derived from the generated at least one square wave output. 2. The power converter of claim 1, wherein at least one of the low voltage source inputs is a semi -direct current (DC) power source. 3. The power converter of claim 1, further comprising at least one series voltage regulator in series with at least one of the plurality inverters. 4. The power converter of claim 1, wherein a level of total harmonic distortion of the power converter is less dependent on a load driven by the power converter. 5. The power converter of claim 3, further comprising a grid interconnection circuit including an output filter. 6. The power converter of claim 1, further comprising a plurality of photovoltaic (PV) modules, each of the plurality of PV modules being coupled to a photovoltaic panel. 7. The power converter of claim 6, wherein each of the plurality of PV modules comprises at least one of a maximum power point tracking system, a rapid shut down circuit, and an arc fault protection circuit. 8. The power converter of claim 7, wherein the PV module includes an operational mode with a maximum power point voltage value substantially matching an inverter desired input voltage. 9. The power converter of claim 8, wherein the PV module stores energy at an inverter dc bus capacitor. 10. The power converter of claim 1, wherein at least one of the plurality of the low voltage source inputs consists of one selected from at least one battery, fuel cells, and solar cells. 11. The power converter of claim 1, further comprising integration circuitry capable of electrically integrating at least one of the plurality of low voltage source inputs with the plurality of inverters. 12. The power converter of claim 9, wherein the PV module further comprises a dedicated module-level controller. 13. The power converter of claim 1, further comprising integration circuitry capable of integrating a plurality of the PV modules. 14. The power converter of claim 1, wherein at least one of the plurality of the low voltage sources is a residential power source. 15. The power converter of claim 1, wherein at least one of the plurality of low voltage sources is a commercial power source. 16. The power converter of claim 1, wherein the semi-sine wave output is coupled to a utility grid. 17. The power converter of claim 1, wherein ones of the plurality of inverters comprise single inductor buck-boost converters. 18. The power converter of claim 17, wherein the power converter is bi-directional. 19. The power converter of claim 1, wherein ones of the plurality of inverters comprise a half bridge topology. 20. The power converter of claim 1, wherein ones of the plurality of inverters comprise an H-bridge topology. [ZH CN108702106A]: 1. 一种能够进行电源转换的低压低频多电平电源转换器，包括： 低压低频电路，包括： 多个低压源输入； 串联的多个相移逆变器，所述多个相移逆变器中的每一者被配置为： 接收所述多个低压源输入中的至少一者，和 生成至少一个方波输出；和 从生成的至少一个方波输出导出的半正弦波输出。 2. 根据权利要求1所述的电源转换器，其中所述低压源输入中的至少一者是半直流 (DC)电源。 3. 根据权利要求1所述的电源转换器，还包括与所述多个逆变器中的至少一者串联的 至少一个串联电压调节器。 4. 根据权利要求1所述的电源转换器，其中所述电源转换器的总谐波失真水平较少地 取决于由所述电源转换器驱动的负载。 5. 如权利要求3所述的电源转换器，还包括电网互联电路，所述电网互联电路包括输出 滤波器。 6. 根据权利要求1所述的电源转换器，还包括多个光伏(PV)模块，所述多个PV模块中的 每一者耦合到光伏板。【可能包括电源优化器】 7. 根据权利要求6所述的电源转换器，其中所述多个PV模块中的每一个包括以下至少 一者:最大功率点跟踪系统、快速关闭电路和电弧故障保护电路。 8. 根据权利要求7所述的电源转换器，其中所述PV模块包括操作模式，所述操作模式具 有与逆变器期望输入电压基本匹配的最大功率点电压值。 9. 根据权利要求8所述的电源转换器，其中所述PV模块将能量存储在逆变器DC总线电 容器处。 10. 根据权利要求1所述的电源转换器，其中所述多个低压源输入中的至少一者包括从 以下中选择的一者:至少一个电池、燃料电池和太阳能电池。 11. 根据权利要求1所述的电源转换器，还包括集成电路，所述集成电路能够将所述多 个低压源输入中的至少一者与所述多个逆变器电气集成。 12. 根据权利要求9所述的电源转换器，其中所述PV模块还包括专用模块级控制器。 13. 根据权利要求1所述的电源转换器，还包括能够集成多个所述PV模块的集成电路。 14. 根据权利要求1所述的电源转换器，其中所述多个低压源中的至少一者是住宅电 源。 15. 根据权利要求1所述的电源转换器，其中所述多个低压源中的至少一者是商用电 源。 16. 根据权利要求1所述的电源转换器，其中所述半正弦波输出耦合到公用电网。 17. 根据权利要求1所述的电源转换器，其中所述多个逆变器中的一些包括单电感器降 压-升压转换器。 18. 根据权利要求17所述的电源转换器，其中所述电源转换器是双向的。 19. 根据权利要求1所述的电源转换器，其中所述多个逆变器中的一些包括半桥拓扑。 20. 根据权利要求1所述的电源转换器，其中所述多个逆变器中的一些包括H桥拓扑。 [JA JP2019502355A]: 電力変換を可能とする低電圧低周波マルチレベル電力変換器であって、 低電圧低周波回路であって、 複数の低電圧源入力と、 直列に接続された複数の位相シフトインバータと、 を具備し、前記複数の位相シフトインバータの各々は、 前記複数の低電圧源入力のうちの少なくとも1つを受け取り、 少なくとも1つの方形波出力を生成する、低電圧低周波回路と、 生成された少なくとも前記1つの方形波出力から導き出されたほぼ完全な正弦波出力と、 を具備することを特徴とする電力変換器。 前記低電圧源入力のうちの少なくとも1つは、不完全な直流(DC)であることを特徴とする請求項1に記載の電力変換器。 前記複数のインバータのうちの少なくとも1つと直列接続された少なくとも1つの直列電圧レギュレータをさらに具備することを特徴とする請求項1に記載の電力変換器。 前記電力変換器の総高調波歪みのレベルは、前記電力変換器によって駆動される負荷にほとんど依存しないことを特徴とする請求項1に記載の電力変換器。 出力フィルタを含むグリッド相互接続回路をさらに具備することを特徴とする請求項3に記載の電力変換器。 複数の光起電力(PV)モジュールをさらに具備し、前記複数のPVモジュールの各々は、光起電性パネルに結合されていることを特徴とする請求項1に記載の電力変換器。 前記複数のPVモジュールの各々は、最大電力点追従システム、高速シャットダウン回路、及びアーク故障保護回路のうちの少なくとも1つを含むことを特徴とする請求項6に記載の電力変換器。 前記PVモジュールは、インバータが要求する入力電圧に実質的に一致する最大電力点電圧値を有する動作モードを含むことを特徴とする請求項7に記載の電力変換器。 前記PVモジュールは、インバータDCバスコンデンサにエネルギーを蓄積することを特徴とする請求項8に記載の電力変換器。 前記複数の低電圧源入力のうちの少なくとも1つは、少なくとも1つのバッテリ、燃料電池、及び太陽電池から選択されるものからなることを特徴とする請求項1に記載の電力変換器。 前記複数の低電圧源入力のうちの少なくとも1つを前記複数のインバータに電気的に組み込むことができる積分回路をさらに具備することを特徴とする請求項1に記載の電力変換器。 前記PVモジュールは、専用モジュールレベルコントローラをさらに具備することを特徴とする請求項9に記載の電力変換器。 複数の前記PVモジュールを統合することができる積分回路をさらに具備することを特徴とする請求項1に記載の電力変換器。 前記複数の低電圧源の少なくとも1つは住宅用電源であることを特徴とする請求項1に記載の電力変換器。 前記複数の低電圧源のうちの少なくとも1つは、商用電源であることを特徴とする請求項1に記載の電力変換器。 前記ほぼ完全な正弦波出力は、ユーティリティグリッドに接続されることを特徴とする請求項1に記載の電力変換器。 前記複数のインバータのうちの1つは、単一インダクタバックブーストコンバータであることを特徴とする請求項1に記載の電力変換器。 前記電力変換器は双方向性であることを特徴とする請求項17に記載の電力変換器。 前記複数のインバータのうちの1つは、ハーフブリッジトポロジーを具備することを特徴とする請求項1に記載の電力変換器。 前記複数のインバータのうちの1つは、Hブリッジトポロジーを具備することを特徴とする請求項1に記載の電力変換器。 | [EN US2021184467A1]: CROSS-REFERENCE TO RELATED APPLICATION This application is a Continuation Application of U.S. application Ser. No. 16/548,502, filed Aug. 22, 2019, entitled: LOW VOLTAGE, LOW FREQUENCY, LOW FREQUENCY, MULTI-LEVEL POWER CONVERTER, which claims the benefit of priority to U.S. application Ser. No. 15/408,219, filed Jan. 17, 2017, entitled LOW VOLTAGE, LOW FREQUENCY, MULTI LEVEL POWER CONVERTER, which claims the benefit of priority to U.S. Provisional Application No. 62/291,333 and U.S. Provisional Application No. 62/278,832, both entitled LOW VOLTAGE, LOW FREQUENCY, MULTI LEVEL POWER CONVERTER, the entirety of both of which are incorporated herein by reference as if set forth in their entireties. FIELD OF THE DISCLOSURE The present disclosure is directed generally to power conversion, such as solar inverters and battery coupled inverters/chargers, and more particularly is directed to a low voltage, low frequency, multi-level power converter. SUMMARY According to certain embodiments of the present disclosure, a low voltage, low frequency multi level power converter (LV LF MLPC) apparatus and method for power conversion (i.e., DC/AC or AC/DC) may be provided. The present disclosure may use low voltage, low cost, high performance components (e.g. MOSFETs, diodes, capacitors, inductors, resistors, etc.) and may drive the power devices (e.g. MOSFETs and diodes) at low frequency (e.g., utility frequency) to generate a desired voltage and current wave (e.g., a semi-sine wave at 220Vrms/50 Hz or 240Vrms/60 Hz) for an AC load. As a result, the present disclosure may provide several advantages, such as low cost, high efficiency, low environmental impact (e.g. low THD, low EMI, low leakage current etc.), high reliability, and safety standard compliance. LV LF MLPC may be used in certain embodiments to convert electricity from a power source (e.g., a photovoltaic (PV) panel, battery, fuel cell, etc.) to a load (e.g., public utility or any other AC loads). The individual LV LF power converters (LV LF PC) may be integrated with power sources, such as in PV panels or battery modules, such as to make integrated AC modules. A number of AC modules may be connected in series to make a LV LF MLPC system, by way of example. By way of non-limiting example, a LV LF MLPC and power conversion system as described herein may be applied to a wide variety of systems, from residential to commercial, industrial to utility scale, and such as, by way of non-limiting example, as grid-tied solar inverters, off-grid solar inverters, solar battery coupled inverters, grid-tied battery chargers, etc. Further, depending on the geographic region of application (e.g., US, Europe, etc.), the input power source (solar, battery, etc.), the load (single/three phase public utility, AC loads, etc.), and the desired power level, the LV LF MLPC system may be any type of a 3-phase/1-phase, PFC/non-PFC, or the like. By way of non-limiting example, the disclosed LV LF MLPC may create a 240 Vrms, 60 Hz voltage wave by adding a predetermined number, such as up to 14, series low voltage (e.g. 24.2Vdc), low frequency (e.g. 60 Hz), and phase shifted power sources. The power sources may be from a PV panel in conjunction with a DC/DC optimizer, or from a battery in conjunction with a bidirectional DC/DC charger, by way of example. By way of non-limiting example, in the solar inverter industry and in comparison with existing solutions (e.g. AC micro-inverters, power optimizers and string inverters), the disclosed LV LF MLPC is lower cost and uses lower voltage with more efficient components. It may also eliminate the need for an isolation transformer, and may dissipate less power in switching intervals due to very lower switching frequency and lower device blocking voltages during typical operation. Disclosed embodiments may also use series cabling, which eliminates the need for an expensive bus connector system. Further, in comparison with DC power optimizers, the disclosed LV LF MLPC may result in large system cost savings due to elimination of a string inverter (to which is often allocated a large portion of the system cost). Also, disclosed embodiments may result in higher overall system efficiency than in the known art, such as due to avoiding high voltage devices and switching at high frequency at the inverting stage. In comparison with previously known string inverters, the disclosed LV LF MLPC may benefit from module level control, which may ultimately be required by National Electric Code (NEC) and Underwriters Laboratories (UL), and may also benefit from module level Maximum Power Point Tracking (MPPT), which utilizes the PV panels at their most efficient operating point. Embodiments also may result in overall cost saving and efficiency improvements by avoiding the need for various additional high voltage components. Accordingly, certain of the embodiments may provide a low voltage, low frequency multi-level power converter that may include a low voltage, low frequency circuit that includes a plurality of low voltage source inputs; and a plurality of phase-shifting inverters in series. Each of the plurality of phase-shifting inverters may be configured to receive at least one of the plurality of low voltage source inputs; and generate at least one square wave output. A semi-sine wave output may be derived from the generated at least one square wave output. BRIEF DESCRIPTION OF THE FIGURES Referring now to the figures incorporated herein, shown are non-limiting embodiments of the present disclosure, wherein like numerals represent like elements, and wherein: FIG. 1A shows a block diagram of a square wave based LV LF MLPC; FIG. 1B shows an enlarged view of a portion of square wave outputs of individual inverters of the LV LF MLPC; FIG. 2 shows asymmetrical and symmetrical (centered) square waves patterns; FIG. 3 shows a block diagram of a sine wave based LV LF MLPC; FIG. 4 shows a block diagram of a square wave based LV LF MLPC with unfolding H bridge converter; FIG. 5 shows a block diagram of a sine wave based LV LF MLPC with unfolding H bridge converter; FIG. 6 shows examples of power source configurations as input to the LV LF PC; FIG. 7A shows a non-limiting example of a LV LF MLPC for regulating output voltage; FIG. 7B shows an enlarged view of the LV SVR and grid interconnection circuit; FIG. 8 shows rise/fall times of step voltages of a square wave output of an inverter of the LV LF MLPC; FIG. 9 shows a high level connection of an LV SVR 900 between the LV LF MLPC connected to PV panels and a load and grid; FIG. 10 shows a PV and battery storage system integrated with public utility. FIG. 11 shows a block diagram of integrated AC PV modules and AC battery modules in a LV LF MLPC system; FIG. 12 illustrates an exemplary database calculation of phase shift angles; and FIG. 13 illustrates an exemplary calculation of THD and optimal phase shift for certain of the embodiments. DETAILED DESCRIPTION The figures and descriptions provided herein may have been simplified to illustrate aspects that are relevant for a clear understanding of the herein described apparatuses, systems, and methods, while eliminating, for the purpose of clarity, other aspects that may be found in typical similar devices, systems, and methods. Those of ordinary skill may thus recognize that other elements and/or operations may be desirable and/or necessary to implement the devices, systems, and methods described herein. But because such elements and operations are known in the art, and because they do not facilitate a better understanding of the present disclosure, for the sake of brevity a discussion of such elements and operations may not be provided herein. However, the present disclosure is deemed to nevertheless include all such elements, variations, and modifications to the described aspects that would be known to those of ordinary skill in the art. Embodiments are provided throughout so that this disclosure is sufficiently thorough and fully conveys the scope of the disclosed embodiments to those who are skilled in the art. Numerous specific details are set forth, such as examples of specific components, devices, and methods, to provide a thorough understanding of embodiments of the present disclosure. Nevertheless, it will be apparent to those skilled in the art that certain specific disclosed details need not be employed, and that embodiments may be embodied in different forms. As such, the disclosed embodiments should not be construed to limit the scope of the disclosure. As referenced above, in some embodiments, well-known processes, well-known device structures, and well-known technologies may not be described in detail. The terminology used herein is for the purpose of describing particular embodiments only and is not intended to be limiting. For example, as used herein, the singular forms “a”, “an” and “the” may be intended to include the plural forms as well, unless the context clearly indicates otherwise. The terms “comprises,” “comprising,” “including,” and “having,” are inclusive and therefore specify the presence of stated features, integers, steps, operations, elements, and/or components, but do not preclude the presence or addition of one or more other features, integers, steps, operations, elements, components, and/or groups thereof. The steps, processes, and operations described herein are not to be construed as necessarily requiring their respective performance in the particular order discussed or illustrated, unless specifically identified as a preferred or required order of performance. It is also to be understood that additional or alternative steps may be employed, in place of or in conjunction with the disclosed aspects. When an element or layer is referred to as being “on”, “upon”, “connected to” or “coupled to” another element or layer, it may be directly on, upon, connected or coupled to the other element or layer, or intervening elements or layers may be present, unless clearly indicated otherwise. In contrast, when an element or layer is referred to as being “directly on,” “directly upon”, “directly connected to” or “directly coupled to” another element or layer, there may be no intervening elements or layers present. Other words used to describe the relationship between elements should be interpreted in a like fashion (e.g., “between” versus “directly between,” “adjacent” versus “directly adjacent,” etc.). Further, as used herein the term “and/or” includes any and all combinations of one or more of the associated listed items. Yet further, although the terms first, second, third, etc. may be used herein to describe various elements, components, regions, layers and/or sections, these elements, components, regions, layers and/or sections should not be limited by these terms. These terms may be only used to distinguish one element, component, region, layer or section from another element, component, region, layer or section. Thus, terms such as “first,” “second,” and other numerical terms when used herein do not imply a sequence or order unless clearly indicated by the context. Thus, a first element, component, region, layer or section discussed below could be termed a second element, component, region, layer or section without departing from the teachings of the embodiments. By way of non-limiting example, the aforementioned figures may demonstrate specific component types, such as a MOSFET, rather than a more generic bidirectional device, but such component choices are not intended to limit the embodiments unless otherwise indicated. That is, the figures are described in sufficient detail to enable those skilled in the art to practice the disclosure, but it is to be understood that other configurations may be utilized at least in that structural, device, and electrical characteristics changes may be made without departing from the scope of the present disclosure. The following description of exemplary embodiments is, therefore, not to be taken as limiting. Referring to FIGS. 1A and 1B, a LV LF MLPC 100 is shown, which is suitable for generating a utility rated voltage wave, V_MLI 120, (e.g. 240Vrms, 60 Hz) by adding up n (e.g. 14) voltage sources 102, V1 . . . Vn (e.g. 24.2V), with proper phase angles, φ1 . . . φn 104. The input voltages 102 (V1, . . ., Vn) need not be equal, and in many applications may be different, as will be appreciated by the skilled artisan. Further, phase angles (φ1 . . . φn) may be equal (symmetrical or centered) or unequal (asymmetrical). Moreover, depending on the number of input power sources (n) and voltage values (V1 . . . Vn), the phase angles (φ1 . . .φn) may be adjusted to reduce the total harmonic distortion (THD) and improve balancing power drawn by individual power sources; however, the dependency of the THD on the power sources voltage values is not noteworthy, and in many cases the phase angles may be calculated off-line and considered fixed, by way of non-limiting example and as discussed further below with respect to FIGS. 12 and 13. The phase angles may be equal (symmetrical) and the pulses duty cycles (Di+and Di−) adjusted to achieve a similar utility rated voltage waveform with a similar level of THD. Such a configuration may, however, cause more imbalanced power to be drawn from individual power sources. Additionally, input power sources for use in the disclosed embodiments may vary. By way of non-limiting example, input power sources may include, but are not limited to, batteries, fuel cells, solar cells, and/or particularly solar panels (and/or the battery storage associated therewith). Returning now to FIG. 1A, the power inverters 110 may be switched at a very low frequency, such as utility frequency (e.g. 50 Hz or 60 Hz); however, the switching frequency may be higher, such as 2X, 3X, 4X of utility frequency. Further, since the power inverters 110 are in series, the circuit components may be low voltage, which provides benefit from low cost, fast switching speeds and low conduction losses. Also, since the disclosed inverter(s) 110 may be driven at low frequency, the switching loss, electromagnetic interferences (EMI), and common mode currents (leakage currents) may be very low. Low switching frequency also allows for adjusting voltage steps rise/fall time to further reduce the EMI and leakage current with an acceptable switching loss increment. In addition, the output voltage (V_MLI) quality (THD) is less dependent on load level and might not change over the entire load range. The output voltage, V_MLI, and output current, I, may be in phase (unity power factor), leading or lagging (non unity power factor), as shown in the bidirectional system illustrated in FIG. 1A. Optionally, a series voltage regulator 112 may be coupled (e.g., in series with) to one or more of the inverters 110 to smooth out voltage steps of the output 120. The series voltage regulator 112 may take the form of a full bridge converter or any other type of voltage regulator as known in the art. By way of non-limiting example, for an asymmetrical case study and considering the power sources' voltages equal to 24.2 Vdc, i.e., V=[24.2V, 24.2V, . . ., 24.2V], the phase angles equal to φ=[1.8°, 6.1°, 10.5°, 14.4°, 18.9°, 23.4°, 27.9°, 32.4°, 37.8°, 43.2°, 48.6°, 55.8°, 63°, 75.6°], the high side devices duty cycles equal to D+=D−=[28.5%, 30.8%, 31.6%, 32.5%, 32.75%, 33%, 33.25%, 33.25%, 33%, 32.75%, 32.5%, 31.6%, 30.8%, 28.5%], and the low side devices duty cycle equal to 1−D+(or 1−D−), the output voltage (V_MLI) THD will be 2.8%. Obviously, the output voltage THD is independent of the output load, which is significant as will be understood to the skilled artisan. Assuming a 14.7A rms load semi-sine current (V_MLI=240Vrms, Rload=16.3 ohms), and knowing that all converters are in series and handle the same load current, the output power of individual converters will be different, as P=[199W, 231W, 246W, 260W, 267W, 272W, 275W, 275W, 272W, 267W, 260W, 246W, 231W, 199W], and the total power will be 3500W. Since in a chain of series converters the sequence of turning on the converters should not impact the output voltage waveform, by way of non-limiting example, one way to balance the average power among similar power sources is to rotate the turn-on period of the converters “circularly” to make individual power source output power balanced in n (14) or n/2 (7) utility voltage cycles (e.g. at 60 Hz the cycle will be 16.66 ms). Also by way of non-limiting example, another method for balancing power among similar power sources is described below. Assuming the input power sources voltages are controllable, then with regulating the input voltages at V=[30.9V, 26.6V, 25V, 23.8V, 23V, 22.5V, 22.3V, 22.3V, 22.5V, 23V, 23.8V, 25V, 26.6V, 30.9V] and keeping the phase angles and duty cycles equal to previous values, the output voltage THD will be 3.6% and the delivered power of individual power sources will be 250W, (balanced powers). As mentioned, the output voltage THD dependency on the input power sources voltages is not noteworthy, and may be readily kept under a desired value, which is allowed by typical global standards. For instance, considering the same phase angles and duty cycles for the 14 power source LV LF MLPC system 100, the THD value will be as follows for different case studies: V=[24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V, 24.2V]→THD=2.8% V=[30.9V, 26.6V, 25V, 23.8V, 23V, 22.5V, 22.3V, 22.3V, 22.5V, 23V, 23.8V, 25V, 26.6V, 30.9V]→THD=3.6% V=[30V, 16V, 13V, 32V, 20V, 15V, 10V, 33V, 38V, 24V, 24V, 12V, 36V, 24V]→THD=4.35% V=[33V, 8V, 45V, 20V, 33V, 12V, 8V, 40V, 22V, 36V, 11V, 20V, 45V, 8V]→THD=4.4% V=[0V, 31V, 31V, 0V, 31V, 31V, 31V, 31V, 0V, 31V, 31V, 31V, 31V, 31V]→THD=4.7% V=[15V, 16V, 13V, 32V, 28V, 15V, 32V, 33V, 38V, 24V, 24V, 20V, 20V, 24V]→THD=4.8% It should be noted that the above discussed low THD values may be achievable without an LV SVR (such as the LV SVR shown in FIG. 7) By way of non-limiting example, FIGS. 1A and 1B demonstrate one of many patterns for creating a semi-sine voltage wave from n series LV LF inverters 110s. Relatedly, FIG. 2 demonstrates power converter turn-on patterns, asymmetrical vs. symmetrical. For example, the first two signal patterns to the left 202, 204 in FIG. 2 show asymmetrical patterns as previously described, as compared to the third pattern 206 (farthest to the right) which shows a symmetrical or centered pattern. However, all patterns may result in the same output voltage wave (V_MLI), and the major difference may be in the amount of power drawn from individual power sources. In short, an asymmetrical pattern helps to split output power more evenly among all power sources per half cycle (assuming similar power sources), and the symmetrical pattern allows splitting output power more evenly among all power sources over one or more full cycles . Since the power converters are in series as a chain in the example of FIG. 2 (i.e., the inverters are in series as illustrated), there is significant flexibility on the converters' turning-on sequence, and thus, with a circularly cyclical turn-on sequence, balancing equal power among converters with similar input power sources is highly feasible. FIG. 3 shows a block diagram of a sine wave based LV LF MLPC 302 suitable for generating a utility-rated voltage wave, V_MLI 120, (e.g. 240Vrms, 60 Hz) by adding up n (e.g. 14) in-phase power sources 102, i.e., V1 . . . Vn (e.g. 24Vrms). As shown in the example, all power sources are full rectified sine waves and all are at the same frequency (e.g. 120Hz) and in phase. The difference may be the voltage magnitude and the power level sourced. The input voltages (V1, Vn) may be equal or different. Requirements may include that summed peak values meet the load rating voltage (e.g. 240Vrms). Since all inverters shown may be in series (as shown) and drive the load current, the individual power converter power delivery depends on the voltage magnitude (e.g. Vi-pk) and its phase angle with the current wave. The sine wave based LV LF MLPC 302 may improve THD, EMI, and leakage current more than the square wave based LV LF MLPC 100 (without an LV SVR, such as the LV SVR 112 described with respect to FIG. 1A) assuming that the power source voltage is pure rectified sine wave and no current distortion at zero crossing points occurs. Of note, in the square wave based LV LF MLPC system 100, the small voltage steps of the output voltage (V_MLI) may initiate some level of THD, EMI, and leakage current. It should be noted that including an LV SVR (such as for example LV SVR 112) in series with the LV LF MLPC 100 may result in a greater improvement of THD, EMI, and leakage current more than the sine wave based LV LF MLPC 302, and, in addition, may reduce the size of utility frequency filters. Moreover, the THD may be independent of a load. FIG. 4 shows a block diagram of a square wave based LV LF MLPC 400 that is differentiable from the exemplary embodiment of FIG. 1A. As shown, a difference may be that the power converters 110 may use a half-bridge topology instead of an H-bridge topology. In such a case, one high voltage unfolding H-bridge converter 402 may be interfaced between the MLPC stage and the output stage to make a semi-sine wave voltage from a full rectified semi-sine wave. More particularly, the power converter 400 of FIG. 4 may provide a multi-level inverter that uses, for example, DC bus capacitors to generate a semi-sine wave. In light of the foregoing and in light of known applications for multi-level inverters, embodiments may provide a higher speed and lower dissipation in implementation than prior known efforts, such as for use with sub-100V devices. Accordingly, the embodiments may provide multi-level inverters to effect distributed power conversion, such as may be connected via cables. Further, embodiments such as those represented in the example of FIG. 4 may use several pulse power supplies in series to thereby generate a semi-sine wave power. However, the multi-level converter 400 of FIG. 4 may nevertheless be subjected to single-center control, and parts may be integrated as compactly as practicable to avoid voltage spikes and similar inefficiencies. Moreover, in the embodiments discussed throughout, and particularly with respect to the example of FIG. 4, the wave frequency may change motor speed control, and given the fixed capacitor voltages and the need to control them, active filters may be employed in the embodiments. It goes without saying that active filters, as may be used in the disclosed applications, are appreciably less bulky, and hence more suitable and efficient in the disclosed applications, than the passive filters of the known art. Yet further, to the extent voltage source inverters are used in the known art, PWM is performed with each pulse, requiring increasingly large and expensive passive filters. However, a current source inverter may be driven by the current pulses as shown, and may use active filtering, thereby avoiding the difficulties inherent in the known art. FIG. 5 shows a block diagram of a sine wave based LV LF MLPC 500 with aspects differentiable from the example of FIG. 3. As shown, a difference is that the series LV power converters may be replaced by one high voltage unfolding H bridge converter 502 interfaced between the series power sources and the output stage, such as to make a sine wave voltage from a full rectified sine wave. FIG. 6 demonstrates a few of many prospective input power sources. By way of non-limiting example, the power source to the individual power converters may be a PV panel 602 or a battery 604. To utilize a PV panel at its maximum deliverable power operating point, a power optimizer or maximum power point tracker may be desired. There are many different power converter topologies that may implement MPPT to PV panels. As a non-limiting example, a single inductor buck-boost converter with DC or sine rectified output voltage may be such a converter. Moreover, to utilize a battery in an efficient way, depending on the battery chemistry, different charge cycles are recommended by battery manufacturers. To fulfill the recommendations, different types of power converters can be utilized. As a non-limiting example, a single inductor buck-boost converter with DC or rectified sine output voltage may be used. For battery charging, the input power source and load may exchange their roles and thus the power and current flow direction may be opposite. In the case of using bidirectional devices (e.g. MOSFETs), the current can flow in both directions, and since the single inductor buck-boost converter is a symmetrical circuit, there is no difference in the case of opposite power flow as long as components' voltage and current ratings are considered. FIG. 7A shows a non-limiting example of a LV LF MLPC 702, for regulating output voltage and smoothing out the voltage steps in the LV LF MLPC output voltage Vg. The LV LF MLPC 702 may be connected in series with a low voltage series voltage regulator (LV SVR) 704 demonstrated in FIG. 7 to smooth out the voltage steps of the LV LF MLPC output voltage wave Vg. This LV SVR 704, along with the LV LF MLPC 702 generates a semi-sine wave that may improve load current THD significantly. Also, the LV SVR 704 may have a quick response time. Thus, the LV SVR 704 may respond to grid transient needs and block their impacts on the LV LF MLPC performance. In case of connection to photovoltaic (PV) panels, in response to quick sun light variation or shade before the control system can response accordingly, the LV SVR 704 may compensate for differences between the desired output voltage and the voltage Vg that LV LF MLPC 702 can deliver temporarily. Subsequently, the LV LF MLPC 702 re-adjusts itself and takes over and brings back the operation to normal mode. Since the LF inverters 706 (the H-bridge (4 MOSFETs)) are driven at low frequency, e.g. 60 Hz, the switching loss is not a concern, so slowing the switching time may be feasible without a considerable switching loss increment. This slowed switching time may slow the rise/fall times of the step voltages as shown in FIG. 8 and may help the LV SVR control system 704 to command more effectively for smoothing out the step voltages out of the output voltage (semi-sine wave). Also, the LV SVR 704 may include a grid interconnection circuit 708 to facilitate integration with the grid. An enlarged view of the grid interconnection circuit 708 showing components thereof, is shown in FIG. 7B. FIG. 9 demonstrates a high level connection of an LV SVR 900 between the LV LF MLPC 902 connected to PV panels 904 and a load 906 and grid 908. In this configuration, the DC bus 910 may be a regulated DC bus capacitor bank or a voltage source. This LV SVR 900 also gains from low voltage and high performance power components but switching at higher switching frequency such as 100 KHz. As a result, the LV SVR 900 may employ small passive components such as magnetics and capacitors. As such the LV SVR 900 may facilitate a reduction of leakage (common mode) current between the PV panels 904 and grid 908. The structure of the PV panels 904 may result in a stray capacitor between PV cells and a panel frame. In addition to the PV panel structure, the capacitance also depends on environmental condition such as rain, dust, etc. It is known that a maximum capacitance may be up to approximately 160 nF/kW. Consequently, a high frequency leakage current may be exhibited due at least in part to suppression of voltage steps of the LV LF MLPC output voltage Vg, resulting in the utility frequency (e.g. 60 Hz) portion of the leakage current will exist after adding the LV SVR 900 which may be relatively small and may be controllable by a common mode choke. FIG. 10 shows a PV 1002 and battery 1004 storage system 1000 integrated with public utility. Obviously, there are many alternatives for making such a system, and as such the example provided in FIG. 10 is non-limiting in nature. This example emphasizes that the disclosed LV LF MLPC system 1000 is a bi-directional system and may be utilized for any power flow direction. For instance, in cases having a battery as power source, during charging cycle, the battery becomes a load and the output (e.g. grid or a PV system) becomes a power source. As mentioned above, the LV LF MLPC system 1000 can thus be controlled to do the same function but in opposite direction. By way of non-limiting example, FIG. 11 shows block diagrams of integrated AC PV modules 1102 and AC battery modules 1104 in a LV LF MLPC system 1100. An LV SVR 1106 may be added as a module or may be integrated into another of the modules, by way of example. FIG. 12 illustrates an exemplary database calculation of phase shift angles, using THD as an index, to obtain semi-sine waves in the form of phase shifted square waves pursuant to the disclosed embodiments. At least because of square-waves, real time but at low frequency (e.g. 60 Hz) THD calculation is easily achievable and may be used for avoiding off line phase shift angles calculation and update optimal angles in real time mode whenever needed. To explore this task burden, Series Fourier and THD calculation may be developed for the 14 PV panel system The Fourier series and THD calculation equations are shown in FIG. 13. The skilled artisan will appreciate that various methodologies to calculate THD are known, and the example provided in FIGS. 12 and 13 experientially inserts different angles to therefrom calculate the optimal angle for a given parameter (such as Vrms) in a particular application. Of course, it may be appreciated that, when the output voltage and/or number of active solar modules change, by way of example, the experiential angles used may change as well. The descriptions of the disclosure are provided to enable any person skilled in the art to make or use the disclosed embodiments. Various modifications to the disclosure will be readily apparent to those skilled in the art, and the generic principles defined herein may be applied to other variations without departing from the spirit or scope of the disclosure. Thus, the disclosure is not intended to be limited to the examples and designs described herein, but rather is to be accorded the widest scope consistent with the principles and novel features disclosed herein. [ZH CN108702106A]: 低压低频多电平电源转换器 [0001] 相关申请的交叉引用 [0002] 本申请要求美国临时申请No. 62/291，333和美国临时申请No . 62/278，832的优先 权，两者均标题为LOW V0LTAGE，L0W FREQUENCY,MULTI LEVEL POWER CONVERTER，两者的全 部内容通过引用并入本文，如同以其整体阐述一样。 技术领域 [0003] 本公开一般涉及电源转换，例如太阳能逆变器和电池耦合的逆变器/充电器，并且 更具体地涉及低压低频多电平电源转换器。 发明内容 [0004] 根据本公开的某些实施例，可以提供用于电源转换（即，DC/AC或AC/DC)的低压低 频多电平电源转换器(LV LF MLPC)装置和方法。本公开可以使用低电压，低成本，高性能的 组件(例如，M0SFET，二极管，电容器，电感器，电阻器等），并且可以以低频率(例如，公用频 率）驱动功率器件（例如，MOSFET和二极管），为AC负载产生所需的电压和电流波（例如， 220Vrms/50Hz或240Vrms/60Hz的半正弦波）。因此，本公开可以提供若干优点，例如低成本， 高效率，低环境影响(例如，低THD，低EMI，低泄漏电流等），高可靠性和安全标准符合性。 [0005] LV LF MLPC可以在某些实施例中用于将电力从电源(例如，光伏(PV)板，电池，燃 料电池等)转换为负载(例如，公共设施或任何其他AC负载）。各个LV LF电源转换器(LV LF PC)可以与电源(例如PV板或电池模块)集成，例如用于制造集成AC模块。作为示例，多个AC 模块可以串联连接以制造LV LF MLPC系统。 [0006] 作为非限制性示例，如本文所述的LV LF MLPC和电源转换系统可以应用于各种系 统，从住宅到商业，工业到公用事业，并且例如，作为非限制性示例，作为并网太阳能逆变 器、离网太阳能逆变器、太阳能电池耦合逆变器、并网电池充电器等。此外，取决于应用的地 理区域(例如，美国，欧洲等）、输入电源(太阳能，电池等）、负载(单相/三相公用设施，交流 负载等)和所需的功率电平，LV LF MLPC系统可以是任何类型的三相/1相，PFC/非PFC等。 [0007] 作为非限制性示例，所公开的LV LF MLPC可以通过添加预定数量(例如，高达14 个）的串联低压（例如，24.2Vdc)、低频(例如，60Hz)相移电源来产生240Vrms，60Hz的电压 波。作为示例，电源可以来自与DC/DC优化器结合的PV板，或者来自与双向DC/DC充电器结合 的电池。 [0008] 作为非限制性示例，在太阳能逆变器工业中并且与现有解决方案(例如AC微型逆 变器，电源优化器和组串式逆变器)相比，所公开的LV LF MLPC成本更低，并且使用的是电 压更低，效率更高的组件。它还可以消除对隔离变压器的需要，并且由于在典型操作期间非 常低的开关频率和较低的器件阻断电压，因此可以在开关间隔中耗散较少的功率。 [0009] 所公开的实施例还可以使用串联电缆，这消除了对昂贵的总线连接器系统的需 要。此外，与DC电源优化器相比，所公开的LV LF MLPC由于消除了组串式逆变器(其通常占 据大部分的系统成本)而可以大大节省系统成本。而且，所公开的实施例可以产生比现有技 术更高的整体系统效率，例如由于避免高压器件和开关在反相阶段以高频切换。 [0010] 与先前已知的组串式逆变器相比，所公开的LV LF MLPC可受益于模块级控制，其 可能最终由国家电气规范(NEC)和美国保险商实验室(UL)要求，并且还可受益于模块级最 大功率点跟踪(MPPT)，它在最有效的工作点使用PV板。通过避免对各种附加高电压组件的 需要，实施例还可以节省总体成本和提高效率。 [0011] 因此，某些实施例可以提
[EN CA3005146C]: MEDIUM VOLTAGE TRANSFORMERLESS MULTILEVEL CONVERTER AND METHOD FOR CONTROLLING A MEDIUM VOLTAGE TRANSFORMERLESS MULTILEVEL CONVERTER [FR CA3005146C]: CONVERTISSEUR A PLUSIEURS NIVEAUX SANS TRANSFORMATEUR DE TENSION MOYENNE ET PROCEDE DE COMMANDE D'UN CONVERTISSEUR A PLUSIEURS NIVEAUX SANS TRANSFORMATEUR DE TENSION MOYENNE [ZH CN108292896B]: 中压无变压器多电平变换器及用于控制中压无变压器多电平变换器的方法 [DE EP3353884A1]: MEHRSTUFIGER TRANSFORMATORLOSER MITTELSPANNUNGSWANDLER UND VERFAHREN ZUR STEUERUNG EINES MEHRSTUFIGEN TRANSFORMATORLOSEN MITTELSPANNUNGSWANDLERS [PT BR112018009080A8]: conversor de níveis múltiplos desprovido de transformador de média tensão, método para controlar um conversor de níveis múltiplos desprovido de transformador de média tensão, e sistema de acionamento elétrico [RU RU2693573C1]: БЕСТРАНСФОРМАТОРНЫЙ МНОГОУРОВНЕВЫЙ ПРЕОБРАЗОВАТЕЛЬ СРЕДНЕГО НАПРЯЖЕНИЯ И СПОСОБ ДЛЯ УПРАВЛЕНИЯ БЕСТРАНСФОРМАТОРНЫМ МНОГОУРОВНЕВЫМ ПРЕОБРАЗОВАТЕЛЕМ СРЕДНЕГО НАПРЯЖЕНИЯ | [EN CA3005146C]: A multilevel converter includes single phase configurations. A single phase configuration has a first half-bridge (HB) module, a second HB module separated by a first capacitor coupled to a DC link, and a neutral point clamped (NPC) module clamped to the first HB module and the second HB module. Further, the single phase configuration has a first individual switching device and a second individual switching device, the first individual switching device operably connected to the first HB module and the NPC module, and the second individual switching device operably connected to the second HB module and the NPC module. The converter further includes a power output assembly comprising multiple phases and providing multiple-phase alternating (AC) power, wherein the single phase configuration supplies power to one of the multiple phases of the power output assembly. [FR EP3353884A1]: Selon l'invention, un convertisseur à plusieurs niveaux comprend des configurations monophasées. Une configuration monophasée comporte un premier module demi-pont (HB), un deuxième module HB séparé par un premier condensateur accouplé à une liaison CC, et un module nivelé par point neutre (NPC) connecté au premier module HB et au deuxième module HB. De plus, la configuration monophasée comporte un premier dispositif de commutation individuelle et un deuxième dispositif de commutation individuelle, le premier dispositif de commutation individuelle étant connecté fonctionnellement au premier module HB et au module NPC, et le deuxième dispositif de commutation individuel étant connecté fonctionnellement au deuxième module HB et au module NPC. Le convertisseur comprend aussi un ensemble de sortie de puissance comprenant plusieurs phases et fournissant une alimentation alternative (CA) polyphasée, où la configuration monophasée fournit de la puissance à une des multiples phases de l'ensemble de sortie de puissance. [ZH CN108292896B]: 一种多电平变换器，包含单相配置。单相配置具有由耦合到DC链路的第一电容器分离的第一半桥(HB)模块、第二HB模块，以及钳位到第一HB模块和第二HB模块的中点钳位(NPC)模块。此外，单相配置具有第一单独开关器件和第二单独开关器件，第一单独开关器件可操作地连接到第一HB模块和NPC模块，并且第二单独开关器件可操作地连接到第二HB模块和NPC模块。变换器还包含功率输出组件，功率输出组件包括多相并且提供多相交流(AC)功率，其中单相配置向功率输出组件的多相中的一相提供功率。 [PT BR112018009080A8]: a presente invenção refere-se a um conversor de níveis múltiplos, que inclui configurações de fase única. uma configuração de fase única tem um primeiro módulo em meia-ponte (hb), um segundo módulo hb separado por um primeiro capacitor acoplado a um enlace cc, e um módulo de diodos de ponto neutro fixo (npc) ligado ao primeiro módulo hb e ao segundo módulo hb. ainda mais, a configuração de fase única tem um primeiro dispositivo de comutação individual e um segundo dispositivo de comutação individual, o primeiro dispositivo de comutação individual ligado operacionalmente ao primeiro módulo hb e ao módulo npc, e o segundo dispositivo de comutação individual ligado operacionalmente ao segundo módulo hb e ao módulo npc. o conversor inclui ainda uma montagem de potência de saída compreendendo fases múltiplas e proporcionando potência de corrente alternada (ca) de fases múltiplas, em que a configuração de fase única fornece alimentação a uma das fases múltiplas do montagem de potência de saída. [RU RU2693573C1]: Изобретение относится к области электротехники и может быть использовано в приводах переменного тока среднего напряжения, гибких системах передачи и системах передачи постоянного тока высокого напряжения. Техническим результатом является упрощение управления многоуровневым преобразователем. Многоуровневый преобразователь включает в себя однофазные конфигурации. Однофазная конфигурация имеет первый полумостовой (HB) модуль, второй HB модуль, разделенные первым конденсатором, связанным с DC-линией, и модуль с фиксированной нейтралью (NPC), подсоединенный к первому НВ модулю и второму НВ модулю. Кроме того, однофазная конфигурация имеет первое отдельное переключающее устройство и второе отдельное переключающее устройство, причем первое отдельное переключающее устройство операционно соединено с первым НВ модулем и модулем NPC и второе отдельное переключающее устройство операционно соединено со вторым НВ модулем и модулем NPC. Преобразователь дополнительно включает в себя узел вывода мощности, содержащий несколько фаз и обеспечивающий многофазную переменную (АС) мощность, причем однофазная конфигурация подает питание на одну из нескольких фаз узла вывода мощности.3 н. и 17 з.п. ф-лы, 11 ил., 4 табл. | WO2017082922A1 | 2017-05-18 | US2015060611W | 2015-11-13 | US2015060611W, 2015-11-13 | WO2017082922A1: 2017-05-18 AU2015414494B2: 2019-04-18 CA3005146C: 2021-03-09 CN108292896B: 2020-07-21 EP3353884A1: 2018-08-01 US10355617B2: 2019-07-16 BR112018009080A8: 2019-02-26 RU2693573C1: 2019-07-03 | SIEMENS AG SIEMENS INDUSTRY INC 西门子股份公司 | MIHALACHE LIVIU LIVIU MIHALACHE | H02M7/483: I H02M1/00: I H02M1/08: I H02M7/487: I H02M7/5395: I H02P27/08: I H02M7/527: I H02P27/14: I | H02M7/483: I H02M7/487: I H02M1/007: A H02M1/0095: I H02M7/4835: A H02M7/4837: I H02M7/527: I H02P27/08: I H02P27/14: I H02M1/08: I H02M7/5395: I | US2013249322A1 EP2945272A1 US9184673B2 CN104242710A US6058031A US9083230B2 US9325252B2 US9571004B2 US2005139259A1 US2011260701A1 US2013207623A1 US2014003095A1 US2015263645A1 CN103401268A CN104883072A EP1742342A1 EP2662969A1 EP2724456A1 ES2319251A1 ES2327371B1 JP2011142783A RU2529017C2 RU2014108141A WO2012024984A1 WO2012176006A1 WO2013017353A1 WO2015003734A1 WO2015007186A1 | US2020028448A1 US2020028448 20200028448 US20200028448A1 US10917021B1 US10917021 10917021 US10396681B1 US10396681 10396681 US10476401B2 US10476401 US10468988B2 US10468988 US2019028031A1 US2019028031 20190028031 US20190028031A1 US11101735B2 US11101735 11101735 | [EN CN108292896B]: 1. A multilevel converter (40), comprising: a plurality of single-phase configurations (10), the single-phase configuration (10) comprising: a first capacitor (C2) coupled to a DC link (14) Separate the first half-bridge module (42) and the second half-bridge module (44), the DC link provides voltage (Vdc) to the single-phase configuration (10), a midpoint clamping module (46), so The midpoint clamping module (46) is clamped to the first half-bridge module (42) and the second half-bridge module (44), the first single switching device (Q2) and the second single switching device (Q2N) ), the first single switching device (Q2) is operatively connected to the first half-bridge module (42) and the midpoint clamping module (46), and the second single switching device (Q2N) Operatively connected to the second half-bridge module (44) and the midpoint clamp module (46); and a power output assembly (16), including three phases (A, B, C) and providing three phases AC power, wherein the single-phase configuration (10) provides power to one of the three phases (A, B, C) of the power output assembly (16), wherein the first half-bridge module (42) ) Includes a first plurality of switching devices (Q1, Q1N) and a second capacitor (C1) whose voltage rating is a quarter of the voltage (Vdc) provided by the DC link (14), wherein the first The second half-bridge module (44) includes a second plurality of switching devices (Q5, Q5N) and a third capacitor (C3) whose voltage rating is a quarter of the voltage (Vdc) provided by the DC link (14), wherein the midpoint clamping module (46) includes a third capacitor Switching devices (Q3, Q3N, Q4, Q4N, Q3C, Q3CN) and a fourth capacitor and a fifth capacitor (C4, C5), each of the fourth capacitor and the fifth capacitor (C4, C5) The voltage rating of is a quarter of the voltage (Vdc) provided by the DC link (14). 2. The multilevel converter (40) according to claim 1, wherein the voltage rating of the first capacitor (C2) is half of the voltage (Vdc) provided by the DC link (14). 3. The multilevel converter (40) of claim 1, wherein a controller (50) is operatively coupled to the first individual switching device (Q2) and the second individual switching device (Q2N ) And switching devices in the first plurality of switching devices, the second plurality of switching devices, and the third plurality of switching devices (Q1, Q1N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5 Each switching device in Q5N) is used to control the switching events of switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) through pulse width modulation. Each of the switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) switches at the same switching frequency. 4. The multilevel converter (40) of claim 1, comprising a single-phase configuration (10) for each phase, wherein all single-phase configurations (10) share the DC link (14) And the first capacitor, the second capacitor, and the third capacitor. 5. A method for controlling a multilevel converter (40), comprising: providing a plurality of switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) ); and using pulse width modulation to switch the plurality of switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N), wherein the multiple Two switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) are switched at the same switching frequency, and among them, multiple pairs of complementary pulse width modulation control signals (S1/ S1N, S2/S2N, S3/S3N, S4/S4N) are used to switch the plurality of switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N), wherein The single-phase configuration (10) includes: a first half-bridge module (42) and a second half-bridge module separated by a first capacitor (C2) coupled to the DC link (14) CN 108292896 Β (44), the DC link provides voltage (Vdc) to the single-phase configuration (10), a midpoint clamping module (46), the midpoint clamping module (46) clamps to the first half Bridge module (42) and the second half-bridge module (44), wherein the first half-bridge module (42) includes a second capacitor (C1), and the voltage rating of the second capacitor is the A quarter of the voltage (Vdc) provided by the DC link (14), and the second half-bridge module (44) includes a third capacitor (C3), the voltage rating of the third capacitor is the DC A quarter of the voltage (Vdc) provided by the link (14), and wherein, the midpoint clamping module (46) includes a fourth capacitor and a fifth capacitor (C4, C5), the fourth capacitor and The voltage rating of each of the fifth capacitors (C4, C5) is a quarter of the voltage (Vdc) provided by the DC link (14). 6. The method for controlling a multilevel converter (40) according to claim 5, wherein the multiple pairs of complementary pulse width modulation control signals (S1/S1N, S2/S2N, S3/S3N, S4/ Each pair in S4N) includes a complementary first control signal and a second control signal, wherein when the first control signal is turned on, the second control signal is turned off. 7. The method for controlling a multilevel converter (40) according to claim 5 or 6, further comprising: obtaining the complementary pulse width modulation by a phase shift pulse width modulation carrier method or a phase stack pulse width modulation method Control signal (S1/S1N, S2/S2N, S3/S3N, S4/S4N). 8. The method for controlling a multilevel converter (40) according to claim 7, wherein the complementary pulse width modulation control signal (S1) is obtained by a phase shift pulse width modulation carrier method based on a plurality of carrier signals. /S1N, S2/S2N, S3/S3N, S4/S4N), the carrier signal includes a waveform having a substantially triangular shape compared with a reference signal, and the reference signal includes a waveform having a substantially sinusoidal shape. 9. The method for controlling a multilevel converter (40) according to claim 7, wherein for each pair of complementary pulse width modulation control signals in the multiple pairs of complementary pulse width modulation control signals of the single-phase configuration (10) For a wide modulation control signal, a separate carrier is used, and the phase shift between the separate carriers Tshift corresponds to &amp; step=y where Ts is the switching frequency. 10. The method for controlling a multilevel converter (40) according to claim 5, further comprising: changing the control device (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C , Q3CN, Q4, Q4N, Q5, Q5N) duty cycle (dl, d2, d3, d4) to affect the current of the capacitor 61333435) (*1, *3, female 4, female 5), where the duty cycle Than modified to meet Δshan + Δ d2+ Δ d3+ Δ cU = 0, where di, d2, d3, and cU are the duty ratios of the multiple switching devices. 1L The method for controlling a multi-level converter (40) according to claim 5, comprising a single-phase configuration (10) for each phase (A, B, C), wherein all single-phase configurations ( 10) Sharing the DC link (14) and the first capacitor, the second capacitor and the third capacitor (C1, C2, C3) ο 12. An electric drive system (100), comprising: a power supply assembly, including a DC link (14); a multilevel converter (40), coupled to the DC link (14), for generating multiphase power , The multi-level converter (40) includes a single-phase configuration (10), wherein the DC link (14) provides a voltage (Vdc) to the single-phase configuration (10), and the single-phase configuration ( 10) Including: a first half-bridge module (42) and a second half-bridge module (44) separated by a first capacitor (C2) coupled to the DC link (14), a midpoint clamping module (46) , The midpoint clamping module (46) is clamped to the first half-bridge module (42) and the second half On the bridge module (44), a first single switching device (Q2) and a second single switching device (Q2N), the first single switching device (Q2) is operatively connected to the first half-bridge module (42) And the midpoint clamping module (46), and the second individual switching device (Q2N) is operatively connected to the second half-bridge module (44) and the midpoint clamping module (46); And a power output component (16), which includes three phases (A, B, C) and provides three-phase AC power, wherein the single-phase configuration (10) supplies the three phases of the power output component (16) One of the phases (A, B, C) provides power, wherein the first half-bridge module (42) includes a first plurality of switching devices (Q1, Q1N), and the second half-bridge module (44) A second plurality of switching devices (Q5, Q5N) are included, and the midpoint clamping module (46) includes a third plurality of switching devices (Q3, Q3N, Q4, Q4N, Q3C, Q3CN). 13. The electric drive system (100) according to claim 12, further comprising: a load including a motor and connected to the power output assembly (16). 14. The electric drive system (100) according to claim 12, further comprising a pulse width modulation controller (50) operably coupled to the individual switching devices (Q2, Q2N) and the The switching devices (Q1, Q1N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) of the first half bridge module and the second half bridge module (42.44) and the midpoint clamp module (46) Each switching device in) is used to control switching events of switching devices (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) through pulse width modulation, wherein the Each switching device (Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N) switches at the same switching frequency. 15. The electric drive system (100) according to claim 13, wherein the motor comprises a medium voltage AC motor operating in the range of 4.16 kV to 13.8 kV. [ZH CN108292896B]: 1.一种多电平变换器(40),包括： 多个单相配置(10)，所述单相配置(10)包括： 由耦合到DC链路(14)的第一电容器(C2)分开的第一半桥模块(42)和第二半桥模块 (44)，所述DC链路向所述单相配置(10)提供电压(Vdc)， 中点钳位模块(46)，所述中点钳位模块(46)夹到所述第一半桥模块(42)和所述第二半 桥模块(44)上， 第一单独开关器件(Q2)和第二单独开关器件(Q2N)，所述第一单独开关器件(Q2)可操 作地连接到所述第一半桥模块(42)和所述中点钳位模块(46)，并且所述第二单独开关器件 (Q2N)可操作地连接到所述第二半桥模块(44)和所述中点钳位模块(46)；以及 功率输出组件(16)，包括三个相(A、B、C)并且提供三相交流功率，其中所述单相配置 (10)向所述功率输出组件(16)的所述三个相(A、B、C)之一提供功率，其中，所述第一半桥模 块(42)包括第一多个开关器件(Q1、Q1N)和电压额定值为所述DC链路(14)提供的电压(Vdc) 的四分之一的第二电容器(C1)，其中，所述第二半桥模块(44)包括第二多个开关器件(Q5、 Q5N)和电压额定值为所述DC链路(14)提供的电压(Vdc)的四分之一的第三电容器(C3)，其 中，所述中点钳位模块(46)包括第三多个开关器件(Q3、Q3N、Q4、Q4N、Q3C、Q3CN)以及第四电 容器和第五电容器(C4、C5)，所述第四电容器和所述第五电容器(C4、C5)中的每一个的电压 额定值为所述DC链路(14)提供的电压(Vdc)的四分之一。 2.根据权利要求1所述的多电平变换器(40)，其中，所述第一电容器(C2)的电压额定值 为所述DC链路(14)提供的电压(Vdc)的一半。 3.根据权利要求1所述的多电平变换器(40)，其中，控制器(50)可操作地耦合到所述第 一单独开关器件(Q2)和所述第二单独开关器件(Q2N)以及所述第一多个开关器件、所述第 二多个开关器件和所述第三多个开关器件中的开关器件(Q1、Q1N、Q3、Q3N、Q3C、Q3CN、Q4、 Q4N、Q5、Q5N)中的每个开关器件，用于通过脉宽调制控制开关器件(Q1、Q1N、Q2、Q2N、Q3、 Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N)的开关事件，其中所述每个开关器件(Q1、Q1N、Q2、Q2N、Q3、 Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N)以相同的开关频率进行开关。 4.根据权利要求1所述的多电平变换器(40)，包括用于每个相的单相配置(10)，其中， 所有单相配置(10)共用所述DC链路(14)以及所述第一电容器、所述第二电容器和所述第三 电容器。 5.一种用于控制多电平变换器(40)的方法，包括： 提供包含多个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N)的单相配 置；以及 使用脉宽调制来开关所述多个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、 Q5、Q5N)， 其中，所述多个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N)以相同 的开关频率进行开关，并且 其中，多对互补脉宽调制控制信号(S1/S1N、S2/S2N、S3/S3N、S4/S4N)用于开关所述多 个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N)，其中，所述单相配置(10) 包括： 由耦合到DC链路(14)的第一电容器(C2)分开的第一半桥模块(42)和第二半桥模块 CN 108292896 Β (44),所述DC链路向所述单相配置(10)提供电压(Vdc), 中点钳位模块(46)，所述中点钳位模块(46)夹到所述第一半桥模块(42)和所述第二半 桥模块(44)上， 其中，所述第一半桥模块(42)包括第二电容器(C1)，所述第二电容器的电压额定值为 所述DC链路(14)提供的电压(Vdc)的四分之一，并且所述第二半桥模块(44)包括第三电容 器(C3),所述第三电容器的电压额定值为所述DC链路(14)提供的电压(Vdc)的四分之一，以 及 其中，所述中点钳位模块(46)包括第四电容器和第五电容器(C4、C5),所述第四电容器 和第五电容器(C4、C5)中的每一个的电压额定值为所述DC链路(14)提供的电压(Vdc)的四 分之一。 6.根据权利要求5所述的用于控制多电平变换器(40)的方法，其中，所述多对互补脉宽 调制控制信号(S1/S1N、S2/S2N、S3/S3N、S4/S4N)中的每一对均包括互补的第一控制信号和 第二控制信号，其中，当所述第一控制信号接通时，所述第二控制信号关断。 7.根据权利要求5或6所述的用于控制多电平变换器(40)的方法,还包括： 通过相移脉宽调制载波方法或相位层叠脉宽调制方法获得所述互补脉宽调制控制信 号(S1/S1N、S2/S2N、S3/S3N、S4/S4N)。 8.根据权利要求7所述的用于控制多电平变换器(40)的方法，其中，基于多个载波信 号，通过相移脉宽调制载波方法获得所述互补脉宽调制控制信号(S1/S1N、S2/S2N、S3/S3N、 S4/S4N),所述载波信号包括具有与参考信号相比大致三角形状的波形，所述参考信号包括 具有大致正弦形状的波形。 9.根据权利要求7所述的用于控制多电平变换器(40)的方法，其中，对于所述单相配置 (10)的多对互补脉宽调制控制信号中的每一对互补脉宽调制控制信号，使用单独的载波, 在单独的载波之间的相移Tshift对应于&amp;步=y其中Ts是开关频率。 10.根据权利要求5所述的用于控制多电平变换器(40)的方法,还包括： 改变用于控制所述多个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、Q5、Q5N) 的占空比(dl、d2、d3、d4),以影响电容器61333435)的电流(*1、*3、女4、女5),其中，占空 比修改符合Δ山+ Δ d2+ Δ d3+ Δ cU = 0,其中di、d2、d3、cU为所述多个开关器件的占空比。 1L根据权利要求5所述的用于控制多电平变换器(40)的方法，包括用于每个相(A、B、 C)的单相配置(10),其中，所有单相配置(10)共用所述DC链路(14)和所述第一电容器、所述 第二电容器和所述第三电容器(C1、C2、C3) ο 12.一种电驱动系统(100),包括： 电源组件,包括直流链路(14)； 多电平变换器(40)，耦合到所述直流链路(14),用于产生多相功率，所述多电平变换器 (40)包括单相配置(10)，其中，所述直流链路(14)向所述单相配置(10)提供电压(Vdc),所 述单相配置(10)包括： 由耦合到所述直流链路(14)的第一电容器(C2)分开的第一半桥模块(42)和第二半桥 模块(44), 中点钳位模块(46),所述中点钳位模块(46)夹到所述第一半桥模块(42)和所述第二半 桥模块(44)上， 第一单独开关器件(Q2)和第二单独开关器件(Q2N)，所述第一单独开关器件(Q2)可操 作地连接到所述第一半桥模块(42)和所述中点钳位模块(46)，并且所述第二单独开关器件 (Q2N)可操作地连接到所述第二半桥模块(44)和所述中点钳位模块(46)；以及 功率输出组件(16)，包括三个相(A、B、C)并且提供三相交流功率，其中，所述单相配置 (10)向所述功率输出组件(16)的所述三个相(A、B、C)中的一个相提供功率，其中，所述第一 半桥模块(42)包括第一多个开关器件(Q1、Q1N)，所述第二半桥模块(44)包括第二多个开关 器件(Q5、Q5N)，并且所述中点钳位模块(46)包括第三多个开关器件(Q3、Q3N、Q4、Q4N、Q3C、 Q3CN)。 13.根据权利要求12所述的电驱动系统(100)，还包括:负载，所述负载包括电机并且连 接到所述功率输出组件(16)。 14.根据权利要求12所述的电驱动系统(100)，还包括脉宽调制控制器(50)，所述脉宽 调制控制器可操作地耦合到单独开关器件(Q2、Q2N)和所述第一半桥模块和所述第二半桥 模块(42.44)和所述中点钳位模块(46)的开关器件(Q1、Q1N、Q3、Q3N、Q3C、Q3CN、Q4、Q4N、Q5、 Q5N)中的每个开关器件，用于通过脉宽调制控制开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、 Q3CN、Q4、Q4N、Q5、Q5N)的开关事件，其中，所述每个开关器件(Q1、Q1N、Q2、Q2N、Q3、Q3N、Q3C、 Q3CN、Q4、Q4N、Q5、Q5N)以相同的开关频率进行开关。 15.根据权利要求13所述的电驱动系统(100),其中，所述电机包括在4.16kV至13.8kV 的范围内工作的中压交流电动机。 | [EN CN108292896B]: Medium voltage transformerless multilevel converter and method for controlling medium voltage transformerless multilevel converter Technical field [0001] Aspects of the present invention generally relate to a medium voltage transformerless multilevel converter and a method for controlling a medium voltage transformerless multilevel converter. Background technique [0002] Traditionally, since a single power semiconductor device cannot handle high voltages, multi-level power converters are used for applications in medium voltage AC drives, flexible AC transmission systems (FACTS), and high voltage DC (HVDC) transmission systems. [0003] Multi-level power converters include a multi-level topology, which provides a clever way of connecting switches in series, so that it can handle voltages higher than the device's rated value. The industrial demand for medium-voltage drives has triggered a lot of research in this field, most of which include drives for pumps, blowers, compressors, conveyors, etc. Provides multi-level voltage, with a limited number of topologies suitable for medium voltage applications. The most well-known topologies are midpoint clamp (NPC) topology, fast capacitor (FC) topology and cascaded H-bridge multilevel topology. [0004] Cascaded multilevel converters are the preferred topology for many medium and high voltage applications. This topology has been established in the industry for more than two decades, but it also has certain shortcomings, mainly the cost associated with the special transformer required to provide isolated power for each power unit. In addition, the cascaded multilevel topology has traditionally been implemented only in unidirectional power flow applications, so it cannot provide regenerative braking in motor applications. For example, four-quadrant operation is possible, but such operation will significantly increase the cost of the power unit and still require a transformer. Modular multilevel converter is another topology, which is still under development. This topology may or may not use a transformer, so it may be beneficial in applications that require regenerative braking; however, this topology requires a larger number of semiconductors, and its operation at low speed/high torque can be very difficult. At the lower end of the medium voltage level, cascaded multilevel topologies and modular multilevel topologies are often very expensive. Summary of the invention [0005] In short, various aspects of the present invention relate to transformerless multilevel converters, electric drive systems including transformerless multilevel converters, and methods for controlling transformerless multilevel converters. [0006] A first aspect of the present invention provides a multi-level converter including a plurality of single-phase configurations, the single-phase configuration including: a first half bridge (HB) separated by a first capacitor coupled to a DC link Module and the second half-bridge HB module, the DC link provides voltage to the single-phase configuration; the midpoint clamp (NPC) module, the NPC module is clamped to the first HB module and the second HB module; the first separate switch and the second Separate switch, the first separate switch is operatively connected to the first HB module and the NPC module, and the second separate switch is operatively connected to the second HB module and the NPC module; and the power output assembly includes three phases and provides three Phase alternating current (AC) power, where a single-phase configuration provides power to one of the three phases of the power output assembly. [0007] A second aspect of the present invention provides a method for controlling a multi-level converter, including: providing a single-phase configuration including multiple switching devices; and using pulse width modulation (PWM) to switch multiple switches A device in which multiple switching devices switch at the same switching frequency, and multiple pairs of complementary PWM control signals are used to switch the multiple switching devices. [0008] A third aspect of the present invention provides an electric drive system, including: a power supply assembly, the power supply assembly includes a direct current (DC) link; a multi-level converter, coupled to the DC link, for generating multi-phase Power, the converter includes a single-phase configuration, where, The DC link supplies voltage to a single-phase configuration, which includes: a first half-bridge (HB) module and a second half-bridge HB module separated by a first capacitor coupled to the DC link, mid-point clamp (NPC) Module, the NPC module is clipped to the first HB module and the second HB module, the first individual switch and the second individual switch, the first individual switch is operatively connected to the first HB module and the NPC module, and the second individual switch can It is operatively connected to the second HB module and the NPC module; and a power output assembly that includes three phases and provides three-phase AC power, wherein the single-phase configuration provides power to one of the three phases of the power output assembly. Description of the drawings [0009] FIG. 1 shows a schematic diagram of an embodiment of the proposed topology for one phase of a transformerless multilevel converter according to an exemplary embodiment of the present invention. [0010] FIG. 2 shows a schematic diagram of another embodiment of the proposed topology for one phase of a transformerless multilevel converter according to an exemplary embodiment of the present invention. [0011] FIG. 3 shows a graphical representation of a carrier structure including a carrier wave of a different reference signal waveform for one phase of a transformerless multilevel converter according to an exemplary embodiment of the present invention. [0012] FIG. 4 shows a schematic diagram of an embodiment of a system including a transformerless multilevel converter, particularly a three-phase motor drive voltage inverter, according to an exemplary embodiment of the present invention. [0013] FIG. 5 shows a schematic diagram of an embodiment of a back-to-back structure including a three-phase motor drive voltage inverter as shown in FIG. 4 according to an exemplary embodiment of the present invention. [0014] FIG. 6 shows a graphical representation of analog output voltage and current waveforms obtained with PSPWM in a transformerless multilevel converter for one phase according to an exemplary embodiment of the present invention. [0015] FIGS. 7 and 8 show graphs of an analog voltage of a capacitor coupled to a DC link obtained by using PSPWM in a transformerless multilevel converter for one phase according to an exemplary embodiment of the present invention Said. [0016] FIG. 9 shows a graphical representation of an analog voltage of a capacitor of an NPC module obtained with PSPWM in a transformerless multilevel converter for one phase according to an exemplary embodiment of the present invention. [0017] FIGS. 10 and 11 show graphical representations of analog waveforms of output current and line voltage obtained by PSPWM in a transformerless multilevel converter for three phases, respectively, according to an exemplary embodiment of the present invention. . detailed description [0018] In order to facilitate the understanding of the embodiments, principles, and features of the present invention, it is described below with reference to the implementation in the illustrative embodiments. In particular, it is described in the context of a transformerless multilevel converter, an electric drive system including such a transformerless multilevel converter, and a method for controlling such a transformerless multilevel converter. However, the embodiments of the present invention are not limited to be used with the described devices or methods. [0019] The components and materials described below as constituting various embodiments are intended to be illustrative and not restrictive. Many suitable components and materials that perform the same or similar functions as the materials described herein are included in the scope of the embodiments of the present invention. [0020] The described transformerless multilevel converter includes a five-level medium voltage topology that can be used in medium voltage motor drive applications. Medium voltage applications are applications of medium voltage alternating current (AC) motors used in industrial process control, for example, which operate above 1 kV and/or below 50 kV, especially between 4.16 kV and 13.8 kV. [0021] FIG. 1 shows a phase diagram for a transformerless multilevel converter according to an exemplary embodiment of the present invention. Schematic diagram of an embodiment of the proposed topology. [0022] FIG. 1 shows a single-phase configuration 10, also referred to herein as a single-phase module 10, with the proposed topology of one phase A for a three-phase motor drive voltage inverter. For each phase of the exemplary inverter, the proposed topology includes two half-bridge (HB) modules 42, 44 separated by a DC link capacitor C2, a midpoint clamp (NPC) module 46, and two separate Switching devices Q2, Q2N. [0023] The circuit for the first HB module 42 includes power semiconductor switching devices Q1 and Q1N and a capacitor C1 having a voltage rating of a quarter of the provided direct current (DC) link voltage Vdc of the DC link 14. . The circuit for the second HB module 44 includes power semiconductor switching devices Q5 and Q5N and a capacitor C3 having a voltage rating of one-quarter of the provided DC link voltage Vdc of the DC link 14. [0024] The configuration of the midpoint clamp (NPC) module 46 includes power semiconductor switching devices Q3, Q3N, Q3C, Q3CN, Q4, Q4N and capacitors C4, C5. The capacitors C4 and C5 each have a voltage rating of one-fourth of the provided DC link voltage Vdc. Another capacitor C2 separates the two HB modules 42, 44, where the capacitor C2 has a voltage rating that is half of the DC link bus voltage Vdc. In addition, the proposed topology of the module 10 includes two separate switching devices Q2 and Q2N, each of which is arranged between one of the HB configurations 42, 44 and the NPC configuration 46. [0025] The switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N may include, for example, but not limited to, power transistors such as insulated gate bipolar transistors (IGBT). As shown in Figure 1, there are no switching devices connected in series. According to the described embodiment, each phase of the proposed topology includes a total of 12 switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N. [0026] The DC link 14 includes a positive input terminal P and a negative input terminal N. For example, the input voltage of the DC link 14 can be provided by a standard transformer/diode rectifier. Alternatively, a back-to-back inverter structure can be used, such as shown in Figure 5, for a typical transformerless motor drive topology. The topology described in Figure 1 produces output as the phase voltage potential of phase A and the phase output current Iout. [0027] FIG. 2 shows a schematic diagram of another embodiment of the proposed topology for one phase A of a transformerless multilevel converter according to an exemplary embodiment of the present invention. FIG. 2 shows an alternative topology with respect to FIG. 1, where the same reference numerals of FIG. 1 are used to label the same elements in FIG. 2. It should be noted that, for the sake of simplicity, the embodiment described further herein is described with reference to the exemplary embodiment of FIG. 1. Those of ordinary skill in the art will recognize that the embodiments of FIG. 1 and FIG. 2 can be easily replaced with each other, and the embodiments described herein now with reference to FIG. 1 are also applicable to the embodiment of FIG. 2. The embodiments of Figures 1 and 2 are similar, but the structures of the DC link capacitors C1, C3 associated with the two HB configurations 42, 44 are different. [0028] Throughout FIG. 1, QxN and QxCN indicate that the corresponding switching devices switch in a complementary manner with respect to Qx and QxC. For example, the switching device Q1N switches in a complementary manner with respect to Q1 and the like. This means that Qx-QxN and QxC-QxCN can be considered as complementary switch pairs, in which when one of the switching devices (such as Q1) is turned on, the complementary switching device Q1N is turned off. [0029] Each switching device Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N of the single-phase configuration 10 responds to the control signal S1 from the controller, particularly from the PWM controller , S1N, S2, S2N, S3, S3N, S4, S4N. According to one embodiment, four pairs of switching signals S1/S1N, S2/S2N, S3/S3N, S4/S4N are used to drive all switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N. The control signal Sx/SxN is a complementary signal, which means that, for example, when S1 is on (1), S1N is off (0). [0030] In conjunction with Table I provided below, FIG. 1 shows how to allocate control signals S1/S1N, S2/S2N, S3/S3N, S4/S4N to the switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N: CN 108292896 Β [0031] [0032] Table 1: PWM signal distribution signal Switching device S1 Q1, Q5 S1N Q1N, Q5N S2 Q2 S2N Q2N S3 Q3, Q3C S3N Q3N,Q3CN S4 Q4 S4N Q4N Four switching signals $1, $2, $3, 54 and their respective complementary switching signals 5 small, $2 steam $3 steam 54? ^ can be used [0033] The phase-shifted PWM carrier method or the phase-stacked PWM method or other suitable PWM methods are obtained from any PWM modulator. [0034] The phase-shifted PWM (PSPWM) carrier method is a method used in many multi-level applications, such as a cascaded H-bridge topology. Using the PSPWM carrier method, a sine waveform used as a reference for a specific phase is compared with, for example, a substantially triangular carrier wave to obtain a switching example for a specific switching device, such as a switching signal S2 for the switching device Q2. Other carriers can be used, such as ladder carriers. A simple logic inverter can provide signals for S2N. A separate carrier is used for each of the other signals S1, S3, S4, and these carriers are roughly triangular carriers. The phase shift Tshift between the carriers of one phase is given by formula (1), where Ts is the switching frequency for all switching devices: [0035] hhift ~ ~ . [0036] FIG. 3 shows a graphical representation of a carrier structure including a carrier wave different from a reference signal waveform for one phase of a transformerless multilevel converter according to an exemplary embodiment of the present invention. Figure 3 shows a typical carrier structure according to the above principle, including four different control signals $1, $2, $3, 54 four different carriers 30, 32, 34, 36, these carriers include relative to the reference signal including a sinusoidal waveform Triangular waveform of waveform 38. [0037] Although the PSPWM carrier method is one of the most widely used principles for generating commands for switching devices, other PWM methods can also be used. For example, an optimized PWM method is described in U.S. Patent No. 9184673 ("Pulse Width Modulation Control for Multilevel Converters") to Mihalache, the content of which is incorporated herein by reference. It should be noted that for the sake of simplicity, the embodiments provided herein are described with respect to the PSPWM carrier method for providing control commands to the switching device. [0038] The table Π provided below shows the possible voltage levels of the exemplary topology shown in FIG. 1, where the phase voltage potential A is measured relative to the negative input terminal N. In Table II, when the corresponding switching device Qx driven by the signal Sx is turned on, the signal Sx is turned on (1). When the switching device Qx driven by the signal Sx is turned off, the signal Sx is turned off (0). [0039] In formula (2), the phase voltage Van can be provided as a function of the switching command (ie, the switching control signal) and the provided DC link voltage Vdc: [0040] [0041] Van= (S1+S2+S3+S4) · V (2) ο Table Π: Relative to the output phase voltage Van in Figure 1: [0042] SI S2 S3 S4 Van CN 108292896 Β [0043] 0 0 0 0 0 0 0 0 1 V 0 0 1 0 V 0 0 1 1 2V 0 1 0 0 V 0 1 0 1 2V 0 1 1 0 2V 0 1 1 1 3V 1 0 0 0 V 1 0 0 1 2V 1 0 1 0 2V 1 0 1 1 3V 1 1 0 0 2V 1 1 0 1 3V 1 1 1 0 3V 1 1 1 1 4V [0044] The instantaneous current through the capacitors C1, C3, C4 and C5 can be expressed as provided in the formula -, respectively:] (3 1 [0045] Ji=House Eight+House, 2=Dia·Yi, (J-SJ + Chen Guo [0046]% = -J·I - = -&amp;§, (1 OnePlus)+ ⑶； (4); [0047] IC4= (S2-S3 · S4) · Lout (5); [0048] Ic5=((S3) · (I-S4)-(S2)), lout (6) o [0049] In order to maintain the voltage of the capacitor (; 1333435 at the desired value, the average current of (; 133 4 4 5 should be equal to zero. Even if there are three capacitors C1, C2, C3 on the DC link 14, the inner capacitor C2 Is twice the voltage of the external capacitors Cl and C3, as long as the external capacitors C1 and C3 can maintain their correct voltage values (one-quarter of the DC link voltage Vdc), the voltage of the internal capacitor C2 will also have the correct Level. [0050] The relationship expressed by formulas (3) to (6) can be further simplified as a function of the instantaneous value of the modulation reference signal waveform 38 (see FIG. 3). Assuming that the phase reference voltage is as given in formula (7), the capacitor currents through the capacitor diagram 333435, House 1, House 3, House 4, and House 5 can be respectively as described in Table 111 provided below, as the phase current 10 gate And the duty cycle of each switching signal S1, S2, S3 and S4, (12, (13, (14): [0051] ref=m, sin (ω · t) (7) [0052] It can be seen that under steady-state and ideal conditions, the relationship shown in formula (8) is true, which means that the The average current of the device (; 13334 some 5 is zero at the output fundamental frequency. This also means that the capacitor (; 13334 some 5 can keep its voltage at the desired initial level: 2 plus 2 plus 2 is 2 production [0053] "g two two J k two f G = 0 0 0 0 [0054] Table III: Average capacitor current as a function of current and duty cycle mountain, (12, (13, (14 (per switching cycle)) Id \ Ic3\ Ic4\ Ic5: [0055] -1 &lt;ref &lt;(m&gt; 0,5) 1 /1--&lt; ref &lt;- 2 2(m &lt;0,5) g &lt;ref &lt;1 (m&gt; 0,5) [0056] Ici Ic3 IC4 &amp;Factory-ds a) /. "(1 + Yoshihiro Yi%) IC5 [0057] However, there may be several non-ideal conditions, such as a limited number of device switching times, device voltage drop, duty cycle mismatch between switching devices, dynamic stepping, etc. All of these conditions will affect the voltage across the capacitor (:1333435. If it is not reduced, one or more capacitors in the capacitor (:1333435) will drift higher or lower than the voltage of its initial condition. [0058] In order to balance any effects of non-ideal conditions, the four duty cycles di, d2, d3, and cU can be slightly changed so as to affect the current of each capacitor. It can be seen that it must be based on the phase current polarity and instantaneous position of the modulation waveform. You can modify the specific capacitor (:1, 3, 435, current room 1, room 3, room 4, h5, to accelerate or decelerate the specific capacitor (; 1333435 The charging/discharging of the capacitor does not affect the output voltage of the specific capacitor. As long as the duty cycle is modified to follow the formula (9), it is a sufficient condition to meet the formula : [0059] Δ di+ Δ dg+ Δ ds+ Δ d4 = 0 (9). [0060] FIG. 4 shows a schematic diagram of an embodiment of a system including a transformerless multi-level converter, particularly a three-phase motor drive voltage inverter, according to an exemplary embodiment of the present invention. [0061] FIG. 4 shows a system 100 including a three-phase motor drive voltage inverter 40, which includes three phases A, B, and C. Each phase includes a single-phase configuration 10 (also referred to herein as a single-phase module 10) connected to the DC link 14, wherein for each phase A, B, C, the single-phase module 10 includes the topology as described in FIG. 1 . Alternatively, the inverter 40 can be packaged It includes one or more phase A, B, and C single-phase modules 10 having the topology as shown in FIG. 2. It can be seen from FIG. 4 that only the complete circuit of phase A is shown, and only the topologies of phases B and C are shown schematically. [0062] As before, for each phase A, B, C of the exemplary inverter 40, the proposed topology includes first and second half-bridge (HB) modules 42 separated by a DC link capacitor C2 , 44, a midpoint clamp (NPC) module 46 and two separate switching devices Q2, Q2N. The individual switching device Q2 is operably connected to the first HB module 42 and the NPC module 46, and the second individual switch Q2N is operably connected to the second HB module 44 and the NPC module 46. [0063] According to the described embodiment, each phase A, B, C of the proposed topology includes a total of 12 switching devices. The DC link 14 provides the voltage Vdc to the single-phase module 10. All phases A, B, and C share the DC link 14, which also means that all phases A, B, and C share capacitors C1, C2, C3 coupled to the DC link 14. Therefore, only eight capacitors (the shared DC link capacitors C1, C3 and the capacitors C4, C5 of each single-phase module 10) may need to be balanced for the three-phase inverter 40. [0064] The inverter 40 may be operatively coupled to the controller 50 (especially a pulse width modulation (PWM) controller) and the electric motor 60 (especially an AC motor). The inverter 40 can be used for a medium voltage drive, such as a 4160V medium voltage drive. The transformerless multilevel converter 40 includes a power output assembly 16 and generates a three-phase AC power output via a phase output line 70. The AC output via line 70 may be connected to a load, which in this example includes a motor 60. The motor 60 can be operated by controlling the frequency and/or amplitude of the output voltage generated by the multi-level inverter 40. [0065] The electric motor 60 may include any AC type electric motor, such as synchronous, asynchronous, permanent magnet, and may have a low, medium, or high voltage rating. For example, medium voltage AC motors used in industrial process control can operate in the range of 4.16kV to 13.8kV. Higher or lower voltage can be used. More than one AC motor 60 can be connected. Other loads can be used as an alternative to or in addition to the motor 60. For example, the AC motor 60 responds to the voltage applied by a multi-level converter on a three-phase A, B, C to increase, decrease, or maintain the speed or position. [0066] The controller 50 may include, for example, a processor with a memory, which can store and execute specific instructions to realize the PWM control shown. The controller 50 may be, for example, but not limited to, a microcontroller with internal or external memory, or a fixed-point or floating-point digital signal processor (DSP), or a programmable logic device (PLD), or any combination of the above. achieve. [0067] FIG. 5 shows a schematic diagram of an embodiment of a back-to-back structure including a three-phase motor drive voltage inverter 40 as shown in FIG. 4 according to an exemplary embodiment of the present invention. [0068] As previously described, the input voltage of the DC link 14 may be provided by a standard transformer/diode rectifier, for example. Or, as shown in Figure 5, a back-to-back inverter structure can be used in a typical transformerless motor drive topology. The structure of FIG. 5 includes two inverters 40 as shown in FIG. 4, wherein the DC link 14 including the voltage Vdc of the input terminals P and N feeds the two inverters 40 so that each inverter 40 It includes input or output in the form of three-phase AC power with three phases A, B, and C. [0069] FIG. 6 shows analog waveforms of output voltage Vout and output current Iout obtained by PSPWM in the transformerless multilevel converter 40 for one phase A, B, or C, respectively, according to an exemplary embodiment of the present invention. Graphical representation of. The simulation parameters are shown in Table IV below. [0070] Table IV: Simulation parameters: [0071] parameter value C1, C3, C4, C5 10,000uF each C2 5,000uF operating frequency 600Hz DC link voltage 1,950*4 = 7,800V Rload 5.41 ohm Lload 7.6mH [0072] FIGS. 7 and 8 show graphical representations of the analog voltages of the DC link capacitors C1, C2, and C3, wherein according to an exemplary embodiment of the present invention, FIG. 7 shows an external DC link capacitor C1 and The analog voltage of C3 (see, for example, FIG. 1), and FIG. 8 shows the analog voltage of the internal DC link capacitor C2 (see, for example, FIG. 1). The analog voltage is obtained when operating the multi-level inverter 40 with PSPWM and the analog parameters shown in Table IV. As shown in Figure 7, capacitors C1 and C3 maintain their initial average values. As a result, the capacitor C2 also maintains the initial average value, which is half the DC link voltage Vdc and twice the voltage of the capacitors C1 and C3. [0073] FIG. 9 shows a graphical representation of the analog voltages of capacitors C4 and C5 of an NPC module 46 (see, for example, FIG. 4) according to an exemplary embodiment of the present invention. The analog voltage is obtained when operating the multilevel inverter 40 with PSPWM and the analog parameters as shown in Table IV. As shown in FIG. 9, capacitors C4 and C5 also basically maintain an initial average value of a quarter of the DC link voltage Vdc provided by them. [0074] FIGS. 10 and 11 show output currents 102, 102 obtained by PSPWM in the transformerless multilevel converter 40 for all three phases A, B, or C, respectively, according to an exemplary embodiment of the present invention. Graphical representation of the simulated waveforms of 104, 106 (Figure 10) and line voltages 110, 112, 114 (Figure 11). Table IV shows the simulation parameters. [0075] In summary, according to an exemplary embodiment, the transformerless multilevel converter 40 as herein includes the following features: [0076]-On each phase A, B and C, the proposed topology includes two half-bridge (HB) modules 42, 44, one in one separated by a DC link capacitor C2 (also called an inner capacitor) Point clamp (NPC) module 46 and two separate switching devices Q2, Q2N. [0077] The two capacitors C1 and C3 at the DC link 14 and the two capacitors C4 and C5 of the NPC module 46 may need to be balanced. Each of these capacitors has a voltage rating of a quarter of the supplied DC bus voltage Vdc. [0078] All the phases A, B, C share the DC link 14; therefore, for the three-phase inverter 40, only eight capacitors may need to be balanced. [0079]-All switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N have a voltage stress equal to a quarter of the provided DC link bus voltage Vdc. [0080] Since there are no switching devices connected in series, the proposed inverter 40 allows simpler gate drive control and results in more reliable products. [0081] Phase shift pulse width modulation (PSPWM) or phase stacked PWM (PDPWM) control can be used. In both cases, the effective output switching frequency is four times the switching frequency of a single switching device. All switching devices Q1, Q1N, Q2, Q2N, Q3, Q3N, Q3C, Q3CN, Q4, Q4N, Q5, Q5N switch at the same frequency. [0082] The proposed exemplary inverter 40 can be used for transformerless applications (back-to-back transformerless topology, see for example Figure 5). But in the case of input-output voltage mismatch, the inverter 40 can also be used with a front-end transformer. In this case, a simpler transformer can be used. [0083] Although the embodiments of the present invention have been disclosed in exemplary form, it is obvious to those skilled in the art that without departing from the spirit and scope of the present invention and its equivalents as set forth in the following claims In the case of the scheme, many modifications, additions and deletions can be made in it. [ZH CN108292896B]: 中压无变压器多电平变换器及用于控制中压无变压器多电平 变换器的方法 技术领域 [0001] 本发明的各方面总体涉及一种中压无变压器多电平变换器和一种用于控制中压 无变压器多电平变换器的方法。 背景技术 [0002]传统上，由于单个功率半导体器件不能处理高电压，所以多电平功率变换器被用 于中压AC驱动器、柔性AC传输系统(FACTS)和高压DC(HVDC)传输系统的应用。 [0003]多电平功率变换器包括多电平拓扑，其提供了串联连接开关的巧妙方式，因此可 以处理高于器件额定值的电压。对于中压驱动器的工业需求引发了该领域的大量研究，其 中大多数应用包括用于泵、鼓风机、压缩机、输送机等的驱动器。提供多电平电压，适用于中 压应用的拓扑数量有限。最著名的拓扑是中点钳位(NPC)拓扑、快速电容(FC)拓扑和级联H 桥多电平拓扑。 [0004]级联多电平变换器是许多中压和高压应用中的优选拓扑。该拓扑在业内已经建立 了二十多年，但它也存在一定的缺点，主要是与为每个功率单元提供隔离的功率所需的特 殊变压器相关的成本。此外，级联多电平拓扑传统上仅在单向功率流应用中实现，因此它不 能在电动机应用中提供再生制动。例如，可以四象限操作，但是这样的操作将显著增加功率 单元成本并且仍然需要变压器。模块化多电平变换器是另一种拓扑，它仍在开发中。该拓扑 可以使用也可以不使用变压器，因此在需要再生制动的应用中可能是有益的；然而，该拓扑 需要更多数量的半导体，并且其在低速/高转矩下的操作会非常困难。在中压电平的较低 端，级联多电平拓扑和模块化多电平拓扑往往都非常昂贵。 发明内容 [0005]简而言之，本发明的各方面涉及无变压器多电平变换器、包括无变压器多电平变 换器的电驱动系统以及用于控制无变压器多电平变换器的方法。 [0006] 本发明的第一方面提供了一种多电平变换器，包括多个单相配置，单相配置包括： 由耦合到DC链路的第一电容器分开的第一半桥(HB)模块和第二半桥HB模块，DC链路向单相 配置提供电压；中点钳位(NPC)模块，NPC模块夹到第一HB模块和第二HB模块上;第一单独开 关和第二单独开关，第一单独开关可操作地连接到第一HB模块和NPC模块，并且第二单独开 关可操作地连接到第二HB模块和NPC模块；以及功率输出组件，包括三个相并且提供三相交 流(AC)功率，其中单相配置向功率输出组件的三个相中的一个相提供功率。 [0007] 本发明的第二方面提供了一种用于控制多电平变换器的方法，包括:提供包含多 个开关器件的单相配置；以及使用脉宽调制(PWM)来开关多个开关器件，其中多个开关器件 以相同的开关频率进行开关，并且其中多对互补PWM控制信号用于开关多个开关器件。 [0008]本发明的第三方面提供了一种电驱动系统，包括：电源组件，该电源组件包括直流 (DC)链路;多电平变换器，耦合到DC链路，用于产生多相功率，变换器包括单相配置，其中， DC链路向单相配置提供电压，单相配置包括：由耦合到DC链路的第一电容器分开的第一半 桥(HB)模块和第二半桥HB模块，中点钳位(NPC)模块，NPC模块夹到第一HB模块和第二HB模 块上，第一单独开关和第二单独开关，第一单独开关可操作地连接到第一HB模块和NPC模 块，并且第二单独开关可操作地连接到第二HB模块和NPC模块；以及功率输出组件，包括三 个相并且提供三相交流功率，其中，单相配置向功率输出组件的三个相中的一个相提供功 率。 附图说明 [0009]图1示出了根据本发明示例性实施例的、用于无变压器多电平变换器的一个相的 所提出的拓扑的实施例的示意图。 [0010]图2示出了根据本发明的示例性实施例的、用于无变压器多电平变换器的一个相 的所提出的拓扑的另一实施例的示意图。 [0011]图3示出了根据本发明示例性实施例的、对于无变压器多电平变换器的一个相的、 包括相对于参考信号波形不同的载波的载波结构的图形表示。 [0012]图4示出了根据本发明示例性实施例的、包括无变压器多电平变换器，特别是三相 电动机驱动电压逆变器的系统的实施例的示意图。 [0013]图5示出了根据本发明的示例性实施例的、包括如图4所示的三相电动机驱动电压 逆变器的背对背结构的实施例的示意图。 [0014]图6示出了根据本发明的示例性实施例的、针对一个相在无变压器多电平变换器 中用PSPWM获得的、模拟输出电压和电流波形的图形表示。 [0015]图7和图8示出了根据本发明的示例性实施例的、针对一个相在无变压器多电平变 换器中用PSPWM获得的、耦合到DC链路的电容器的模拟电压的图形表示。 [0016]图9示出了根据本发明的示例性实施例的、针对一相在无变压器多电平变换器中 用PSPWM获得的NPC模块的电容器的模拟电压的图形表示。 [0017]图10和图11示出了根据本发明的示例性实施例的、分别针对三个相在无变压器多 电平变换器中用PSPWM获得的输出电流和线电压的模拟波形的图形表示。 具体实施方式 [0018] 为了便于理解本发
[EN US2021044216A1]: A MULTI-LEVEL MODULAR CONVERTER [FR WO2019147144A1]: CONVERTISSEUR MODULAIRE MULTINIVEAU | [EN US2021044216A1]: The present disclosure relates to an integrated boost modular multilevel converter, which has particular, but not sole, relevance to a converter for an inductive or capacitive (wireless) power transfer system. More particularly, the present invention according to an embodiment discloses a modular multilevel power converter (MMPC) comprising: at least one submodule stack having an output for connection to a load and an input for connection to an input power source, at least one inductive element provided between the input and the output, the at least one submodule stack including at least two submodules, each submodule comprising at least one capacitor and a plurality of controllable switches, and the submodules being operable to selectively transfer energy from the at least one inductive element to boost a voltage at the output relative to a voltage at the input. [FR WO2019147144A1]: La présente invention concerne un convertisseur multiniveau modulaire survolteur intégré, qui présente en particulier, mais pas uniquement, la pertinence d'un convertisseur pour un système de transfert d'énergie inductif ou capacitif (sans fil). Plus particulièrement, la présente invention concerne, selon un mode de réalisation, un convertisseur de puissance multiniveau modulaire (MMPC) comprenant : au moins un empilement de sous-modules ayant une sortie pour une connexion à une charge et une entrée pour une connexion à un bloc d'alimentation d'entrée, au moins un élément inductif disposé entre l'entrée et la sortie, ledit au moins un empilement de sous-modules comprenant au moins deux sous-modules, chaque sous-module comprenant au moins un condensateur et une pluralité de commutateurs pouvant être commandés, et les sous-modules pouvant fonctionner pour transférer sélectivement de l'énergie provenant du ou des éléments inductifs pour amplifier une tension à la sortie par rapport à une tension à l'entrée. | WO2019147144A1 | 2019-08-01 | NZ2019050006W | 2019-01-25 | NZ73939618A, 2018-01-25 | WO2019147144A1: 2019-08-01 US2021044216A1: 2021-02-11 | RIAR BALJIT SINGH THRIMAWITHANA DULEEPA JAYANATH ZANE REGAN ANDREW WANG VICTOR AUCKLAND UNISERVICES LTD | RIAR BALJIT SINGH THRIMAWITHANA DULEEPA JAYANATH ZANE REGAN ANDREW WANG VICTOR | H02M7/501: I B60L53/12: I H02J5/00: I H02J50/05: I H02J50/10: I H02M7/19: I H02M7/44: I H02M7/49: I H02M7/483: I H02J50/12: I H02M1/12: I | B60L53/126: A B60L53/55: A G05F1/10: I H02J7/02: A H02M7/19: I H02M7/49: I H02M7/501: I H04B5/0037: A H04B5/0075: A H02J50/05: I H02J50/10: I H02J50/12: I B60L50/60: I B60L53/12: I B60L53/22: A B60L58/21: I H02M1/12: I H02M7/483: I H02J2310/48: A H02M1/0095: I H02M7/4835: A Y02T10/70: A Y02T10/7072: A Y02T90/14: A | US2014355321A1 US2013119970A1 US2016105109A1 | CN111342691A CN111342691 111342691 WO2021048209A1 WO2021048209 2021/048209 WO2021/048209A1 EP3820040A1 EP3820040 3820040 US11050357B2 US11050357 11050357 | [EN US2021044216A1]: 1. A modular multilevel power converter (MMPC) comprising: at least one submodule stack having an output for connection to a load and an input for connection to an input power source; andat least one inductive element provided between the input and the output, whereinthe at least one submodule stack includes at least two submodules respectively including at least one capacitor and a plurality of controllable and switches, andthe submodules are operable to selectively transfer energy from the at least one inductive element to boost a voltage at the output relative to a voltage at the input. 2. The MMPC as claimed in claim 1 wherein the energy is transferred between at least two of: the submodule(s), input power source or load. 3. The MMPC as claimed in claim 1, wherein the submodules are operable to provide a staircase voltage waveform at the output. 4. The MMPC as claimed in claim 1, wherein the modular multilevel power converter comprises a plurality of submodule stacks. 5. The MMPC as claimed in claim 1, wherein there is no DC voltage offset across the input power source. 6. The MMPC as claimed in claim 1, wherein switches are operable to dispose the converter in a first operational state and a second operational state. 7. The MMPC as claimed in claim 6, elating wherein the duration, or relative duration, of the states is controlled to control the AC output. 8. The MMPC as claimed in claim 6, elating wherein, in the first state, one capacitor is charged while the other is discharged. 9. The MMPC as claimed in claim 6, wherein the MMPC includes at least one half bridge, wherein at least one of the at least one of the half bridges delivers power to the output during the states. 10. A method of controlling a modular multilevel power converter, the method comprising: operating controllable switches of one or more submodules in a submodule stack of the power converter to selectively transfer energy from an inductive element of the power converter to boost a voltage at an output of the power converter relative to a voltage at an input of the power converter, wherein the modular multilevel power converter includes the submodule stack and the inductive element is provided between the input and the output. 11. The method as claimed in claim 10, further including operating the switches to produces a staircase voltage waveform at the output. 12. A method, comprising: obtaining a modular multilevel power converter, the power converter including: at least one submodule stack having an output for connection to a load and an input for connection to an input power source; andat least one inductive element provided between the input and the output, wherein the at least one submodule stack includes at least two submodules respectively including at least one capacitor and a plurality of controllable switches; andoperating the controllable switches to selectively transfer energy from the at least one inductive element to boost a voltage at the output relative to a voltage at the input. 13. The method as claimed in claim 12, further comprising operating the switches to selectively transfer energy between at least two of: the submodule(s), input power source or load. 14. The method as claimed in claim 10, further comprising operating the switches to selectively transfer energy between at least two of: the submodule(s), input power source or load. 15. The MMPC as claimed in claim 7, wherein, in the first state, one capacitor is charged while the other is discharged. 16. The MMPC as claimed in claim 6, wherein the MMPC includes at least one half bridge, wherein at least one of the at least one of the half bridges delivers power to the output during the states. 17. The MMPC as claimed in claim 7, wherein the MMPC includes at least one half bridge, wherein at least one of the at least one of the half bridges delivers power to the output during the states. 18. The MMPC as claimed in claim 8, wherein the MMPC includes at least one half bridge, wherein at least one of the at least one of the half bridges delivers power to the output during the states. | [EN US2021044216A1]: FIELD OF THE DISCLOSURE The present disclosure relates to an integrated boost modular multilevel converter, which has particular, but not sole, relevance to a converter for an inductive or capacitive (wireless) power transfer system. BACKGROUND Electric Vehicles (EVs) are becoming increasingly popular as the preferred transportation method for a sustainable future. Although currently EVs employ wired chargers, Wireless Power Transfer (WPT) technology is expected to revolutionize the way EVs are charged by offering an attractive alternative. This has fuelled the development of cost effective commercially viable WPT solutions to allow EVs to be simply charged by parking over a designated ground-based charging pad. In-home wired and wireless EV chargers were traditionally designed to operate with a single-phase supply and with power ratings of up to 7.4 kW, which results in charging times of between 3-7 hours. However, there is an increasing demand for faster charging speeds, especially at public EV charging stations. As a result, the industry focus is now shifting towards the design of wired and wireless fast chargers with power ratings of up to 150 kW. For example, the Nissan Leaf can be charged using its 50 kW rapid charger technology to achieve a charging time of 20˜30 mins/100 km. The Tesla Model S, on the other hand, can be charged using their 120 kW supercharger technology at a rate of 10 mins/100 km. In the future, wireless fast chargers and new battery technologies are expected to be developed to make the charging of EVs convenient and comparable to the refuelling time of a vehicle with an internal combustion engine There is also a growing interest among researchers and industries to explore the feasibility of using WPT technology to charge EVs while being driven on roadways with special lanes containing underground charging pads. This application is referred to as in-motion charging or dynamic charging. It is expected to provide a cost-effective solution to issues such as limited range and charging speed, which are considered as the two main factors hindering the widespread use of EVs. As an example, a study conducted by Utah State University has shown that an EV with a 25 mile on-board electrical range and a 50 kW in-motion charging system can meet 99% of the mobility requirements of a typical light-duty vehicle user. Currently, the accumulators used in electric vehicles have an on-board range of about 70 miles to 300 miles, and accounts for a significant portion of the cost of an EV. Therefore, a significantly smaller accumulator is expected to dramatically reduce the ownership cost of an electric vehicle. To address these future needs, there is a significant drive to develop high-power WPT systems that are suitable for fast-charging of stationary and moving vehicles. IGBT based full-bridge converters have traditionally been used in the primary supply of high-power WPT systems and recently the use of SiC MOSFET based full-bridge converter designs have been explored. In these designs, the primary full-bridge converter is operated close to the resonant frequency of the system and phase-shift modulation is used to regulate the power flow. As a result, the voltage waveform generated by the full-bridge converter has significant harmonic content, which becomes a considerable issue at higher-power levels due to additional conduction losses introduced in switches and the tuning network. Although pulse width modulation (PWM) schemes can be employed to improve the Total Harmonic Distortion (THD) of the converter output, the higher switching losses from increased switching frequency will have a significant impact on the efficiency. Alternatively, multilevel converters with pulse amplitude modulation schemes, which yield high quality output waveform with lower THD, can be utilized in high power WPT systems. Multilevel converters also greatly reduce the voltage stress on the switching devices, making it possible to use low voltage rated devices such as high-performance Si and GaN MOSFET switches. Therefore, the combination of lower THD and better switching devices could enable the development of efficient and affordable high-power WPT systems using multilevel converter topologies. Among the many different types of multilevel converter topologies developed to-date, diode clamped converter, flying capacitor converter, cascaded full-bridge converter and modular multilevel converters become the industry standard. A diode clamped converter, shown in FIG. 1(a), utilizes a number of cascaded capacitors together with a special arrangement of diodes to synthesize an output voltage waveform with multiple voltage levels. The disadvantages of this technology are the need for clamping diodes and the difficulty to control real power flow. In contrast, a flying capacitor converter, shown in FIG. 1(b), employs a special arrangement of capacitors to generate a pulse amplitude modulated output voltage. The drawbacks of such a topology include the need for an excessive number of bulky storage capacitors, and the large circulating current when the capacitor voltages are imbalanced. A cascaded full-bridge converter, shown in FIG. 1(c), consists of a number of series connected full-bridge modules with its own storage capacitors. However, the need for separate DC sources increases the losses and the cost for such topology. The modular multilevel converter (MMC), depicted in FIG. 1(d), consists of a number of series-connected full-bridge or half-bridge modules, which are controlled to synthesize a multilevel output voltage. However, complex control techniques are required to balance the capacitor voltages and therefore to reduce circulating current. To-date, the application of multilevel converters in WPT systems has been very limited, mainly as the WPT systems are operated at relatively lower voltages, typically in the range of 400 V to 800 V. The use of a few commonly known multilevel converter topologies in WPT systems have been recently investigated. Unfortunately, these WPT systems inherited some of the drawbacks of the multilevel converter topologies employed, limiting their suitability as an economical and efficient solution to high-power WPT systems. Therefore, currently, there is a significant drive to develop new and improved multilevel and modular converter topologies to address the limitations imposed by the existing converters employed in high-power WPT systems. In this specification where reference has been made to patent specifications, other external documents, or other sources of information, this is generally for the purpose of providing a context for discussing the features of the disclosure. Unless specifically stated otherwise, reference to such external documents is not to be construed as an admission that such documents, or such sources of information, in any jurisdiction, are prior art, or form part of the common general knowledge in the art. OBJECTS OF HTE DISCLOSURE It is an object of the disclosure to provide a converter which will at least go some way to overcoming disadvantages of existing systems, or which will at least provide a useful alternative to existing systems. Further objects of the disclosure will become apparent from the following description. SUMMARY OF DISCLOSURE Accordingly in one aspect the disclosure may broadly be said to consist in a modular multilevel power converter comprising: at least one submodule stack having an output for connection to a load and an input for connection to an input power source,at least one inductive element provided between the input and the output, the at least one submodule stack including at least two submodules, each submodule comprising at least one capacitor and a plurality of controllable switches, and the submodules being operable to selectively transfer energy from the at least one inductive element to boost a voltage at the output relative to a voltage at the input. Preferably, the energy is transferred between at least two of: the submodule(s), input power source and load. Preferably the submodules are operable to provide a staircase voltage waveform at the output. Preferably, the modular multilevel power converter comprises a plurality of submodule stacks. A method of controlling a modular multilevel power converter having: at least one submodule stack having an output for connection to a load and an input for connection to an input power source, at least one inductive element provided between the input and the output, the at least one submodule stack including at least two submodules, each submodule comprising at least one capacitor and a plurality of controllable switches, the method comprising: operating the controllable switches to selectively transfer energy from the at least one inductive element to boost a voltage at the output relative to a voltage at the input. Preferably the method includes operating the switches to selectively transfer energy between at least two of: the submodule(s), input power source and load. The disclosed subject matter also provides method or system which may broadly be said to consist in the parts, elements and features referred to or indicated in this specification, individually or collectively, in any or all combinations of two or more of those parts, elements or features. Where specific integers are mentioned in this specification which have known equivalents in the art to which the disclosure relates, such known equivalents are deemed to be incorporated in the specification. DRAWING DESCRIPTION A number of embodiments of the disclosure will now be described by way of example with reference to the drawings as follows. FIGS. 1 to 1D is a circuit diagram of a traditional multilevel converter topology, depicting the topopgies (a) diode clamped converter; (b) flying capacitor converter; (c) cascaded H-bridge converter; (d) modular multilevel converter. FIG. 2 is a general circuit diagram of the Integrated Boost Multilevel Converter (IBMC) of the present disclosure. FIGS. 3 to 3E depicts a state and diagram of all the 16 circuit states. The corresponding circuit diagram of the circuit states are also illustrated, for example (b) circuit state #1 current flow (c) circuit state #2 current flow (d) circuit state #3 current flow (e) circuit states #1-7 resulting 5 level staircase voltage waveform Vpi FIG. 4 shows a state signal describing the state of the submodule. FIGS. 5 to 5B show the (a) total harmonic distortion and (b) Power level for different combinations of Duty Cycle and Phase Angle in an IB-MMC with 2 SMs in each arm FIG. 6 depicts the PI controller for power regulation FIG. 7 is a graph showing SM state signals and Vpi waveforms at 100% and 70% rated power FIG. 8 shows simulated waveforms produced by a grid connected converter. FIGS. 9a to 9I show current flows for different circuit states of the present IBMC disclosure. FIG. 10 depicts an embodiment of the circuit diagram of the present IBMC system. FIGS. 11A to 11E depict the circuit diagrams of various embodiments of the present IBMC system, more specifically the figures illustrate the multilevel converter arrangements and sub module configurations (to half bridge, full bridge, cascaded half-bridge, neutral-point clamped configurations). FIG. 12 shows a flowchart of the sorting algorithm for capacitor balancing. FIG. 13 depicts an example embodiment of the present IBMC system used in the simulation and testing. FIG. 14 illustrates the power level and THD for different combinations of duty cycle and phase angles FIG. 15 illustrates the optimal Duty Cycle and Phase Angle for Minimal THD of the IBMC system. FIG. 16 illustrates a voltage curve V1 and a curve of a total harmonic distortion (THD) against varying phase angles, at different fixed duty cycles. FIG. 17 shows a schematic of a PI controller for power transfer FIG. 18 shows curves of submodule state signals and voltage V1 waveforms at different values of power delivery. FIG. 19 shows the comparison of the graphs of the percentage of rated power between a traditional H-Bridge converter and the current IBMC THD comparison. FIG. 20 depicts an embodiment comprising a 5-level IBMMC WPT system. FIGS. 21A to 21G depict the operations of the circuit in seven different circuit states. FIG. 21 H graphically depicts a 5-level staircase voltage waveform. FIG. 22 shows an embodiment of a simplified LCL-LC WPT circuit diagram. FIG. 23 shows the relationship between the modulation index vs coupling factor in a graphical representation. FIG. 24 shows the relationship between the simulated efficiency vs coupling factor in a graphical representation. FIG. 25 depicts a contour plot of the Modulation index and control trajectories for 3-level and 5-level mode. FIG. 26 shows a flowchart for the capacitor voltage balancing algorithm. FIGS. 27A to C depict the Experimental waveforms at (a) the best coupling, (b) the nominal coupling and (c) the worst coupling positions). FIG. 28 depicts in graphical form the effect of capacitor voltage on SM1 and SM3. FIGS. 29A to B show the circuit configurations of the generic submodules according to an embodiment of the present invention. In the first configuration (a) a separate DC coupling network such as a inductor or a coupled inductor is used. In the second configuration (b) the DC coupling network is integrated with the resonant network. DETAILED DESCRIPTION OF THE DRAWINGS In comparison to traditional conductive EV charging, Inductive Power Transfer (IPT) based Wireless Power Transfer technologies have become attractive for charging EVs when they are simply parked over a designated ground-based charging pad. While WPT technologies provide aesthetically pleasing, convenient and safe EV charging solutions, they also enable automated charging. Over the past decade, IPT based WPT technologies have advanced considerably making low to medium power stationary charging commercially feasible. However, in recent years, the focus has been shifted to explore the feasibility of high-power IPT solutions that enable fast charging as well as in-motion charging. The refuelling time of EVs can be significantly reduced using fast chargers, while in-motion charging or dynamic charging can help extending the effective range and avoid deep-cycling of the EV batteries. This trend is further evident by the emphasis on WPT3 (11 kW) and WPT4 (22 kW) power classes defined in the SAE J2954 standard. In order to develop high-power WPT systems, the use of SiC MOSFET based full-bridge converter designs in the primary power supply has been explored in the past. These systems commonly employed a significantly high-voltage DC bus, which was derived through the grid-side converter or a separate boost converter, to feed the SiC MOSFET based full-bridge converter. Some solutions also utilised a high-frequency step-up transformer to drive the compensation network at a higher voltage, thereby increasing the power transfer capability. Alternatively, other designs proposed that the WPT transmitter and receiver coils can be partially series tuned to increase the power transfer capability. While these solutions helped increasing the power transfer, the voltage waveform generated by full bridge converters to drive the compensation network contained a significant amount of harmonic content. At higher power levels, this leads to the increased conduction losses in the switches and the compensation network. Among the many different types of multilevel converter topologies proposed to-date, the diode-clamped or neutral point clamped converter (NPC), flying capacitor converter (FC), cascaded H-bridge converter (CHBC) and modular multilevel converter (MMC) have become the industry standard. However, the application of these multilevel converters in WPT systems has been very limited, mainly as the WPT systems are operated at relatively lower voltages, typically in the range of 400 V to 800 V. These multilevel converter based solutions, which were predominantly based on the CHBC topology, helped improving the power transfer capability. However, the requirement for separate DC power supplies to power each full-bridge module in a CHBC, somewhat limited the suitability of these topologies as economical and efficient solutions. As such, there is a significant drive to develop new and improved multilevel converter topologies, which address the limitations imposed by the existing converters employed in high-power WPT systems. To help address this need, a novel Integrated Boost Multilevel Converter (IB-MMC) 10 for high power WPT applications has been proposed. Similar to a traditional MMC, the proposed IB-MMC consists of series-connected half-bridge or full-bridge sub-modules (SMs) forming each arm of the converter. However, the DC source in an IB-MMC is interfaced with each arm through an inductor, which together functions as a boost converter delivering energy to each SM from the DC source. In contrast to a traditional MMC, this unique circuit configuration enables the IB-MMC to generate higher AC voltages to drive the WPT coil and eliminates the circulating currents, thus making it an attractive option for high-power WPT systems. Consequently, the current IB-MMC provides a unique boost circuit configuration in the modular multilevel converter arrangement, which allows it to produce low THD staircase voltage waveforms with significantly higher amplitude than traditional multilevel converters, while eliminating circulating current. A mathematical model of IB-MMC is presented and the control technique is discussed below. The present mathematical model describes the behaviour of the IB-MMC topology, which is derived to show the voltages and currents in an IB-MMC. An expression for power transferred is derived and the control techniques that allow regulating the output power as well as voltages across each module are discussed. Results obtained from a 7.7 kW proof of concept prototype are presented to validate the suitability of the proposed IB-MMC technology for high-power WPT systems. The generic form of the proposed Integrated Boost Modular Multilevel Converter (IB-MMC) is shown in FIG. 2(a). Similar to a traditional MMC, each arm of an IB-MMC consists of a number of series connected half-bridge (or full-bridge) SMs that produce a staircase modulated output voltage. The SMs in each arm of the IB-MMC are controlled to generate a regulated low THD AC voltage, Vpi, which, in this example, drives the primary transmitter coil, Lpt, through the primary compensation network. The DC power source, VDC, of this unique topology, is connected across the output of the left and the right arms, V1 and V2, through DC inductors, L1 and L2, respectively. As such, this configuration enables the SMs to extract energy from VDC, which will be typically derived from the utility grid. Because of the use of a single power source VDC, the SMs can extract energy without requiring additional circuitry, unlike traditional multilevel converters such as CHBC where multiple DC sources are needed. Each DC inductor together with the SMs attached to it also functions as a boost converter, thereby enabling the IB-MMC to generate a significantly higher Vpi across the transmitter coil from a low voltage DC source. Furthermore, the proposed circuit topology eliminates circulating currents since the design ensures zero DC offset across Vpi. In comparison to traditional full-bridge and multilevel converter based WPT systems, IB-MMC offers a number of advantages that can simplify the design of high power WPT systems. Referring to the Integrated Boost Modular Multilevel Converter (IB-MMC) 10 shown in FIG. 2., similar to a traditional MMC, each arm 100, 200 of this IB-MMC 10 includes of a stack of series connected half-bridge (or full-bridge) submodules (SMs) that produce a staircase modulated output voltage. The simplest IB-MMC 10 can employ a single arm 100 to drive a single transmitter coil, whereas higher power poly-phase WPT systems may utilize multiple arms to drive a poly-phase transmitter. Each SM has a set of switches to insert or bypass the capacitor voltage. In the embodiment as depicted in should be 11a, the DC power source 400 is connected across the output of the multilevel converter 10 through a DC inductive element 110 (L1). As such, this configuration enables the SMs of the proposed multilevel converter 10 to extract energy from the DC power source 400 without requiring additional circuitry, which are typically found in other multilevel converter topologies. The DC inductor 110 also functions as a boost inductor, thereby enabling the converter 10 to generate a significantly higher AC voltage across the load 300 from a low voltage DC power source 400. Furthermore, the proposed circuit topology eliminates circulating current issues found in commonly used multilevel converter topologies and by design ensures zero DC offset across V1. Thus, the converter 10 shown in FIG. 2 may represent one phase module of a poly-phase converter. To avoid confusion, the modules in each arm or limb 100, 200 of the converter module are referred to herein using the terminology commonly adopted in the art, as submodules SMs. As depicted in FIG. 2, one embodiment of an IB-MMC 10 employs two submodule stacks, limbs or arms 100, 200 and drives a single transmitter coil Lpt as a load 300. It should be noted that the load 300 is not limited to the WPT systems. The SMs in each arm 100, 200 of the IB-MMC 10 in FIG. 2 are controlled to generate a regulated low THD AC voltage, Vpi, which drives the primary transmitter coil, Lpt, through the primary compensation network. In this embodiment, the DC power source 400 (VDC), is connected across the output of left 100 and right 200 arms, V1 and V2, through DC inductors 110, 210 (L1 and L2), respectively. As such, this configuration enables the SMs to extract energy from the power source 400 (VDC), which will be typically derived from the utility grid, without requiring additional circuitry. Each DC inductor 110, 210 together with the SMs attached to it also functions as a boost converter, thereby enabling the IB-MMC 10 to generate a significantly higher Vpi across the transmitter coil from a low voltage DC power source 400. Furthermore, the proposed circuit topology eliminates circulating currents since the design ensures zero DC offset across Vpi. As such, in comparison to traditional full-bridge and multilevel converter based WPT systems, WPT systems based on IB-MMC as disclosed herein offer a number of advantages that can simplify the design of high-power WPT systems. To gain an insight to the operating principles of the proposed technology, consider an IB-MMC based WPT system utilising two arms 100, 200 with only two half-bridge SMs 120, 130, 220, 230 in each arm 100, 200 as shown in FIG. 3. The primary and the pick-up of this WPT system employ LCL compensation networks formed by Lpi-Cpt-Lpt and Lsi-Cst-Lst, respectively. The WPT system, alternatively, can employ other types of compensation networks depending on the application. In FIG. 3, the red line indicates the DC current path whereas the blue dotted line indicates the AC current path. The DC part of the current flows from the DC power source 400 into the SMs 120, 130, 220, 230 and charges the capacitors 122, 132, 222, 232, thus transferring energy from the DC power source 400 to the SMs 120, 130, 220, 230. The AC part of the current flows through the LCL compensation network and represents the power transferred to the load 300 attached to the pick-up converter, which is denoted by a voltage source, Vsi. Turning on the top switch 124, 134, 224, 234 of each SM 120, 130, 220, 230 inserts its storage capacitor 122, 132, 222, 232 in series with the current flow, while turning on the bottom switch 126, 136, 226, 236 bypasses the current flow. Therefore, in this particular example, assuming all SMs 120, 130, 220, 230 are operating at the same duty-cycle D, where D is the ratio between the time SM 120, 130, 220, 230 is inserted to the switching time-period, there are 16 circuit states. Although, all 16 circuit states, which are summarised in FIG. 3(a), can be utilised for circuit operation, the proposed system only utilises circuit states #1-7 to regulate Vpi and the power delivered to the load 300. Brief descriptions of these states #1-7 are given below to highlight the operating principles of the converter 10: In state #1, as shown in FIG. 3(b), all the SMs 120, 130, 220, 230 are bypassed, and therefore the voltage driving the LCL network, Vpi, is 0. As the voltages V1 and V2 are also 0 V, DC currents, IL1 and IL2 linearly increase storing energy in inductive elements 110, 210 (L1 and L2), respectively. In state #2, as shown in FIG. 3(c), SM 120 (SM1) is inserted and the rest of SMs 130, 220, 230 are bypassed. SM 120 (SM1) together with the inductive element 110 (L1) and the power source 400 (VDC) acts as a boost converter, thus charging the capacitor 122 (C1) to Vdc/2D by transferring the energy stored in inductive element 110 (L1) during state #1. In contrast, current IL2 continues increasing and storing energy in inductive element 210 (L2). Since SMs 130, 220, and 230 (2-4) are bypassed, the resulting voltage across the primary LCL network is VDC/2D and energy is also transferred from capacitor 122 (C1) to the load 300 as indicated by the AC current. The operating principles are similar during circuit states #4, #5 and #7, as only a single SM 120, 130, 220, 230 is inserted, and the resulting Vpi is either VDC/2D or −VDC/2D depending on whether the SM 120, 130, 220, 230 inserted is in the right or the left arm, respectively. In state #3, as shown in FIG. 3 (d), SM 120 (SM1) and SM 130 (SM2) are inserted while SM 220 (SM3) and SM 230 (SM4) are bypassed. This part of the circuit can also be seen as a boost converter where the energy stored in inductive element 110 (L1) is transferred to both capacitor 122 (C1) and capacitor 132 (C2). Therefore, under steady state conditions, the average voltage across the left arm 100, V1, is equal to VDC/D. Since the right arm 200 is bypassed, the voltage across the LCL network is VDC/D and energy is transferred from capacitor 122 (C1) and capacitor 132 (C2) to the load 300. Similarly, in state #6, energy stored in inductive element 210 (L2) is transferred to capacitor 222 (C3) and capacitor 234 (C4) while capacitor 222 (C3) and capacitor 234 (C4) generates −VDC/D to drive the primary LCL network. By operating the circuit in states #1-7 described above, a 5-level staircase voltage waveform Vpi can be derived as shown in FIG. 3(e). The duration of each voltage-level can be controlled either by changing D or introducing a phase-shift, φ_k, to the outputs generated by each SM 120, 130, 220, 230. As shown in FIG. 3(e), under steady state operating conditions, the average of V1 and V2 is VDC. As a result, the design ensures zero DC offset across V-pi and eliminates the need for the DC-blocking capacitor employed in traditional LCL tuned WPT systems. Apart from circuit states #1-7, other states shown in FIG. 3(a) can be used to improve control flexibility. Circuit operation during states #8-11 is similar to state 2 as the IB-MMC 10 generates ±VDC/2D to drive the primary LCL network. Similar to state #4, states #12-16 generates 0 V across the primary LCL network, and thus these redundant states can be used for voltage balancing. In another embodiment as seen in FIGS. 29(a)-(b), a circuit configuration of a generic submodule is shown. This may be used as a single module by itself. Alternatively they can be connected in series to form a branch of the proposed IBMMC. The first configuration in 29(a) shows where a separate DC coupling network such as a inductor or a coupled inductor is used. In the second configuration in 29(b) the DC coupling network is integrated with the resonant circuit. Another embodiment incorporating a 5-level IB-MMC based WPT converter, provides further insights as to the topology of the present converter. The 5-level IB-MMC utilizes two arms, where each arm consists of two half-bridge SMs as shown in FIG. 20. The output voltage of the IB-MMC drives an inductor-capacitor-inductor (LCL) compensation network formed by Lpi-Cp-Lpt for wireless power transfer. The pick-up circuit consists of a parallel-tuned inductor-capacitor (LC) compensation network formed by Lst-Cs, and a diode rectifier that feeds a battery. The WPT system, alternatively, can employ other types of compensation networks depending on the application. The circuit states are shown in FIG. 21, where the red lines indicate the DC current paths while the blue dotted lines indicate the AC current paths. The DC part of the current flows from the DC source into the SMs and charges the capacitors, thus transferring energy from the DC source to the SMs. The AC part of the current flows through the LCL compensation network and represents the power transferred to the load attached to the pick-up converter, which is denoted by a battery, Vbatt. Turning on the top switch of each SM inserts its storage capacitor in series with the current flow, while turning on the bottom switch bypasses the current flow. Each SM of an IB-MMC is typically operated at the same duty-cycle, D, where D is the ratio between the time SM is inserted to the switching time-period. This operation results in 16 circuit states, which are summarised in Table. I, where “0” represents bypassing the SM, “1” represents inserting the SM. A description of the circuit states are given below to highlight the operating principles of the converter. TABLE I 5-level IB-MMC Circuit States Circuit State SM1 SM2 SM3 SM4 Vpi #1 0 0 0 0 0 #2 1 0 0 0 VDC/2D #3 1 1 0 0 VDC/D #4 0 1 0 0 VDC/2D #5 0 0 1 0 −VDC/2D #6 0 0 1 1 −VDC/D #7 0 0 0 1 −VDC/2D #8 0 1 1 1 −VDC/2D #9 1 0 1 1 −VDC/2D #10 1 1 0 1 VDC/2D
[ZH CN110994560B]: 一种低损耗模块化多电平换流器故障穿越方法 [EN CN110994560B]: A low-loss modular multilevel converter fault ride-through method | [ZH CN110994560B]: 本发明提供一种低损耗模块化多电平换流器故障穿越方法，所述换流器包括三个相单元，每一个单元分上下桥臂，每个桥臂包括若干个串联的子模块，子模块由两个半桥结构、四个电容和两个续流二极管组成，第一个半桥包括第一开关模块和第二开关模块，第二个半桥包括第三开关模块和第四开关模块；第一开关模块的负极与第二开关模块的正极相连，第二开关模块的负极与第三开关模块的正极相连，第三开关模块的负极与第四开关模块的正极相连；利用逆阻型绝缘栅双极晶体管性质，在发生直流侧极间短路故障时，关断逆阻型绝缘栅双极晶体管组成的双向开关，阻断故障回路。本发明通过控制开关模块的开断即可实现直流侧短路的故障阻断，同时不会增加损耗。 [EN CN110994560B]: The invention provides a low-loss modular multilevel converter fault ride-through method. A converter comprises three phase units, each unit is divided into an upper bridge arm and a lower bridge arm,and each bridge arm comprises a plurality of sub-modules which are connected in series. Each sub-module consists of two half-bridge structures, four capacitors and two fly-wheel diodes, the first half-bridge comprises a first switch module and a second switch module, and the second half-bridge comprises a third switch module and a fourth switch module. The cathode of the first switch module is connected with the anode of the second switch module, the cathode of the second switch module is connected with the anode of the third switch module, and the cathode of the third switch module is connected with the anode of the fourth switch module. By utilizing the properties of the reverse-blocking insulated gate bipolar transistors, when a direct-current side inter-electrode short-circuit fault occurs, a two-way switch composed of the reverse-blocking insulated gate bipolar transistors is turned off, and a fault loop is blocked. According to the method, the fault blocking of direct-current side short circuit can be achieved by controlling the on-off of the switch modules, and meanwhile loss is not increased. | CN110994560B | 2020-04-10 2020-11-20 | CN201911168951A | 2019-11-25 2019-11-25 | CN201911168951A, 2019-11-25 CN201911168951A, 2019-11-25 | CN110994560B: 2020-11-20 | UNIV SHANGHAI JIAOTONG 上海交通大学 | PENG CHENG LI RUI CAI XU | H02H7/122: I H02M7/483: I | H02H7/122: I H02H7/1222: I H02M7/483: I | CN104320011A CN105610336A CN110224623A CN110417290A CN102868290A CN109842142A |  | [ZH CN110994560B]: 1 .一种低损耗模块化多电平换流器故障穿越方法,其特征在于： 所述换流器包括三个相单元，每一个单元分上下桥臂，每个桥臂包括若干个串联的子 模块，所述子模块由两个半桥结构、四个电容和两个续流二极管组成，其中： 第一个半桥包括第一开关模块和第二开关模块，第二个半桥包括第三开关模块和第四 开关模块;所述第一开关模块的负极与所述第二开关模块的正极相连，所述第二开关模块 的负极与所述第三开关模块的正极相连，所述第三开关模块的负极与所述第四开关模块的 正极相连;所述第二开关模块由第一逆阻型绝缘栅双极晶体管和与之反并联的第二逆阻型 绝缘栅双极晶体管组成;所述第三开关模块由第三逆阻型绝缘栅双极晶体管和与之反并联 的第四逆阻型绝缘栅双极晶体管组成； 第一个电容的正极与所述第一开关模块的正极相连;所述第一个电容的负极与第二个 电容的正极相连;所述第二个电容的负极与所述第二开关模块的负极相连;第三个电容的 正极与所述第三开关模块的正极相连;所述第三个电容的负极与第四个电容的正极相连， 所述第四个电容的负极与所述第四开关模块的负极相连； 第一个续流二极管的负极与所述第一个电容的负极相连，所述第一个续流二极管的正 极与所述第四开关模块的正极相连，所述第二个续流二极管的负极与所述第二开关模块的 正极相连，所述第二个续流二极管的正极与所述第三个电容的负极相连； 所述第一开关模块的负极和所述第二开关模块的正极之间的节点作为整个子模块的 第一个输出端子;所述第三开关模块的负极和所述第四开关模块的正极之间的节点作为整 个子模块的第二个输出端子； 所述故障穿越方法包括： 利用所述逆阻型绝缘栅双极晶体管性质，在发生直流侧极间短路故障时，关断所述逆 阻型绝缘栅双极晶体管组成的双向开关，阻断故障回路，从而使得故障电流经过所述电容， 继而利用电容电压和子模块中的二极管的反向阻断性质来阻断故障电流。 2 .根据权利要求1所述的低损耗模块化多电平换流器故障穿越方法，其特征在于：当检 测到直流侧发生双极短路故障时： 关断所述子模块中的第一开关模块〜第四开关模块中所有全控开关，从而利用所述子 模块的电容电压使续流二极管承受反压，从而关断;所述全控开关包括所述第一开关模块、 所述第四开关模块中的绝缘栅双极晶体管，以及所述第二开关模块、所述第三开关模块中 的逆阻型绝缘栅双极晶体管。 3 .根据权利要求1所述的低损耗模块化多电平换流器故障穿越方法，其特征在于：当发 生的故障为直流侧永久性故障时： 利用所述续流二极管反压关断特性阻断故障电流之后，断开交流侧断路器，再断开直 流侧开关； 故障修复后，闭合直流侧开关，若未过流则对所述逆阻型绝缘栅双极晶体管施加触发 脉冲，之后系统进入有功给定为零的状态，若不出现直流侧过流,则可进行交流侧重合闸， 之后恢复正常运行状态； 若出现直流侧过流，则再次封锁所述第一开关模块〜所述第四开关模块中所有全控开 关脉冲。 4 .根据权利要求1所述的一种低损耗模块化多电平换流器故障穿越方法，其特征在于： 当发生的故障为直流侧暂时性故障时： 利用所述续流二极管反压关断特性阻断故障电流之后，达到设定时间后，对所述逆阻 型绝缘栅双极晶体管施加触发脉冲，之后换流器进入有功给定为零的运行状态； 若未出现直流侧短路情况，则证明暂时性故障已清除，将换流器有功给定软起动;若仍 出现短路情况，说明直流侧暂时性故障还未清除，重新闭锁脉冲，并定时重启动，直到重启 动成功为止； 若重启动超过三次，则认为是发生了永久性故障。 5 .根据权利要求1所述的一种低损耗模块化多电平换流器故障穿越方法，其特征在于: 所述换流器中，每相上、下桥臂串联的子模块数量相同。 6 .根据权利要求5所述的一种低损耗模块化多电平换流器故障穿越方法，其特征在于: 所述换流器中，上、下桥臂分别串联限流电抗器，每相从上至下为:上桥臂所有子模块、上桥 臂电抗器、下桥臂电抗器、下桥臂所有子模块;且每相上下桥臂连接处外接三相交流电压， 上桥臂最上面子模块拓扑的第一个输出端子与直流母线正极相连，下桥臂最下端子模块第 二个输出端子与直流母线负极相连。 7 .根据权利要求6所述的一种低损耗模块化多电平换流器故障穿越方法，其特征在于: 所述第一个输出端子连接第一个半桥结构的输出口和第二续流二极管的阴极，所述第二个 输出端子连接第二个半桥结构的输出口和第一续流二极管的阳极。 8 .根据权利要求1-6任一项所述的一种低损耗模块化多电平换流器故障穿越方法，其 特征在于:所述第一开关模块、所述第四开关模块均由一个绝缘栅双极晶体管和一个二极 管反并联组成。 9 .根据权利要求1-6任一项所述的一种低损耗模块化多电平换流器故障穿越方法，其 特征在于：正常工作情况下，所述第二开关模块的负极接第一个输出端子的第二逆阻型绝 缘栅双极晶体管以及第三开关模块的正极接第二个输出端子的第四逆阻型绝缘栅双极晶 体管保持导通状态；所述两个续流二极管由于承受反压保持关断状态，不加入电路，从而不 产生导通损耗。 [EN CN110994560B]: 1 A low-loss modular multi-level converter fault ride-through method, characterized in that: the converter includes three phase units, each unit is divided into upper and lower bridge arms, each bridge arm includes a number of series connected sub Module, the sub-module is composed of two half-bridge structures, four capacitors and two freewheeling diodes, wherein: the first half-bridge includes the first switch module and the second switch module, and the second half-bridge includes the third A switch module and a fourth switch module; the negative pole of the first switch module is connected to the positive pole of the second switch module, the negative pole of the second switch module is connected to the positive pole of the third switch module, and the third The negative pole of the switch module is connected to the positive pole of the fourth switch module; the second switch module is composed of a first reverse resistance insulated gate bipolar transistor and a second reverse resistance insulated gate bipolar transistor in anti-parallel connection; The third switch module is composed of a third reverse resistance insulated gate bipolar transistor and a fourth reverse resistance insulated gate bipolar transistor connected in anti-parallel with it; the anode of the first capacitor is connected to the anode of the first switch module Connected; the negative pole of the first capacitor is connected to the positive pole of the second capacitor; the negative pole of the second capacitor is connected to the negative pole of the second switch module; the positive pole of the third capacitor is connected to the third switch The anode of the module is connected; the cathode of the third capacitor is connected to the anode of the fourth capacitor, and the cathode of the fourth capacitor is connected to the cathode of the fourth switch module; The cathode of the first freewheeling diode is connected to the cathode of the first capacitor, the anode of the first freewheeling diode is connected to the anode of the fourth switch module, and the cathode of the second freewheeling diode is connected Connected to the anode of the second switch module, the anode of the second freewheeling diode is connected to the cathode of the third capacitor; one of the cathode of the first switch module and the anode of the second switch module The node between the two serves as the first output terminal of the entire submodule; the node between the negative pole of the third switch module and the positive pole of the fourth switch module serves as the second output terminal of the entire submodule; the fault ride-through The method includes: using the properties of the reverse resistance insulated gate bipolar transistor to turn off the bidirectional switch composed of the reverse resistance insulated gate bipolar transistor when a short-circuit fault occurs between the DC side electrodes to block the fault circuit, so that The fault current passes through the capacitor, and then the capacitor voltage and the reverse blocking property of the diode in the sub-module are used to block the fault current. 2 The low-loss modular multilevel converter fault ride-through method according to claim 1, characterized in that: when a bipolar short-circuit fault is detected on the DC side: the first switch module in the sub-module is turned off ~ All the full control switches in the fourth switch module, so as to use the capacitor voltage of the sub-module to cause the freewheeling diode to withstand the back pressure, thereby turning off; the full control switch includes the first switch module, the fourth switch The insulated gate bipolar transistor in the module, and the reverse resistance insulated gate bipolar transistor in the second switch module and the third switch module. 3 The low-loss modular multilevel converter fault ride-through method according to claim 1, characterized in that: when the fault occurs is a permanent fault on the DC side: the reverse voltage shut-off characteristic of the freewheeling diode is used to prevent After breaking the fault current, open the AC side circuit breaker, and then open the DC side switch; after the fault is repaired, close the DC side switch, if there is no overcurrent, apply a trigger pulse to the reverse resistance insulated gate bipolar transistor, and then the system Enter the state where the active power is set to zero. If there is no overcurrent on the DC side, the AC side can be reclosed, and then the normal operation state can be restored; if there is an overcurrent on the DC side, the first switch module is blocked again~the All full control switch pulses in the fourth switch module. 4 A low-loss modular multilevel converter fault ride-through method according to claim 1, characterized in that: When the fault that occurs is a temporary fault on the DC side: After the fault current is blocked by the freewheeling diode back-voltage turn-off feature, after a set time is reached, a trigger pulse is applied to the reverse resistance insulated gate bipolar transistor, After that, the converter enters the operating state where the active power setting is zero; if there is no short-circuit on the DC side, it proves that the temporary fault has been cleared, and the active power setting of the converter is soft-started; if the short circuit still occurs, it means that the DC side is temporarily If the fault has not been cleared, the pulse will be blocked again and restarted regularly until the restart is successful; if the restart is more than three times, it is considered that a permanent fault has occurred. 5 The fault ride-through method for a low-loss modular multilevel converter according to claim 1, characterized in that: in the converter, the number of sub-modules connected in series with the upper and lower arms of each phase is the same. 6 A low-loss modular multi-level converter fault ride-through method according to claim 5, characterized in that: in the converter, the upper and lower arms are respectively connected in series with current-limiting reactors, and each phase is from From top to bottom: all the sub-modules of the upper bridge arm, the upper bridge arm reactor, the lower bridge arm reactor, and all the sub-modules of the lower bridge arm; and the connection of the upper and lower bridge arms of each phase is connected with three-phase AC voltage, and the uppermost sub-module of the upper bridge arm The first output terminal of the module topology is connected to the positive pole of the DC bus, and the second output terminal of the lowermost terminal module of the lower bridge arm is connected to the negative pole of the DC bus. 7 The fault ride-through method of a low-loss modular multilevel converter according to claim 6, wherein: the first output terminal is connected to the output port of the first half-bridge structure and the second freewheeling The cathode of the diode, and the second output terminal is connected to the output port of the second half-bridge structure and the anode of the first freewheeling diode. 8 The fault ride-through method of a low-loss modular multilevel converter according to any one of claims 1-6, wherein: the first switch module and the fourth switch module are both insulated by The gate bipolar transistor and a diode are anti-parallel. 9 The fault ride-through method for a low-loss modular multilevel converter according to any one of claims 1-6, characterized in that: under normal working conditions, the negative pole of the second switch module is connected to the first The second reverse resistance insulated gate bipolar transistor of the output terminal and the fourth reverse resistance insulated gate bipolar transistor of which the anode of the third switch module is connected to the second output terminal remain in conduction; the two freewheeling diodes Withstand the back pressure to maintain the off state, do not join the circuit, so that no conduction loss occurs. | [ZH CN110994560B]: 一种低损耗模块化多电平换流器故障穿越方法 技术领域 [0001]本发明涉及电力系统输配电技术领域，具体地，涉及一种具备故障阻断能力的低 损耗的模块化多电平换流器的故障穿越方法。 背景技术 [0002]随着可再生能源发电量的提升，可再生能源并网成为了当下一个非常重要的研究 方向。 [0003]柔性直流输电技术为解决可再生能源并网提供了一种解决思路，具有较强的技术 优势。其中利用模块化多电平换流器的柔性直流输电技术相比传统的两电平、三电平换流 器具有更好的可维护性、拓展性，且不存在开关管串联均压、并联均流问题。模块化多电平 换流器的每个子模块的结构相对简单，控制容易，且由于模块化易于拓展的特性使之特别 适合与高压直流输电领域。模块化多电平换流器输出的电平数可以通过调整桥臂中子模块 的数目进行调整，直流侧的电压也可以通过调整每相子模块的数目进行控制，这样模块化 多电平换流器构成的系统的电压等级和输出的谐波含量都可以得到有效的控制。 [0004]传统的模块化多电平换流器采用半桥结构的子模块拓扑，而半桥子模块拓扑由于 下管的反并联二极管不受控制脉冲控制，在直流侧发生短路故障时会形成交流侧到直流故 障点的续流回路，从而将短路故障传递到交流侧，对电网稳定性造成影响。所以需要通过直 流、交流断路器或其他方式阻断故障电流。然而，直流断路器目前暂无成熟的技术，且造价 过于昂贵;交流断路器需要较长的响应时间，在交流断路器断开前需要换流阀器件承受较 大的电流应力，极易造成器件的损坏。故需要一种子模块拓扑，对这种子模块进行控制即可 阻断直流侧故障。 [0005]现有具有故障阻断能力的子模块拓扑普遍存在一个问题，即在换流器正常工作状 态下每个子模块中会有一个额外开关器件位于正常的电流路径上，该器件处于常开状态。 当出现故障时，该开关器件关断，从而使得电流从另一条路径流通，以实现故障电流阻断或 限制的效果。该额外的开关器件将增加系统的导通损耗，从而造成资源的损失。现有故障穿 越方式几乎全部基于该额外的开关器件的控制，从而无法降低系统的导通损耗。 发明内容 [0006]针对现有技术的缺陷，本发明的目的提供一种基于具备故障阻断能力的低损耗的 模块化多电平换流器故障穿越方法，无需额外的开关器件即可实现直流侧短路的故障阻 断，进而实现故障穿越。 [0007]根据本发明的第一方面，提供一种低损耗模块化多电平换流器故障穿越方法，所 述换流器包括三个相单元，每一个单元分上下桥臂，每个桥臂包括若干个串联的子模块，所 述子模块由两个半桥结构、四个电容和两个续流二极管组成，其中： [0008]第一个半桥包括第一开关模块和第二开关模块，第二个半桥包括第三开关模块和 第四开关模块;所述第一开关模块的负极与所述第二开关模块的正极相连，所述第二开关 模块的负极与所述第三开关模块的正极相连，所述第三开关模块的负极与所述第四开关模 块的正极相连;所述第二开关模块由第一逆阻型绝缘栅双极晶体管和与之反并联的第二逆 阻型绝缘栅双极晶体管组成;所述第三开关模块由第三逆阻型绝缘栅双极晶体管和与之反 并联的第四逆阻型绝缘栅双极晶体管组成； [0009]第一个电容的正极与所述第一开关模块的正极相连;所述第一个电容的负极与第 二个电容的正极相连;所述第二个电容的负极与所述第二开关模块的负极相连;第三个电 容的正极与所述第三开关模块的正极相连;所述第三个电容的负极与第四个电容的正极相 连，所述第四个电容的负极与所述第四开关模块的负极相连； [0010]第一个续流二极管的正极与所述第一个电容的负极相连，所述第一个续流二极管 的负极与所述第四开关模块的正极相连，所述第二个续流二极管的正极与所述第二开关模 块的正极相连，所述第二个续流二极管的负极与所述第三个电容的负极相连； [0011]所述第一开关模块的负极和所述第二开关模块的正极之间的节点作为整个子模 块的第一个输出端子;所述第三开关模块的负极和所述第四开关模块的正极之间的节点作 为整个子模块的第二个输出端子； [0012] 所述故障穿越方法包括： [0013]利用所述逆阻型绝缘栅双极晶体管性质，在发生直流侧极间短路故障时，关断所 述逆阻型绝缘栅双极晶体管组成的双向开关，阻断故障回路，从而使得故障电流经过所述 电容，继而利用电容电压和子模块中的二极管的反向阻断性质来阻断故障电流。此处二极 管是指对应的子模块的续流通路中包含的器件，这些器件在直流侧故障发生时进行桥臂电 感电流的续流，在电感电流过零后，又因为各子模块的电容电压串联后大于交流侧线电压 而承受反压完成关断。 [0014]可选地，当检测到直流侧发生双极短路故障时： [0015]关断所述子模块中的第一开关模块〜第四开关模块中所有全控开关，从而利用所 述子模块的电容电压使续流二极管承受反压，从而关断;所述全控开关包括所述第一开关 模块、所述第四开关模块中的绝缘栅双极晶体管，以及所述第二开关模块、所述第三开关模 块中的逆阻型绝缘栅双极晶体管。 [0016]可选地,当发生的故障为直流侧永久性故障时： [0017]利用所述续流二极管反压关断特性阻断故障电流之后，断开交流侧断路器，再断 开直流侧开关； [0018]故障修复后，闭合直流侧开关，若未过流则对所述逆阻型绝缘栅双极晶体管施加 触发脉冲，之后系统进入有功给定为零的状态，若不出现直流侧过流，则可进行交流侧重合 闸，之后恢复正常运行状态； [0019]若出现直流侧过流，则再次封锁所述第一开关模块〜所述第四开关模块中所有全 控开关脉冲。 [0020]可选地,当发生的故障为直流侧暂时性故障时： [0021]利用所述续流二极管反压关断特性阻断故障电流之后，达到设定时间后，对所述 逆阻型绝缘栅双极晶体管施加触发脉冲，之后换流器进入有功给定为零的运行状态； [0022]若未出现直流侧短路情况，则证明暂时性故障已清除，将换流器有功给定软起动； 若仍出现短路情况，说明直流侧暂时性故障还未清除，重新闭锁脉冲，并定时重启动，直到 重启动成功为止； [0023] 若重启动超过三次，则认为是发生了永久性故障。 [0024]可选地，所述换流器中，每相上、下桥臂串联的子模块数量相同。 [0025]可选地，所述换流器中，上、下桥臂分别串联限流电抗器，每相从上至下为:上桥臂 所有子模块、上桥臂电抗器、下桥臂电抗器、下桥臂所有子模块;且每相上下桥臂连接处外 接三相交流电压，上桥臂最上面子模块拓扑的第一个输出端子与直流母线正极相连，下桥 臂最下端子模块第二个输出端子与直流母线负极相连。 [0026]可选地，所述第一个输出端子连接第一个半桥结构的输出口和第二续流二极管的 阴极，所述第二个输出端子连接第二个半桥结构的输出口和第一续流二极管的阳极。 [0027]可选地，所述第一开关模块、所述第四开关模块均由一个绝缘栅双极晶体管和一 个二极管反并联组成。 [0028]可选地，正常工作情况下，所述第二开关模块的负极接第一个输出端子的第二逆 阻型绝缘栅双极晶体管以及第三开关模块的正极接第二个输出端子的第四逆阻型绝缘栅 双极晶体管保持导通状态；所述两个续流二极管由于承受反压保持关断状态，不加入电路， 从而不产生导通损耗。 [0029]与现有技术相比，本发明具有如下有益效果： [0030]本发明上述的低损耗模块化多电平换流器故障穿越方法，无需额外的开关器件， 通过控制逆阻型绝缘栅双极晶体管的开断即可实现直流侧短路的故障阻断，进而实现故障 穿越。 [0031]本发明上述的低损耗模块化多电平换流器故障穿越方法，通过控制开关模块和续 流二极管的状态，能够实现直流故障情况下的故障隔离，隔离速度快。 [0032]本发明上述的低损耗模块化多电平换流器故障穿越方法，在故障时能保持子模块 电容电压，恢复供电速度快。 附图说明 [0033] 通过阅读参照以下附图对非限制性实施例所作的详细描述，本发明的其它特征、 目的和优点将会变得更明显： [0034]图1为本发明一实施例方法中低损耗模块化多电平换流器原理图； [0035]图2为本发明一实施例方法中低损耗模块化多电平换流器的子模块拓扑结构； [0036]图3为本发明一实施例方法中低损耗模块化多电平换流器的子模块在直流故障下 经开关管控制后的等效电路图。 具体实施方式 [0037]下面结合具体的实施例对本发明进行详细的说明。以下实施例将有助于本领域的 技术人员进一步理解本发明，但不以任何形式限制本发明。应当指出的是，对本领域的普通 技术人员来说，在不脱离本发明构思的前提下，还可以做出若干变形和改进，这都属于本发 明的保护范围。 [0038]参照图1-3所示，本发明实施例中提供一种低损耗模块化多电平换流器故障穿越 方法，该方法利用逆阻型绝缘栅双极晶体管性质，在发生直流侧极间短路故障时，关断逆阻 型绝缘栅双极晶体管组成的双向开关，阻断故障回路，从而使得故障电流经过电容，继而利 用电容电压和模块中的二极管的反向阻断性质来阻断故障电流。由于逆阻型绝缘栅双极晶 体管的导通压降小于串联的同电压等级的绝缘栅双极晶体管和二极管的总导通压降，因 此，相对传统混合桥电路，可以使得系统整体的导通压降更小，在多模块系统中。系统损耗 主要取决于导通损耗，因此系统具有更高的效率。 [0039]具体的，上述低损耗模块化多电平换流器故障穿越方法适用的低损耗模块化多电 平换流器如图1-2所示。图1是一种三相模块化多电平换流器结构，其中每个桥臂的每个子 模块均由图2所示的子模块组成。该换流器无需依靠额外的开关器件，在具备故障阻断能力 的同时，具有低损耗的特点，可实现直流侧短路的故障阻断。 [0040]参照图1所示，低损耗模块化多电平换流器包括三个相单元，每一个单元分上下桥 臂，每个桥臂包括若干个串联的子模块，每相上、下桥臂串联的子模块数量相同；上、下桥臂 分别串联限流电抗器，每相从上至下为:上桥臂所有子模块、上桥臂电抗器、下桥臂电抗器、 下桥臂所有子模块；且每相上下桥臂连接处外接三相交流电压，上桥臂最上面子模块拓扑 的第一个输出端子与直流母线正极相连，下桥臂最下端子模块第二个输出端子与直流母线 负极相连。 [0041]参照图2所示，多电平直流直流变换器中每个桥臂的子模块由两个半桥结构、四个 电容C1〜C4和两个续流二极管D3〜D4组成。 [0042]两个半桥结构中，第一个半桥包括第一开关模块、第二开关模块;第一开关模块T1 的负极与第二开关模块的正极相连。第二个半桥包括第三开关模块和第四开关模块;第三 开关模块的负极与第四开关模块的正极相连;第三开关模块的正极与第二开关模块的负极 相连。具体的，参照图2所示，第一开关模块由一个绝缘栅双极晶体管T1和一个二极管D1反并 联组成;第四开关模块由一个绝缘栅双极晶体管T2和一个二极管D2反并联组成；第二开关模 块为逆阻型开关模块，由第一逆阻型绝缘栅双极晶体管TR1和与之反并联的第二逆阻型绝缘 栅双极晶体管TR2组成，第三开关模块也为逆阻型开关模块，由第三逆阻型绝缘栅双极晶体 管TR3和与之反并联的第四逆阻型绝缘栅双极晶体管TR4组成。 [0043]四个电容中，第一个电容C1的正极与第一开关模块T1的正极相连;第一个电容C1的 负极与第二个电容C2的正极相连;第二个电容C2的负极与第二开关模块的负极相连;第三个 电容C3的正极与第三开关模块的正极相连;第三个电容C3的负极与第四个电容C4的正极相 连;第四个电容C4的负极与第四开关模块的负极相连;第一个续流二极管正极D3与第一个电 容C1的负极相连;第一个续流二极管D3的负极与第四开关模块正极相连;第二个续流二极管 D4的正极与第二开关模块正极相连;第二个续流二极管D4负极与第三个电容C3的负极相连。 [0044]上述实施例的多电平换流器子模块，第一开关模块的负极和第二开关模块正极之 间的节点为第一个输出端子1；第三开关模块负极和第四开关模块正极之间的节点作为第 二个输出端子2。其中第一个输出端子1连接一个半桥结构的输出口和第二续流二极管D4的 阴极，第二个输出端子2连接另一个半桥结构的输出口和第一续流二极管D3的阳极。 [0045]上述子模块在直流侧正常工况下，第二开关模块、第三开关模块中TR2和TR4管处于 常通状态，等效于TR1和TR3的反并联二极管，整个模块等效于两个半桥模块串联，因此可输 出0,Vc,2Vc三种电平。正常工况下，续流二极管D3和D4由于至少承受幅值为0.5VC的反向电 压，处于关断状态，因此不会产生损耗。 [0046] 在正常工况下，该子模块产生3种电平时电流均只通过2个开关器件，与两个串联 的半桥模块的在正常工作时，电流流过的开关器件数目相同。由已有器件的数据手册分析 可以得出，该新提出的子模块具备低于所有现有具备故障阻断能力的子模块的导通损耗。 [0047]图3为本发明一实施例方法中低损耗模块化多电平换流器的子模块在直流故障下 经开关管控制后的等效电路图。图3是当直流侧发生故障后，封锁所有可控开关之后，系统 的等效电路。当电流从第一个输出端子1流入时，该子模块等效于两个二极管和四个电容串 联;当电流从第二个输出端子2流入时，该子模块相当于两个二极管和两个电容串联。 [0048]当检测到直流侧发生双极短路故障，立即关断子模块中的所有全控开关(全控开 关包括绝缘栅双极晶体管T1和T2,逆阻型绝缘栅双极晶体管Tri〜TR4),从而利用系统内子模 块电容电压使续流二极管承受反压，从而关断。具体的，当发生直流双极短路故障后，由于 直流侧电压低于每个相单元中所有子模块电容电压的串联，故电流方向应为从2端流入。图 3中标注出了该模块化多电平换流器系统的一条电流通路。故障电流的路径为D3-〉C「〉C2-〉 设直流侧电压额定值为Vd0,系统调制比为m,二极管D3两端的电压为Vd3,二极管D4两端的 电压为Vd4,各桥臂均有N个子模块，每个独立电容的电压为0.5Vc,电网每相电压的峰值为 Vgm。可以由模块化多电平换流器运行特点得出： [0049] Vdc = N · 4 · 0.5Vc = 2NVc [0050] 曝=；朗曝 [0051] 故障态时，取图3所示的电流路径,可得： [0052] 曝 [0053] Vab=2N · 2 · 0.5Vc+2N · (Vd3+VD4) [0054] 由此可得： Γ Ί w “ 2NVc-43-m-2NVc 耳 [0055] y +(/ =2N%-%=_____2____i =(i_也mjz 03 ΰ4 2N 2N ( 2)c [0056] 而通常情况下有调制比m不大于1,故： [0057] Vd3+Vd4&lt;0 [0058]即两个续流二极管处于反向偏置状态，电流会被阻断。 [0059] 之后，根据故障情况确定是否需要断开交流断路器和直流侧开关。若需要进行直 流侧电路检修，则需要在检修前断开直流侧开关和交流侧断路器，检修完成后闭合直流侧 开关，使系统于零有功指令下开始工作，若不出现过流,则可进行交流侧重合闸操作，从而 实现故障穿越。 [0060]当发生的故障为直流侧暂时性故障时，不需要断开直流侧和交流侧开关，利用续 流二极管反压关断特性阻断故障电流之后，等待一个设定重启动时间。达到设定时间后，对 逆阻型绝缘栅双极晶体管施加触发脉冲,之后换流器系统进入有功给定为零的运行状态, 若未出现直流侧短路情况，则证明暂时性故障已清除，可将换流器有功给定软起动;若仍出 现短路情况，说明直流侧暂时性故障还未清除，重新闭锁Tri、Tr2、Tr3、Tr4脉冲，并定时重启 动，直到重启动成功为止。若重启动次数超过三次，也可认为是发生了永久性故障，可以断 开开关进行检修。 [0061]当发生的故障为直流侧永久性故障时，利用续流二极管反压关断特性阻断故障电 流之后，断开交流侧断路器，再断开直流侧开关。进行检修，故障修复后，闭合直流侧开关， 若未过流则可对逆阻型绝缘栅双极晶体管施加触发脉冲，之后系统进入有功给定为零的状 态，若不出现直流侧过流，则可进行交流侧重合闸，之后恢复正常运行状态；若出现直流侧 过流，则再次封锁所有全控开关脉冲。 [0062]本发明上述实施例提出一种新型的低导通损耗的换流器故障穿越方法，无需依靠 外部开关器件，控制换流器的逆阻型绝缘栅双极晶体管，即可实现直流侧短路的故障阻断， 同时，可以实现相对传统双向开关更低的导通损耗。 [0063]以上对本发明的具体实施例进行了描述。需要理解的是，本发明并不局限于上述 特定实施方式，本领域技术人员可以在权利要求的范围内做出各种变形或修改，这并不影 响本发明的实质内容。 [EN CN110994560B]: Technical field of a low-loss modular multilevel converter fault ride-through method [0001] The present invention relates to the technical field of power system transmission and distribution, and in particular, to a fault ride-through method for a low-loss modular multilevel converter with fault blocking capability. Background technique [0002] With the increase in power generation from renewable energy sources, grid connection of renewable energy sources has become a very important research direction. [0003] The flexible direct current transmission technology provides a solution for the grid connection of renewable energy and has strong technical advantages. Among them, the flexible DC transmission technology using modular multi-level converters has better maintainability and expandability than traditional two-level and three-level converters, and there is no series-connected voltage equalization and parallel connection of switching tubes. Current sharing problem. The structure of each sub-module of the modular multilevel converter is relatively simple and easy to control, and due to the easy expansion of modularization, it is particularly suitable for the field of HVDC transmission. The number of levels output by the modular multilevel converter can be adjusted by adjusting the number of sub-modules in the bridge arm. The voltage on the DC side can also be controlled by adjusting the number of sub-modules per phase. Both the voltage level and the output harmonic content of the system constituted by the converter can be effectively controlled. [0004] The traditional modular multilevel converter adopts a sub-module topology of a half-bridge structure, while the half-bridge sub-module topology is not controlled by the control pulse due to the anti-parallel diode of the down tube, which will form when a short circuit fault occurs on the DC side. The freewheeling circuit from the AC side to the DC fault point transmits the short-circuit fault to the AC side and affects the stability of the power grid. Therefore, the fault current needs to be blocked by DC, AC circuit breakers or other methods. However, there is currently no mature technology for DC circuit breakers, and the cost is too expensive; AC circuit breakers require a long response time, and the converter valve device needs to bear a large current stress before the AC circuit breaker is disconnected, which is very easy to cause the device Damage. Therefore, a sub-module topology is needed, and the DC side fault can be blocked by controlling this sub-module. [0005] The existing sub-module topology with fault blocking capability generally has a problem, that is, in the normal working state of the converter, there will be an additional switching device in each sub-module located on the normal current path, and the device is normally open. status. When a fault occurs, the switching device is turned off, so that the current flows through another path to achieve the effect of blocking or limiting the fault current. This additional switching device will increase the conduction loss of the system, thereby causing a loss of resources. The existing fault ride-through methods are almost entirely based on the control of this additional switching device, so that the conduction loss of the system cannot be reduced. Summary of the invention [0006] In view of the shortcomings of the prior art, the purpose of the present invention is to provide a low-loss modular multilevel converter fault ride-through method based on fault blocking capability, which can realize short-circuit on the DC side without additional switching devices. The fault is blocked to realize fault ride-through. [0007] According to the first aspect of the present invention, there is provided a low-loss modular multilevel converter fault ride-through method, the converter includes three phase units, each unit is divided into upper and lower bridge arms, each bridge The arm includes several sub-modules connected in series, and the sub-modules are composed of two half-bridge structures, four capacitors and two freewheeling diodes, among which: [0008] The first half-bridge includes a first switch module and a second switch module, and the second half-bridge includes a third switch module and a fourth switch module; the negative electrode of the first switch module and the second switch module The positive pole of the second switch The negative pole of the module is connected to the positive pole of the third switch module, and the negative pole of the third switch module is connected to the positive pole of the fourth switch module; the second switch module is composed of a first reverse resistance insulated gate bipolar transistor And a second reverse resistance type insulated gate bipolar transistor in anti-parallel connection; the third switch module is composed of a third reverse resistance type insulated gate bipolar transistor and a fourth reverse resistance type insulated gate bipolar transistor in anti-parallel connection Transistor composition; [0009] The positive pole of the first capacitor is connected to the positive pole of the first switch module; the negative pole of the first capacitor is connected to the positive pole of the second capacitor; the negative pole of the second capacitor is connected to the second capacitor. The negative pole of the switch module is connected; the positive pole of the third capacitor is connected to the positive pole of the third switch module; the negative pole of the third capacitor is connected to the positive pole of the fourth capacitor, and the negative pole of the fourth capacitor is connected to the The negative pole of the fourth switch module is connected; [0010] The anode of the first freewheeling diode is connected to the cathode of the first capacitor, the cathode of the first freewheeling diode is connected to the anode of the fourth switch module, and the second freewheeling diode The anode of the diode is connected to the anode of the second switch module, and the cathode of the second freewheeling diode is connected to the cathode of the third capacitor; [0011] The node between the negative pole of the first switch module and the positive pole of the second switch module serves as the first output terminal of the entire submodule; the negative pole of the third switch module and the fourth switch module The node between the positive poles of is used as the second output terminal of the entire sub-module; [0012] The fault ride-through method includes: [0013] Utilizing the nature of the reverse resistance insulated gate bipolar transistor, in the event of a short-circuit fault between the DC side electrodes, the bidirectional switch composed of the reverse resistance insulated gate bipolar transistor is turned off to block the fault circuit, so that The fault current passes through the capacitor, and then the capacitor voltage and the reverse blocking property of the diode in the sub-module are used to block the fault current. The diode here refers to the devices included in the freewheeling path of the corresponding sub-module. These devices carry out the freewheeling of the inductance current of the bridge arm when the DC side fault occurs. After the inductance current crosses zero, the capacitor voltage of each sub-module After being connected in series, it is greater than the AC side line voltage and is subjected to back pressure to complete the shutdown. [0014] Optionally, when a bipolar short-circuit fault is detected on the DC side: [0015] Turn off all the full control switches in the first switch module ~ fourth switch module in the sub-module, thereby using the capacitor voltage of the sub-module to make the freewheeling diode bear the back pressure, thereby turning off; The control switch includes insulated gate bipolar transistors in the first switch module and the fourth switch module, and reverse resistance insulated gate bipolar transistors in the second switch module and the third switch module. [0016] Optionally, when the fault that occurs is a permanent fault on the DC side: [0017] After using the freewheeling diode back-voltage shutdown characteristic to block the fault current, open the AC side circuit breaker, and then open the DC side switch; [0018] After the fault is repaired, close the DC side switch, if there is no overcurrent, apply a trigger pulse to the reverse resistance insulated gate bipolar transistor, and then the system enters a state where the active power is set to zero, if there is no overcurrent on the DC side , The AC side recloser can be performed, and then the normal operation state will be restored; [0019] If there is an overcurrent on the DC side, all full control switching pulses in the first switch module ~ the fourth switch module are blocked again. [0020] Optionally, when the occurring fault is a temporary fault on the DC side: [0021] After using the freewheeling diode back-voltage turn-off characteristic to block the fault current, after a set time is reached, a trigger pulse is applied to the reverse resistance insulated gate bipolar transistor, and then the inverter enters the active power set as Zero operating status; [0022] If there is no short-circuit on the DC side, it proves that the temporary fault has been cleared, and the inverter is soft-started with a given active power; if there is still a short-circuit, it means that the temporary fault on the DC side has not been cleared, and the pulse is blocked again, and Restart regularly until Until the restart is successful; [0023] If the restart is more than three times, it is considered that a permanent fault has occurred. [0024] Optionally, in the converter, the number of sub-modules connected in series with the upper and lower bridge arms of each phase is the same. [0025] Optionally, in the converter, the upper and lower bridge arms are respectively connected in series with current-limiting reactors, and each phase from top to bottom is: all sub-modules of the upper bridge arm, the upper bridge arm reactor, and the lower bridge arm Reactor and all sub-modules of the lower bridge arm; and each phase is connected with three-phase AC voltage at the upper and lower bridge arms. The first output terminal of the uppermost sub-module topology of the upper bridge arm is connected to the positive pole of the DC bus, and the bottom terminal module of the lower bridge arm The second output terminal is connected to the negative pole of the DC bus. [0026] Optionally, the first output terminal is connected to the output port of the first half-bridge structure and the cathode of the second freewheeling diode, and the second output terminal is connected to the output port of the second half-bridge structure And the anode of the first freewheeling diode. [0027] Optionally, the first switch module and the fourth switch module are both composed of an insulated gate bipolar transistor and a diode in anti-parallel connection. [0028] Optionally, under normal working conditions, the negative pole of the second switch module is connected to the second reverse resistance insulated gate bipolar transistor of the first output terminal and the positive pole of the third switch module is connected to the second output terminal The fourth reverse-resistance insulated gate bipolar transistor keeps the conduction state; the two freewheeling diodes remain in the off state due to the back pressure, so they are not added to the circuit, so no conduction loss occurs. [0029] Compared with the prior art, the present invention has the following beneficial effects: [0030] The above-mentioned low-loss modular multilevel converter fault ride-through method of the present invention does not require additional switching devices, and can realize the fault blocking of the DC side short circuit by controlling the opening and closing of the reverse resistance type insulated gate bipolar transistor , And then realize fault ride-through. [0031] The above-mentioned low-loss modular multi-level converter fault ride-through method of the present invention can realize fault isolation under DC fault conditions by controlling the state of the switch module and the freewheeling diode, and the isolation speed is fast. [0032] The above-mentioned low-loss modular multi-level converter fault ride-through method of the present invention can maintain the capacitor voltage of the sub-module in the event of a fault, and the power supply recovery speed is fast. Description of the drawings [0033] By reading the detailed description of the non-limiting embodiments with reference to the following drawings, other features, objectives and advantages of the present invention will become more apparent: [0034] FIG. 1 is a schematic diagram of a low-loss modular multilevel converter in a method according to an embodiment of the present invention; [0035] FIG. 2 is a sub-module topology of a low-loss modular multilevel converter in a method according to an embodiment of the present invention; [0036] FIG. 3 is an equivalent circuit diagram of a sub-module of a low-loss modular multi-level converter in a method of an embodiment of the present invention after being controlled by a switch tube under a DC fault. Detailed ways [0037] The present invention will be described in detail below in conjunction with specific embodiments. The following examples will help those skilled in the art to further understand the present invention, but do not limit the present invention in any form. It should be pointed out that for those of ordinary skill in the art, without departing from the concept of the present invention, several modifications and improvements can be made, which all fall within the protection scope of the present invention. [0038] With reference to FIGS. 1-3, an embodiment of the present invention provides a low-loss modular multilevel converter fault ride-through method, which utilizes the properties of reverse resistance insulated gate bipolar transistors, In case of short circuit fault between poles, turn off the reverse resistance The two-way switch composed of insulated gate bipolar transistor blocks the fault circuit, so that the fault current passes through the capacitor, and then uses the capacitor voltage and the reverse blocking property of the diode in the module to block the fault current. Since the turn-on voltage drop of the reverse resistance insulated gate bipolar transistor is smaller than the total turn-on voltage drop of the insulated gate bipolar transistors and diodes of the same voltage level connected in series, compared with traditional hybrid bridge circuits, the overall system can be turned on The pressure drop is smaller, in a multi-module system. The system loss mainly depends on the conduction loss, so the system has higher efficiency. [0039] Specifically, the low-loss modular multi-level converter applicable to the above-mentioned low-loss modular multi-level converter fault ride-through method is shown in Figure 1-2. Figure 1 is a three-phase modular multilevel converter structure, in which each sub-module of each bridge arm is composed of the sub-modules shown in Figure 2. The converter does not need to rely on additional switching devices, and has the characteristics of low loss while having the fault blocking capability, and can realize the fault blocking of the DC side short circuit. [0040] Referring to Figure 1, the low-loss modular multilevel converter includes three phase units, each unit is divided into upper and lower bridge arms, each bridge arm includes a number of serial sub-modules, each phase upper and lower The number of sub-modules connected in series in the bridge arms is the same; the upper and lower bridge arms are respectively connected in series with current-limiting reactors, from top to bottom for each phase: all sub-modules in the upper bridge arm, upper bridge arm reactor, lower bridge arm reactor, and lower bridge All sub-modules of the arm; and the connection of the upper and lower arms of each phase is connected with a three-phase AC voltage, the first output terminal of the uppermost sub-module topology of the upper arm is connected to the positive pole of the DC bus, and the second output terminal of the lowermost terminal module of the lower arm Connect with the negative pole of the DC bus. [0041] Referring to FIG. 2, the sub-module of each bridge arm in the multi-level DC-DC converter is composed of two half-bridge structures, four capacitors C1 to C4, and two freewheeling diodes D3 to D4. [0042] In the two half bridge structures, the first half bridge includes a first switch module and a second switch module; the negative pole of the first switch module T1 is connected to the positive pole of the second switch module. The second half-bridge includes a third switch module and a fourth switch module; the negative pole of the third switch module is connected with the positive pole of the fourth switch module; the positive pole of the third switch module is connected with the negative pole of the second switch module. Specifically, referring to Figure 2, the first switch module is composed of an insulated gate bipolar transistor T1 and a diode D1 in anti-parallel connection; the fourth switch module is composed of an insulated gate bipolar transistor T2 and a diode D2 in anti-parallel connection; The second switch module is a reverse resistance type switch module, which is composed of a first reverse resistance type insulated gate bipolar transistor TR1 and a second reverse resistance type insulated gate bipolar transistor TR2 anti-parallel to it. The third switch module is also a reverse resistance type. The switch module is composed of a third reverse resistance insulated gate bipolar transistor TR3 and a fourth reverse resistance insulated gate bipolar transistor TR4 connected in anti-parallel. [0043] Among the four capacitors, the positive electrode of the first capacitor C1 is connected to the positive electrode of the first switch module T1; the negative electrode of the first capacitor C1 is connected to the positive electrode of the second capacitor C2; the negative electrode of the second capacitor C2 is connected to The negative electrode of the second switch module is connected; the positive electrode of the third capacitor C3 is connected to the positive electrode of the third switch module; the negative electrode of the third capacitor C3 is connected to the positive electrode of the fourth capacitor C4; the negative electrode of the fourth capacitor C4 is connected to the positive electrode of the fourth capacitor C4. The cathode of the four switch module is connected; the anode D3 of the first freewheeling diode is connected to the cathode of the first capacitor C1; the cathode of the first freewheeling diode D3 is connected to the anode of the fourth switch module; the anode of the second freewheeling diode D4 is connected The anode is connected with the anode of the second switch module; the cathode of the second freewheeling diode D4 is connected with the cathode of the third capacitor C3. [0044] In the multi-level converter sub-module of the above embodiment, the node between the negative pole of the first switch module and the positive pole of the second switch module is the first output terminal 1; the negative pole of the third switch module and the fourth switch module The node between the positive poles serves as the second output terminal 2. The first output terminal 1 is connected to the output port of a half-bridge structure and the cathode of the second freewheeling diode D4, and the second output terminal 2 is connected to the output port of the other half-bridge structure and the anode of the first freewheeling diode D3. [0045] In the above-mentioned sub-module under normal operating conditions on the DC side, the TR2 and TR4 tubes in the second switch module and the third switch module are in a normally-on state, which is equivalent to the anti-parallel diodes of TR1 and TR3, and the entire module is equivalent to two Two half-bridge modules are connected in series, so they can output three levels of 0, Vc, and 2Vc. Under normal operating conditions, the freewheeling diodes D3 and D4 are in the off state because they withstand at least a reverse voltage of 0.5VC, so no loss occurs. [0046] Under normal operating conditions, when the sub-module generates three levels, the current only passes through two switching devices, which is the same as the number of switching devices through which the current flows during normal operation of the two series-connected half-bridge modules. It can be concluded from the data manual analysis of existing devices that the newly proposed sub-module has a conduction loss lower than that of all existing sub-modules with fault blocking capability. [0047] FIG. 3 is an equivalent circuit diagram of the sub-modules of the low-loss modular multilevel converter in the method of an embodiment of the present invention after being controlled by a switch tube under a DC fault. Figure 3 is the equivalent circuit of the system after all controllable switches are blocked after a failure occurs on the DC side. When the current flows in from the first output terminal 1, the sub-module is equivalent to two diodes and four capacitors in series; when the current flows in from the second output terminal 2, the sub-module is equivalent to two diodes and two The capacitors are connected in series. [0048] When a bipolar short-circuit fault on the DC side is detected, all the fully-controlled switches in the sub-module are immediately turned off (the fully-controlled switches include insulated gate bipolar transistors T1 and T2, and reverse resistance insulated gate bipolar transistors Tri~TR4 ), so as to use the sub-module capacitor voltage in the system to make the freewheeling diode bear the back pressure, thereby turning off. Specifically, when a DC bipolar short-circuit fault occurs, since the DC side voltage is lower than the series connection of the capacitor voltages of all sub-modules in each phase unit, the current direction should flow in from end 2. Figure 3 shows a current path of the modular multilevel converter system. The path of the fault current is D3-&gt;C"&gt;C2-&gt; Set the DC side voltage rating to Vd0, the system modulation ratio to m, the voltage across diode D3 to Vd3, the voltage across diode D4 to Vd4, each bridge arm has N sub-modules, the voltage of each independent capacitor is 0.5Vc, and the peak value of each phase voltage of the power grid is Vgm. It can be derived from the operating characteristics of the modular multilevel converter: [0049] Vdc = N · 4 · 0.5Vc = 2NVc [0050] Exposure =; Loud exposure [0051] In the fault state, take the current path shown in FIG. 3 to obtain: [0052] Exposure [0053] Vab=2N·2·0.5Vc+2N·(Vd3+VD4) [0054] It can be obtained from this: Γ Ί w "2NVc-43-m-2NVc ear [0055] y +(/ =2N%-%=_____2____i = (i_also mjz 03 ΰ4 2N 2N (2)c [0056] Generally, the modulation ratio m is not greater than 1, so: [0057] Vd3+Vd4&lt;0 [0058] That is, the two freewheeling diodes are in a reverse bias state, and the current will be blocked. [0059] After that, it is determined whether the AC circuit breaker and the DC side switch need to be opened according to the fault condition. If the DC side circuit needs to be overhauled, it is necessary to disconnect the DC side switch and AC side circuit breaker before the overhaul, and close the DC side switch after the overhaul is completed to make the system start working under the zero active power command. If no overcurrent occurs, then Perform AC-side re-closing operation to achieve fault ride-through. [0060] When the occurrence of the fault is a temporary fault on the DC side, there is no need to disconnect the DC side and AC side switches. After blocking the fault current using the freewheeling diode back-voltage shutdown feature, wait for a set restart time. After the set time is reached, a trigger pulse is applied to the reverse resistance insulated gate bipolar transistor, and then the converter system enters the operating state where the active power is set to zero. If there is no short circuit on the DC side, it proves that the temporary fault has been cleared. The inverter can be soft-started with a given active power; if there is still a short circuit, it means that the temporary fault on the DC side has not been cleared. Re-lock Tri, Tr2, Tr3, Tr4 pulse, and restart regularly until the restart is successful. If the number of restarts exceeds three times, it can be considered that a permanent fault has occurred, and the switch can be opened for maintenance. [0061] When the fault that occurs is a permanent fault on the DC side, after the fault current is blocked by the back-voltage shutdown characteristic of the freewheeling diode, the AC side circuit breaker is turned off, and then the DC side switch is turned off. After the fault is repaired, close the DC side switch. If there is no overcurrent, a trigger pulse can be applied to the reverse resistance insulated gate bipolar transistor. Then the system enters a state where the active power is set to zero. If there is no overcurrent on the DC side, Then the AC side recloser can be performed
[DE CH713723B1]: Modularer Multilevel-Stromrichter. [EN CH713723B1]: Modular multilevel power converter. | [DE CH713723B1]: Die Erfindung betrifft einen modularen Multilevel-Stromrichter, der mehrere Phasen mit Phasenzweigen (11) aufweist, jeweils mit einem oberen Arm (111) und einem unteren Arm (112), wobei jeder der Arme (111, 112) eine serielle Verbindung einer Mehrzahl von MMC-Modulen und einer Arminduktivität (3) aufweist und die MMC-Module steuerbare Spannungsquellen sind. Es liegt dabei pro Phase ein aktives Filtermodul (4) vor, welches einen ersten Anschluss aufweist, der mit dem oberen Mittenanschluss der Phase verbunden ist, einen zweiten Anschluss, der mit dem unteren Mittenanschluss der Phase verbunden ist, und einen dritten Anschluss, der mit dem Phasenanschluss der Phase verbunden ist. Das aktive Filtermodul (4) weist eine Zwischenkreisspannung zwischen einem oberen Anschlusspunkt (P) und einem unteren Anschlusspunkt (N) auf, und für jeden der drei Anschlüsse des Filtermoduls (4) liegt jeweils ein Brückenzweig vor, mit welchem wahlweise der obere oder der unteren Anschlusspunkt mit dem jeweiligen Anschluss verbindbar ist. [EN CH713723B1]: The invention relates to a modular multilevel power converter which has several phases with phase branches (11), each with an upper arm (111) and a lower arm (112), each of the arms (111, 112) being a serial connection of a plurality of MMC modules and an arm inductance (3) and the MMC modules are controllable voltage sources. There is an active filter module (4) per phase, which has a first connection that is connected to the upper center connection of the phase, a second connection that is connected to the lower center connection of the phase, and a third connection that is connected to is connected to the phase connection of the phase. The active filter module (4) has an intermediate circuit voltage between an upper connection point (P) and a lower connection point (N), and for each of the three connections of the filter module (4) there is a bridge branch with which either the upper or the lower Connection point can be connected to the respective connection. | CH713723B1 | 2018-10-31 2021-07-30 | CH5572017A | 2017-04-26 2017-04-26 | CH5572017A, 2017-04-26 CH5572017A, 2017-04-26 | CH713723B1: 2021-07-30 | ETH ZUERICH | JOHANN WALTER KOLAR JONAS EMANUEL HUBER | H02M7/483: I | H02M7/483: I H02M1/12: I H02M7/4835: I |  |  | [DE CH713723B1]: Patentansprüche 1. Modularer Multilevel-Stromrichter, aufweisend einen positiven Anschluss und einen negativen Anschluss und eine Mehrzahl von Phasen mit je einem Phasenanschluss pro Phase; einen Phasenzweig (11) pro Phase, aufweisend einen oberen Arm (111), welcher zwischen den positiven Anschluss und einen oberen Mittenanschluss der Phase geschaltet ist, und einen unteren Arm (112), welcher zwischen den negativen Anschluss und einen unteren Mittenanschluss der Phase geschaltet ist, wobei jeder der Arme (111,112) eine serielle Verbindung einer Mehrzahl von Modulen, im Folgenden als MMC-Module (2) bezeichnet, und einer Arminduktivität (3) aufweist, und die MMC-Module (2) steuerbare Spannungsquellen sind, dadurch gekennzeichnet, dass pro Phase ein aktives Filtermodul (4) vorliegt, welches einen ersten Anschluss aufweist, der mit dem oberen Mittenanschluss der Phase verbunden ist, einen zweiten Anschluss, der mit dem unteren Mittenanschluss der Phase verbunden ist, und einen dritten Anschluss, der mit dem Phasenanschluss der Phase verbunden ist, wobei das aktive Filtermodul (4) einen Zwischenkreiskondensator zwischen einem oberen Anschlusspunkt (P) und einem unteren Anschlusspunkt (N) aufweist, und fürjeden der drei Anschlüsse des Filtermoduls (4) jeweils ein Brückenzweig vorliegt, und für jeden der drei Anschlüsse gilt, dass er einen Mittelpunkt aufweist, der an diesen Anschluss der drei Anschlüsse geschaltet ist, und mit dem Brückenzweig wahlweise der obere oder der untere Anschlusspunkt mit diesem Anschluss der drei Anschlüsse verbindbar ist. 2. Modularer Multilevel-Stromrichter gemäss Anspruch 1, wobei die MMC-Module (2) jeweils eine Kapazität aufweisen, welche im Betrieb des modularen t Multilevel-Stromrichters eine Zwischenkreisgleichspannung (VDcm) aufweist, und wahlweise diese Zwischenkreisgleichspannung (VDcm) oder die Spannung Null an Anschlussklemmen des MMC-Modules (2) schaltbar ist. 3. Modularer Multilevel-Stromrichter gemäss Anspruch 1, wobei die MMC-Module (2) jeweils eine Kapazität aufweisen, welche im Betrieb des modularen Multilevel-Stromrichters eine Zwischenkreisgleichspannung (VDcm) aufweist, und wahlweise diese Zwischenkreisgleichspannung (VDcm) in positiver oder negativer Richtung oder die Spannung Null an Anschlussklemmen des MMC-Modules (2) schaltbar ist. [EN CH713723B1]: Claims 1. Modular multilevel power converter, having a positive connection and a negative connection and a plurality of phases, each with one phase connection per phase; a phase branch (11) per phase, having an upper arm (111) which is connected between the positive connection and an upper center connection of the phase, and a lower arm (112) which is connected between the negative connection and a lower center connection of the phase each of the arms (111, 112) having a serial connection of a plurality of modules, hereinafter referred to as MMC modules (2), and an arm inductance (3), and the MMC modules (2) are controllable voltage sources, characterized in that there is an active filter module (4) per phase, which has a first connection connected to the upper center connection of the phase and a second connection connected to the lower The center connection of the phase is connected, and a third connection that is connected to the phase connection of the phase, wherein the active filter module (4) has an intermediate circuit capacitor between an upper connection point (P) and a lower connection point (N), and for each of the three connections of the filter module (4) there is a bridge branch, and for each of the three connections it applies that it has a center point that is connected to this connection of the three connections, and with the bridge branch either the upper or the lower connection point can be connected to this connection of the three connections. 2. Modular multilevel converter according to claim 1, wherein the MMC modules (2) each have a capacitance which, when the modular multilevel converter is in operation, generates an intermediate circuit DC voltage (VD.cm), and optionally this DC link voltage (VD.cm) or zero voltage can be switched at the connection terminals of the MMC module (2). 3. Modular multilevel converter according to claim 1, wherein the MMC modules (2) each have a capacity which, when the modular multilevel converter is in operation, an intermediate circuit DC voltage (VD.cm), and optionally this DC link voltage (VD.cm) can be switched in the positive or negative direction or the voltage zero at the connection terminals of the MMC module (2). | [DE CH713723B1]: Beschreibung [0001] Die Erfindung bezieht sich auf das Gebiet der elektronischen Wandler Sie bezieht sich auf einen Modularen Multilevel-Stromrichter. Grundlegende Funktionsweise eines Modularen Multilevel-Stromrichters (MMC) [0002] Ein modularer Multilevel-Stromrichter (Modular Multilevel Converter, MMC oder M2LC) ist eine modulare und skalierbare Multilevel-Topologie [Marquardt2002], welche sich für vielfältige Anwendungen im Bereich hoher Spannungen und hoher Leistungen eignet, wie zum Beispiel für HGÜ oder Antriebssysteme mit grosser Leistung. Fig. 1a zeigt eine typische Konfiguration eines solchen MMC in einer dreiphasigen Ausführung 1 zur Übertragung von elektrischer Energie zwischen einem Gleichspannungssystem und einem, im beispielhaft betrachteten Fall dreiphasigen, Wechselspannungssystem. [0003] Jeder Phasenzweig - als Beispiel sei hier ein Phasenzweig 11 der Phase R betrachtet - besteht aus einem oberen Arm 111 und einem unteren Arm 112. Jeder dieser Arme besteht wiederum aus N seriell verbundenen MMC-Modulen 2 sowie einer Arminduktivität 3, wobei die Arminduktivitäten des oberen Arms 111 und des unteren Arms 112 eines Phasenzweigs auch in einer gekoppelten Spule realisiert werden können. Eine Zwischenkreisgleichspannung eines MMC-Moduls beträgt VDcm = VDc/N, d.h. nur einen Bruchteil der Spannung VDc des Gleichspannungssystems. [0004] Typischerweise sind die MMC-Module wie in Fig. 1 gezeigt als Halbbrückenmodule realisiert, welche zwei Schaltzustände aufweisen können: ein MMC-Modul ist entweder eingefügt (inserted), d.h. der Armstrom fliesst durch den Kondensator des MMC-Moduls und die Spannung dieses Kondensators tritt zwischen den Klemmen des MMC-Moduls auf; oder das MMC-Modul ist überbrückt (bypassed), d.h. der Armstrom fliesst durch den unteren Schalter und die Spannung zwischen den Klemmen des MMC-Moduls ist ideal gleich Null. Alternativ dazu ist auch eine Realisierung der MMC-Module als Vollbrückenschaltungen möglich, was es erlaubt, die lokale Zwischenkreisspannung in beiden Richtungen zwischen den Ausgangsklemmen anzulegen, nicht nur in einer wie bei der Halbbrückenschaltung. Die folgenden Diskussionen beziehen sich aufgrund deren deutlich grösseren Verbreitung auf die Variante mit den Halbbrückenmodulen. Indem eine bestimmte Anzahl von MMC-Modulen eines Arms eingefügt oder überbrückt werden, wobei die jeweils benötigte Anzahl beispielsweise mittels phasenversetzter Pulsbreitenmodulation oder anderen bekannten Modulationsverfahren bestimmt werden kann, verhält sich jeder Arm wie eine gesteuerte Spannungsquelle. Dies ist auch im Ersatzschaltbild von Fig. 1b dargestellt. Dementsprechend ist es offensichtlich, dass das Potential der Phasenausgangsklemme (Mittelpunkt des Phasenzweiges, in der Regel an einen Phasenabgang oder Phasenanschluss zu einer Phase des Wechselspannungssystems geschaltet) bezüglich eines gedachten Mittelpunktes, Μ, des Gleichspannungssystems zwischen +VDc/2 und -VDc/2 variiert werden kann, indem jeweils eine entsprechende Anzahl von Modulen im oberen und im unteren Arm eingefügt oder überbrückt wird. Die Kondensatorspannungen der MMC-Module müssen aktiv balanciert werden: typischerweise wird ein Sortieralgorithmus verwendet, um zu entscheiden, welches MMC-Modul eines Armes hinzugefügt oder überbrückt werden soll, wobei sowohl das Vorzeichen des Armstromes als auch die individuellen Kondensatorspannungen der MMC-Module bekannt sein müssen. [0005] Wiederum am Beispiel der Phase R betrachtet, sind die Armströme gegeben als _____ - i J-rt J-zirk 'TJ” unc( lrb ^-zirk ^7 d.h. die Armströme enthalten jeweils einen Anteil des Phasenstroms ir sowie zusätzlich einen zirkulierenden Strom izirk, der in einer durch das Gleichspannungssystem sowie den beiden Armen des Phasenzweiges aufgespannten Schleife fliesst. Im Mittel müssen also immer N MMC-Module pro Phasenzweig, d.h. im oberen und unteren Arm zusammen, eingefügt sein, um einen exzessiven Anstieg des zirkulierenden Stromes zufolge der andernfalls an der Serieschaltung der beiden Arminduktivitäten anliegenden Spannung zu vermeiden. [0006] Vorteilhaft besteht der zirkulierende Strom ausschliesslich aus einem Gleichanteil (und einem überlagerten schaltfrequenten Rippel) derart, dass der Energieaustausch mit dem Gleichspannungssystem jenem mit dem Wechselspannungssystem entspricht, d.h. idealerweise gilt also . __ . __ if __ Mc lrtrac — “ lrb,ac — V und lzirk — ·— r Li [0007] Werden jedoch keine speziellen Vorkehrungen getroffen, d.h. wenn also wie oben beschrieben der obere und der untere Arm jeweils direkt mit einer sinusförmigen Referenz moduliert werden um eine sinusförmige Phasenspannung zu erzeugen, enthält der zirkulierende Strom nicht nur die für die Funktionsweise des Konverters notwendigen und oben beschriebenen Anteile, sondern zusätzlich signifikante unerwünschte harmonische Komponenten. Insbesondere weist erei CH 713 723 B1 ne grosse Komponente bei der zweiten Harmonischen der Ausgangsfrequenz (d.h. der Frequenz des Wechselspannungssystems) auf, wie dies in Fig. 4e während der ersten 100ms zu sehen ist. Dementsprechend weisen auch die Armströme harmonische Verzerrungen auf, wodurch ihre RMS-Werte gegenüber dem oben beschriebenen idealen Fall ansteigen und höhere Leitverluste verursachen. Stand der Technik für die Regelung des zirkulierenden Stromes [0008] In der Literatur werden deshalb verschiedene Verfahren zur Unterdrückung dieser unerwünschten Harmonischen im zirkulierenden Strom bzw. in den Armströmen beschrieben. Die direkteste Variante besteht darin, zu den Armspannungen durch eine entsprechende Anpassung der Modulationsreferenz eine Gleichtaktspannung hinzuzufügen, welche dann an der Serienschaltung der beiden Arminduktivitäten anliegt und dementsprechend zur Regelung des zirkulierenden Stromes verwendet werden kann. Dieses Verfahren wird in [Antonopooulos2009] beschrieben. Potentiell nachteilig ist dabei, dass eine entsprechende Spannungsreserve benötigt wird, die das Erzeugen der Gleichtaktanteile der Armspannungen erlaubt. Anders gesagt bedeutet dies, dass für eine gegebene Spannung des Gleichspannungssystems die maximale wechselspannungsseitige Ausgangsspannung verkleinert wird. In MMC-Systemen mit vielen MMC-Modulen ist dies typischerweise von untergeordneter Bedeutung, da dort oftmals ohnehin mehr MMC-Module pro Arm als unbedingt notwendig eingesetzt werden, um die Zuverlässigkeit mittels Redundanz zu erhöhen. Umgekehrt kann die Anwendung dieses Verfahren bei MMC-Systemen mit nur wenigen MMC-Modulen unvorteilhaft sein. [0009] Deshalb wurde in [Madawala2015] eine andere Variante beschrieben, den zirkulierenden Strom zu regeln. Wie in Fig. 2 gezeigt, wird dabei jeder Arm um ein dediziertes Spannungskorrekturmodul 3 ergänzt. Diese Spannungskorrekturmodule arbeiten als aktive Filter, indem sie Spannungskomponenten zu den Armspannungen hinzufügen, die zu einer Unterdrückung der harmonischen Komponenten des zirkulierenden Stromes führen. D.h. die Gleichtaktspannung wird hier nicht mehr durch die Modulation der Armspannungen erzeugt, sondern durch die dedizierten Spannungskorrekturmodule. In beiden Fällen wird die Ausgangsspannung eines Phasenzweiges dadurch nicht beeinflusst. Vorteilhaft dabei ist, dass die Spannungskorrekturmodule mit einer verhältnismässig tiefen lokalen Zwischenkreisspannung VDck arbeiten können, welche insbesondere deutlich kleiner als die Zwischenkreisspannung eines MMC-Moduls ist. Dadurch ist der Aufwand zur Realisierung der Spannungskorrekturmodule deutlich kleiner als jener für das Hinzufügen weiterer MMC-Module, wie sie bei der oben beschriebenen Variante zur Regelung des zirkulierenden Stromes für die Erhöhung der Spannungsreserve ggf. benötigt würden. Des Weiteren erlauben die dedizierten Spannungskorrekturmodule vorteilhaft eine Trennung der Regelung der Ausgangsgrössen und des zirkulierenden Stromes: die MMC-Module werden zur Erzeugung der gewünschten Ausgangsspannung des Phasenzweigs verwendet, während die Spannungskorrekturmodule zur Regelung des zirkulierenden Stromes auf seinen idealen Wert dienen. Die lokale Zwischenkreisspannung der Spannungskorrekturmodule kann mittels eines geeigneten Regelkreises stabilisiert werden, d.h. es wird keine externe Versorgungsschaltung benötigt. [0010] Nachteilig bei dieser zweiten Variante istdie Verwendung von je einem Spannungskorrekturmodul pro Arm, d.h. von zwei Spannungskorrekturmodulen pro Phasenzweig, was einen entsprechenden Aufwand für die Realisierung bedingt. Zusätzlich unterliegt die Ansteuerung dieser Vielzahl von Spannungskorrekturmodulen einer gewissen Komplexität und bedingt ebenfalls einen verhältnismässig hohen Aufwand für die notwendige Kommunikationselektronik. Literatur zum Stand der Technik [0011] [Marquardt2002] [Antonopoulos2009] [Madawala2015] R. Marquardt, A. Lesnicar, and J. Hildinger, „Modulares Stromrichterkonzept für Netzkupplungsanwendungen bei hohen Spannungen,“ in ETG-Fachtagung, 2002. A. Antonopoulos, L. Ängquist, and H.-P. Nee, „On dynamics and voltage control of the modular multilevel converter,“ in Proc. 13th Europ. Power Electron, and Appi. Conf. (EPE), Barcelona, Spanien, 2009. U. K. Madawala and B. S. Riar, „Modular multi-level converters,“ U.S. Patent Appi. US 2015/ 0288287 A1,2015. [0012] Aufgabe der vorliegenden Erfindung ist es, einen modularen Multilevel-Stromrichter zu schaffen, welcher eine Regelung des zirkulierenden Stromes mittels eines dedizierten aktiven Filtermoduls ermöglicht, dabei aber einfacher zu realisieren ist. [0013] Die Aufgabe wird gelöst durch einen Modularen Multilevel-Stromrichter gemäss den Patentansprüchen. [0014] Gegenüber dem Stand der Technik stellt dies eine konzeptionelle Vereinfachung dar: zur Erzielung der dem Stand der Technik entsprechenden Funktionalität wird nur noch ein einzelnes aktives Filtermodul pro Phase anstelle von deren zwei verwendet. Dadurch wird der Aufwand zur Realisierung deutlich verringert, und gleichzeitig die Komplexität der notwendigen Kommunikations- und Regelungssysteme reduziert. [0015] Weitere bevorzugte Ausführungsformen gehen aus den abhängigen Patentansprüchen hervor. [0016] Im Folgenden wird der Erfindungsgegenstand anhand von bevorzugten Ausführungsbeispielen, welche in den beiliegenden Abbildungen dargestellt sind, näher erläutert. Diese zeigen: CH 713 723 B1 Fig. 1: MMC-Topologie gemäss dem Stand der Technik sowie ein Ersatzschaltbild. Fig.2: MMC-Topologie mit zwei dedizierten Spannungskorrekturmodulen pro Phasenzweig gemäss dem Stand der Technik. Fig. 3: Ausführungsform der erfindungsgemässen MMC-Topologie mit einem einzelnen aktiven Filtermodul (AFM) pro Phasenzweig. Fig. 4: Charakteristische Spannungs- und Stromverläufe, wobei fürt &lt; 100ms die AFM deaktiviert sind und bei t = 100ms aktiviert werden. Die Bezeichnungen der dargestellten Grössen beziehen sich auf Fig. 3; im Detail sind die folgenden Grössen gezeigt: a) Phasenspannungen b) Phasenströme c) Gleichstrom der aus dem Gleichspannungssystem bezogen wird d) Armströme der Phase R e) Zirkulierender Strom der Phase R f) Lokale Zwischenkreisspannung des AFMs 4 der Phase R g) Kondensatorspannungen der MMC-Module des oberen Arms 111 der Phase R h) Kondensatorspannungen der MMC-Module des unteren Arms 112 der Phase R [0017] Grundsätzlich sind in den Figuren gleiche oder gleich wirkende Elemente mit gleichen Bezugszeichen versehen. [0018] Insbesondere liegt gemäss Fig. 3 ein modularer Multilevel-Stromrichter mit einem einzelnen aktiven Filtermodul (AFM) 4 pro Phasenzweig vor. Dieses AFM ist mittels dreier Anschlüsse jeweils mit den Arminduktivitäten des oberen Arms 111 und des unteren Arms 112 des entsprechenden Phasenzweigs verbunden, sowie auch mit dem Phasenabgang, auch Phasenanschluss genannt. Jeder dieser drei Anschlüsse ist auf den Mittelpunkt jeweils eines Brückenzweiges bestehend aus jeweils einem oberen und einem unteren Halbleiterschalter geführt. Ausserdem weist ein AFM einen lokalen für alle drei Brückenzweige des AFMs gemeinsamen Zwischenkreiskondensator auf. Analog zu den oben für den Stand der Technik beschrieben Ansätzen, welche zwei Spannungskorrekturmodule pro Phasenzweig einsetzen, kann hierdurch geeignete Modulation der beiden mit den Arminduktivitäten verbundenen Brückenzweigen des AFM ebenfalls eine Gleichtaktspannung in den Phasenzweig derart eingefügt werden, dass der zirkulierende Strom wunschgemäss beeinflusst wird und damit dessen Regelung auf einen Sollwert möglich wird. Im Gegensatz zum Stand der Technik wird dazu bei der vorliegenden Erfindung jedoch nur ein einzelnes AFM pro Phasenzeig benötigt anstelle von je einem Spannungskorrekturmodul pro Arm des Phasenzweiges (d.h. zwei Spannungskorrekturmodulen pro Phasenzweig). [0019] Die Zwischenkreisspannung des AFMs bemisst sich nach dem Spannungsabfall, der durch die oben erwähnte, ohne Gegenmassnahmen im zirkulierenden Strom vorhandene zweite Harmonische über der Serieschaltung der Arminduktivitäten des oberen und des unteren Arms eines Phasenzweiges verursacht wird, sowie einer angemessenen Reserve für die Regelung. In Ausführungsformen wird keine externe Speisung für den lokalen Zwischenkreis des AFMs benötigt, da dessen Spannung mittels eines geeigneten Regelkreises konstant gehalten werden kann. [0020] Der dritte Brückenzweig des AFMs, dessen Mittelpunkt mit dem Phasenanschluss des Phasenzweiges verbunden ist, wird beispielsweise mit einem Tastverhältnis von 50% betrieben, wodurch eine virtuelle Verbindung zwischen dem Phasenanschluss und dem Mittelpunkt der beiden Arminduktivitäten hergestellt wird. Dadurch enthält die Phasenspannung entsprechend Harmonische bei der Schaltfrequenz des AFMs und deren Vielfachen. Werden gemäss Ausführungsformen die AFMs der drei Phasenzweige synchron betrieben, löschen sich jedoch diese Anteile in den Aussenleiterspannungen aus und treten stattdessen als zusätzliche Gleichtaktspannung zwischen einem Laststernpunkt und dem (gedachten) Mittelpunkt Μ des Gleichspannungssystems in Erscheinung. Insbesondere weisen jedoch die Phasenströme dann keine entsprechenden zusätzlichen harmonischen Komponenten aufgrund des Betriebs der AFM auf. Ausserdem ist darauf hinzuweisen, dass die Zwischenkreisspannung der AFM gegenüber der Kondensatorspannung der MMC-Module klein gewählt werden kann, und daher auch die Amplituden der durch die Modulation der MMC-Module erzeugten Harmonischen gross sind gegenüber jenen, die von den AFM erzeugt werden. Hinzu kommt, dass die Schaltfrequenz der AFM aufgrund der tiefen Zwischenkreisspannung in den AFM verhältnismässig gross gewählt werden kann; vorteilhaft insbesondere grösser als die effektive Schaltfrequenz des MMC-Phasenzweiges. Dadurch erfordert der Betrieb der AFM keinen nennenswerten zusätzlichen Filteraufwand. [0021] Wie in den Strom- und Spannungsverläufen in Fig. 4 zu sehen ist, ist es mit der erfindungsgemässen modularen Multilevel-Stromrichterschaltung mit einem einzelnen AFM pro Phasenzweig möglich, den zirkulierenden Strom auf einen konstanten Wert zu regeln, wodurch die Armströme ebenfalls ihren idealen Verlauf aufweisen (siehe oben). Des Weiteren CH 713 723 B1 ist zu sehen, dass die Zwischenkreisspannung des AFMs durch die implementierte PI-Regelung nach der Aktivierung der AFM auf ihren Nennwert erhöht und danach stabil dort gehalten wird. Die Ausgangsspannungen und Ausgangsströme werden nicht beeinflusst. Ausserdem führt der ideale Verlauf der Armströme auf einen kleineren Spannungsrippel der Kondensatoren der MMC-Module. [0022] Die erfindungsgemässe Schaltung in Fig. 3 erreicht also die eingangs erwähnten Zielsetzungen auf ähnliche Weise wie die Schaltung gemäss dem Stand der Technik [Madawala2015] in Fig. 2. Im Gegensatz zu diesem Stand der Technik verwendet die vorliegende Erfindung jedoch nur ein einzelnes zusätzliches Konvertermodul pro Phasenzweig anstelle von deren zwei. Durch diese konzeptionelle Vereinfachung wird die in der vorliegenden Erfindung benötigte Anzahl zusätzlicher Halbleiterschalter mit zughöriger Ansteuerung von 8 auf 6 reduziert und die Anzahl der benötigten zusätzlichen Zwischenkreiskondensatoren von 2 auf 1 halbiert. Ausserdem werden die Steuerungs- und Kommunikationssysteme vereinfacht, da nur mehr ein statt zwei Konvertermodule vorhanden sind. [EN CH713723B1]: description The invention relates to the field of electronic converters, it relates to a modular multilevel converter. Basic functionality of a modular multilevel converter (MMC) A modular multilevel converter (Modular Multilevel Converter, MMC or M2LC) is a modular and scalable multilevel topology [Marquardt2002], which is suitable for a wide range of applications in the field of high voltages and high powers, such as for HVDC or drive systems with great performance. Fig. 1a shows a typical configuration of such an MMC in a three-phase embodiment 1 for the transmission of electrical energy between a direct voltage system and an alternating voltage system, which is three-phase in the example considered. Each phase branch - as an example, consider a phase branch 11 of phase R - consists of an upper arm 111 and a lower arm 112. Each of these arms in turn consists of N serially connected MMC modules 2 and an arm inductance 3, the Arm inductances of the upper arm 111 and the lower arm 112 of a phase branch can also be implemented in a coupled coil. A DC link voltage of an MMC module is V.D.cm = VD.c / N, ie only a fraction of the voltage VD.c of the DC voltage system. Typically, the MMC modules are implemented as half-bridge modules as shown in FIG. 1, which can have two switching states: an MMC module is either inserted, ie the arm current flows through the capacitor of the MMC module and the voltage this capacitor occurs between the terminals of the MMC module; or the MMC module is bypassed, ie the arm current flows through the lower switch and the voltage between the terminals of the MMC module is ideally zero. Alternatively, the MMC modules can also be implemented as full-bridge circuits, which allows the local intermediate circuit voltage to be applied in both directions between the output terminals, not just in one like the half-bridge circuit. The following discussions relate to the variant with the half-bridge modules due to their much greater prevalence. By inserting or bridging a certain number of MMC modules of an arm, whereby the respectively required number can be determined, for example, by means of phase-shifted pulse width modulation or other known modulation methods, each arm behaves like a controlled voltage source. This is also shown in the equivalent circuit diagram of Fig. 1b shown. Accordingly, it is obvious that the potential of the phase output terminal (center point of the phase branch, usually connected to a phase output or phase connection to a phase of the AC voltage system) with respect to an imaginary center point, Μ, of the DC voltage system is between + VD.c / 2 and -VD.c / 2 can be varied by inserting or bridging a corresponding number of modules in the upper and lower arm. The capacitor voltages of the MMC modules must be actively balanced: a sorting algorithm is typically used to decide which MMC module of an arm should be added or bridged, whereby both the sign of the arm current and the individual capacitor voltages of the MMC modules are known have to. Again using the example of phase R, the arm currents are given as _____ - i J-rt J-district 'TJ ” unc(lrb ^ -circle ^ 7 ie the arm currents each contain a portion of the phase current ir as well as a circulating stream idistrictwhich flows in a loop spanned by the DC voltage system and the two arms of the phase branch. On average, N MMC modules must always be inserted per phase branch, ie in the upper and lower arm together, in order to avoid an excessive increase in the circulating current as a result of the voltage that would otherwise be applied to the series circuit of the two arm inductances. Advantageously, the circulating current consists exclusively of a direct component (and a superimposed switching frequency ripple) in such a way that the energy exchange with the direct voltage system corresponds to that with the alternating voltage system, ie ideally the following applies. __. __ if __ Mclrtrac - " lrb, ac — V and ldistrict - r Li However, if no special precautions are taken, ie if, as described above, the upper and lower arms are each modulated directly with a sinusoidal reference to generate a sinusoidal phase voltage, the circulating current contains not only the necessary for the operation of the converter and proportions described above, but also significant undesirable harmonic components. In particular, erei points CH 713 723 B1 ne large component at the second harmonic of the output frequency (ie the frequency of the AC voltage system), as can be seen in FIG. 4e during the first 100 ms. Accordingly, the arm currents also have harmonic distortions, as a result of which their RMS values ​​increase compared to the ideal case described above and cause higher conduction losses. State of the art for regulating the circulating current Various methods for suppressing these undesired harmonics in the circulating flow or in the arm flows are therefore described in the literature. The most direct variant is to add a common-mode voltage to the arm voltages by adapting the modulation reference accordingly, which is then applied to the series circuit of the two arm inductances and can accordingly be used to regulate the circulating current. This procedure is described in [Antonopooulos2009]. It is potentially disadvantageous that a corresponding voltage reserve is required, which allows the common-mode components of the arm voltages to be generated. In other words, this means that for a given voltage of the DC voltage system, the maximum AC voltage-side output voltage is reduced. In MMC systems with many MMC modules, this is typically of subordinate importance, since there often more MMC modules per arm than are absolutely necessary are used anyway in order to increase reliability by means of redundancy. Conversely, the use of this method in MMC systems with only a few MMC modules can be disadvantageous. [0009] Therefore, another variant was described in [Madawala2015] to regulate the circulating current. As shown in FIG. 2, a dedicated voltage correction module 3 is added to each arm. These voltage correction modules work as active filters by adding voltage components to the arm voltages that result in suppression of the harmonic components of the circulating current. Ie the common-mode voltage is no longer generated here by modulating the arm voltages, but by the dedicated voltage correction modules. In both cases, this does not affect the output voltage of a phase branch. It is advantageous that the voltage correction modules with a relatively low local intermediate circuit voltage V.D.ck can work, which in particular is significantly lower than the intermediate circuit voltage of an MMC module. As a result, the effort required to implement the voltage correction modules is significantly less than that required to add further MMC modules, as might be required in the variant described above for regulating the circulating current to increase the voltage reserve . Furthermore, the dedicated voltage correction modules advantageously allow the regulation of the output variables and the circulating current to be separated: the MMC modules are used to generate the desired output voltage of the phase branch, while the voltage correction modules are used to regulate the circulating current to its ideal value. The local intermediate circuit voltage of the voltage correction modules can be stabilized by means of a suitable control circuit, ie no external supply circuit is required. The disadvantage of this second variant is the use of one voltage correction module per arm, ie two voltage correction modules per phase branch, which requires a corresponding effort for the implementation. In addition, the control of this large number of voltage correction modules is subject to a certain complexity and also requires a relatively high expenditure for the necessary communication electronics. Prior art literature [0011] [Marquardt2002] [Antonopoulos2009] [Madawala2015] R. Marquardt, A. Lesnicar, and J. Hildinger, "Modular converter concept for network coupling applications at high voltages," in ETG symposium, 2002. A. Antonopoulos, L. Ängquist, and H.-P. Nope, "On dynamics and voltage control of the modular multilevel converter," in Proc. 13th Europ. Power Electron, and Appi. Conf. (EPE), Barcelona, ​​Spain, 2009. UK Madawala and BS Riar, "Modular multi-level converters," US Patent Appi. US 2015/0288287 A1,2015. The object of the present invention is to create a modular multilevel converter which enables the circulating current to be regulated by means of a dedicated active filter module, but which is easier to implement. The object is achieved by a modular multilevel converter according to the claims. Compared to the prior art, this represents a conceptual simplification: to achieve the functionality corresponding to the prior art, only a single active filter module per phase is used instead of two. This significantly reduces the effort required for implementation and at the same time reduces the complexity of the communication and control systems required. Further preferred embodiments emerge from the dependent claims. In the following, the subject matter of the invention is explained in more detail with reference to preferred exemplary embodiments, which are shown in the accompanying figures. These show: CH 713 723 B1 1: MMC topology according to the prior art and an equivalent circuit diagram. Fig. 2: MMC topology with two dedicated voltage correction modules per phase branch according to the State of the art. 3: Embodiment of the MMC topology according to the invention with a single active filter module (AFM) per phase branch. Fig. 4: Characteristic voltage and current curves, the AFM being deactivated for t &lt;100 ms and activated at t = 100 ms. The designations of the sizes shown refer to FIG. 3; The following sizes are shown in detail: a) phase voltages b) phase currents c) Direct current drawn from the direct voltage system d) arm currents of phase R e) R phase circulating current f) Local intermediate circuit voltage of AFM 4 of phase R g) Capacitor voltages of the R-phase MMC modules of the upper arm 111 h) R-phase capacitor voltages of the lower arm 112 MMC modules In principle, elements that are the same or have the same effect are provided with the same reference symbols in the figures. In particular, according to FIG. 3, there is a modular multilevel converter with a single active filter module (AFM) 4 per phase branch. This AFM is connected to the arm inductances of the upper arm 111 and the lower arm 112 of the corresponding phase branch by means of three connections, as well as to the phase output, also called phase connection. Each of these three connections is routed to the center point of a bridge arm each consisting of an upper and a lower semiconductor switch. In addition, an AFM has a local intermediate circuit capacitor that is common to all three bridge branches of the AFM. Analogous to the approaches described above for the prior art, which use two voltage correction modules per phase branch, suitable modulation of the two bridge branches of the AFM connected to the arm inductances can also insert a common-mode voltage into the phase branch in such a way that the circulating current is influenced as desired and so that it can be regulated to a setpoint value. In contrast to the prior art, however, the present invention only requires a single AFM per phase indicator instead of one voltage correction module per arm of the phase branch (ie two voltage correction modules per phase branch). The intermediate circuit voltage of the AFM is measured according to the voltage drop caused by the above-mentioned, without countermeasures in the circulating current existing second harmonic over the series circuit of the arm inductances of the upper and lower arm of a phase branch, as well as an appropriate reserve for the scheme . In embodiments, no external supply is required for the local intermediate circuit of the AFM, since its voltage can be kept constant by means of a suitable control circuit. The third bridge arm of the AFM, the center point of which is connected to the phase connection of the phase arm, is operated, for example, with a duty cycle of 50%, whereby a virtual connection between the phase connection and the center point of the two arm inductances is established. As a result, the phase voltage contains corresponding harmonics at the switching frequency of the AFM and their multiples. If, according to the embodiments, the AFMs of the three phase branches are operated synchronously, these components are canceled out in the line-to-line voltages and instead appear as an additional common-mode voltage between a load star point and the (imaginary) center point Μ of the DC voltage system. In particular, however, the phase currents then have no corresponding additional harmonic components due to the operation of the AFM. It should also be pointed out that the intermediate circuit voltage of the AFM can be selected to be small compared to the capacitor voltage of the MMC modules, and therefore the amplitudes of the harmonics generated by the modulation of the MMC modules are also large compared to those generated by the AFM. In addition, the switching frequency of the AFM can be selected to be relatively high due to the low intermediate circuit voltage in the AFM; advantageously, in particular, greater than the effective switching frequency of the MMC phase branch. As a result, the operation of the AFM does not require any additional filter effort worth mentioning. As can be seen in the current and voltage curves in Fig. 4, it is possible with the inventive modular multilevel converter circuit with a single AFM per phase branch to regulate the circulating current to a constant value, whereby the arm currents also their have an ideal course (see above). Further CH 713 723 B1 it can be seen that the intermediate circuit voltage of the AFM is increased to its nominal value by the implemented PI control after the activation of the AFM and is then kept stable there. The output voltages and output currents are not influenced. In addition, the ideal curve of the arm currents leads to a smaller voltage ripple in the capacitors of the MMC modules. The circuit according to the invention in FIG. 3 thus achieves the objectives mentioned at the beginning in a manner similar to the circuit according to the prior art [Madawala2015] in FIG. 2. In contrast to this prior art, however, the present invention only uses a single one additional converter module per phase branch instead of two. As a result of this conceptual simplification, the number of additional semiconductor switches with associated control required in the present invention is reduced from 8 to 6 and the number of additional intermediate circuit capacitors required is halved from 2 to 1. In addition, the control and communication systems are simplified because there are only one converter module instead of two.
[DE DE102014100256B4]: Modularer Stromrichter | [DE DE102014100256B4]: Modularer Stromrichter (20, 70, 90) zur Verbindung mit wenigstens einem elektrischen Mehrleitungsnetz (30, 40) mittels elektronische Halbleiterschalter (5, 6, 7, 8, 13, 14) aufweisenden Brückenmodulen (1), wobei aus einer Vielzahl von in Reihe geschalteten Brückenmodulen (1) jeweils Stromrichterzweige (21-29, 71-76) gebildet sind, wobei mehrere Stromrichterzweige (21-29, 71-76) vorhanden sind, die jeweils eine Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) mit einer Leitung (41, 42, 43) des zweiten Mehrleitungsnetzes (40) oder einer anderen Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) verbinden, wobei der Stromrichter (20, 70, 90) eine Stromrichterzweig-Redundanz derart aufweist, dass wenigstens ein weiterer Stromrichterzweig als redundanter Stromrichterzweig (22, 24, 29, 69) ausgebildet ist oder durch eine Steuerungseinrichtung (97) des Stromrichters (20, 70, 90) als redundanter Stromrichterzweig (22, 24, 29, 69) betrieben ist, wobei der wenigstens eine redundante Stromrichterzweig (22, 24, 29, 69) zur wenigstens teilweisen Übernahme der Funktion eines anderen Stromrichterzweiges (21-29, 71-76) eingerichtet ist, wobei der Stromrichter als Multilevelmatrixkonverter ausgebildet ist, der für die Kopplung zweier Dreileitungsnetze neun Stromrichterzweige aufweist, dadurch gekennzeichnet, dass eine Steuerungseinrichtung (97) des Stromrichters (20, 70, 90) dazu eingerichtet ist, die für den Betrieb des Stromrichters (20, 70, 90) genutzten Stromrichterzweige (21-29, 71-76) im laufenden Betrieb zyklisch zu wechseln und dabei den Stromrichter mit einer variablen, durch die Steuerungseinrichtung (97) festlegbaren Anzahl von Stromrichterzweigen zwischen sechs und neun Stromrichterzweigen zu betreiben. | DE102014100256B4 | 2015-07-16 2021-09-09 | DE102014100256A | 2014-01-10 2014-01-10 | DE102014100256A, 2014-01-10 DE102014100256A, 2014-01-10 | DE102014100256B4: 2021-09-09 | GOTTFRIED WILHELM LEIBNIZ UNIVERSITÄT HANNOVER UNIV HANNOVER GOTTFRIED WILHELM LEIBNIZ | HOFEN MALTE VON BARUSCHKA LENNART KARWATZKI DENNIS | H02M5/293: I H02J3/06: I H02M1/32: I H02M7/483: I | H02M5/293: I H02M7/483: I H02M7/49: I H02M7/4835: I | DE102010013862A1 DE102011107737A1 ES2341693A1 JP2009136098A DE102010013826A1 |  | [DE DE102014100256B4]: Modularer Stromrichter (20, 70, 90) zur Verbindung mit wenigstens einem elektrischen Mehrleitungsnetz (30, 40) mittels elektronische Halbleiterschalter (5, 6, 7, 8, 13, 14) aufweisenden Brückenmodulen (1), wobei aus einer Vielzahl von in Reihe geschalteten Brückenmodulen (1) jeweils Stromrichterzweige (21-29, 71-76) gebildet sind, wobei mehrere Stromrichterzweige (21-29, 71-76) vorhanden sind, die jeweils eine Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) mit einer Leitung (41, 42, 43) des zweiten Mehrleitungsnetzes (40) oder einer anderen Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) verbinden, wobei der Stromrichter (20, 70, 90) eine Stromrichterzweig-Redundanz derart aufweist, dass wenigstens ein weiterer Stromrichterzweig als redundanter Stromrichterzweig (22, 24, 29, 69) ausgebildet ist oder durch eine Steuerungseinrichtung (97) des Stromrichters (20, 70, 90) als redundanter Stromrichterzweig (22, 24, 29, 69) betrieben ist, wobei der wenigstens eine redundante Stromrichterzweig (22, 24, 29, 69) zur wenigstens teilweisen Übernahme der Funktion eines anderen Stromrichterzweiges (21-29, 71-76) eingerichtet ist, wobei der Stromrichter als Multilevelmatrixkonverter ausgebildet ist, der für die Kopplung zweier Dreileitungsnetze neun Stromrichterzweige aufweist, dadurch gekennzeichnet, dass eine Steuerungseinrichtung (97) des Stromrichters (20, 70, 90) dazu eingerichtet ist, die für den Betrieb des Stromrichters (20, 70, 90) genutzten Stromrichterzweige (21-29, 71-76) im laufenden Betrieb zyklisch zu wechseln und dabei den Stromrichter mit einer variablen, durch die Steuerungseinrichtung (97) festlegbaren Anzahl von Stromrichterzweigen zwischen sechs und neun Stromrichterzweigen zu betreiben. Stromrichter nach einem der vorhergehenden Ansprüche, dadurch gekennzeichnet, dass für einen, mehrere oder alle Stromrichterzweige (21-29, 71-76) und/oder für einen, mehrere oder alle redundanten Stromrichterzweige (22, 24, 29, 69) wenigstens ein in Reihe zu den Brückenmodulen (1) des Stromrichterzweigs geschalteter Trennschalter (50, 52) vorhanden ist, mit dem der Stromrichterzweig (21-29, 71-76) oder der redundante Stromrichterzweig (22, 24, 29, 69) galvanisch abschaltbar ist. Stromrichter nach Anspruch 2, dadurch gekennzeichnet, dass wenigstens ein Trennschalter (50, 52) an jedem Ende eines Stromrichterzweigs (21-29, 71-76) oder redundanten Stromrichterzweigs (22, 24, 29, 69), der Trennschalter (50, 52) aufweist, vorhanden ist. Stromrichter nach einem der vorhergehenden Ansprüche, dadurch gekennzeichnet, dass der Stromrichter (20, 70, 90) als Direktumrichter, Wechselrichter, Blindleistungskompensator oder unterbrechungsfreie Stromversorgungseinheit ausgebildet ist. Stromrichter nach einem der vorhergehenden Ansprüche, dadurch gekennzeichnet, dass das Brückenmodul (1) wenigstens zwei elektronische Halbleiterschalter (5, 6, 7, 8, 13, 14) in Halbbrückenschaltung oder vier elektronische Halbleiterschalter (5, 6, 7, 8, 13, 14) in Vollbrückenschaltung (4) aufweist, und das Brückenmodul (1) wenigstens einen Kondensator (9) aufweist, der über die Halbleiterschalter (5, 6, 7, 8, 13, 14) mit äußeren Anschlusskontakten (2, 3) des Brückenmoduls (1) verbindbar ist. Stromrichter nach einem der vorhergehenden Ansprüche, dadurch gekennzeichnet, dass der wenigstens eine redundante Stromrichterzweig (22, 24, 29, 69) über eine erste schaltbare elektrische Verbindungseinrichtung (60) mit jeweils einer elektrischen Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) galvanisch verbindbar und davon trennbar ist und über eine zweite schaltbare elektrische Verbindungseinrichtung (64) mit einer elektrischen Leitung (41, 42, 43) des zweiten Mehrleitungsnetzes (40) oder einer anderen Leitung (31, 32, 33) des ersten Mehrleitungsnetzes (30) galvanisch verbindbar und davon trennbar ist. [EN DE102014100256B4]: Modular converter (20, 70, 90) for connection to at least one electrical multi-line network (30, 40) by means of bridge modules (1) having electronic semiconductor switches (5, 6, 7, 8, 13, 14), whereby from a plurality of in series connected bridge modules (1) each converter branches (21-29, 71-76) are formed, wherein several converter branches (21-29, 71-76) are present, each of which has a line (31, 32, 33) of the first multi-line network (30 ) with one line (41, 42, 43) of the second multi-line network (40) or another line (31, 32, 33) of the first multi-line network (30), the converter (20, 70, 90) having a converter branch redundancy such that at least one further converter branch as redundant converter branch (22, 24, 29, 69) is formed or is operated by a control device (97) of the converter (20, 70, 90) as a redundant converter branch (22, 24, 29, 69), wherein the at least one redundant converter branch (22, 24, 29, 69) is set up to at least partially take over the function of another converter branch (21-29, 71-76), the converter being designed as a multilevel matrix converter for coupling two three-line networks has nine converter branches, characterizedthat a control device (97) of the converter (20, 70, 90) is set up to cyclically change the converter branches (21-29, 71-76) used for operating the converter (20, 70, 90) during operation and operating the converter with a variable number of converter branches between six and nine converter branches that can be determined by the control device (97). Converter according to one of the preceding claims, characterizedthat for one, several or all converter branches (21-29, 71-76) and / or for one, several or all redundant converter branches (22, 24, 29, 69) at least one in series with the bridge modules (1) of the converter branch switched disconnector (50, 52) is present, with which the converter branch (21-29, 71-76) or the redundant converter branch (22, 24, 29, 69) can be galvanically switched off. Converter according to Claim 2, characterizedthat at least one disconnector (50, 52) is present at each end of a converter branch (21-29, 71-76) or redundant converter branch (22, 24, 29, 69) which has disconnectors (50, 52). Converter according to one of the preceding claims, characterizedthat the converter (20, 70, 90) is designed as a direct converter, inverter, reactive power compensator or uninterruptible power supply unit. Converter according to one of the preceding claims, characterizedthat the bridge module (1) has at least two electronic semiconductor switches (5, 6, 7, 8, 13, 14) in a half-bridge circuit or four electronic semiconductor switches (5, 6, 7, 8, 13, 14) in a full-bridge circuit (4), and the bridge module (1) has at least one capacitor (9) which can be connected to external connection contacts (2, 3) of the bridge module (1) via the semiconductor switches (5, 6, 7, 8, 13, 14). Converter according to one of the preceding claims, characterizedthat the at least one redundant converter branch (22, 24, 29, 69) can be galvanically connected to and disconnected from each electrical line (31, 32, 33) of the first multi-line network (30) via a first switchable electrical connection device (60), and Via a second switchable electrical connection device (64) with an electrical line (41, 42, 43) of the second multi-line network (40) or another line (31, 32, 33) of the first multi-line network (30) can be electrically connected and separated therefrom. | [DE DE102014100256B4]: Die Erfindung betrifft einen modularen Stromrichter zur Verbindung eines ersten elektrischen Mehrleitungsnetzes mit einem zweiten elektrischen Mehrleitungsnetz mittels elektronische Halbleiterschalter aufweisenden Brückenmodulen gemäß dem Anspruch 1. Allgemein betrifft die Erfindung das Gebiet der elektrischen Energieversorgungstechnik. Mit einem solchen Stromrichter kann elektrische Energie zwischen Energieversorgungsnetzen transferiert werden, die z. B. unterschiedliche Nennspannungen oder, im Falle von Wechselspannung, unterschiedliche Frequenzen haben. Ein solcher Stromrichter wird auch als Umrichter bezeichnet. Dies kann durch Verwendung von elektronische Halbleiterschalter aufweisenden Brückenmodulen ohne teure und aufwändige Transformatoren realisiert werden. Entsprechende Vorschläge sind z. B. aus der DE 10 2010 013 862 A1 und der DE 10 2011 107 737 A1 bekannt. Solche bekannten Stromrichter weisen mehrere Stromrichterzweige auf, die jeweils eine Leitung des ersten Mehrleitungsnetzes mit einer Leitung des zweiten Mehrleitungsnetzes verbinden. In jedem Stromrichterzweig sind so viele Brückenmodule in Reihe geschaltet, dass die gewünschte Energieübertragung von dem einen Mehrleitungsnetz in das andere Mehrleitungsnetz durchgeführt werden kann und die einzelnen Brückenmodule dabei nicht überlastet werden. Um eine erhöhte Ausfallsicherheit zu erreichen, kann die Anzahl der in Reihe geschalteten Brückenmodule pro Stromrichterzweig so groß gewählt werden, dass eine gewisse Redundanz vorhanden ist. So kann z. B. bei einem internen Defekt eines Brückenmoduls der Reihenschaltung dieses Brückenmodul über die interne Brückenschaltung oder auf andere Weise elektrisch überbrückt werden. Der hierdurch verursachte Spannungsausfall kann durch die übrigen Brückenmodule der Reihenschaltung kompensiert werden, indem durch entsprechende Steuerung der elektronischen Halbleiterschalter der Brückenmodule pro Brückenmodul eine im zeitlichen Mittel jeweils erhöhte Ausgangsspannung bereitgestellt wird. Bei einem solchen Stromrichter erfolgt die Wartung und Reparatur im Regelfall in einem vollständig abgeschalteten Zustand des Stromrichters. Aus der ES 2 341 693 A1 geht ein Matrixkonverter hervor. Aus der Veröffentlichung von Yun Wan, Steven Liu, Jianguo Jiang gehen Vorschläge für analytische Methoden und für die Auslegung modularer Multilevelkonverter hervor. Aus der JP 2009- 136 098 A geht ein Hochdruck-Direktumrichter hervor. Der Erfindung liegt die Aufgabe zugrunde, einen modularen Stromrichter der zuvor erläuterten Art anzugeben, der bei im Wesentlichen gleichem Hardware-Aufwand eine verbesserte Ausfallsicherheit bietet. Diese Aufgabe wird durch einen modularen Stromrichter gemäß Anspruch 1 gelöst. Der modulare Stromrichter, im Folgenden nur kurz als Stromrichter bezeichnet, hat den Vorteil, dass durch ein gegenüber Vorschlägen aus dem Stand der Technik völlig anderes Redundanzkonzept bei im Wesentlichen gleichem oder nur geringfügig erhöhtem Hardware-Aufwand eine deutliche Verbesserung der Ausfallsicherheit erzielt werden kann. Infolgedessen ist seltener mit Ausfällen der elektrischen Energieversorgung zu rechnen. Zudem wird die Wartungsfreundlichkeit des Stromrichters erhöht. Dies wird durch die Einführung einer Stromrichterzweig-Redundanz erreicht, im Gegensatz zu einer Redundanz innerhalb eines Stromrichterzweigs. Durch Vorsehen eines zusätzlichen Stromrichterzweigs als redundanten Stromrichterzweig oder durch Betreiben eines vorhandenen Stromrichterzweigs als redundanten Stromrichterzweig wird es möglich, bei einer Störung in einem anderen Stromrichterzweig, z. B. einem Ausfall eines Brückenmoduls, die Funktion des gestörten Stromrichterzweigs solange durch den redundanten Stromrichterzweig ausführen zu lassen, bis der Ausfall oder die Störung des gestörten Stromrichterzweigs behoben ist. Um eine ausreichende Sicherheit für das Wartungspersonal zu gewährleisten, kann der gestörte Stromrichterzweig während der Durchführung der Wartungsarbeiten galvanisch abgetrennt werden, z. B. durch entsprechende Trennschütze. Hierin liegt ein weiterer Vorteil des erfindungsgemäßen Redundanzkonzepts, nämlich, dass nur relativ wenige Trennschütze erforderlich sind, nur zwei pro Stromrichterzweig, um den gesamten Stromrichterzweig in einen für Wartungsarbeiten sicheren Zustand zu versetzen. Bei der reinen Redundanz durch die Reihenschaltung der Brückenmodule wären Trennschütze auf beiden Seiten jedes Brückenmoduls erforderlich, was aufgrund des erheblichen Aufwands nicht praxisgerecht wäre. Durch das erfindungsgemäße neue Redundanzkonzept der Stromrichterzweig-Redundanz können damit auch reparaturbedingte Abschaltphasen des Stromrichters reduziert oder ganz vermieden werden. Dass wenigstens ein Stromrichterzweig als redundanter Stromrichterzweig ausgebildet ist oder durch eine Steuerungseinrichtung des Stromrichters als redundanter Stromrichterzweig betrieben ist, umfasst die Ausführungsformen, dass einer oder mehrere Stromrichterzweig als redundante Stromrichterzweige ausgebildet sind oder als solche betrieben sind. Ein weiterer Vorteil der Erfindung ist, dass die Anzahl der erforderlichen Brückenmodule des Stromrichters und damit die installierte Schaltleistung, der Platzbedarf und die Investitionskosten gesenkt werden können. Der Ausfall eines Brückenmoduls führt maximal zu einem Ausfall des entsprechenden Stromrichterzweigs, nicht jedoch zu einem Ausfall des gesamten Stromrichters. Hieraus lässt sich eine Erhöhung der Verfügbarkeit des Stromrichters ableiten. Wartungsarbeiten wie der Austausch von Brückenmodulen oder anderen Bauteilen können im laufenden Betrieb geschehen. Hierbei kann der Stromrichter ggf. mit verminderter Leistung am Netz bleiben. Gemäß der Erfindung ist eine Steuerungseinrichtung des Stromrichters dazu eingerichtet, die für den Betrieb des Stromrichters genutzten Stromrichterzweige zu wechseln. Insbesondere können auch ein oder mehrere redundante Stromrichterzweige für den Betrieb des Stromrichters genutzt werden, ohne dass Fehler oder Störungen vorliegen. Gemäß der Erfindung ist eine Steuerungseinrichtung des Stromrichters dazu eingerichtet, den Stromrichter mit einer variablen, durch die Steuereinrichtungseinrichtung festlegbaren Anzahl von Stromrichterzweigen zu betreiben. Dies hat den Vorteil, dass durch die Steuerungseinrichtung ein gestörter Stromrichterzweig abgeschaltet werden kann und durch einen redundanten Stromrichterzweig ersetzt werden kann. Ein weiterer Vorteil besteht darin, dass bei entsprechender schaltungstechnischer Anordnung der einzelnen Stromrichterzweige einschließlich des oder der redundanten Stromrichterzweige ein Wechsel zwischen gerade aktiven Stromrichterzweigen durch die Steuerungseinrichtung durchgeführt werden kann, auch ohne dass eine Störung in einem Stromrichterzweig vorliegt. Dies hat den Vorteil, dass alle Stromrichterzweige hin und wieder im laufenden Betrieb eingesetzt werden, so dass eventuelle Fehler oder Störungen frühzeitig entdeckt werden. Insbesondere kann hiermit vermieden werden, dass ein redundanter Stromrichterzweig im Normalfall nie betrieben wird und erst dann, wenn der redundante Stromrichterzweig benötigt wird, festgestellt wird, dass der redundante Stromrichterzweig einen Fehler aufweist. Ein weiterer Vorteil der genannten Weiterbildung der Erfindung besteht darin, dass durch ein regelmäßiges Umschalten der aktiv in Betrieb befindlichen Stromrichterzweige eine gleichmäßige Belastung und Abnutzung der Bauteile erfolgt, insbesondere der einzelnen Bauteile der Brückenmodule. Anders gesagt, im zeitlichen Mittel werden hierdurch sämtliche Bauteile geschont, weil sie nicht ständig in Betrieb sind. Eine Abschaltung eines Stromrichterzweigs, z. B. bei einer Störung, kann z. B. durch Durchführung einer Stromregelung derart erfolgen, dass der Strom auf den Wert Null geregelt wird, so dass der Stromrichterzweig elektrisch neutral ist. Anschließend ist es beispielsweise möglich, sämtliche Halbleiterschalter im Brückenmodul zu deaktivieren und somit zu entlasten. Eine Änderung der genutzten Stromrichterzweige kann durch die Steuerungseinrichtung z.B. vorgenommen werden, wenn der Stromrichter nicht in Betrieb ist. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist die Steuerungseinrichtung zur Änderung der genutzten Stromrichterzweige bzw. der genutzten Anzahl von Stromrichterzweigen während des laufenden Betriebs des Stromrichters eingerichtet. Somit muss der Stromrichter für einen Wechsel der genutzten Stromrichterzweige nicht heruntergefahren werden. Die Energieversorgung durch den Stromrichter wird daher nicht unterbrochen. Auf diese Weise können je nach elektrischer Belastungssituation jederzeit mehr oder weniger Stromrichterzweige genutzt werden. Es können z. B. redundante Stromrichterzweige genutzt werden, um in zeitlichen Phasen hoher Belastung des Stromrichters die übrigen Stromrichterzweige zu entlasten. Das erste und/oder das zweite elektrische Mehrleitungsnetz kann z. B. ein Zweileitungsnetz oder ein Dreileitungsnetz sein, insbesondere ein Wechselstromnetz. Der Stromrichter eignet sich z. B. für die Verbindung zweier dreiphasiger Netze miteinander, d. h. von zwei Drehstromnetzen. Der Stromrichter eignet sich auch z. B. zur Verbindung eines einphasigen Wechselstromnetzes mit einem dreiphasigen Netz. Ebenso kann ein dreiphasiges Netz z. B. mit einem Gleichstromnetz mit zwei Leitungen verbunden werden, z. B. zur Hochspannungsgleichstrom übertragung. Erfindungsgemäß ist der Stromrichter als Multilevelmatrixkonverter ausgebildet, der für die Kopplung zweier Dreileitungsnetze neun Stromrichterzweige aufweist, wobei der Stromrichter variabel mit einer Anzahl von Stromrichterzweigen zwischen 6 und 9 betreiben wird. Wird der Stromrichter mit 6 Stromrichterzweigen betrieben, kann ein vorteilhaftes Betriebsverfahren gemäß DE 10 2011 107 737 A1 realisiert werden. Die Anzahlen m und n von Leitungen der Mehrleitungsnetze beziehen sich dabei auf die bei gleichmäßiger Belastung stromtransportierenden Leitungen, d.h. bei einem Dreiphasennetz auf die drei Phasenleiter. Ein ggf. vorhandener Neutralleiter ist hier nicht mitgezählt. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist für einen, mehrere oder alle Stromrichterzweige und/oder für einen, mehrere oder alle redundanten Stromrichterzweige wenigstens ein in Reihe zu den Brückenmodulen des Stromrichterzweigs geschalteter Trennschalter vorgesehen, mit dem der Stromrichterzweig oder der redundante Stromrichterzweig galvanisch abschaltbar ist. Der Trennschalter kann z. B. als manuell betätigbarer Trennschalter oder als durch eine Steuerungseinrichtung steuerbares Trennschütz ausgebildet sein. Der Trennschalter kann insbesondere am Ende eines Stromrichterzweigs angeordnet sein, d. h. an der Verbindung des Stromrichterzweigs zu einer Leitung eines angeschlossenen Mehrleitungsnetzes. Dies hat den Vorteil, dass mittels des Trennschalters ein Stromrichterzweig auch galvanisch abgeschaltet werden kann. Hierdurch kann der Stromrichter im Fehlerfall einfacher und sicherer repariert werden oder es können Wartungsarbeiten durchgeführt werden. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist wenigstens ein Trennschalter an jedem Ende eines Stromrichterzweigs oder redundanten Stromrichterzweigs, der Trennschalter aufweist, vorhanden. Dies hat den Vorteil, dass der Stromrichterzweig beidseitig galvanisch abgetrennt werden kann, so dass er vollständig potentialfrei geschaltet werden kann. Hierdurch wird die größtmögliche Sicherheit für Reparatur- und Wartungsarbeiten erreicht. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist der Stromrichter als Direktumrichter oder als Zwischenkreis-Umrichter, insbesondere mit einem Gleichspannungszwischenkreis, oder als Wechselrichter, Blindleistungskompensator oder unterbrechungsfreie Stromversorgungseinheit ausgebildet. Der Stromrichter kann insbesondere als transformatorloser Stromrichter ausgebildet sein. Hierdurch kann der Stromrichter vergleichsweise kostengünstig und kompakt realisiert werden. Gemäß einer vorteilhaften Weiterbildung der Erfindung weist das Brückenmodul wenigstens zwei elektronische Halbleiterschalter in Halbbrückenschaltung oder vier elektronische Halbleiterschalter in Vollbrückenschaltung auf. Das Brückenmodul weist wenigstens einen Kondensator auf, der über die Halbleiterschalter mit äußeren Anschlusskontakten des Brückenmoduls verbindbar ist. Mit der Vollbrückenschaltung lassen sich bipolare Vollbrückenmodule realisieren, mit denen beliebige Wechselstrom-Energieumwandlungen zwischen dem ersten und dem zweiten Mehrleitungsnetz durchgeführt werden können. Über den Kondensator kann in dem Brückenmodul ein gewisser elektrischer Energieinhalt gespeichert werden, wodurch energietechnisch besonders günstige Betriebsmodi des Stromrichters realisiert werden können, z. B. die in DE 10 2011 107 737 A1 beschriebene Energieinhaltsregelung. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist der wenigstens eine redundante Stromrichterzweig über eine schaltbare elektrische Verbindungseinrichtung mit jeweils einer elektrischen Leitung des ersten Mehrleitungsnetzes galvanisch verbindbar und davon trennbar und über eine zweite elektrische Verbindungseinrichtung mit einer elektrischen Leitung des zweiten Mehrleitungsnetzes oder einer anderen Leitung des ersten Mehrleitungsnetzes galvanisch verbindbar und davon trennbar. Die erste und die zweite elektrische Verbindungseinrichtung können z. B. als Umschalter ausgebildet sein. Dies hat den Vorteil, dass der redundante Stromrichterzweig variabel zum Ersatz unterschiedlicher anderer Stromrichterzweige des Stromrichters eingesetzt werden kann, wenn einer davon eine Störung aufweist. Hierdurch kann die Zahl der erforderlichen redundanten Stromrichterzweige minimiert werden, ggf. bis hinunter auf nur einen redundanten Stromrichterzweig. Ist nur ein redundanter Stromrichterzweig vorhanden, ist es vorteilhaft, die erste und die zweite elektrische Verbindungseinrichtung so auszubilden, dass der redundante Stromrichterzweig wahlweise als Ersatz für jeden der sonstigen Stromrichterzweige des Stromrichters geschaltet werden kann. Die Erfindung erlaubt die Durchführung des folgenden Betriebsverfahrens. Zunächst erfolgt im laufenden Betrieb eine Stromregelung einzelner Stromrichterzweige auf den Wert Null und der Übergang zu einer anderen Betriebsart des Stromrichters, z. B. einer Hexverter-Regelung in den nicht abgeschalteten Stromrichterzweigen. Da in den für den Hexverter-Betrieb nicht benötigten Stromrichterzweigen auf diese Weise kein Strom fließt, erlaubt das Vorgehen, diese Stromrichterzweige im laufenden Betrieb des Stromrichters mittels der Trennschalter vom restlichen Stromrichter zu trennen. Gemäß einer vorteilhaften Weiterbildung der Erfindung weist wenigstens ein Brückenmodul folgende Merkmale auf: a) Das Brückenmodul weist einen ersten und einen zweiten Anschluss zur Verbindung mit einer Leitung des Energieversorgungsnetzes oder einem Anschluss eines weiteren Brückenmoduls auf,b) das Brückenmodul weist vier elektronische Halbleiterschalter in Vollbrückenschaltung auf,c) der erste und der zweite Anschluss des Brückenmoduls ist mit einander gegenüberliegenden Anschlusspunkten der Vollbrückenschaltung verbunden,d) das Brückenmodul weist einen Kondensator auf, der mit den weiteren einander gegenüberliegenden Anschlusspunkten der Vollbrückenschaltung verbunden ist. Die Vollbrückenschaltung erlaubt dabei variabel eine Vielzahl einstellbarer Schaltzustände, z.B. die Schaltung einer direkten Verbindung zwischen dem ersten und dem zweiten Anschluss des Brückenmoduls (Überbrücken des Brückenmoduls) oder ein Laden oder Entladen des Kondensators mit der jeweils gewünschten, über die Halbleiterschalter wählbaren Polarität. Durch entsprechende Ansteuerung der Halbleiterschalter über eine Steuerungseinrichtung, die z.B. pulsbreitenmodulierte Ansteuersignale ausgibt, ist eine relativ feinstufige Ladung und Entladung des Kondensators möglich. Gemäß einer vorteilhaften Weiterbildung der Erfindung weist wenigstens ein Brückenmodul folgende Merkmale auf: a) das Brückenmodul weist eine Batterie auf,b) das Brückenmodul weist einen steuerbaren Gleichspannungswandler auf, dessen eine Anschlussseite parallel zum Kondensator angeschlossen ist und an dessen andere Anschlussseite die Batterie angeschlossen ist. Dies erlaubt auf elegante Weise und mit geringem schaltungstechnischem Aufwand eine Einbindung einer Batterie in den Direktstromrichter. Mit der Batterie bzw. einer Mehrzahl von Batterien bei Verwendung einer Mehrzahl von Brückenmodulen kann eine unterbrechungsfreie Stromversorgung mit wenig Aufwand integriert werden. Bei Einsatz des Direktstromrichters an einem Stromversorgungsnetz lässt sich so beispielsweise die Bereitstellung einer Minutenreserve zur Netzstabilisierung realisieren. Mittels der Batterien der Brückenmodule ist eine Pufferung der Energieversorgung je nach Auslegung der Batterien auch für einen größeren Zeitraum möglich, z.B. während Zeiten geringerer Energieerzeugung eines Windenergieparks. In vergleichbarer Weise kann eine Solarzellenenergieversorgungseinrichtung vorteilhaft mit der genannten Einrichtung an ein Dreiphasennetz angekoppelt werden. Vorteilhaft kann über die Batterien eine Zwischenspeicherung der Energie für sonnenlichtarme Zeiten oder die Nacht erfolgen. Die Batterie ist vorteilhaft als aufladbare Batterie ausgebildet, z.B. als Nickelmetallhydrid-Akkumulator, Blei-Akkumulator oder Lithiumpolymer-Akkumulator. Selbstverständlich können auch andere Akkumulator-Technologien eingesetzt werden. Eine solche Ausführung des Brückenmoduls ermöglicht es, die mit Hilfe der Batterie erzeugte Brückengleichspannung des Brückenmoduls unabhängig von der Batteriespannung konstant zu halten, und zwar durch entsprechende Steuerung des Gleichspannungswandlers. Hierdurch kann auch bei sinkender Batteriespannung eine konstante Ausgangsspannung aufrechterhalten werden. Als Brückenmodul sei in diesem Zusammenhang jegliche räumliche und bauliche Anordnung der genannten Elemente verstanden, unabhängig davon, ob die Elemente beispielsweise in einem Gehäuse zusammengefasst sind oder verteilt angeordnet sind. Beispielsweise kann die Batterie baulich getrennt von den übrigen Elementen des Brückenmoduls angeordnet sein. In einer vorteilhaften Weiterbildung der Erfindung ist die Batterie baulich in das Brückenmodul integriert. Ein weiterer Vorteil ist, dass die Welligkeit des Leistungsbedarfs bzw. des durch das Brückenmodul fließenden Stroms im Wesentlichen von der Batterie entkoppelt werden kann. Es ist ein im Wesentlichen konstanter Stromfluss durch die Batterie möglich, d.h. die höherfrequenten Anteile im Energieversorgungsnetz können von der Batterie ferngehalten werden. Dies erhöht die potentielle Lebensdauer der Batterien erheblich. Vorteilhaft kann eine Reihenschaltung von Brückenmodulen eingesetzt werden. Hierdurch kann eine direkte Reihenschaltung einer großen Anzahl von Batterien vermieden werden. Eine Integration einer Mehrzahl von Batterien ist dann über eine Mehrzahl der Brückenmodule, die jeweils eine eigene Batterie aufweisen, möglich. Dies vermeidet schaltungstechnischen Aufwand für gesonderte Balancier- oder Lade-/Entladeschaltungen für die Batterien und verringert damit den gesamten schaltungstechnischen Aufwand. Vorteilhaft wird die Batteriespannung mit Rücksicht auf die Brückengleichspannung bzw. die Nennspannung des jeweiligen Brückenmoduls gewählt. Große Übersetzungsverhältnisse des Gleichspannungswandlers lassen sich somit vermeiden und der Wirkungsgrad wird optimiert. Im Fall unterschiedlicher Nennspannungen in den Brückenmodulen eines Stromrichters unterscheiden sich dann auch die Spannungen der verwendeten Batterien voneinander. Ein weiterer Vorteil ist, dass eine Abschaltung des Brückenmoduls über die Vollbrückenschaltung möglich ist. So kann etwa bei einem defekten Leistungshalbleiter die Abschaltung eines Brückenmoduls in einer Reihenschaltung von Brückenmodulen erfolgen. Über die verbleibenden Brückenmodule kann trotz Ausfall eines Brückenmoduls weiterhin die gewünschte Ausgangsspannung der Reihenschaltung konstant gehalten werden. Ein weiterer Vorteil der Erfindung ist, dass ein Brückenmodul, dessen Batterie defekt ist, weiter in Betrieb bleiben kann. Im zeitlichen Mittel kann das Modul mit defekter Batterie zwar keine Energie liefern, es kann jedoch genutzt werden, um die Spannung über der Reihenschaltung von Brückenmodulen während eines Teils der Netzperiode zu erhöhen, und hilft so, die für einen ausfallsicheren Betrieb des Stromrichters nötige Überdimensionierung der Nennspannungen der einzelnen Brückenmodule zu reduzieren. Durch die beiden genannten Maßnahmen können besonders ausfallsichere unterbrechungsfreie Stromversorgungen bzw. Stromrichtersysteme geschaffen werden. Ein weiterer Vorteil der Erfindung ist, dass durch den Gleichspannungswandler unterschiedliche Spannungsniveaus der Batterie, die sich je nach Ladezustand einstellen, kompensiert werden können. Hierdurch kann das Brückenmodul eine gewünschte konstante Ausgangsspannung erzeugen. Somit kann auch bei Verwendung der Brückenmodule in einer Reihenschaltung, z.B. in einem Stromrichter, eine konstante Spannung am Dreileitungsnetz aufrechterhalten werden. Ein weiterer Vorteil ist, dass die bei bekannten Stromrichtern vorgesehene Überdimensionierung bezüglich der Modulanzahl bzw. der Batteriespannung nicht mehr erforderlich ist, da bei Ausfall eines Brückenmoduls bzw. der Batterie des Brückenmoduls die fehlende Spannung durch eine entsprechende Anhebung der Ausgangsspannungen und gegebenenfalls der Brückengleichspannungen der übrigen Brückenmodule ausgeglichen werden kann. Bei entsprechender Auslegung des Gleichspannungswandlers kann grundsätzlich auch mit einer geringeren Anzahl von Brückenmodulen bzw. Batterien die Einrichtung im Vergleich zu unterbrechungsfreien Stromversorgungen aus dem Stand der Technik aufgebaut werden. Hierdurch lassen sich besonders kostengünstige unterbrechungsfreie Stromversorgungen realisieren. Je nach Sicherheits- und Zuverlässigkeitsanforderungen kann in einer vorteilhaften Ausgestaltung die Reihenschaltung der Brückenmodule von vornherein überdimensioniert ausgeführt werden, d.h. es kann eine größere Anzahl von Brückenmodulen bzw. Batterien vorgesehen werden als für die Erreichung der gewünschten Ausgangsspannung an sich notwendig wäre. Es werden somit redundante Brückenmodule vorgesehen. Die gewünschte Ausgangsspannung kann durch Abwärtswandlung der Brückengleichspannungen der einzelnen Brückenmodule über deren Brückenschaltungen erfolgen. Da jedes einzelne Modul so weniger Energie bereitstellen muss, werden hierdurch einerseits die Batterien geschont. Zudem kann auch bei Ausfall einer größeren Anzahl von Brückenmodulen die gewünschte Ausgangsspannung aufrechterhalten werden. Hierdurch kann auch die Ausfallsicherheit der gesamten Einrichtung z.B. gegenüber reinen Reihenschaltungen von Batterien weiter erhöht werden. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist der Gleichspannungswandler zur Bereitstellung einer Ausgangsspannung an dem Kondensator eingerichtet, die je nach Ausführung und Steuerung des Gleichspannungswandlers höher, niedriger oder gleich der Spannung der Batterie einstellbar ist. Die Verwendung eines solchen steuerbaren Gleichspannungswandlers erlaubt eine hohe Flexibilität bei der Verwendung des Brückenmoduls bzw. einer Mehrzahl von Brückenmodulen und der Steuerung von deren Ausgangsspannung. Der Gleichspannungswandler kann als reiner Aufwärtswandler (Ausgangsspannung höher oder gleich der Batteriespannung), reiner Abwärtswandler (Ausgangsspannung niedriger oder gleich der Batteriespannung) oder als kombinierter Aufwärts-/Abwärtswandler ausgelegt sein. Vorteilhaft ist der Einsatz eines Aufwärtswandlers, da hierfür zum einen weniger Bauteile benötigt werden als für einen kombinierten Aufwärts-/Abwärtswandler und zum anderen eine geringere Batteriespannung benötigt wird, was den potentiellen Bedarf an Balanciermöglichkeiten verringert. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist der Gleichspannungswandler ein bidirektionaler Gleichspannungswandler. Hierdurch kann nicht nur in der einen Richtung die Energie für die Brückengleichspannung am mit dem Kondensator verbundenen Ausgang des Gleichspannungswandlers variabel bereitgestellt werden, sondern zusätzlich auch die Batterie mit einer von der mit dem Kondensator verbundenen Seite des Gleichspannungswandlers abgeleiteten Spannung mit einer für den jeweiligen Batteriezustand geeigneten Ladespannung geladen werden. Zusätzlich ist auch eine definierte Entladung der Batterie über den bidirektionalen Gleichspannungswandler steuerbar, z.B. zum Zweck der Formierung der Batterie. Gemäß einer vorteilhaften Weiterbildung der Erfindung weist der Gleichspannungswandler eine Halbbrücke mit zwei elektronischen Halbleiterschaltern auf. Vorteilhaft können Halbleiterschalter des gleichen Typs verwendet werden wie für die Vollbrückenschaltung. Dies erlaubt einen einfachen und kostengünstigen Aufbau des Gleichspannungswandlers aus wenigen Bauteilen und damit einen kostengünstigen Aufbau des gesamten Brückenmoduls. In einer vorteilhaften Weiterbildung der Erfindung sind die elektronischen Halbleiterschalter in Form eines dreiphasigen IGBT-Moduls vorgesehen. Als IGBT (Insulated Gate Bipolar Transistor) bezeichnet man ein Vierschicht-Halbleiterbauelement, das mittels eines Gates gesteuert wird. IGBTs sind eine Weiterentwicklung von Leistungs-MOSFETs. Ausgangsseitig weisen IGBTs P-N-Halbleiterübergänge auf. Somit ist ein IGBT eine Art Kombination aus einem Feldeffekt-Halbleiterbauelement und einem Bipolar-Halbleiterbauelement. IGBTs werden in der Energieversorgungstechnik häufig in Form von Modulen mit drei Halbbrücken, d.h. sechs IGBT-Halbleiterschaltern, verwendet. Solche Module sind daher einfach und kostengünstig erhältlich. Die Erfindung zeigt einen eleganten Weg auf, die in einem dreiphasigen IGBT-Modul vorhandenen sechs Halbleiterschalter bzw. drei Halbbrücken effizient für den Aufbau eines Brückenmoduls einzusetzen. Gemäß einer vorteilhaften Weiterbildung der Erfindung ist in Reihe zu einem Brückenmodul oder einer Reihenschaltung von Brückenmodulen wenigstens eine Drossel geschaltet. Die Drossel bewirkt durch ihre Energiespeicherungseigenschaft einer Glättung des Stromverlaufs durch das Brückenmodul bzw. durch die Reihenschaltung von Brückenmodulen. Die Erfindung wird nachfolgend anhand von Ausführungsbeispielen unter Verwendung von Zeichnungen näher erläutert: Es zeigen: 1 bis 3 verschiedene Ausführungsformen von Brückenmodulen und4 einen modularen Multilevelmatrixkonverter und5 den Multilevelmatrixkonverter gemäß 4 mit abgeschalteten Stromrichterzweigen und6 einen Stromrichterzweig mit Trennschaltern und7 einen Stromrichterzweig mit schaltbaren elektrischen Verbindungseinrichtungen und8 den Multilevelmatrixkonverter gemäß 4 mit einem zusätzlichen redundanten Stromrichterzweig und9 einen Hexverter und10 einen Stromrichter mit einer Steuerungseinrichtung und11 bis 14 weitere Anwendungsbeispiele der Erfindung. In den Figuren werden gleiche Bezugszeichen für einander entsprechende Elemente verwendet. Die 1 zeigt ein Brückenmodul 1, das als Einrichtung zur Einbindung wenigstens einer Batterie in ein Energieversorgungsnetz geeignet ist. Das Brückenmodul 1 weist als externe Anschlüsse einen ersten Anschluss 2 und einen zweiten Anschluss 3 auf. Die Anschlüsse 2, 3 sind die Außenverbindungen des Brückenmoduls mit einem Energieversorgungsnetz, weiteren Brückenmodulen eines Stromrichterzweigs oder sonstigen Bauelementen. Das Brückenmodul 1 weist eine Vollbrückenschaltung 4 mit vier elektronischen Halbleiterschaltern 5, 6, 7, 8 auf. Zwischen zwei gegenüberliegenden Anschlusspunkten 116, 117 der Vollbrückenschaltung 4 ist ein Kondensator 9 angeschlossen. Die übrigen zwei gegenüberliegenden Anschlusspunkte 118, 119 der Vollbrückenschaltung 4 sind mit den Außenanschlüssen 2, 3 verbunden. Die Anschlusspunkte 116, 117 sind mit einem steuerbaren, bidirektionalen Gleichspannungswandler 10 verbunden, der als kombinierter Aufwärts-/Abwärtswandler ausgebildet ist. Der Gleichspannungswandler ist parallel zum Kondensator 9 geschaltet. Auf der gegenüberliegenden Anschlussseite des Gleichspannungswandlers 10 ist eine mit dem Gleichspannungswandler 10 verbundene Batterie 11 vorgesehen. Das Brückenmodul 1 weist außerdem eine lokale Steuereinheit 12 auf, z.B. in Form eines Mikroprozessors oder einer Logikschaltung. Die lokale Steuereinheit 12 ist mit Steueranschlüssen der Halbleiterschalter 5, 6, 7, 8 sowie mit einem Steuereingang des Gleichspannungswandlers 10 verbunden. Die lokale Steuereinheit 12 führt ein Steuerprogramm aus, mit dem die Funktion des Gleichspannungswandlers 10 sowie die Schaltzustände der Halbleiterschalter 5, 6, 7, 8 gesteuert werden. Die Halbleiterschalter 5, 6, 7, 8 der Vollbrücke 4 sind jeweils z.B. als IGBT ausgebildet. Ferner weist der Gleichspannungswandler 10 zwei weitere elektronische Halbleiterschalter 13, 14 auf, die z.B. als IGBT ausgebildet sind. Die Gateanschlüsse der Halbleiterschalter 13, 14 sind, ebenso wie die Gateanschlüsse der Halbleiterschalter 5, 6, 7, 8, mit der lokalen Steuereinheit 12 verbunden. Die lokale Steuereinheit 12 führt hierüber eine Steuerung des Gleichspannungswandlers 10 durch entsprechende Ansteuerung der Halbleiterschalter 13, 14 durch. Die Halbleiterschalter 13, 14 sind in Halbbrückenschaltung angeordnet. Hierbei ist der Kollektoranschluss des Halbleiterschalters 13 mit dem Anschlusspunkt 116 der Vollbrückenschaltung 4 verbunden. Der Emitteranschluss des Halbleiterschalters 14 ist mit dem Anschlusspunkt 117 der Vollbrückenschaltung 4 verbunden. Der Emitteranschluss des Halbleiterschalters 13 ist mit dem Kollektoranschluss des Halbleiterschalters 14 sowie mit einer Drossel 15 verbunden. Die Drossel 15 ist mit einem Anschluss der Batterie 11 verbunden, z.B. mit dem Pluspol. Ein zweiter Anschluss, z.B. der Minuspol, der Batterie 11 ist mit dem Emitteranschluss des Halbleiterschalters 14 und damit mit dem Anschlusspunkt 117 der Vollbrückenschaltung 4 verbunden. Die Verwendung der Halbleiterschalter 13, 14 sowie der Drossel 15 erlaubt einen einfachen und kostengünstigen Aufbau eines bidirektionalen, steuerbaren Gleichspannungswandlers, der damit als Aufwärtswandler ausgebildet ist. Zudem kann ein dreiphasiges IGBT-Modul verwendet werden, das bereits sechs IGBTs aufweist, die jeweils paarweise in Halbbrückenschaltung geschaltet sind. Hierbei kann eine erste Halbbrücke des IGBT-Moduls für die Anordnung der Halbleiterschalter 5, 6 verwendet werden, eine zweite Halbbrücke für die Halbleiterschalter 7, 8 und die dritte Halbbrücke für die Halbleiterschalter 13, 14. Die lokale Steuereinheit 12 ist über eine Leitung 16 mit einer zentralen elektronischen Steuerungseinrichtung verbunden, deren Aufbau und Funktion später noch erläutert wird. Die Leitung 16 kann z.B. ein Datenbus sein, z.B. ein serieller Datenbus. Über die Leitung 16 erhält die lokale Steuereinheit 12 Sollwerte, anhand derer sie die Vollbrückenschaltung 4 und den Gleichspannungswandler 10 steuert. Über die Leitung 16 übermittelt die lokale Steuereinheit 12 zudem Kennwerte an die zentrale elektronische Steuerungseinrichtung, z.B. den Ladungszustand des Kondensators 9 und/oder der Batterie 11. Die 2 zeigt eine weitere Ausführungsform eines Brückenmoduls 1. Das Brückenmodul 1 gemäß 2 ist vergleichbar aufgebaut wie das Brückenmodul 1 gemäß 1, jedoch ohne den Gleichspannungswandler 10 und die Batterie 11. Hierdurch kann ein einfacheres kostengünstigeres Brückenmoduls bereitgestellt werden, wenn eine kurzzeitige Energiespeicherung über den Kondensator 9 ausreichend ist. Die 3 zeigt eine weitere Ausführungsform eines Brückenmoduls 1. Das Brückenmodul 1 gemäß 3 ist vergleichbar aufgebaut wie das Brückenmodul 1 gemäß 2, jedoch ohne die Halbleiterschalter 7, 8. Hierdurch kann ein noch einfacheres kostengünstigeres Brückenmoduls bereitgestellt werden, wenn keine bipolaren Vollbrückenmodule, wie anhand der 1 und 2 beschrieben, erforderlich sind. Die beschriebenen Stromrichterzweige des Stromrichters können z.B. wahlweise mit Brückenmodulen der 1, 2 oder 3 bestückt sein. Die 4 zeigt einen modularen Stromrichter 20 in Form eines modularen Multilevelmatrixkonverters, der neun Stromrichterzweige 21, 22, 23, 24, 25, 26, 27, 28, 29 aufweist. Jeder Stromrichterzweig weist eine Reihenschaltung einer Mehrzahl von Brückenmodulen 1 auf. In der Reihenschaltung der Brückenmodule 1 kann zusätzlich eine Drossel 19 vorgesehen sein. In der 4 sind je Stromrichterzweig beispielha
[EN EP3729631B1]: MMC PHASE LEG AND METHOD FOR CONTROL THEREOF [FR EP3729631B1]: BRANCHE DE PHASE MMC ET PROCÉDÉ DE COMMANDE ASSOCIÉ [DE EP3729631B1]: MMC-PHASENZWEIG UND VERFAHREN ZU DESSEN STEUERUNG | [EN WO2019120468A1]: The present disclosure relates to a power converter phase leg (2) for a Modular Multilevel Converter, MMC, (1). The phase leg comprises a first cell arrangement (6) comprising a plurality of series connected converter cells (3). The phase leg also comprises a second cell arrangement (6) comprising a plurality of series-connected converter cells (3). The phase leg also comprises a breaker arrangement (B) comprising a plurality of breakers (B1, B2, B3) and arranged to enable alternately connecting the first and second cell arrangements in series and in parallel by means of said plurality of breakers. [FR WO2019120468A1]: L'invention concerne une branche de phase de convertisseur de puissance (2) d'un convertisseur modulaire multiniveaux (MMC) (1). La branche de phase comprend un premier agencement de cellules (6) comprenant une pluralité de cellules de convertisseur connectées en série (3). La branche de phase comprend également un second agencement de cellules (6) comprenant une pluralité de cellules de convertisseur connectées en série (3). La branche de phase comprend également un agencement de disjoncteur (B) comprenant une pluralité de disjoncteurs (B1, B2, B3) et conçu pour permettre de connecter alternativement les premier et second agencements de cellules en série et en parallèle au moyen de ladite pluralité de disjoncteurs. | WO2019120468A1 | 2019-06-27 | EP2017083252W | 2017-12-18 | EP2017083252W, 2017-12-18 | WO2019120468A1: 2019-06-27 EP3729631B1: 2021-09-15 | ABB SCHWEIZ AG ABB POWER GRIDS SWITZERLAND AG | MV ARAVIND NAMI ALIREZA | H02M7/493: I H02M1/00: I H02M7/483: I H02M7/49: I | H02M7/49: I H02M7/493: I H02M1/0077: A H02M7/4835: I | WO2017016675A1 US2014140104A1 US2015365011A1 | CN111342691A CN111342691 111342691 WO2021052730A1 WO2021052730 2021/052730 WO2021/052730A1 CN111665393A CN111665393 111665393 EP3796539A1 EP3796539 3796539 | [EN EP3729631B1]: A Modular Multilevel Converter, MMC, (1), comprising: a control system (10) arranged for controlling the MMC; anda power converter phase leg (2), the phase leg comprising: a first cell arrangement (6a) comprising a plurality of series connected converter cells (3);a second cell arrangement (6b) comprising a plurality of series-connected converter cells (3); anda breaker arrangement (B) comprising a plurality of breakers (B1, B2, B3) and arranged to enable alternately connecting the first and second cell arrangements in series and in parallel by means of said plurality of breakers;wherein the breaker arrangement comprises three breakers (B1, B2, B3) connected in series along a bus of the phase leg, where the first cell arrangement (6a) is connected across the first and second breakers (B1, B2) and the second cell arrangement (6b) is connected across the second and third breakers (B2, B3); andwherein the control system (10) comprises processing circuitry (11) and data storage (12) storing instructions (13) executable by said processing circuitry whereby said control system is operative to: obtain current information that a current through the phase leg is above a predetermined current threshold, and based on the obtained current information, by means of the plurality of breakers, connect the first and second cell arrangements in parallel; andobtain voltage information that a voltage across the phase leg is above a predetermined voltage threshold, and based on the obtained voltage information, by means of the plurality of breakers, connect the first and second cell arrangements in series;such that the first and second cell arrangements are alternatingly connected in series, when the voltage across the phase leg is high, and in parallel, when the current through the phase leg is high. The MMC of claim 1, wherein the first cell arrangement (6a) has a topology which is symmetrical to a topology of the second cell arrangement (6b). The MMC of claim 1, wherein the first cell arrangement (6a) has a topology which is asymmetrical to a topology of the second cell arrangement (6b). The MMC of any preceding claim, wherein the first and second cell arrangements (6a, 6b) in combination with the breaker arrangement (B) constitutes a module (7), and wherein the phase leg (2) comprises a plurality of series connected such modules. The MMC of claim 4, wherein the series connected modules all have the same topology. The MMC of any preceding claim, wherein the first and/or second cell arrangement comprises: a first cell sub-arrangement (6a) comprising a plurality of series connected converter cells (3);a second cell sub-arrangement (6b) comprising a plurality of series-connected converter cells (3); anda breaker sub-arrangement (B) comprising a plurality of breakers (B1, B2, B3) and arranged to alternately connect the first and second cell sub-arrangements in series and in parallel by means of said plurality of breakers. The MMC of any preceding claim, wherein the MMC (1) is a Static Synchronous Compensator, STATCOM, or a High-Voltage Direct Current, HVDC, converter. A method of controlling a power converter phase leg (2) of a Modular Multilevel Converter, MMC, (1), wherein voltage and current are in quadrature with each other such that the current through, and the voltage across, the phase leg do not reach their maximum at the same time, the phase leg comprising: a first cell arrangement (6a) comprising a plurality of series connected converter cells (3);a second cell arrangement (6b) comprising a plurality of series-connected converter cells (3); anda breaker arrangement (B) comprising a plurality of breakers (B1, B2, B3) wherein the breaker arrangement comprises three breakers (B1, B2, B3) connected in series along a bus of the phase leg, where the first cell arrangement (6a) is connected across the first and second breakers (B1, B2) and the second cell arrangement (6b) is connected across the second and third breakers (B2, B3);the method comprising: obtaining (M1) current information that a current through the phase leg is above a predetermined current threshold, andbased on the obtained (M1) current information, by means of the plurality of breakers, connecting (M2) the first and second cell arrangements in parallel; andobtaining (M3) voltage information that a voltage across the phase leg is above a predetermined voltage threshold, andbased on the obtained (M3) voltage information, by means of the plurality of breakers, connecting (M4) the first and second cell arrangements in series;such that the first and second cell arrangements are alternatingly connected in series, when the voltage across the phase leg is high, and in parallel, when the current through the phase leg is high. The method of claim 8, performed in a control system (10) comprised in the MMC (1). A computer program product (12) comprising computer-executable components (13) for causing a control system (10) to perform the method of any one of claims 8-9 when the computer-executable components are run on processing circuitry (11) comprised in the control system. [DE EP3729631B1]: Modularer mehrstufiger Umrichter, MMC, (1) umfassend: ein Steuersystem (10), das zum Steuern des MMC angeordnet ist; undeinen Leistungsumrichter-Phasenzweig (2), wobei der Phasenzweig umfasst: eine erste Zellenanordnung (6a), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst;eine zweite Zellenanordnung (6b), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst; undeine Unterbrecheranordnung (B), die mehrere Unterbrecher (B1, B2, B3) umfasst und so angeordnet ist, dass sie das abwechselnde Verbinden der ersten und der zweiten Zellenanordnung in Reihe und parallel mithilfe der mehreren Unterbrecher ermöglicht;wobei die Unterbrecheranordnung drei Unterbrecher (B1, B2, B3) umfasst, die entlang einer Sammelschiene des Phasenzweigs in Reihe geschaltet sind, wobei die erste Zellenanordnung (6a) über den ersten und zweiten Unterbrecher (B1, B2) verbunden ist und die zweite Zellenanordnung (6b) über den zweiten und dritten Unterbrecher (B2, B3) verbunden ist; undwobei das Steuersystem (10) eine Verarbeitungsschaltung (11) und einen Datenspeicher (12) umfasst, der Anweisungen (13) speichert, die durch die Verarbeitungsschaltung ausführbar sind, wodurch das Steuersystem betreibbar ist, um: Strominformationen zu erhalten, dass ein Strom durch den Phasenzweig über einem vorbestimmten Stromschwellenwert liegt, und basierend auf den erhaltenen Strominformationen mithilfe der mehreren Unterbrecher die erste und zweite Zellenanordnung parallel zu schalten; undSpannungsinformationen zu erhalten, dass eine Spannung über dem Phasenzweig über einem vorbestimmten Spannungsschwellenwert liegt, und basierend auf den erhaltenen Spannungsinformationen mithilfe der mehreren Unterbrecher die erste und zweite Zellenanordnung in Reihe zu schalten;so dass die erste und zweite Zellenanordnung abwechselnd in Reihe geschaltet sind, wenn die Spannung über dem Phasenzweig hoch ist, und parallel geschaltet sind, wenn der Strom durch den Phasenzweig hoch ist. MMC nach Anspruch 1, wobei die erste Zellenanordnung (6a) eine Topologie aufweist, die symmetrisch zu einer Topologie der zweiten Zellenanordnung (6b) ist. MMC nach Anspruch 1, wobei die erste Zellanordnung (6a) eine Topologie aufweist, die asymmetrisch zu einer Topologie der zweiten Zellanordnung (6b) ist. MMC nach einem der vorhergehenden Ansprüche, wobei die erste und zweite Zellenanordnung (6a, 6b) in Kombination mit der Unterbrecheranordnung (B) ein Modul (7) darstellen, und wobei der Phasenzweig (2) mehrere in Reihe geschaltete solche Module umfasst. MMC nach Anspruch 4, wobei die in Reihe geschalteten Module alle die gleiche Topologie aufweisen. MMC nach einem der vorhergehenden Ansprüche, wobei die erste und/oder die zweite Zellenanordnung umfasst: eine erste Zellunteranordnung (6a), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst;eine zweite Zellenunteranordnung (6b), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst; undeine Unterbrecher-Unteranordnung (B), die mehrere Unterbrecher (B1, B2, B3) umfasst und so angeordnet ist, dass sie abwechselnd die erste und die zweite ZellenUnteranordnung in Reihe und parallel mithilfe der mehreren Unterbrecher verbindet. MMC nach einem der vorhergehenden Ansprüche, wobei der MMC (1) ein statischer Synchronkompensator, STATCOM, oder ein Hochspannungs-Gleichstrom-Umrichter, HVDC-Umrichter, ist. Verfahren zum Steuern eines Leistungsumrichter-Phasenzweigs (2) eines modularen mehrstufigen Umrichters, MMC, (1), wobei Spannung und Strom in Quadratur zueinander stehen, so dass der Strom durch und die Spannung über den Phasenzweig nicht ihr Maximum zur gleichen Zeit erreichen, wobei der Phasenzweig umfasst: eine erste Zellenanordnung (6a), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst;eine zweite Zellenanordnung (6b), die mehrere in Reihe geschaltete Umrichterzellen (3) umfasst; undeiner Unterbrecheranordnung (B), die mehrere Unterbrecher (B1, B2, B3) umfasst, wobei die Unterbrecheranordnung drei Unterbrecher (B1, B2, B3) umfasst, die entlang eines Busses des Phasenzweigs in Reihe geschaltet sind, wobei die erste Zellenanordnung (6a) über den ersten und zweiten Unterbrecher (B1, B2) verbunden ist und die zweite Zellenanordnung (6b) über den zweiten und dritten Unterbrecher (B2, B3) verbunden ist;wobei das Verfahren umfasst: Erhalten (M1) von Strominformationen, dass ein Strom durch den Phasenzweig über einem vorbestimmten Stromschwellenwert liegt, undbasierend auf den erhaltenen (M1) Strominformationen, mithilfe der mehreren Unterbrecher, Parallelschalten (M2) der ersten und zweiten Zellenanordnungen; undErhalten (M3) von Spannungsinformationen, dass eine Spannung über dem Phasenzweig über einem vorbestimmten Spannungsschwellenwert liegt, undbasierend auf den erhaltenen (M3) Spannungsinformationen mithilfe der mehreren Unterbrecher, in Reihe schalten (M4) der ersten und zweiten Zellenanordnung;so dass die erste und zweite Zellenanordnung abwechselnd in Reihe geschaltet sind, wenn die Spannung über dem Phasenzweig hoch ist, und parallel geschaltet sind, wenn der Strom durch den Phasenzweig hoch ist. Verfahren nach Anspruch 8, durchgeführt in einem Steuersystem (10), das in dem MMC (1) umfasst ist. Computerprogrammprodukt (12), das computerausführbare Komponenten (13) umfasst, um ein Steuersystem (10) zu veranlassen, das Verfahren nach einem der Ansprüche 8 bis 9 durchzuführen, wenn die computerausführbaren Komponenten auf einer Verarbeitungsschaltung (11) ausgeführt werden, die in dem Steuersystem umfasst ist. [FR EP3729631B1]: Convertisseur modulaire multi-niveaux, MMC (1), comprenant : un système de commande (10) conçu pour commander le MMC ; etune branche de phase de convertisseur de puissance (2), la branche de phase comprenant : un premier agencement de cellules (6a) comprenant une pluralité de cellules de convertisseur connectées en série (3) ;un second agencement de cellules (6b) comprenant une pluralité de cellules de convertisseur connectées en série (3) ; etun agencement de disjoncteurs (B) comprenant une pluralité de disjoncteurs (B1, B2, B3) et conçu pour permettre la connexion alternée des premier et second agencements de cellules en série et en parallèle au moyen de ladite pluralité de disjoncteurs ;dans lequel l'agencement de disjoncteurs comprend trois disjoncteurs (B1, B2, B3) connectés en série le long d'un bus de la branche de phase, le premier agencement de cellules (6a) étant connecté aux bornes des premier et deuxième disjoncteurs (B1, B2) et le second agencement de cellules (6b) étant connecté aux bornes des deuxième et troisième disjoncteurs (B2, B3) ; etdans lequel le système de commande (10) comprend des circuits de traitement (11) et une mémoire de données (12) qui mémorise des instructions (13) exécutables par ledit circuit de traitement moyennant quoi ledit système de commande sert à : obtenir des informations de courant qu'un courant passant par la branche de phase dépasse un seuil de courant prédéterminé et en fonction des informations de courant obtenues, au moyen de la pluralité de disjoncteurs, connecter les premier et second agencements de cellules en parallèle ; etobtenir des informations de tension qu'une tension aux bornes de la branche de phase dépasse un seuil de tension prédéterminé, et en fonction des informations de tension obtenues au moyen de la pluralité de disjoncteurs, connecter les premier et second agencements de cellules en série ;de telle sorte que les premier et second agencements de cellules soient connectés alternativement en série quand la tension aux bornes de la branche de phase est élevée et en parallèle quand le courant à travers la branche de phase est élevé. MMC selon la revendication 1, dans lequel le premier agencement de cellules (6a) a une topologie qui est symétrique à une topologie du second agencement de cellules (6b). MMC selon la revendication 1, dans lequel le premier agencement de cellules (6a) à une topologie qui est asymétrique à une topologie du second agencement de cellules (6b). MMC selon n'importe quelle revendication précédente, dans lequel les premier et second agencements de cellules (6a, 6b) en combinaison avec l'agencement de disjoncteurs (B) constituent un module (7), et dans lequel la branche de phase (2) comprend une pluralité de tels modules connectés en série. MMC selon la revendication 4, dans lequel les modules connectés en série ont tous la même topologie. MMC selon n'importe quelle revendication précédente, dans lequel le premier et/ou le second agencement de cellules comprennent : un premier sous-agencement de cellules (6a) comprenant une pluralité de cellules de convertisseur connectées en série (3) ;un second sous-agencement de cellules (6b) comprenant une pluralité de cellules de convertisseur connectées en série (3) ; etun sous-agencement de disjoncteurs (B) comprenant une pluralité de disjoncteurs (B1, B2, B3) et conçu pour connecter alternativement les premier et second sousagencements de cellules en série et en parallèle au moyen de ladite pluralité de disjoncteurs. MMC selon n'importe quelle revendication précédente, le MMC (1) étant un compensateur synchrone statique, STATCOM, ou un convertisseur haute tension à courant continu, HVDC. Procédé de commande d'une branche de phase de convertisseur de puissance (2) d'un convertisseur modulaire multi-niveaux, MMC, (1), dans lequel la tension et le courant sont en quadrature l'une par rapport à l'autre de telle sorte que le courant passant par la branche de phase et la tension aux bornes de cette dernière n'atteignent pas leur maximum en même temps, la branche de phase comprenant : un premier agencement de cellules (6a) comprenant une pluralité de cellules de convertisseur connectées en série (3) ;un second agencement de cellules (6b) comprenant une pluralité de cellules de convertisseur connectées en série (3) ; etun agencement de disjoncteurs (B) comprenant une pluralité de disjoncteurs (B1, B2, B3), l'agencement de disjoncteurs comprenant trois disjoncteurs (B1, B2, B3) connectés en série le long d'un bus de la branche de phase, le premier agencement de cellules (6a) étant connecté aux bornes des premier et deuxième disjoncteurs (B1, B2) et le second agencement de cellules (6b) étant connecté aux bornes des deuxième et troisième disjoncteurs (B2, B3) ; etle procédé comprenant : l'obtention (Ml) d'informations de courant qu'un courant passant par la branche de phase dépasse un seuil de courant prédéterminé eten fonction des informations de courant obtenues (M1), au moyen de la pluralité de disjoncteurs, la connexion (M2) des premier et second agencements de cellules en parallèle ; etl'obtention (M3) d'informations de tension qu'une tension aux bornes de la branche de phase dépasse un seuil de tension prédéterminé, eten fonction des informations de tension obtenues (M3), au moyen de la pluralité de disjoncteurs, la connexion (M4) des premier et second agencements de cellules en série ;de telle sorte que les premier et second agencements de cellules soient connectés alternativement en série, quand la tension aux bornes de la branche de phase est élevée, et en parallèle, quand le courant à travers la branche de phase est élevé. Procédé selon la revendication 8, réalisé dans un système de commande (10) compris dans le MMC (1). Produit-programme informatique (12) comprenant des composantes exécutables par ordinateur (13) pour amener un système de commande (10) à réaliser le procédé selon l'une quelconque des revendications 8-9 quand les composantes exécutables par ordinateur sont exécutées sur des circuits de traitement (11) compris dans le système de commande. | [EN EP3729631B1]: TECHNICAL FIELD The present disclosure relates to a power converter phase leg of a Modular Multilevel Converter (MMC) and to a method for control thereof. BACKGROUND An MMC, also known as Chain-Link Converter (CLC), comprises a plurality of converter cells (also known as modules or submodules), serially connected in phase legs, which may comprise converter branches (also known as arms), that in turn may be arranged in a star (also known as Y or wye), double-star (double-Y/wye) or delta (Δ), direct or indirect converter topology. Each converter cell comprises, in the form of a half-bridge (also known as monopolar) or full-bridge (also known as H-bridge or bipolar) circuit, a capacitor for storing energy and power semiconductor switches such as Insulated Gate Bipolar Transistor (IGBT) devices, Gate-Turn-Off Thyristor (GTO) devices, Integrated Gate Commutated Thyristor (IGCT) devices or Metal-Oxide-Semiconductor Field-Effect Transistor (MOSFET) devices for connecting the capacitor to the converter branch with one or two polarities. Documents WO2017/016675, US2014/140104 and US2015/365011 are prior art to the present application. SUMMARY In a conventional MMC, each of the phase legs contains series connected full bridge (or half bridge) cells. Each of the legs is rated to 1 p.u. (per unit) voltage and 1 p.u. current considering normal operation. For unbalanced operation, there is current de-rating for a Static Synchronous Compensator (STATCOM) in delta configuration and voltage de-rating for a STATCOM in wye configuration. In order to balance the energies of the cell capacitors, the net power absorbed or given by each leg must be zero for STATCOM applications. This indicates that the voltage and current of each leg are in quadrature with each other, i.e. at maximum +/- voltage the current is zero, and at maximum +/- current the voltage is zero, the voltage and current being essentially sinusoidal. Hence, chain-link legs with 1 p.u. voltage and current is not required to generate these voltage and current waveforms. In accordance with the present invention, it has been realized that chain-link legs with lower current and voltage ratings may be series or parallel connected using breakers, also called director switches, to achieve the voltage and current waveforms. By doing so, a significant reduction in conduction losses and cell capacitor size can be achieved. Though STATCOM is considered as an example of study the same logic holds true also for other MMC, e.g. for High-Voltage Direct Current (HVDC) converter applications. The invention is defined by the features of device claim 1 and method claim 8. The dependent claims recite advantageous embodiments of the invention. According to an aspect of the present invention, there is provided a power converter phase leg for an MMC. The phase leg comprises a first cell arrangement comprising a plurality of series connected converter cells. The phase leg also comprises a second cell arrangement comprising a plurality of series-connected converter cells. The phase leg also comprises a breaker arrangement comprising a plurality of breakers and arranged to enable alternately connecting the first and second cell arrangements in series and in parallel by means of said plurality of breakers. According to another aspect of the present invention, there is provided an MMC comprising an embodiment of the phase leg of the present disclosure, and a control system arranged for controlling the MMC. According to another aspect of the present invention, there is provided a method of controlling a power converter phase leg of an MMC. The phase leg comprises a first cell arrangement comprising a plurality of series connected converter cells, a second cell arrangement comprising a plurality of series-connected converter cells, and a breaker arrangement comprising a plurality of breakers. The method comprises obtaining current information that a current through the phase leg is above a predetermined current threshold. The method also comprises, based on the obtained current information, by means of the plurality of breakers, connecting the first and second cell arrangements in parallel. The method also comprises obtaining voltage information that a voltage across the phase leg is above a predetermined voltage threshold. The method also comprises, based on the obtained voltage information, by means of the plurality of breakers, connecting the first and second cell arrangements in series. According to another aspect of the present invention, there is provided a computer program product comprising computer-executable components for causing a control system to perform an embodiment of the method of the present disclosure when the computer-executable components are run on processing circuitry comprised in the control system. By being able to alternately connecting the first and second cell arrangements in either series or parallel, semiconductor devices having lower voltage and/or current ratings may be used in the converter cells, since the current through and voltage across the converter leg (or arm, if the leg comprises more than one, e.g. two, arms) do not both reach their +/- maximum at the same time, i.e. none of the semiconductor devices will need to withstand maximum voltage and maximum current at the same time. Rather, the cell arrangements may alternatingly be connected in series (when the voltage is high) and in parallel (when the current is high), reducing the ratings needed, thus also reducing the cost of the semiconductor devices. The current information and voltage information, respectively, may be obtained based on real-time voltage and/or current measurements, preferably voltage measurements, in the MMC. With knowledge of the relationship between the voltage and current (they are typically in quadrature with each other) it may be enough to measure either of the current and the voltage, e.g. the voltage, in order to also know the other one of the current and the voltage, e.g. the current. Alternatively, especially if the relationship between the voltage and current is known, the current and voltage information may be obtained without real-time measurements of either voltage and current. The current and voltage information may e.g. be based on time points when firing pulses are sent to the switches/valves of the converter cells. It is to be noted that any feature of any of the aspects may be applied to any other aspect, wherever appropriate. Likewise, any advantage of any of the aspects may apply to any of the other aspects. Other objectives, features and advantages of the enclosed embodiments will be apparent from the following detailed disclosure, from the attached dependent claims as well as from the drawings. Generally, all terms used in the claims are to be interpreted according to their ordinary meaning in the technical field, unless explicitly defined otherwise herein. All references to "a/an/the element, apparatus, component, means, step, etc." are to be interpreted openly as referring to at least one instance of the element, apparatus, component, means, step, etc., unless explicitly stated otherwise. The steps of any method disclosed herein do not have to be performed in the exact order disclosed, unless explicitly stated. The use of "first", "second" etc. for different features/components of the present disclosure are only intended to distinguish the features/components from other similar features/components and not to impart any order or hierarchy to the features/components. BRIEF DESCRIPTION OF THE DRAWINGS Embodiments will be described, by way of example, with reference to the accompanying drawings, in which: Fig 1a is a schematic diagram of an embodiment of an MMC in delta (Δ) configuration, in accordance with the present invention.Fig 1b is a schematic diagram of an embodiment of an MMC in wye (Y) configuration, in accordance with the present invention.Fig 1c is a schematic diagram of an embodiment of an MMC in double-wye (also known as double-star) configuration, in accordance with the present invention.Fig 2 is a schematic diagram of an embodiment of a converter cell of an MMC, in accordance with the present invention.Fig 3 is a schematic diagram of an embodiment of a part of an MMC phase leg, comprising two cell arrangements (one of which is shown in a zoom view) and associated breakers arranged to connect the cell arrangements in either parallel or series, in accordance with the present invention.Fig 4 is a schematic diagram of an embodiment of a part of an MMC phase leg, comprising a plurality of series connected cell modules, each module comprising two cell arrangements (e.g. as in figure 3), in accordance with the present invention.Fig 5 is a schematic block diagram of an embodiment of a control system of an MMC, in accordance with the present invention.Fig 6 is a schematic flow chart of an embodiment of a method of the present invention. DETAILED DESCRIPTION Embodiments will now be described more fully hereinafter with reference to the accompanying drawings, in which certain embodiments are shown. However, other embodiments in many different forms are possible within the scope of the present disclosure. Rather, the following embodiments are provided by way of example so that this disclosure will be thorough and complete, and will fully convey the scope of the disclosure to those skilled in the art. Like numbers refer to like elements throughout the description. Figures 1a and 1b illustrate different MMC configurations, delta configuration in figure 1a and wye configuration in figure 1b. In each case, the MMC 1 comprises three phase legs 2, each thus comprising only one arm/branch, each leg (and thus arm) comprising a plurality of converter cells 3, here conventionally series connected. In applications where each leg 2 comprises a plurality of arms 4, such as in case of e.g. a double-wye configuration as depicted in figure 1c where each leg 2 comprises two arms 4. What is herein said about a phase leg 2 may thus be relevant for each arm 4 of a configuration where a phase leg comprises more than one arm. The delta connected MMC 1 of figure 1a may e.g. be comprised in a STATCOM of a three-phase alternating current (AC) system, having the three phases U, V and W, and thus the voltages Vu, Vv and Vw, and currents iu, iv and iw, as shown in the figure. The wye connected MMC 1 in figure 1b may e.g. be between an three-phase AC network and a DC network, e.g. a HVDC network, where each of the three phase legs 2a, 2b and 2c correspond to a phase of the AC network and all connect to the DC network. The MMC 1 also comprises a control system 10, as schematically illustrated in figures 1a and 1b. Figure 2 illustrates an MMC cell 3, e.g. of a converter 1 as illustrated in figures 1a and 1b. The cell 3 comprises an energy storage 5, typically a capacitor arrangement comprising at least one capacitor, over which a DC voltage of the cell is formed. A plurality of semiconductor switches S form a half-bridge (also called monopolar) or full-bridge (also called H-bridge or bipolar) topology, herein (as is preferred in some embodiments of the invention) four semiconductor switches S1-S4 form a full-bridge topology. The converter cells 3 used in embodiments of the present invention may be half or full bridge cells depending on the application and requirement. The industrial Insulated-Gate Bipolar Transistor (IGBT), e.g. linpak (or) low voltage IGBT, may be a convenient choice as semiconductor device in the switches S in the cells. However, other semiconductor devices may additionally or alternatively be used, such as Integrated Gate-Commutated Thyristor (IGCT) or silicon carbide (SiC) devices, etc. It is to be noted that the cell arrangements 6 may need some inductance in series with the cells 3 therein to control the circulating current between the cell arrangements when they are connected in parallel. If an inductance is added in series with the cells in each cell arrangement, e.g. in a module 7, the effective inductance of any smoothing reactor at the MMC arm or leg 2 level could be reduced. Also, another option could be to add a small inductor to only one of the cell arrangements in a module. The idea may then be to use this one cell arrangement in the module as a current source and the other cell arrangement in that module as a voltage source. This may give more flexibility when the connection of the cell arrangements is changed from series to parallel or vice versa. However, such an arrangement may lose the mechanical symmetry of the module topology. Figure 3 illustrates a series-parallel hybrid part or module 7 of chain-link arm of a phase leg 2 in accordance with the present invention, for MMC topologies, e.g. for Flexible Alternating Current Transmission Systems (FACTS) applications. For example for STATCOM application, the voltage and current are in quadrature with each other which ensures that the peaks of voltage and current, respectively, do not happen at the same time (which is also true for e.g. HVDC applications). Hence, the idea is to have two lesser voltage and current rated chain-link arms 6, herein called cell arrangements, which can be connected in series or parallel, alternately, to meet the voltage and current requirements, respectively, using director switches, herein called breakers. The phase leg 2 comprises a first cell arrangements 6a and a second cell arrangement 6b, each comprising a plurality of series-connected converter cells 3. The first and second cell arrangements 6 may each comprise the same number of cells 3, or the first cell arrangement 6a may comprise a different number of cells 3 compared to the second cell arrangement 6b. Similarly, the cells in the first cell arrangement 6a may be arranged in the same topology as the cells in the second cell arrangement 6b, or the cells in the first cell arrangement 6a may be arranged in a different topology compared to the cells in the second cell arrangement 6b. The most simple topology, and often preferred, for the first and/or the second cell arrangement (preferably both) is with all cells 3 in the cell arrangement 6 connected in series, as shown in figure 3 for the second cell arrangement 6b. However, other topologies for the cells in either or both cell arrangements 6a and 6b are contemplated, as long as the topology comprises a plurality of series connected cells 3. For instance, the topology in either or both cell arrangements 6a and 6b may comprise two parallel connected chains of series connected cells 3. A breaker arrangement B comprising a plurality of breakers (diverter switches) is arranged to alternately connect the first and second cell arrangements 6 in parallel and in series with each other. For example, as shown in figure 3, the breaker arrangement B may comprise three breakers, B1, B2 and B3 along a bus of the phase leg 2, where the first cell arrangement 6a is connected across the first and second breakers B1 and B2, and the second cell arrangement is connected across the second and third breakers B2 and B3. In this way, the first and second cell arrangements 6a and 6b are connected in series when the first and third breakers B1 and B3 are open (not conducting) and the second breaker B2 is closed (conducting). Conversely, the first and second cell arrangements 6a and 6b are connected in parallel when the first and third breakers B1 and B3 are closed (conducting) and the second breaker B2 is open (not conducting). It is to be noted that when the cell arrangements 6 are connected in parallel, a circulating current may flow depending on the capacitor charge levels in the cell arrangements. Hence, a smoothing reactor may be included in series with either or both of the cell arrangements to limit and control the circulating current if desired. Each of the breakers may be of any suitable type, including a mechanical circuit breaker/switch or a semiconductor switch e.g. comprising a, or a plurality of, semiconductor switch S as discussed herein. For instance, the breaker arrangement may comprise a series connection of semiconductor switches S, e.g. a series connection of converter cells 3. The breakers of the breaker arrangement B may comprise bi-directional switches, e.g. conduct and block voltage in both directions with a gate command. It may be desirable to use only one switch per breaker to reduce the complexity compared with series connection of switches in each breaker. Hence, the choice of semiconductor switch for the breaker may be any of e.g. Reverse-Blocking IGBT (RB-IGBT), Reverce-Blocking IGCT (RB-IGCT), Bi-directional Conducting Thyristor (BCT), Bidirectional SiC switches, etc. Using BCT may be convenient in terms of conduction losses and robustness. But, for the commutation of thyristors, the cell arrangements may need to generate reverse voltage from its current voltage state for a duration of thyristor commutation time (tq). This may increase the switching losses and also generates voltage notches on the generated AC voltage waveform. The distortion on the generated AC voltage can be eliminated by sequential turn-off of the thyristors one by one among the various modules 7 and using a cell arrangement 6 of other module to generate an exact opposite voltage to compensate for the AC side notches utilizing the voltage over-rating from redundancy. By this method the AC side notches may be eliminated completely, but still there may be higher switching losses and over-rating of the converter as the thyristors are commutated module by module. Note, that with this method the net transition from parallel to series or vice versa for all the modules may happen with a time duration of tq*No. of modules. Hence, the voltage rating of the modules may need to be Vrating=cos2πtqNmoduleƒb+sin−1Irating, to accommodate this effect as well. Thus, it may be desired to have lesser commutation time for the thyristors, e.g. in the range of 100 µs to 200 µs. Due to the complexity introduced by the thyristors, it may be preferred to use RB-IGBT's or RB-IGCT's for the breakers of the breaker arrangement(s) B. In a specific embodiment, the topology in either or both cell arrangements 6a and 6b comprises first and second cell arrangements with breakers arranged for alternately connecting them in series or parallel, i.e. a cell arrangement 6 may itself contain the topology of a phase leg module 7 shown in figure 3 (see also figure 4 with modules 7). The topology of a module 7 may thus recursively also occur in any or both of the cell arrangements 6a and 6b. For ease of reading, cell arrangements occurring recursively within a cell arrangement is herein called a sub-arrangement. Thus, the first and/or second cell arrangement may comprise a first cell sub-arrangement 6a comprising a plurality of series connected converter cells 3, a second cell sub-arrangement 6b comprising a plurality of series-connected converter cells 3, and a breaker sub-arrangement B comprising a plurality of breakers B1, B2 and B3 and arranged to alternately connect the first and second cell sub-arrangements in series and in parallel by means of said plurality of breakers. For STATCOM, and other, applications, the voltage and currents are in quadrature with each other. Hence, the voltage and current rating Vrating and Irating of the cell arrangements 6 are chosen to meet the voltage and current requirement for rated zero power factor operation either by connecting the cell arrangements in series or parallel mode. Some of the voltage and current rating of the cell arrangements for which rated zero power factor operation is feasible is shown in Table 1. For case #1 shown in the table, the cell arrangements are connected in parallel when the voltage is between ±0.5 p.u. and connected in series otherwise. For zero power factor operation, the current is 0.866 p.u. when the voltage is 0.5 p.u. which dictates the current requirement. Table1Case No.Voltage (V) [p.u.]Current (I) [p.u.]#10.50.866#20.7070.707#30.8660.5 Similarly the other cases (#2 and #3) shown in Table 1 can be arrived at. A simple equation relating the voltage and current rating is given by Equation 1. The equation is valid for voltage rating greater than 0.5 p.u. when the current input to the equation is between 0.5 p.u to 1 p.u. Vrating=cossin−1Irating,where0.5&lt;Irating&lt;0.866 It is to be noted that it may be beneficial to have lower current ratings since they have a direct impact on the conduction losses, cell capacitance and cost reduction on the auxiliary components like bus bars, cell capacitors and other protection equipment etc. Hence, the chosen voltage and current rating for the cell arrangements 6 and breakers B for the MMC leg 2 may be chosen as e.g. 0.866 p.u. and 0.5 p.u., respectively. Figure 4 illustrates a part of an arm of a phase leg 2, comprising a plurality of modules 7, as in figure 3, in series. In the figure, three series connected modules are shown but any number of series connected modules may be used in different embodiments. By the use of a plurality of modules 7 in series, more flexibility is allowed for the number of cell arrangements 6 which may at any time be connected in series and in parallel. For example, in the example of figure 4 with three series connected modules 7, each with two cell arrangements 6 for a total of six cell arrangements, all six cell arrangements may be connected in series (if, in each module 7, the first and third breakers B1 and B3 are open and the second breaker B2 is closed), or three parallel connected pairs of cell arrangements may be in series (if, in each module 7, the first and third breakers B1 and B3 are closed and the second breaker B2 is open), but it is also possible to allow the cell arrangements 6 of some module(s) 7 to be connected in series while the cell arrangements of some other module(s) are connected in parallel. Thereby, the proposed hybrid arms/legs 2 may be further scaled down to modules 7. Each of the modules may represent one stack where several such stacks in series form one arm of the phase leg 2 of the MMC 1. It may be convenient to have two to four cells 3 per cell arrangement 6 in each module 7 so that a single position high voltage reverse blocking switch can be used for the breakers (director valves) of the breaker arrangement B of each module 7. The ability to modularize aids in scalability and redundancy of the converter design. Figure 5 schematically illustrates an embodiment of a control system 10 for or comprised in an MMC 1 of the present disclosure. The control system 10 comprises processing circuitry 11 e.g. a central processing unit (CPU). The processing circuitry 11 may comprise one or a plurality of processing units in the form of microprocessor(s). However, other suitable devices with computing capabilities could be comprised in the processing circuitry 11, e.g. an application specific integrated circuit (ASIC), a field programmable gate array (FPGA) or a complex programmable logic device (CPLD). The processing circuitry 11 is configured to run one or several computer program(s) or software (SW) 13 stored in a data storage 12 of one or several storage unit(s) e.g. a memory. The storage unit 12 is regarded as a computer readable means as discussed herein and may e.g. be in the form of a Random Access Memory (RAM), a Flash memory or other solid state memory, or a hard disk, or be a combination thereof. The processing circuitry 11 may also be configured to store data in the storage 12, as needed. The control system 10 may also comprise a communication interface for internal communication within the system and/or external communication with e.g. the other parts of the MMC, e.g. for sending firing pulses to the switches S of the converter cells 3. The control system may be centralized or distributed, or (typically) a combination thereof with a central part, e.g. located in a control room, and a local part, co-located with the phase leg 2, e.g. comprising local controllers with each of the cells 3 of the phase leg. When the topology of a cell arrangement 6 or module 7 is discussed herein, the number and connection of cells 3 therein is intended. For instance, if two entities (e.g. cell arrangements or modules) are symmetrical (have the same topology), they each contain the same number of cells 3 which are all connected in the same way as in the other entity. Conversely, if two entities (e.g. cell arrangements or modules) are asymmetrical (differ in topology) they differ in either how many cells 3 are in each entity and/or in how the cells are connected (e.g. in series or parallel). Mirror symmetrical entities are regarded as symmetrical, having the same topology. In some embodiments of the present invention, the first cell arrangement 6a has a topology which is symmetrical to a topology of the second cell arrangement 6b. The cell arrangements thus each contains the same number of cells, connected in the same way. In some other embodiments of the present invention, the first cell arrangement 6a has a topology which is asymmetrical to a topology of the second cell arrangement 6b. In some embodiments of the present invention, the first and second cell arrangements 6a and 6b in combination with the breaker arrangement B constitutes a module 7, and the phase leg 2 comprises a plurality of series connected such modules. In some embodiments, the series connected modules all have the same topology, i.e. are symmetrical in relation to each other. Figure 6 is a schematic flow chart of an embodiment of the method of the present invention. The method is for controlling a power converter phase leg 2 of an MMC 1. The phase leg 2 comprises a first cell arrangement 6 comprising a plurality of series connected converter cells 3, a second cell arrangement 6 comprising a plurality of series-connected converter cells 3, and a breaker arrangement B comprising a plurality of breakers B1, B2 and B3. The method comprises obtaining M1 current information that a current through the phase leg is above a predetermined current threshold. The method also comprises, based on the obtained M1 current information, by means of the plurality of breakers, connecting M2 the first and second cell arrangements in parallel. Before or after steps M1 and M2, the method also comprises obtaining M3 voltage information that a voltage across the phase leg is above a predetermined voltage threshold. Then the method also comprises, based on the obtained M3 voltage information, by means of the plurality of breakers, connecting M4 the first and second cell arrangements in series. Thus, steps M3 and M4 may be performed either before or after steps M1 and M2. In some embodiments, the control system 10 may be arranged to perform embodiments of the method of the present disclosure, especially when comprised in an MMC 1 comprising at least one phase leg 2 comprising a first cell arrangement 6 comprising a plurality of series connected converter cells 3, a second cell arrangement 6 comprising a plurality of series-connected converter cells 3, and a breaker arrangement B comprising a plurality of breakers B1, B2 and B3. Thus, the control system 10 may comprise processing circuitry 11, and data storage 12 storing instructions 13 executable by said processing circuitry 11 whereby said control system 10 is operative to obtain M1 current information that a current through the phase leg is above a predetermined current threshold; based on the obtained M1 current information, by means of the plurality of breakers, connect M2 the first and second cell arrangements in parallel; obtain M3 voltage information that a voltage across the phase leg is above a predetermined voltage threshold; and based on the obtained M3 voltage information, by means of the plurality of breakers, connecting M4 the first and second cell arrangements in series. Embodiments of the present invention may be conveniently implemented using one or more conventional general purpose or specialized digital computer, computing device, machine, or microprocessor, including one or more processors 11, memory and/or computer readable storage media 12 programmed according to the teachings of the present disclosure. Appropriate software 13 coding can readily be prepared by skilled programmers based on the teachings of the present disclosure, as will be apparent to those skilled in the software art. In some embodiments, the present invention includes a computer program product 12 which is a non-transitory storage medium or computer readable medium (media) having instructions 13 stored thereon/in, in the form of computer-executable components or SW, which can be used to program a computer to perform any of the methods/processes of the present invention. Examples of the storage medium can include, but is not limited to, any type of disk including floppy disks, optical discs, DVD, CD-ROMs, microdrive, and magneto-optical disks, ROMs, RAMs, EPROMs, EEPROMs, DRAMs, VRAMs, flash memory devices, magnetic or optical cards, nanosystems (including molecular memory ICs), or any type of media or device suitable for storing instructions and/or data. The present disclosure has mainly been described above with reference to a few embodiments. However, as is readily appreciated by a person skilled in the art, other embodiments than the ones disclosed above are equally possible within the scope of the present disclosure, as defined by the appended claims.
[ZH CN110707699B]: 一种模块化多电平混合式配电变压器 [EN CN110707699B]: Modular multilevel hybrid distribution transformer | [ZH CN110707699B]: 本发明公开一种模块化多电平混合式配电变压器，包括由多个功率单元子模块构成的模块化多电平变流器及变压器本体。变流器包含模块化多电平并联变流器和模块化多电平串联变流器，两者都由多个功率单元子模块构成，模块化多电平并联变流器接入电流补偿绕组，通过磁势平衡原理调控电网电流；模块化多电平串联变流器接入电压补偿绕组调节负载电压；所述变压器本体包括主变压器、副变压器及滤波电感。其中，主变压器每相包括一个主边绕组，一个副边绕组和一个电流补偿绕组，副变压器每相包括一个串联绕组和一个电压补偿绕组。采用模块化多电平混合式配电变压器能降低器件的开关频率，减小高次谐波，可以在更大功率场合的应用。 [EN CN110707699B]: The invention discloses a modular multi-level hybrid distribution transformer. The modular multi-level hybrid distribution transformer comprises a modular multi-level converter and a transformer body,wherein the modular multi-level converter is composed of a plurality of power unit submodules. The converter comprises a modular multi-level parallel converter and a modular multi-level series converter, the modular multi-level parallel converter and the modular multi-level series converter are each composed of a plurality of power unit sub-modules, the modular multi-level parallel converter is connected into a current compensation winding, and the power grid current is regulated and controlled through the magnetic potential balance principle. The modular multi-level series converter is connected to the voltage compensation winding to adjust the load voltage; the transformer body comprises a main transformer, an auxiliary transformer and a filter inductor. Each phase of the main transformer comprises a main side winding, a secondary side winding and a current compensation winding, and each phase of the secondary transformer comprises a series winding and a voltage compensation winding. By adopting the modular multi-level hybrid distribution transformer, the switching frequency of a device can be reduced, higher harmonics can be reduced, and the modular multilevel hybrid distribution transformer can be applied to occasions with higher power. | CN110707699B | 2020-01-17 2021-05-28 | CN201911078170A | 2019-11-06 2019-11-06 | CN201911078170A, 2019-11-06 CN201911078170A, 2019-11-06 | CN110707699B: 2021-05-28 | UNIV XI AN JIAOTONG 西安交通大学 | ZHOU KUN LIANG DELIANG LIU YIBIN CAI SHENGLIANG LUO YATING ZHANG LISHI | H02J3/01: I H02J3/18: I | H02J3/01: I H02J3/1878: I Y02E40/20: A Y02E40/30: A Y02E40/40: A | CN106655805A CN205377675U CN107546983A |  | [ZH CN110707699B]: 1 .一种模块化多电平混合式配电变压器，其特征在于：该配电变压器包括变压器本体 以及模块化多电平变流器，所述变压器本体包括主变压器模块与副变压器模块，所述主变 压器每相的绕组包括一个主边绕组、一个副边绕组及一个电流补偿绕组，所述副变压器每 相的绕组包括一个串联绕组，一个电压补偿绕组;主变压器的主边绕组与串联绕组首先连 成一个整体，然后采用三角形接法接入电网，三相副边绕组、三相电流补偿绕组及三相电压 补偿绕组均采用星型中性点引出接法，所述模块化多电平变流器包括与混合式配电变压器 中的电流补偿绕组相连的模块化多电平并联变流器和与混合式配电变压器中的电压补偿 绕组相连的模块化多电平串联变流器，模块化多电平并联变流器与模块化多电平串联变流 器的每个桥臂均由多个采用IGBT半桥与直流电容构成的子模块串联构成。 2 .根据权利要求1所述一种模块化多电平混合式配电变压器，其特征在于:模块化多电 平并联变流器与模块化多电平串联变流器的每个桥臂均由多个采用IGBT半桥与直流电容 构成的子模块串联构成，两个变流器共用一个高压直流母线电容，该直流母线电容由两个 电容串联而成，中点引出，模块化多电平并联变流器、模块化多电平串联变流器各自的交流 侧均接有滤波电感。 3 .根据权利要求1所述一种模块化多电平混合式配电变压器，其特征在于:模块化多电 平变流器借助载波相移等多电平调制技术进行信号调制以减小补偿电流中的高次谐波含 量，同时，由于级联的结构可以满足大容量高电压的设备需求。 4 .根据权利要求1所述一种模块化多电平混合式配电变压器，其特征在于:模块化多电 平混合式配电变压器的电流补偿绕组的首端接入模块化多电平并联变流器的输出端，模块 化多电平混合式配电变压器的电压补偿绕组的首端接入模块化多电平串联变流器的输出 端，模块化多电平混合式配电变压器的电流补偿绕组及模块化多电平混合式配电变压器的 电压补偿绕组的末端接入高压直流母线电容中点。 5 .根据权利要求2所述一种模块化多电平混合式配电变压器，其特征在于:所述模块化 多电平并联变流器及模块化多电平串联变流器各个桥臂的功率单元模块数目相等，各功率 单元彼此独立，各模块的直流电容能对外提供多个彼此隔离的直流电源。 [EN CN110707699B]: 1 A modular multi-level hybrid distribution transformer, characterized in that: the distribution transformer includes a transformer body and a modular multi-level converter, the transformer body includes a main transformer module and an auxiliary transformer module, the The windings of each phase of the main transformer include a main winding, a secondary winding, and a current compensation winding. The windings of each phase of the auxiliary transformer include a series winding and a voltage compensation winding. The main winding and the series winding of the main transformer are first Connected as a whole, and then connected to the power grid by delta connection. The three-phase secondary winding, the three-phase current compensation winding and the three-phase voltage compensation winding all adopt the star-shaped neutral point lead connection method. The modular multi-level change The converter includes a modular multi-level parallel converter connected to the current compensation winding in the hybrid distribution transformer and a modular multi-level series converter connected to the voltage compensation winding in the hybrid distribution transformer. Modules Each bridge arm of the modular multilevel parallel converter and the modular multilevel series converter is composed of multiple sub-modules composed of IGBT half bridges and DC capacitors in series. 2 The modular multi-level hybrid distribution transformer according to claim 1, wherein each bridge arm of the modular multi-level parallel converter and the modular multi-level series converter is composed of Multiple sub-modules composed of IGBT half-bridges and DC capacitors are connected in series, and the two converters share a high-voltage DC bus capacitor. The DC bus capacitor is formed by two capacitors connected in series, the midpoint is led out, and the modular multi-level parallel connection The AC side of the converter and the modular multilevel series converter are all connected with filter inductors. 3 The modular multi-level hybrid distribution transformer according to claim 1, characterized in that: the modular multi-level converter uses multi-level modulation techniques such as carrier phase shift to perform signal modulation to reduce the compensation current At the same time, due to the cascaded structure, it can meet the needs of large-capacity and high-voltage equipment. 4 The modular multi-level hybrid distribution transformer according to claim 1, characterized in that: the head end of the current compensation winding of the modular multi-level hybrid distribution transformer is connected to the modular multi-level parallel transformer The output end of the current transformer, the first end of the voltage compensation winding of the modular multi-level hybrid distribution transformer is connected to the output end of the modular multi-level series converter, and the current of the modular multi-level hybrid distribution transformer The end of the voltage compensation winding of the compensation winding and the modular multilevel hybrid distribution transformer is connected to the midpoint of the high-voltage DC bus capacitor. 5 The modular multilevel hybrid distribution transformer according to claim 2, characterized in that: the power of each bridge arm of the modular multilevel parallel converter and the modular multilevel series converter The number of unit modules is equal, each power unit is independent of each other, and the DC capacitor of each module can provide multiple isolated DC power supplies to the outside. | [ZH CN110707699B]: 一种模块化多电平混合式配电变压器 技术领域 [0001]本发明涉及一种模块化多电平混合式配电变压器，属于变压器技术领域。 背景技术 [0002]传统配电变压器运行可靠，具备电压等级变换，电能传输等基本功能。而智能电网 的发展对配电变压器的可控性提出了很高的要求。于是ABB科研机构的Sandeep bala、 Jyoti Sastry等学者提出了混合式配电变压器的设计思想。其显著特点是，将模块化多电 平变流器接入配电变压器中，通过变流器变换部分功率实现配电变压器的高可控性，因而 非常适合作为下一代配电网用智能变压器。 [0003] 在目前的大部分配电场景中，负荷容量往往很大，虽然混合式配电变压器中的变 流器仅仅承担总功率的一部分。但由于负荷容量大，此时，仍需要变流器具备很大的容量。 从而使现有的混合式配电变压器在大容量场合的应用受到了限制。 [0004] 现有的发明中通过多绕组变压器方案实现了一种适用于大容量场合的混合式配 电变压器，但绕组较多，变流器单元较多。变流器实质上采用并联方案，存在环流。于是提出 将模块化多电平技术与混合式配电变压器相结合的方式。 发明内容 [0005]为解决现有技术中存在的上述缺陷，本发明的目的在于提供一种模块化多电平混 合式配电变压器。将模块化多电平变流器接入配电变压器中，通过较高的直流母线电压实 现了混合式配电变压器的大容量。 [0006]为达到上述目的，本发明采用了以下技术方案： [0007] 一种模块化多电平混合式配电变压器，该模块化多电平混合式配电变压器主要由 两部分组成，分别为变压器本体及模块化多电平变流器。上述变压器由主变压器模块和串 联变压器模块构成;上述模块化多电平变流器为由多个功率单元子模块级联构成的模块化 多电平并联变流器与模块化多电平串联变流器构成，每个桥臂均由多个采用IGBT半桥与直 流电容构成的子模块串联构成。模块化多电平变流器的模块化多电平并联变流器与变压器 本体的电流补偿绕组相连，模块化多电平变流器的模块化多电平串联变流器与变压器本体 的电压补偿绕组相连。 [0008]模块化多电平模块化多电平变流器主要分为两个部分，模块化多电平并联变流器 与模块化多电平串联变流器，模块化多电平并联变流器与模块化多电平串联变流器共用一 个高压直流母线电容，该直流母线电容由两个电容串联而成，中点引出。 [0009]模块化多电平变流器借助载波相移等多电平调制技术进行信号调制以减小补偿 电流中的高次谐波含量，同时，由于级联的结构可以满足大容量高电压的设备需求。 [0010] 所述主变压器由三相绕组构成，每相绕组包括一个主边绕组（AXrBJrC.1）、一 个副边绕组（a2x2、b2y2、c2z2）及一个电流补偿绕组（a3x3、b3y3、c3z3），同时所述串联变压器模 块也由三相绕组构成，每相绕组包括一个串联绕组（a4x4、b4y4、c4z4）及一个电压补偿绕组 （a5x5、b5y5、c5z5）；主变压器的主边绕组与串联绕组首先连成一个整体，然后采用三角形接 法接入电网。三相副边绕组、三相电流补偿绕组及三相电压补偿绕组均采用星型中性点引 出接法。 [0011]所述模块化多电平变流器的模块化多电平并联变流器负责通过补偿负载无功电 流和谐波电流来实现补偿负载的无功功率。所述模块化多电平变流器的模块化多电平串联 变流器负责满足在电网输入电压有谐波、非额定、不对称情况下负载端对电压的要求。所述 模块化多电平变流器单元由六个相单元构成，每个相单元均有上、下两个桥臂，每个桥臂由 多个子模块构成，每个子模块由一个作为开关单元的IGBT半桥和一个直流电容构成。所述 模块化多电平并联变流器及模块化多电平串联变流器各个桥臂的功率单元模块数目相等。 各功率单元彼此独立，各模块的直流电容能对外提供多个彼此隔离的直流电源。 [0012]与现有技术相比，本发明至少具有以下技术效果： [0013] 本发明在混合式配电变压器的基础上，采用基于模块化多电平技术的变流器，有 效提高了混合式配电变压器的补偿容量。同时，借助载波相移等多电平调制技术来控制模 块化电平变流器单元，可以在采用较低开关频率的期间等效实现相同的开关效率，从而有 效地减少混合式配电变压器的负载电压及电网电流中的高频谐波。 附图说明 [0014] [0015] [0016] 图1为模块化多电平混合式配电变压器的整体结构示意图。 图2为模块化多电平混合式配电变压器变流器的一个功率单元子模块示意图。 图1中标注了各元件的连接端子。 具体实施方式 [0017]为了更加清晰说明本发明的目的、技术方案及优点，以下结合附图及实施例对本 发明进行进一步详细说明。此处所述的实施例子仅仅用以解释本发明，并不用于限定本发 明。 [0018]本发明所述的模块化多电平混合式配电变压器采用模块化多电平技术，将集成了 多个功率单元子模块的模块化多电平变流器应用在多绕组变压器上。模块化多电平变流器 包括模块化多电平并联变流器及模块化多电平串联变流器，二者共用一个直流母线电容， 变流器采用了模块化多电平技术，级联了多个功率单元子模块。所述变压器本体包括同心 绕制在三个上铁芯柱上的主变压器、同心绕制在三个下铁芯柱上的副变压器，其中，主变压 器包括一个主边绕组、一个副边绕组及一个电流补偿绕组，副变压器包括一个串联绕组、一 个电压补偿绕组。 [0019]本发明所述的模块化多电平混合式配电变压器主要分为变压器主体模块和模块 化多电平变流器。如图1所示，本发明所述的模块化多电平混合式配电变压器的变压器主体 模块由主变压器模块和串联变压器模块两部分首尾相连构成。主变压器模块每相绕组由一 个主边绕组、一个副边绕组及一个电流补偿绕组构成。A、B、C各相主边绕组分别为依次为 AA,BJrC.^A,B,C各相副边绕组分别为a2x2、b2y2、c2z2；A、B、C各相电流补偿绕组分别为 a3X3'b3y3'C3Z3° [0020]如图1所示，串联变压器模块每相绕组由一个串联绕组及一个电压补偿绕组构成。 A、B、C各相串联绕组分别为a4x4、b4y4、c4z4；A、B、C各相电压补偿绕组分别为a5x5、b5y5、c5z5。 ［0021］如图1所示，主变压器的主边绕组与串联绕组首先连成一个整体，然后采用三角形 接法接入电网，副边绕组对负载供电。 ［0022］如图1所示，本发明所述的模块化多电平混合式配电变压器的变流器模块是一个 集成了多个功率单元子模块的模块化多电平变流器，模块化多电平变流器由一个模块化多 电平并联变流器和一个模块化多电平串联变流器构成，模块化多电平并联变流器包含三个 相单元，每个相单元分别有两个桥臂：一个上桥臂，一个下桥臂，每个桥臂由多个功率单元 子模块构成，依次为SM1、SM2……SMn。同样，模块化多电平串联变流器包含三个相单元，每 个相单元分别有两个桥臂：一个上桥臂，一个下桥臂，每个桥臂由多个功率单元子模块构 成，依次为SM1、SM2……SMn。模块化多电平并联变流器和模块化多电平串联变流器共用一 个直流母线电容，其由两个容量相同的电容CrC2串联而成，并将电容中点又引出，以提供零 序补偿通路。该模块化多电平变流器的模块化多电平并联变流器的三相桥臂中点（在图1中 为u^v^W］）为模块化多电平并联变流器的三相输出；模块化多电平串联变流器侧的三相桥 臂中点（在图1中为u2、v2、w2）为模块化多电平串联变流器的三相输出。 ［0023］如图2所示，单个功率单元子模块由两个IGBT串联而成，每个IGBT均带有一个反并 联的二极管。在两个IGBT的两端并联了一个储能电容。单个功率单元模块的输出由两个 IGBT的中点引出，各个功率单元子模块的输出端首尾相连。 ［0024］模块化多电平变流器的模块化多电平并联变流器输出与变压器本体的电流补偿 绕组相接，模块化多电平串联变流器输出与变压器本体的电压补偿绕组相接，具体为:A、B、 C各相电流补偿绕组a3x3、b3y3、c3z3的首端子a3、b3、c3与模块化多电平变流器的模块化多电 平并联变流器侧的输出端（即%、％^］）相连，末端子x3、y3、z3连接在一起与模块化多电平变 流器中直流母线电容对应的电容中点J0相连;A、B、C各相电压补偿绕组a5x5、b5y5、c5z5的首 端子a5、b5、c5与模块化多电平变流器的模块化多电平串联变流器侧的输出端（即u2、v2、w2） 相连，末端子x5、y5、z5连接在一起并与模块化多电平变流器中直流母线电容“与“对应的电 容中点J0相连。 ［0025］本发明中的模块化多电平变流器集成了多个子模块,以功率模块级联构成功率桥 臂，因此，各个功率单元只传递总容量中的部分容量，从而能有效降低单个变流器的功率要 求，同时在单个功率单元传递能量相同的情况下大大提高了整体装置的容量;在相同波形 下可以降低开关频率，以降低开关损耗；同时，由于输出电平数量多，输出电压更接近正弦 波，谐波含量较小，从而可以减小输出滤波器，输出电压跳变较小，同时减小了电磁干扰，使 得电磁兼容性能较好。 ［0026］本发明中整体装置不仅具有一般混合式变压器的基本功能，同时采用模块化多电 平技术实现混合式配电变压器能减小输出电压谐波含量，提高应用电压等级，满足大功率 应用场合。总之，本发明采用模块化多电平技术，基于混合式配电变压器结构提出一种新型 模块化多电平混合式配电变压器，控制容量更大、控制功能更为丰富，对于实现配电网的智 能化具有重要意义。 [EN CN110707699B]: A modular multilevel hybrid distribution transformer technical field [0001] The present invention relates to a modular multi-level hybrid distribution transformer, which belongs to the technical field of transformers. Background technique [0002] Traditional distribution transformers are reliable in operation and possess basic functions such as voltage level conversion and power transmission. The development of smart grids puts forward high requirements on the controllability of distribution transformers. So scholars such as Sandeep bala and Jyoti Sastry of ABB scientific research institute put forward the design idea of hybrid distribution transformer. Its notable feature is that the modular multi-level converter is connected to the distribution transformer, and the high controllability of the distribution transformer is realized by converting part of the power of the converter, so it is very suitable as a smart transformer for the next generation of distribution network . [0003] In most of the current power distribution scenarios, the load capacity is often very large, although the converter in the hybrid distribution transformer only bears part of the total power. However, due to the large load capacity, the converter still needs a large capacity at this time. As a result, the application of the existing hybrid distribution transformers in large-capacity occasions is restricted. [0004] In the existing invention, a hybrid distribution transformer suitable for large-capacity occasions is realized through a multi-winding transformer solution, but there are more windings and more converter units. The converter essentially adopts a parallel scheme, and there is circulating current. So a way to combine modular multilevel technology with hybrid distribution transformers is proposed. Summary of the invention [0005] In order to solve the above-mentioned defects in the prior art, the purpose of the present invention is to provide a modular multi-level hybrid distribution transformer. The modular multi-level converter is connected to the distribution transformer, and the large capacity of the hybrid distribution transformer is realized through the higher DC bus voltage. [0006] In order to achieve the above objective, the present invention adopts the following technical solutions: [0007] A modular multi-level hybrid distribution transformer, the modular multi-level hybrid distribution transformer is mainly composed of two parts, namely a transformer body and a modular multi-level converter. The above-mentioned transformer is composed of a main transformer module and a series transformer module; the above-mentioned modular multi-level converter is a modular multi-level parallel converter composed of multiple power unit sub-modules and a modular multi-level series transformer. Each bridge arm is composed of multiple sub-modules composed of IGBT half bridges and DC capacitors in series. The modular multilevel parallel converter of the modular multilevel converter is connected to the current compensation winding of the transformer body, and the voltage between the modular multilevel series converter of the modular multilevel converter and the transformer body The compensation winding is connected. [0008] Modular multi-level modular multi-level converter is mainly divided into two parts, modular multi-level parallel converter and modular multi-level series converter, modular multi-level parallel converter The converter and the modular multi-level series converter share a high-voltage DC bus capacitor, which is formed by two capacitors connected in series, and the middle point is led out. [0009] The modular multi-level converter uses multi-level modulation techniques such as carrier phase shift to perform signal modulation to reduce the content of higher harmonics in the compensation current. At the same time, due to the cascade structure, it can meet the requirements of large capacity and high voltage Equipment requirements. [0010] The main transformer is composed of three-phase windings, each phase winding includes a primary winding (AXrBJrC.1), a secondary winding (a2x2, B2y2, C2z2) And a current compensation winding (a3x3, B3y3, C3z3), and the series transformer module is also composed of three-phase windings, each phase winding includes a series winding (a4x4, B4y4, C4z4) And a voltage compensation winding (A5x5, B5y5, C5z5); The main winding of the main transformer and the series winding are first connected as a whole, and then the delta connection is used to connect to the grid. The three-phase secondary winding, the three-phase current compensation winding and the three-phase voltage compensation winding all adopt the star-shaped neutral point lead connection method. [0011] The modular multi-level parallel converter of the modular multi-level converter is responsible for compensating the reactive power of the load by compensating the reactive current and harmonic current of the load. The modular multi-level series converter of the modular multi-level converter is responsible for meeting the voltage requirements of the load end when the grid input voltage has harmonics, non-rated, and asymmetrical conditions. The modular multilevel converter unit is composed of six phase units, each phase unit has two upper and lower bridge arms, each bridge arm is composed of multiple sub-modules, and each sub-module is composed of one as a switch unit The IGBT half bridge and a DC capacitor are formed. The number of power unit modules in each bridge arm of the modular multilevel parallel converter and the modular multilevel series converter is equal. Each power unit is independent of each other, and the DC capacitor of each module can provide multiple isolated DC power supplies. [0012] Compared with the prior art, the present invention has at least the following technical effects: [0013] On the basis of the hybrid distribution transformer, the present invention adopts a converter based on modular multilevel technology, which effectively improves the compensation capacity of the hybrid distribution transformer. At the same time, with the help of multi-level modulation techniques such as carrier phase shift to control the modular level converter unit, the same switching efficiency can be equivalently achieved during the period when a lower switching frequency is used, thereby effectively reducing the cost of hybrid distribution transformers. High frequency harmonics in load voltage and grid current. BRIEF DESCRIPTION [0014] [0015] [0016] FIG. 1 is a schematic diagram of the overall structure of a modular multi-level hybrid distribution transformer. Figure 2 is a schematic diagram of a power unit sub-module of a modular multi-level hybrid distribution transformer converter. Figure 1 shows the connection terminals of each component. Detailed ways [0017] In order to more clearly illustrate the purpose, technical solutions and advantages of the present invention, the present invention will be further described in detail below with reference to the accompanying drawings and embodiments. The embodiments described here are only used to explain the present invention, but not to limit the present invention. [0018] The modular multi-level hybrid distribution transformer of the present invention adopts modular multi-level technology, and a modular multi-level converter integrating multiple power unit sub-modules is applied to a multi-winding transformer . Modular multi-level converters include modular multi-level parallel converters and modular multi-level series converters. Both share a DC bus capacitor. The converter adopts modular multi-level technology. Multiple power unit sub-modules are connected. The transformer body includes a main transformer concentrically wound on three upper core legs, and a secondary transformer concentrically wound on three lower core legs, wherein the main transformer includes a primary winding, a secondary winding and A current compensation winding, and the auxiliary transformer includes a series winding and a voltage compensation winding. [0019] The modular multi-level hybrid distribution transformer of the present invention is mainly divided into a transformer main module and a modular multi-level converter. As shown in Fig. 1, the main transformer module of the modular multi-level hybrid distribution transformer of the present invention is composed of two parts, a main transformer module and a series transformer module, which are connected end to end. Each phase winding of the main transformer module consists of a primary winding, a secondary winding and a current compensation winding. The primary windings of each phase of A, B, and C are AA, BJrC. ^ The secondary windings of each phase of A, B, and C are respectively a2x2, B2y2, C2z2; The current compensation windings of each phase of A, B, and C are respectively a3X3'b3y3'C3Z3° [0020] As shown in FIG. 1, each phase winding of the series transformer module is composed of a series winding and a voltage compensation winding. The series windings of each phase of A, B, and C are respectively a4x4, B4y4, C4z4; The voltage compensation windings of each phase of A, B, and C are respectively a5x5, B5y5, C5z5。 [0021] As shown in Figure 1, the main winding and series winding of the main transformer are first connected as a whole, and then the delta connection is used to connect to the grid, and the secondary winding supplies power to the load. [0022] As shown in Figure 1, the converter module of the modular multi-level hybrid distribution transformer of the present invention is a modular multi-level converter that integrates multiple power unit sub-modules. The modular multi-level converter consists of a modular multi-level parallel converter and a modular multi-level series converter. The modular multi-level parallel converter contains three phase units, each of which There are two bridge arms: an upper bridge arm and a lower bridge arm. Each bridge arm is composed of multiple power unit sub-modules, which are SM1, SM2...SMn in turn. Similarly, the modular multi-level series converter contains three phase units, and each phase unit has two bridge arms: an upper bridge arm and a lower bridge arm. Each bridge arm is composed of multiple power unit sub-modules. , Followed by SM1, SM2...SMn. The modular multilevel parallel converter and the modular multilevel series converter share a DC bus capacitor, which consists of two capacitors with the same capacity CrC2It is connected in series and leads out the midpoint of the capacitor to provide a zero-sequence compensation path. The midpoint of the three-phase bridge arm of the modular multilevel parallel converter of the modular multilevel converter (u^v^W in Figure 1) is the modular multilevel parallel converter Three-phase output; the midpoint of the three-phase bridge arm on the side of the modular multilevel series converter (u in Figure 12, V2, W2) Is the three-phase output of the modular multi-level series converter. [0023] As shown in Figure 2, a single power unit sub-module is formed by two IGBTs connected in series, and each IGBT has an anti-parallel diode. An energy storage capacitor is connected in parallel at both ends of the two IGBTs. The output of a single power unit module is derived from the midpoint of the two IGBTs, and the output ends of each power unit sub-module are connected end to end. [0024] The output of the modular multilevel parallel converter of the modular multilevel converter is connected with the current compensation winding of the transformer body, and the output of the modular multilevel series converter is connected with the voltage compensation winding of the transformer body. Connect, specifically: A, B, C phase current compensation winding a3x3, B3y3, C3z3The first terminal a3, B3, C3Connected to the output terminal (ie %, %^]) of the modular multilevel parallel converter side of the modular multilevel converter, the terminal x3, Y3,z3Connected to the midpoint J of the capacitor corresponding to the DC bus capacitor in the modular multilevel converter0Connected; A, B, C phase voltage compensation winding a5x5, B5y5, C5z5The first terminal a5, B5, C5With the output terminal of the converter side of the modular multi-level series converter of the modular multi-level converter (i.e. u2, V2, W2) Connected, terminal x5, Y5,z5Connected together and connected to the midpoint J of the capacitor corresponding to the DC bus capacitor "and" in the modular multilevel converter0Connected. [0025] The modular multi-level converter in the present invention integrates multiple sub-modules, and power modules are cascaded to form a power bridge arm. Therefore, each power unit only transmits part of the total capacity, which can effectively reduce the single The power requirements of the converter, and at the same time, the capacity of the whole device is greatly increased under the same energy transmission of a single power unit; the switching frequency can be reduced under the same waveform to reduce the switching loss; at the same time, due to the large number of output levels, the output The voltage is closer to the sine wave, and the harmonic content is smaller, so that the output filter can be reduced, the output voltage jump is smaller, and the electromagnetic interference is reduced, so that the electromagnetic compatibility performance is better. [0026] The overall device in the present invention not only has the basic functions of a general hybrid transformer, but also adopts modular multi-level technology to realize that the hybrid distribution transformer can reduce the output voltage harmonic content, improve the application voltage level, and meet high-power applications. occasion. In a word, the present invention adopts modular multi-level technology and proposes a new type of modular multi-level hybrid distribution transformer based on the structure of hybrid distribution transformer, which has larger control capacity and richer control functions, which is useful for realizing distribution network The intelligence of it is of great significance.
[PT BR102014011275B1]: conversor de energia multinível, e, sistema de conversão de energia [EN EP2816719B1]: Improved multilevel voltage source converters and systems [ZH CN104242710B]: 改进的多电平电压源转换器和系统 [DE EP2816719B1]: Verbesserte mehrstufige Spannungsquellenwandler und Systeme [FR EP2816719B1]: Convertisseurs de source de tension à niveaux multiples améliorés et systèmes [ES MX337494B]: CONVERTIDORES Y SISTEMAS DE FUENTE DE VOLTAJE DE MULTINIVEL MEJORADOS. | [PT BR102014011275B1]: conversor de energia multinível, e, sistema de conversão dr energia estágios (100) e sistemas (300) de conversor de energia multinível de ponto neutro grampeado aninhado (nnpc) são apresentados, nos quais o estágio de conversor inclui um circuito de núcleo de inversor npc (110) com um circuito de aninhamento de capacitor (comutado) flutuante (104), com as chaves do núcleo npc (110) e o circuito de capacitor comutado (104) sendo disparadas utilizando estados de comutação redundantes selecionados para controlar a tensão dos capacitores comutados ou atingir uma tensão de saída multinível tendo valores de degrau de tensão espaçados igualmente. múltiplos estágios de inversor (100) podem se encontrar em cascata ou conectados em diversas configurações para implementar sistemas de conversão de energia monofásicos ou multifásicos, e tensões de saída mais altas podem ser atingidas ao formar dois estágios de conversor (100) em uma configuração de ponte h, e conectar múltiplos estágios de ponte h em série uns com os outros. [EN EP2816719B1]: Nested neutral point clamped (NNPC) multilevel power converter stages (100) and systems (300) are presented, in which the converter stage includes an NPC inverter core circuit (110) with a flying (switched) capacitor nesting circuit (104), with the switches of the NPC core (110) and the switched capacitor circuit (104) being gated using selected redundant switching states to control the voltage of the switched capacitors to achieve a multilevel output voltage having equally spaced voltage step values. Multiple inverter stages (100) can meet cascaded or connected in various configurations to implement single or multiphase power conversion systems, and higher output voltages can be achieved by forming to converter stages (100) into an H-bridge configuration, and connecting multiple H-bridge stages in series with one another. [ZH CN104242710B]: 本发明涉及种改进的多电平电压源转换器和系统。呈现了嵌套中性点钳位(NNPC)多电平电力转换器级(100)和系统(300)，其中，转换器级包括具有飞跨(开关)电容器嵌套电路(104)的NPC逆变器核心电路(110)，使用所选择的冗余开关状态来选通NPC核心电路(110)和开关电容器电路(104)的开关以控制开关电容器的电压，以实现具有等间隔的电压步进值的多电平输出电压。多个逆变器级(100)能够满足以各种配置进行级联或连接以实施单相或多相电力转换系统，可以通过将转换器级(100)形成为H桥接配置并且使多个H桥接级彼此串联连接来实现更高的输出电压。 [ES MX337494B]: Se presentan fases (100) y sistemas (300) de convertidor de energía multinivel de enclavamiento de punto neutro anidado (NNPC), en los cuales la fase del convertidor incluye un circuito (110) de núcleo inversor de NPC con un condensador volante (conmutado) que anida en el circuito (104), con los conmutadores del núcleo (110) de NPC y el circuito (104) del condensador conmutado se controlan por compuerta utilizando estados de conmutación redundantes seleccionados para controlar el voltaje de los condensadores conmutados para alcanzar un voltaje de salida multinivel que tiene valores de etapa de voltaje igualmente separados. Las fases (100) de inversor múltiple pueden reunirse en cascada o conectarse en diversas configuraciones para implementar sistemas de conversión de energía sencillos o de multifase, y pueden alcanzarse voltajes de salida más altos al conformar las fases (100) del convertidor en una configuración de puente H, y conectar múltiples fases de puente de H en serie entre sí. | EP2816719B1 | 2014-12-24 2015-04-01 2021-03-31 | EP14167709A | 2014-05-09 2014-05-09 2014-05-09 | US201313922401A, 2013-06-20 US201313922401A, 2013-06-20 US201313922401A, 2013-06-20 | BR102014011275B1: 2021-05-18 CN104242710B: 2017-05-31 EP2816719B1: 2021-03-31 MX337494B: 2016-03-08 US9083230B2: 2015-07-14 | ROCKWELL AUTOMATION TECH INC 洛克威尔自动控制技术股份有限公司 NARIMANI MEHDI WU BIN CHENG ZHONGYUAN ZARGARI NAVID R | NARIMAN MEHDI WU BIN CHENG ZHONGYUAN ZARGARI NAVID R BIN WU MEHDI NARIMAN NAVID R ZARGARI ZHONGYUAN CHENG MEHDI NARIMANI NARIMANI MEHDI | H02M7/483: I H02M7/487: I H02M7/49: N H02M7/5387: N H02M7/5395: N H02M7/42: I H02M7/537: I H02M3/07: I H02M7/487: N | H02M7/483: I H02M7/487: A H02M7/49: A H02M7/5395: A H02M1/0095: A H02M7/4837: I H02M7/53876: A H02M3/07: I | CN1201471C JP2013102674A US2013148390A1 JP2006223009A US2004267468A1 US2013044526A1 US2013249322A1 US2013270917A1 US4443841A US4894621A US5298848A US5361196A US5502633A US5625545A US5638263A US5642275A US5790396A US5933339A US5986909A US6005788A US6031738A US6058031A US6075350A US6222284B1 US6229722B1 US6236580B1 US6320767B1 US6411530B2 US6556461B1 US6697271B2 US6697274B2 US6795323B2 US6842354B1 US7057905B2 US7068526B2 US7106025B1 US7164254B2 US7170767B2 US7215559B2 US7428158B2 US7568931B2 US7649281B2 US7800254B2 US7830681B2 US7894224B2 US7978488B2 US8008923B2 US8093764B2 US8107267B2 US8130501B2 US8144491B2 US8159840B2 US8279640B2 US8400793B2 US8441147B2 US2008079314A1 US2008174182A1 US2009073622A1 US2010301975A1 US2011249479A1 US2012057380A1 US2012113698A1 US2013121042A1 US2014063870A1 US2014204632A1 CN1190278A CN1253999A CN1414692A CN2577503A CN1925289A EP0874448A1 EP1713168A2 EP2698912A2 GB1295261A KR20080061641A WO2012105737A1 | US10177679B2 US10177679 10177679 WO2017076367A1 WO2017076367 2017/076367 CN110365240A CN110365240 110365240 CN108631631A CN108631631 108631631 CN106329974A CN106329974 106329974 CN104779824A CN104779824 104779824 CN106559004A CN106559004 106559004 CN108292896A CN108292896 108292896 CN108476000A CN108476000 108476000 US10177683B2 US10177683 10177683 EP2757678A3 EP2757678 2757678 EP3343749A4 EP3343749 3343749 US10205407B2 US10205407 10205407 US2017077836A1 US2017077836 20170077836 US10389271B2 US10389271 10389271 US2018309384A1 US2018309384 20180309384 US9425705B2 US9425705 09425705 US9871466B2 US9871466 09871466 US09871466B2 US2015381073A1 US2015381073 20150381073 US9559610B2 US9559610 09559610 US09559610B2 US2016099661A1 US2016099661 20160099661 US20160099661A1 US2015256064A1 US2015256064 20150256064 US20150256064A1 US9917543B1 US9917543 09917543 US9559541B2 US9559541 09559541 US10439494B2 US10439494 10439494 US9673735B2 US9673735 09673735 US09673735B2 US2016315557A1 US2016315557 20160315557 US20160315557A1 US10355609B2 US10355609 10355609 US9800175B2 US9800175 09800175 US09800175B2 US2017012554A1 US2017012554 20170012554 US20170012554A1 US10404175B2 US10404175 10404175 US10355617B2 US10355617 10355617 US9991820B2 US9991820 09991820 US09991820B2 US9899948B2 US9899948 09899948 US09899948B2 US2017070175A1 US2017070175 20170070175 US20170070175A1 EP2897279A1 EP2897279 2897279 EP2894780A1 EP2894780 2894780 US9780658B2 US9780658 09780658 US2016094128A1 US2016094128 20160094128 US10476428B1 US10476428 WO2016152738A1 WO2016152738 2016/152738 WO2016/152738A1 CN108476001A CN108476001 108476001 US10277144B2 US10277144 10277144 US2018269803A1 US2018269803 20180269803 US9787213B2 US9787213 09787213 US9912221B2 US9912221 09912221 US09912221B2 US10305368B2 US10305368 10305368 US9780663B2 US9780663 09780663 US09780663B2 US10389246B1 US10389246 10389246 US10361637B2 US10361637 10361637 US2018278175A1 US2018278175 20180278175 US10158299B1 US10158299 10158299 US10447158B2 US10447158 10447158 US10050515B1 US10050515 10050515 US9973071B2 US9973071 09973071 US09973071B2 US2014265605A1 US2014265605 20140265605 US20140265605A1 US9748862B2 US9748862 09748862 US9300210B1 US9300210 09300210 US9780656B2 US9780656 09780656 US09780656B2 US10622890B1 US10622890 10622890 US10218285B2 US10218285 10218285 US2017110977A1 US2017110977 20170110977 US20170110977A1 US10284092B1 US10284092 10284092 US10581312B2 US10581312 10581312 US11005388B2 US11005388 11005388 US2020052594A1 US2020052594 20200052594 US20200052594A1 US10516365B1 US10516365 10516365 US10833584B2 US10833584 10833584 US10658920B2 US10658920 10658920 US2018337590A1 US2018337590 20180337590 US11056982B2 US11056982 11056982 US9812990B1 US9812990 09812990 US11119159B2 US11119159 11119159 US2018026548A1 US2018026548 20180026548 US20180026548A1 | [ZH CN104242710B]: 1. 一种多电平电力转换器，包括： 逆变器电路，所述逆变器电路包括： 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆变器 电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开关器 件中的两个逆变器开关器件的逆变器输出节点，以及 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部节点 之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所述第 二钳位元件的第三内部节点； 开关电容器电路，所述开关电容器电路包括： 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流输入 与相应的逆变器电路输入节点之间，以及 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器电路 输入节点中的相应一个与所述第三内部节点之间；以及 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器件提 供开关控制信号，以提供在多个不同电平之一处的所述逆变器输出节点处的多电平输出电 压； 其中，所述控制器在提供所述开关控制信号时、从针对不同输出电压电平中的至少一 个的多个冗余开关状态中进行选择，以控制所述第一电容器和第二电容器的充电和放电、 以将相应的第一电容器电压和第二电容器电压调节成第一直流输入与第二直流输入之间 的直流输入电压的三分之一。 2. 根据权利要求1所述的多电平电力转换器， 其中，所述逆变器开关电路包括： 第一逆变器开关器件，所述第一逆变器开关器件具有连接至所述第一逆变器电路输入 节点的第一端子和连接至所述第一内部节点的第二端子， 第二逆变器开关器件，所述第二逆变器开关器件具有连接至所述第一内部节点的第一 端子和连接至所述逆变器输出节点的第二端子， 第三逆变器开关器件，所述第三逆变器开关器件具有连接至所述逆变器输出节点的第 一端子和连接至所述第二内部节点的第二端子，以及 第四逆变器开关器件，所述第四逆变器开关器件具有连接至所述第二内部节点的第一 端子和连接至所述第二逆变器电路输入节点的第二端子； 其中，所述第一钳位元件包括连接至所述第三内部节点的第一端子和连接至所述第一 内部节点的第二端子； 其中，所述第二钳位元件包括连接至所述第二内部节点的第一端子和连接至所述第三 内部节点的第二端子； 其中，所述开关电容器电路包括： 第一开关电容器电路开关器件，所述第一开关电容器电路开关器件具有连接至第一直 流输入的第一端子和连接至所述第一逆变器电路输入节点的第二端子，以及 第二开关电容器电路开关器件，所述第二开关电容器电路开关器件具有连接至所述第 二逆变器电路输入节点的第一端子和连接至第二直流输入的第二端子； 其中，所述第一电容器包括连接至所述第一逆变器电路输入节点的第一端子和连接至 所述第三内部节点的第二端子；以及 其中，所述第二电容器包括连接至所述第三内部节点的第一端子和连接至所述第二逆 变器电路输入节点的第二端子。 3. 根据权利要求2所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件 以及所述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同的电平之一 处的输出电压。 4. 根据权利要求3所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信 号时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控 制所述第一电容器和第二电容器的充电和放电。 5. 根据权利要求1所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件 和所述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同电平之一处的 输出电压。 6. 根据权利要求5所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信 号时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控 制所述第一电容器和第二电容器的充电和放电。 7. —种多电平电力转换器，包括： 逆变器电路，所述逆变器电路包括： 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆变器 电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开关器 件中的两个逆变器开关器件的逆变器输出节点，以及 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部节点 之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所述第 二钳位元件的第三内部节点； 开关电容器电路，所述开关电容器电路包括： 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流输入 与相应的逆变器电路输入节点之间，以及 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器电路 输入节点中的相应一个与所述第三内部节点之间；以及 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器件提 供开关控制信号，以提供在多个不同电平之一处的在所述逆变器输出节点处的多电平输出 电压； 其中，所述控制器在提供所述开关控制信号时、从针对不同输出电压电平中的至少一 个的多个冗余开关状态中进行选择，以控制所述第一电容器和第二电容器的充电和放电、 以将相应的第一电容器电压和第二电容器电压调节成所述直流输入之间的直流输入电压 的五分之一。 8. 根据权利要求5所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件 以及所述开关电容器电路开关器件提供所述开关控制信号，以提供在等间隔步进的四个不 同的电平之一处的输出电压。 9. 根据权利要求1所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件 和所述开关电容器电路开关器件提供所述开关控制信号，以提供在等间隔步进的多个不同 电平之一处的输出电压。 10. 根据权利要求1所述的多电平电力转换器， 其中，所述开关电容器电路包括： 第一开关电容器电路开关器件，所述第一开关电容器电路开关器件具有连接至第一直 流输入的第一端子和连接至第四内部节点的第二端子， 第二开关电容器电路开关器件，所述第二开关电容器电路开关器件具有连接至所述第 四内部节点的第一端子和连接至所述第一逆变器电路输入节点的第二端子， 第三开关电容器电路开关器件，所述第三开关电容器电路开关器件具有连接至所述第 二逆变器电路输入节点的第一端子和连接至第五内部节点的第二端子， 第四开关电容器电路开关器件，所述第四开关电容器电路开关器件具有连接至所述第 五内部节点的第一端子和连接至第二直流输入的第二端子， 第一电容器，所述第一电容器包括连接至所述第一逆变器电路输入节点的第一端子和 连接至所述第三内部节点的第二端子， 第二电容器，所述第二电容器包括连接至所述第三内部节点的第一端子和连接至所述 第二逆变器电路输入节点的第二端子， 第三电容器，所述第三电容器包括连接至所述第四内部节点的第一端子和连接至第六 内部节点的第二端子，以及 第四电容器，所述第四电容器包括连接至所述第六内部节点的第一端子和连接至所述 第五内部节点的第二端子。 11. 一种电力转换系统，包括多个多电平电力转换器，各个多电平电力转换器包括： 逆变器电路，所述逆变器电路包括： 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆变器 电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开关器 件中的两个逆变器开关器件的逆变器输出节点，以及 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部节点 之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所述第 二钳位元件的第三内部节点； 开关电容器电路，所述开关电容器电路包括： 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流输入 与相应的逆变器电路输入节点之间，以及 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器电路 输入节点中的相应一个与所述第三内部节点之间；以及 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器件提 供开关控制信号，以提供在多个不同电平之一处的所述逆变器输出节点处的多电平输出电 压； 其中，所述控制器在提供所述开关控制信号时、从针对不同输出电压电平中的至少一 个的多个冗余开关状态中进行选择，以控制所述第一电容器和第二电容器的充电和放电、 以将相应的第一电容器电压和第二电容器电压调节成第一直流输入与第二直流输入之间 的直流输入电压的三分之一。 12. 根据权利要求11所述的电力转换系统，包括： 第一多电平电力转换器；以及 第二多电平电力转换器； 其中，所述第一多电平电力转换器与所述第二多电平电力转换器的直流输入被连接在 一起； 其中，所述第一多电平电力转换器的逆变器输出节点连接至系统中性节点；以及 其中，所述第二多电平电力转换器的逆变器输出节点提供用于所述电力转换系统的交 流输出。 13. 根据权利要求11所述的电力转换系统，其中，所述控制器向所述逆变器开关器件以 及所述开关电容器电路开关器件提供所述开关控制信号，以提供在至少四个不同电平之一 处的每个多电平电力转换器的输出电压。 14. 根据权利要求13所述的电力转换系统，其中，所述控制器在提供所述开关控制信号 时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控制 所述第一电容器和第二电容器的充电和放电。 15. 根据权利要求11所述的电力转换系统，其中，所述多电平电力转换器的至少一个提 供针对所述电力转换系统的多个输出相的每个相的输出电压。 16. 根据权利要求7所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器 件以及所述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同的电平之 一处的输出电压。 17. 根据权利要求16所述的多电平电力转换器，其中，所述控制器在提供所述开关控制 信号时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和第二电容器的充电和放电。 18. 根据权利要求1所述的多电平电力转换器，其中，所述第三内部节点不具有与中性 节点的固定或受控连接，所述中性节点与所述直流输入相关联。 19. 根据权利要求7所述的多电平电力转换器，其中，所述第三内部节点不具有与中性 节点的固定或受控连接，所述中性节点与所述直流输入相关联。 20. 根据权利要求11所述的电力转换系统，其中，所述第三内部节点不具有与中性节点 的固定或受控连接，所述中性节点与所述直流输入相关联。 21. —种多电平电力转换器，包括： 逆变器电路，所述逆变器电路包括： 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆变器 电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开关器 件中的两个逆变器开关器件的逆变器输出节点，以及 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部节点 之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所述第 二钳位元件的第三内部节点，其中，所述第三内部节点不具有与中性节点的固定或受控连 接，所述中性节点与直流输入相关联； 开关电容器电路，所述开关电容器电路包括： 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流输入 与相应的逆变器电路输入节点之间，以及 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器电路 输入节点中的相应一个与所述第三内部节点之间；以及 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器件提 供开关控制信号，以提供所述逆变器输出节点处的多电平输出电压并控制所述第一电容器 和第二电容器的充电和放电。 22. 根据权利要求21所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器 件以及所述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同的电平之 一处的输出电压。 23. 根据权利要求22所述的多电平电力转换器，其中，所述控制器在提供所述开关控制 信号时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和第二电容器的充电和放电、以将相应的第一电容器电压和第二电容 器电压调节成小于在第一直流输入与第二直流输入之间的直流输入电压的一半。 [EN EP2816719B1]: A multilevel power converter (100), comprising: an inverter circuit (110), comprising: an inverter switching circuit including: a plurality of inverter switching devices (S2-S5) connected in series with one another between first and second inverter circuit input nodes (111, 112), and an inverter output node (116) connecting two of the plurality of inverter switching devices (S3, S4), wherein the inverter switching circuit comprises: a first inverter switching device (S2) with a first terminal connected to the first inverter circuit input node (111) and a second terminal connected to a first internal node (114),a second inverter switching device (S3) with a first terminal connected to the first internal node (114) and a second terminal connected to the inverter output node (116),a third inverter switching device (S4) with a first terminal connected to the inverter output node (116) and a second terminal connected to a second internal node (118), anda fourth inverter switching device (S5) with a first terminal connected to the second internal node (118) and a second terminal connected to the second inverter circuit input node (112); anda clamping circuit including first and second clamping elements (D1, D2) connected in series with one another between first and second internal nodes (114, 118) of the inverter switching circuit, and a third internal node (119) joining the first and second clamping elements (D1, D2); wherein the first clamping element (D1) includes a first terminal connected to a third internal node (119), and a second terminal connected to the first internal node (114);wherein the second clamping element (D2) includes a first terminal connected to the second internal node (118) and a second terminal connected to the third internal node (119);a switched capacitor circuit (104), comprising: switched capacitor circuit switching devices (S1, S6) individually connected between a corresponding DC input (101, 102) and a corresponding inverter circuit input node (111, 112), andfirst and second capacitors (C1, C2) individually connected between a corresponding one of the inverter circuit input nodes (111, 112) and the third internal node (119); andwherein the switched capacitor circuit switching devices (S1, S6), further comprise: a first switched capacitor circuit switching device (S1) with a first terminal connected to a first DC input (101), and a second terminal connected to the first inverter circuit input node (111), anda second switched capacitor circuit switching device (S6) with a first terminal connected to the second inverter circuit input node (112), and a second terminal connected to a second DC input (102);wherein the first capacitor (C1) includes a first terminal connected to the first inverter circuit input node (111) and a second terminal connected to the third internal node (119); andwherein the second capacitor (C2) includes a first terminal connected to the third internal node (119) and a second terminal connected to the second inverter circuit input node (112),wherein the third internal node (119) is not connected to any system neutral,a controller (122) arranged to provide switching control signals to the plurality of inverter switching devices (S2-S5) and to the switched capacitor circuit switching devices (S1, S6) to provide a multilevel output voltage at the inverter output node (116) and to control charging and discharging of the first and second capacitors (C1, C2), wherein the control signals form six possible switching vectors V1, V2, V3, V4, V5, V6, comprising: vector V1 corresponding to a switching state in which the first switched capacitor circuit switching device (S1) and the first and second inverter switching device (S2, S3) are on and the second switched capacitor circuit switching device (S6) and the third and fourth inverter switching device (S4, S5) are off;vector V2 corresponding to a switching state in which the first switched capacitor circuit switching device (S1) and the second and third inverter switching device (S3, S4) are on and the second switched capacitor circuit switching device (S6) and the first and fourth inverter switching device (S2, S5) are off;vector V3 corresponding to a switching state in which the first and second inverter switching device (S2, S3) and the second switched capacitor circuit switching device (S6) are on and the first switched capacitor circuit switching device (S1) and the third and fourth inverter switching device (S4, S5) are off;vector V4 corresponding to a switching state in which the first switched capacitor circuit switching device (S1) and the third and fourth inverter switching device (S4, S5) are on and the first and second inverter switching device (S2, S3) and the second switched capacitor circuit switching device (S6) are off;vector V5 corresponding to a switching state in which the second and third inverter switching device (S3, S4) and the second switched capacitor circuit switching device (S6) are on and the first switched capacitor circuit switching device (S1) and the first and fourth inverter switching device (S2, S5) are off; andvector V6 corresponding to a switching state in which the third and fourth inverter switching device (S4, S5) and the second switched capacitor circuit switching device (S6) are on and the first switched capacitor circuit switching device (S1) and the first and second inverter switching device (S2, S3) are off; andwherein switching vectors V2 and V3 are redundant with one another relative to the line-to-neutral output voltage, and wherein the switching vector V3 allows the first and second capacitors (C1, C2) to be charged or discharged simultaneously andwherein switching vectors V4 and V5 are redundant with one another relative to the line-to-neutral output voltage, and wherein the switching vector V4 allows the first and second capacitors (C1, C2) to be charged or discharged simultaneously. The multilevel power converter (100) of claim 1, wherein the controller (122) provides the switching control signals to the inverter switching devices (S2-S5) and to the switched capacitor circuit switching devices (S1, S2) to provide the output voltage at one of four distinct levels. The multilevel power converter (100) of claim 2, wherein the controller (122) selects from among a plurality of redundant switching states for at least one of the four distinct output voltage levels in providing the switching control signals to control charging and discharging of the first and second capacitors (C1, C2) to regulate corresponding first and second capacitor voltages (VC1, VC2) to less than half of a DC input voltage (VDC) between the first and second DC inputs (101, 102). The multilevel power converter (100) of claim 2, wherein the controller (122) provides the switching control signals to the inverter switching devices (S2-S5) and to the switched capacitor circuit switching devices (S1, S2) to provide the output voltage at one of four distinct levels of substantially equally spaced steps. The multilevel power converter (100) of any one of claims 1 to 4, wherein the controller (122) provides the switching control signals to the inverter switching devices (S2-S5) and to the switched capacitor circuit switching devices (S1, S2) to provide the output voltage at one of a plurality of distinct levels of substantially equally spaced steps. A power conversion system (300, 400, 420, 430, 440, 450, 1000), comprising a plurality of multilevel power converters (100) according to claim 1. The power conversion system (300) of claim 6, wherein the controller (122) provides the switching control signals to the inverter switching devices (S2-S5) and to the switched capacitor circuit switching devices (S1, S2) to provide the output voltage of each multilevel power converter (100) at one of at least four distinct levels. [DE EP2816719B1]: Mehrstufenleistungswandler (100), umfassend: eine Inverterschaltung (110), die umfasst: eine Inverterschaltschaltung, die beinhaltet: mehrere Inverterschaltvorrichtungen (S2-S5) in Reihenverbindung miteinander zwischen ersten und zweiten Inverterschaltungseingabeknoten (111, 112) und einem Inverterausgabeknoten (116), der zwei der mehreren Inverterschaltvorrichtungen (S3, S4) verbindet, wobei die Inverterschaltschaltung umfasst: eine erste Inverterschaltvorrichtung (S2) mit einem ersten Anschluss, der mit dem ersten Inverterschaltungseingabeknoten (111) verbunden ist, und einem zweiten Anschluss, der mit einem ersten internen Knoten (114) verbunden ist,eine zweite Inverterschaltvorrichtung (S3) mit einem ersten Anschluss, der mit dem ersten internen Knoten (114) verbunden ist, und einem zweiten Anschluss, der mit dem Inverterausgabeknoten (116) verbunden ist,eine dritte Inverterschaltvorrichtung (S4) mit einem ersten Anschluss, der mit dem Inverterausgabeknoten (116) verbunden ist, und einem zweiten Anschluss, der mit einem zweiten internen Knoten (118) verbunden ist, undeine vierte Inverterschaltvorrichtung (S5) mit einem ersten Anschluss, der mit dem zweiten internen Knoten (118) verbunden ist, und einem zweiten Anschluss, der mit dem zweiten Inverterschaltungseingabeknoten (112) verbunden ist; undeine Klemmschaltung, die beinhaltet: erste und zweite Klemmelemente (D1, D2) in Reihenverbindung miteinander zwischen ersten und zweiten internen Knoten (114, 118) der Inverterschaltschaltung und einem dritten internen Knoten (119), der die ersten und zweiten Klemmelemente (D1, D2) verbindet; wobei das erste Klemmelement (D1) beinhaltet: einen ersten Anschluss, der mit einem dritten internen Knoten (119) verbunden ist, und einen zweiten Anschluss, der mit dem ersten internen Knoten (114) verbunden ist;wobei das zweite Klemmelement (D2) beinhaltet: einen ersten Anschluss, der mit dem zweiten internen Knoten (118) verbunden ist, und einen zweiten Anschluss, der mit dem dritten internen Knoten (119) verbunden ist;eine Schaltkondensatorschaltung (104), die umfasst: die Schaltkondensatorschaltung schaltende Vorrichtungen (S1, S6) in Einzelverbindung zwischen einer entsprechenden DC-Eingabe (101, 102) und einem entsprechenden Inverterschaltungseingabeknoten (111, 112), underste und zweite Kondensatoren (C1, C2) in Einzelverbindung zwischen einem entsprechenden der Inverterschaltungseingabeknoten (111, 112) und dem dritten internen Knoten (119); undwobei die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S6) des Weiteren umfassen: eine erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) mit einem ersten Anschluss, der mit einer ersten DC-Eingabe (101) verbunden ist, und einem zweiten Anschluss, der mit dem ersten Inverterschaltungseingabeknoten (111) verbunden ist, undeine zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) mit einem ersten Anschluss, der mit dem zweiten Inverterschaltungseingabeknoten (112) verbunden ist, und einem zweiten Anschluss, der mit einer zweiten DC-Eingabe (102) verbunden ist;wobei der erste Kondensator (C1) beinhaltet: einen ersten Anschluss, der mit dem ersten Inverterschaltungseingabeknoten (111) verbunden ist, und einen zweiten Anschluss, der mit dem dritten internen Knoten (119) verbunden ist; undwobei der zweite Kondensator (C2) beinhaltet: einen ersten Anschluss, der mit dem dritten internen Knoten (119) verbunden ist, und einen zweiten Anschluss, der mit dem zweiten Inverterschaltungseingabeknoten (112) verbunden ist,wobei der dritte interne Knoten (119) nicht mit einer Systemnullleitung verbunden ist, eine Steuerung bzw. Regelung (122) in einer Anordnung zur Bereitstellung von Schaltsteuer- bzw. Regelsignalen für die mehreren Inverterschaltvorrichtungen (S2-S5) und für die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S6), um eine mehrstufige Ausgabespannung an dem Inverterausgabeknoten (116) bereitzustellen und um das Laden und Entladen der ersten und zweiten Kondensatoren (C1, C2) zu steuern bzw. zu regeln, wobei die Steuer- bzw. Regelsignale sechs mögliche Schaltvektoren V1, V2, V3, V4, V5, V6 bilden, die umfassen: einen Vektor V1 entsprechend einem Schaltzustand, in dem die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die erste und zweite Inverterschaltvorrichtung (S2, S3) EIN sind und die die zweite Schaltkondensatorschaltung schaltende Vorrichtung (S6) und die dritte und vierte Inverterschaltungsvorrichtung (S4, S5) AUS sind;einen Vektor V2 entsprechend einem Schaltzustand, in dem die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die zweite und dritte Inverterschaltvorrichtung (S3, S4) EIN sind und die zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) und die erste und vierte Inverterschaltvorrichtung (S2, S5) AUS sind;einen Vektor V3 entsprechend einem Schaltzustand, in dem die erste und zweite Inverterschaltvorrichtung (S2, S3) und die zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) EIN sind und die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die dritte und vierte Inverterschaltvorrichtung (S4, S5) AUS sind;einen Vektor V4 entsprechend einem Schaltzustand, in dem die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die dritte und vierte Inverterschaltvorrichtung (S4, S5) EIN sind und die erste und zweite Inverterschaltvorrichtung (S2, S3) und die zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) AUS sind;einen Vektor V5 entsprechend einem Schaltzustand, in dem die zweite und dritte Inverterschaltvorrichtung (S3, S4) und die zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) EIN sind und die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die erste und vierte Inverterschaltvorrichtung (S2, S5) AUS sind; undeinen Vektor V6 entsprechend einem Schaltzustand, in dem die dritte und vierte Inverterschaltvorrichtung (S4, S5) und die zweite die Schaltkondensatorschaltung schaltende Vorrichtung (S6) EIN sind und die erste die Schaltkondensatorschaltung schaltende Vorrichtung (S1) und die erste und zweite Inverterschaltvorrichtung (S2, S3) AUS sind; undwobei die Schaltvektoren V2 und V3 relativ zu der Leitung-zu-Nullleitung-Ausgabespannung redundant zueinander sind und wobei der Schaltvektor V3 ermöglicht, dass die ersten und zweiten Kondensatoren (C1, C2) gleichzeitig geladen oder entladen werden, undwobei die Schaltvektoren V4 und V5 relativ zu der Leitung-zu-Nullleitung-Ausgabespannung redundant zueinander sind und wobei der Schaltvektor V4 ermöglicht, dass die ersten und zweiten Kondensatoren (C1, C2) gleichzeitig geladen oder entladen werden. Mehrstufenleistungswandler (100) nach Anspruch 1, wobei die Steuerung bzw. Regelung (122) die Schaltsteuer- bzw. Regelsignale für die Inverterschaltvorrichtungen (S2-S5) und für die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S2) derart bereitstellt, dass die Ausgabespannung auf einer von vier verschiedenen Stufen bereitgestellt wird. Mehrstufenleistungswandler (100) nach Anspruch 2, wobei die Steuerung bzw. Regelung (122) unter mehreren redundanten Schaltzuständen für wenigstens eine der vier verschiedenen Ausgabespannungsstufen beim Bereitstellen der Schaltsteuer- bzw. Regelsignale zur Steuerung bzw. Regelung des Ladens und Entladens der ersten und zweiten Kondensatoren (C1, C2) derart auswählt, dass entsprechende erste und zweite Kondensatorspannungen (VC1, VC2) auf weniger als die Hälfte einer DC-Eingabespannung (VDC) zwischen den ersten und zweiten DC-Eingaben (101, 102) reguliert werden. Mehrstufenleistungswandler (100) nach Anspruch 2, wobei die Steuerung bzw. Regelung (122) die Schaltsteuer- bzw. Regelsignale für die Inverterschaltvorrichtungen (S2-S5) und für die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S2) derart bereitstellt, dass die Ausgabespannung auf einer von vier verschiedenen Stufen in im Wesentlichen gleich beabstandeten Schritten bereitgestellt wird. Mehrstufenleistungswandler (100) nach einem der Ansprüche 1 bis 4, wobei die Steuerung bzw. Regelung (122) die Schaltsteuer- bzw. Regelsignale für die Inverterschaltvorrichtungen (S2-S5) und für die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S2) derart bereitstellt, dass die Ausgabespannung auf einer von mehreren verschiedenen Stufen in im Wesentlichen gleich beabstandeten Schritten bereitgestellt wird. Leistungswandlungssystem (300, 400, 420, 430, 440, 450, 1000), umfassend mehrere Mehrstufenleistungswandler (100) nach Anspruch 1. Leistungswandlungssystem (300) nach Anspruch 6, wobei die Steuerung bzw. Regelung (122) die Schaltsteuer- bzw. Regelsignale für die Inverterschaltvorrichtungen (S2-S5) und für die die Schaltkondensatorschaltung schaltenden Vorrichtungen (S1, S2) derart bereitstellt, dass die Ausgabespannung eines jeden Mehrstufenleistungswandlers (100) auf einer von wenigstens vier verschiedenen Stufen bereitgestellt wird. [FR EP2816719B1]: Convertisseur de puissance à multiples niveaux (100), comprenant : un circuit onduleur (110), comprenant : un circuit de commutation d'onduleur comprenant : une pluralité de dispositifs de commutation d'onduleur (S2-S5) connectés en série les uns aux autres entre des premier et second nœuds d'entrée de circuit onduleur (111, 112), et un nœud de sortie d'onduleur (116) connectant deux de la pluralité de dispositifs de commutation d'onduleur (S3, S4), dans lequel le circuit de commutation d'onduleur comprend : un premier dispositif de commutation d'onduleur (S2) avec une première borne connectée au premier nœud d'entrée de circuit onduleur (111) et une seconde borne connectée au premier nœud interne (114),un deuxième dispositif de commutation d'onduleur (S3) avec une première borne connectée au premier nœud interne (114) et une seconde borne connectée au nœud de sortie d'onduleur (116),un troisième dispositif de commutation d'onduleur (S4) avec une première borne connectée au nœud de sortie d'onduleur (116) et une seconde borne connectée à un deuxième nœud interne (118), etun quatrième dispositif de commutation d'onduleur (S5) avec une première borne connectée au deuxième nœud interne (118) et une seconde borne connectée au second nœud d'entrée de circuit d'onduleur (112) ; etun circuit de serrage comprenant des premier et second éléments de serrage (D1, D2) connectés en série l'un à l'autre entre des premier et deuxième nœuds internes (114, 118) du circuit de commutation d'onduleur, et un troisième nœud interne (119) raccordant les premier et second éléments de serrage (D1, D2) ; dans lequel le premier élément de serrage (D1) comprend une première borne connectée à un troisième nœud interne (119), et un seconde borne connectée au premier nœud interne (114) ;dans lequel le second élément de serrage (D2) comprend une première borne connectée au deuxième nœud interne (118) et une seconde borne connectée au troisième nœud interne (119) ;un circuit à condensateurs commutés (104), comprenant : des dispositifs de commutation de circuit à condensateurs commutés (S1, S6) connectés individuellement entre une entrée DC correspondante (101, 102) et un nœud d'entrée de circuit onduleur correspondant (111, 112), etdes premier et second condensateurs (C1, C2) connectés individuellement entre un nœud correspondant des nœuds d'entrée de circuit onduleur (111, 112) et le troisième nœud interne (119) ; etdans lequel les dispositifs de commutation de circuit à condensateurs commutés (S1, S6) comprennent en outre : un premier dispositif de commutation de circuit à condensateurs commutés (S1) avec une première borne connectée à une première entrée DC (101), et une seconde borne connectée au premier nœud d'entrée de circuit onduleur (111), etun second dispositif de commutation de circuit à condensateurs commutés (S6) avec une première borne connectée au second nœud d'entrée de circuit onduleur (112), et une seconde borne connectée à une seconde entrée DC (102) ;dans lequel le premier condensateur (C1) comprend une première borne connectée au premier nœud d' entrée de circuit onduleur (111) et une seconde borne connectée au troisième nœud interne (119) ; etdans lequel le second condensateur (C2) comprend une première borne connectée au troisième nœud interne (119) et une seconde borne connectée au second nœud d'entrée de circuit onduleur (112),dans lequel le troisième nœud interne (119) n'est pas connecté à un quelconque neutre système,un dispositif de commande (122) conçu pour fournir des signaux de commande de commutation à la pluralité de dispositifs de commutation d'onduleur (S2-S5) et aux dispositifs de commutation de circuit à condensateurs commutés (S1, S6) pour fournir une tension de sortie à multiples niveaux au niveau du nœud de sortie d'onduleur (116) et pour commander la charge et la décharge des premier et second condensateurs (C1, C2), dans lequel les signaux de commande forment six vecteurs de commutation possibles V1, V2, V3, V4, V5, V6, comprenant : vecteur V1 correspondant à un état de commutation dans lequel le premier dispositif de commutation de circuit à condensateurs commutés (S1) et les premier et deuxième dispositifs de commutation d'onduleur (S2, S3) sont activés et le second dispositif de commutation de circuit à condensateurs commutés (S6) et les troisième et quatrième dispositif de commutation d'onduleur (S4, S5) sont désactivés ;vecteur V2 correspondant à un état de commutation dans lequel le premier dispositif de commutation de circuit à condensateurs commutés (S1) et les deuxième et troisième dispositifs de commutation d'onduleur (S3, S4) sont activés et le second dispositif de commutation de circuit à condensateurs commutés (S6) et les premier et quatrième dispositifs de commutation d'onduleur (S2, S5) sont désactivés ;vecteur V3 correspondant à un état de commutation dans lequel les premier et deuxième dispositifs de commutation d'onduleur (S2, S3) et le second dispositif de commutation de circuit à condensateurs commutés (S6) sont activés et le premier dispositif de commutation de circuit à condensateurs commutés (S1) et les troisième et quatrième dispositifs de commutation d'onduleur (S4, S5) sont désactivés ;vecteur V4 correspondant à un état de commutation dans lequel le premier dispositif de commutation de circuit à condensateurs commutés (S1) et les troisième et quatrième dispositifs de commutation d'onduleur (S4, S5) sont activés et les premier et deuxième dispositifs de commutation d'onduleur (S2, S3) et le second dispositif de commutation de circuit à condensateurs commutés (S6) sont désactivés ;vecteur V5 correspondant à un état de commutation dans lequel les deuxième et troisième dispositifs de commutation d'onduleur (S3, S4) et le second dispositif de commutation de circuit à condensateurs commutés (S6) sont activés et le premier dispositif de commutation circuit à condensateurs commutés (S1) et les premier et quatrième dispositifs de commutation d'onduleur (S2, S5) sont désactivés ; etvecteur V6 correspondant à un état de commutation dans lequel les troisième et quatrième dispositifs de commutation d'onduleur (S4, S5) et le second dispositif de commutation de circuit à condensateurs commutés (S6) sont activés et le premier dispositif de commutation de circuit à condensateurs commutés (S1) et les premier et deuxième dispositifs de commutation d'onduleur (S2, S3) sont désactivés ; etdans lequel les vecteurs de commutation V2 et V3 sont redondants l'un avec l'autre par rapport à la tension de sortie entre ligne et neutre, et dans lequel le vecteur de commutation V3 permet aux premier et second condensateurs (C1, C2) d'être chargés ou déchargés simultanément etdans lequel les vecteurs de commutation V4 et V5 sont redondants l'un avec l'autre par rapport à la tension de sortie entre ligne et neutre, et dans lequel le vecteur de commutation V4 permet aux premier et second condensateurs (C1, C2) d'être chargés ou déchargés simultanément. Convertisseur de puissance à multiples niveaux (100) selon la revendication 1, dans lequel le dispositif de commande (122) fournit les signaux de commande de commutation aux dispositifs de commutation d'onduleur (S2-S5) et aux dispositifs de commutation de circuit à condensateurs commutés (S1, S2) pour fournir la tension de sortie à l'un parmi quatre niveaux distincts. Convertisseur de puissance à multiples niveaux (100) selon la revendication 2, dans lequel le dispositif de commande (122) sélectionne parmi une pluralité d'états de commutation redondants au moins l'un des quatre niveaux de tension de sortie distincts lors de la fourniture des signaux de commande de commutation pour commander la charge et la décharge des premier et second condensateurs (C1, C2) pour réguler des première et seconde tensions de condensateur correspondantes (VC1, VC2) à moins de la moitié d'une tension d'entrée DC (VDC) entre les première et seconde entrées DC (101, 102). Convertisseur de puissance à multiples niveaux (100) selon la revendication 2, dans lequel le dispositif de commande (122) fournit les signaux de commande de commutation aux dispositifs de commutation d'onduleur (S2-S5) et aux dispositifs de commutation de circuit à condensateurs commutés (S1, S2) pour fournir la tension de sortie à l'un parmi quatre niveaux distincts d'échelons sensiblement espacés de manière égale. Convertisseur de puissance à multiples niveaux (100) selon l'une quelconque des revendications 1 à 4, dans lequel le dispositif de commande (122) fournit les signaux de commande de commutation aux dispositifs de commutation d'onduleur (S2-S5) et aux dispositifs de commutation de circuit à condensateurs commutés (S1, S2) pour fournir la tension de sortie à l'un d'une pluralité de niveaux distincts d'échelons sensiblement espacés de manière égale. Système de conversion de puissance (300, 400, 420, 430, 440, 450, 1000), comprenant une pluralité de convertisseurs de puissance à multiples niveaux (100) selon la revendication 1. Système de conversion de puissance (300) selon la revendication 6, dans lequel le dispositif de commande (122) fournit les signaux de commande de commutation aux dispositifs de commutation d'onduleur (S2-S5) et aux dispositifs de commutation de circuit à condensateurs commutés (S1, S2) pour fournir la tension de sortie de chaque convertisseur de puissance à multiples niveaux (100) à l'un parmi au moins quatre niveaux distincts. | [ZH CN104242710B]: 改进的多电平电压源转换器和系统 背景技术 [0001] 电力转换器用于将输入电能从一种形式转换为另一种形式以驱动负载。电力转换 器系统的一种形式为电机驱动器，其可以被采用用于电动机负载的变速操作。针对需要相 对大的输出电压的应用，开发了所谓的多电平电压源转换器结构，包括飞跨电容器设计、中 性点钳位(NPC)设计以及级联混合类型。NPC设计包括跨提供中性节点的直流输入连接的一 对电容器，每个电容器被充电至直流输入值的一半。跨直流母线连接了一系列开关，一对二 极管将中间开关节点连接至中性点。NPC转换器有利地提供了相对简单的电路结构，但是增 加NPC转换器中的输出电平的个数增加了开关和二极管传导损耗并且导致增加的反向恢复 电流。另外，高输出电平NPC转换器经受开关器件损耗的不均匀分布，从而限制针对给定开 关类型的最大电力定额、输出电流和开关频率。此外，随着输出电平的个数增加，钳位二极 管的个数基本上增加。飞跨电容器设计利用选择性地互连的一个或更多个电容器以提供输 出电压。然而，该类多电平转换器经受高切换频率的需求以保持电容器适当平衡，并且飞跨 电容器上的电压必须初始化。可以使用级联H桥接(CHB)类型以实现显著高的输出电压电平 和高输出电力定额，并且使得能够使用相对低的切换频率和低电压部件。然而，CHB设计需 要显著更高个数的部件以实现再生操作，CHB转换器通常需要相移变压器，导致更高的成 本。另外，CHB方法需要大量的隔离直流源。因此，仍然需要能够提供用于以可变的速度和扭 矩驱动负载的多电平逆变器输出能力的改进的多电平电力转换器和系统设计。 发明内容 [0002] 现在总结本公开内容的各个方面以便利对本公开内容的基本理解，其中，本发明 内容不是本公开内容的宽泛概述，既不意在标识本公开内容的特定元素，也不意在描述本 公开内容的范围。更确切地，本发明内容的主要目的为在以下呈现更详细的描述之前以简 化形式来呈现本公内容的各种构思。 [0003] 本公开内容提供了多电平电力转换器级和采用以多种配置连接的两个或更多个 这样的多电平转换器的电力转换系统。多电平电力转换器包括NPC型逆变器电路，其嵌套在 开关电容器电路中以形成嵌套NPC(NNPC)电力转换器，其中，控制器操作逆变器和开关电容 器电路的开关以提供多电平输出电压。在某些实施方式中，控制器采用对冗余开关状态的 选择性选择来控制开关电容器的充电和放电以实现预定的目标电容器电压值。在某些实施 中，开关控制和电容器电压调节有利地确保开关电容器电压小于直流输入电压值的一半， 便利提供在基本上等间隔步进的多个不同电平之一处的转换器输出电压，从而平衡由各个 开关器件可见的电压。 [0004] 在某些实施方式中，逆变器电路包括在逆变器电路输入节点之间串联连接的两个 或更多个逆变器开关器件、以及连接所述逆变器开关器件中的两个逆变器开关器件的逆变 器输出节点。所述逆变器还包括钳位电路，所述钳位电路具有在所述逆变器开关电路的第 一内部节点与第二内部节点之间串联连接的第一钳位元件和第二钳位元件例如钳位开关 或二极管、以及接合所述第一钳位元件与所述第二钳位元件的第三内部节点。在某些实施 中，开关电容器电路包括:两个或更多个开关，所述两个或更多个开关各自连接在所述逆变 器输入节点之一与相应的直流输入之间；以及第一电容器和第二电容器，所述第一电容器 和第二电容器各自连接在所述逆变器电路输入节点中的相应一个与所述第三内部节点之 间。所述控制器向逆变器开关和开关电容器电路开关器件提供开关控制信号，以提供在所 述逆变器输出节点处的多电平输出并且控制第一电容器和第二电容器的充电和放电。各种 实施是可以的，例如四个或更多个不同的线与中性点之间的输出电压电平。某些实施提供 了级联的开关电容器电路系统，其包括针对更高个数的可能输出电平的两个飞跨电容器以 及相关联的开关器件的多个集合。 [0005] 根据本公开内容的另外的方面，提供了一种电力转换系统，包括两个或更多个嵌 套NPC转换器级或模块。在某些实施方式中，两个NNPC模块的直流输入被连接在一起，其中， 第一转换器级的逆变器输出连接至系统中性节点，第二级的逆变器输出提供系统的交流输 出。以这种方式，可以实现NNPC H桥接配置，两个或更多个这样的配置可以级联或串联连接 以实现各种输出电力电平和输出电压。此外，可以使用这样的模块或其组的多个集合来构 造电力转换系统，以提供用于驱动负载的多相输出。另外，在这些多级系统中，可以提供开 关控制以从各种冗余总开关状态中进行选择以实现对各个开关电容器的充电和放电的控 制，并且可以便利由各个开关器件可见的电压平衡并且有利地提供在基本上等间隔步进的 任何合适个数的不同电平处的输出电压。 附图说明 [0006] 以下描述和附图详细提出了本公开内容的某些示例性实施，其表示其中可以执行 本公开内容的各种原理的若干个示例性方式。然而，所示示例并不是本公开内容的许多可 能实施方式的穷举。当结合附图考虑时，本公开内容的其他目的、优点和创新特征将在以下 详细描述中提出，在附图中： [0007] 图1是示出了根据本公开内容的一个或更多个方面的示例性嵌套中性点钳位 (NNPC)多电平电力转换器的示意图，该NNPC多电平电力转换器包括逆变器电路和开关电容 器电路以及控制器，该控制器使用冗余开关状态选择以控制第一飞跨电容器和第二飞跨电 容器的充电和放电以提供多电平输出电压、并将飞跨电容器调节为直流输入电压电平的三 分之一； [0008] 图2是示出了以基本上等间隔的步进提供四电平电压输出的图1中的NNPC电力转 换器的开关状态的示例性集合的部分示意图； [0009] 图3是示出了提供三相电压输出以驱动电机负载的三个NNPC电力转换器和相关联 的直流源的示意图； [0010] 图4是示出了针对图1和图2的NNPC电力转换器的四电平线与中性点间的电压输出 波形的曲线图； [0011] 图5是示出了针对图3的三相电机驱动实施的七电平线间电压输出波形的曲线图； [0012] 图6是示出了在图1和图2的NNPC电力转换器控制器中的示例性电平移位脉宽调制 实施的曲线图； [0013] 图7是示出了用于在图1和图2的NNPC电力转换器控制器中提供脉宽调制开关控制 信号的示例性空间矢量调制技术的曲线图； [0014]图8是示出了在图1和图2的NNPC电力转换器控制器中的示例性脉宽调制处理的流 程示意图，所述脉宽调制处理向一个或更多个NNPC电力转换器提供开关控制信号，以在逆 变器输出节点处提供多电平输出电压并且将飞跨电容器的充电和放电控制为预定电平； [0015]图9是示出了NNPC H桥接(NNPCHB)电力转换系统的示意图，该NNPCHB电力转换系 统包括具有提供系统中性点的第一级的逆变器输出和提供线电压输出以驱动电机负载的 第二级的逆变器输出的两个NNPC电力转换器级； [0016] 图10A至10D示出了如下开关状态表:其向图9的NNPC H桥接电力转换系统提供开 关控制信号，以生成多电平输出电压并且控制每个NNPC电力转换器级的飞跨电容器的充电 和放电； [0017] 图11是示出了针对图9的NNPC H桥接电力转换系统的示例性七电平线与中性点间 的电压输出波形的曲线图； [0018] 图12是示出了针对图9的NNPC H桥接电力转换系统的示例性13电平线间电压输出 波形的曲线图； [0019]图13是示出了具有被配置成提供三相校正用于生成直流母线电压的三个NNPC电 力转换器的示例性三相电力转换系统的示意图，其中，三个NNPC电力转换器提供三相交流 输出，直流母线中点节点通过可选阻抗链接连接至可选的输入和输出滤波器； [0020] 图14是示出了具有提供校正的三个NNPC转换器和提供交流输出的三个NNPC转换 器的另一个示例性三相电力转换系统的示意图，其中，输入变压器和直流母线中点节点通 过可选阻抗链接连接至输出滤波器； [0021] 图15是示出了多相电力转换系统的示意图，该多相电力转换系统使用向用于三个 输出相的电力NNPC转换器提供直流母线的三个串联连接的输入整流器； [0022]图16是示出了具有针对分别由多脉冲整流器驱动的三个输出相中的每个相的 NNPC H桥接(NNPCHB)转换器级的另一个示例性三相电力转换系统的示意图； [0023]图17是示出了具有针对每个相的多个级联NNPC H桥接(NNPCHB)电力转换器的另 一个三相电力转换系统的示意图； [0024] 图18是示出了具有连接在直流输入端子之间的集成式电容器的NNPC电力转换器 级的另一个实施方式的示意图； [0025] 图19是示出了与电感器串联连接以形成模块化输出相的图18中的两个NNPC电力 转换器级的示意图； [0026] 图20是示出了与电感器串联连接以形成模块化输出相的图18中的整数个NNPC电 力转换器级的示意图； [0027] 图21是示出了针对图19中的NNPC电力转换器级的七电平线与中性点间的电压输 出波形的曲线图； [0028]图22是示出了针对图19中的NNPC电力转换器级的13电平线间电压输出波形的曲 线图； [0029]图23是示出了级联的基于NNPC的电力转换系统的单相的示意图，其中，第一NNPC 转换器的逆变器输出连接至第二NNPC转换器的直流电源中点节点； [0030]图24是示出了针对图23的级联的基于NNPC的电力转换系统的示例性七电平线与 中性点间的电压输出波形的曲线图； [0031] 图25是示出了针对图23中的电力转换系统的示例性13电平线间电压输出波形的 曲线图； [0032] 图26是示出了另一个示例性NNPC电力转换器和相关联的开关表的部分示意图，其 中，控制器将开关电容器电压调节成直流输入电压的四分之一； [0033] 图27是示出了另一个示例性NNPC电力转换器和相关联的开关表的部分示意图，其 中，控制器将开关电容器电压调节成直流输入电压的五分之一； [0034]图28是示出了根据本公开内容的另外的方面的具有多个开关电容器嵌套级的另 一个交替NNPC电力转换器的示意图；以及 [0035]图29是示出了使用向针对三个输出相的电力NNPC转换器提供直流母线的三个串 联连接的输入整流器的另一个多相电力转换系统的示意图，该多相电力转换系统具有用于 对开关电容器进行预充电和电压平衡的主电力变压器或不同变压器的辅助绕组。 具体实施方式 [0036] 现在参照附图，以下结合附图描述若干个实施方式或实施，其中，相同的附图标记 用于贯穿全文指代相同元件，以及其中各个特征未必是按比例的。以下将说明并描述电力 转换器级100以及通过所示转换器级100的各种互连形成的电力转换系统，其中，可以使用 所描述的嵌套NPC (NNPC)电力转换器100以形成用于驱动任何类型的负载的单相或多相电 源，可以在电机驱动器中采用所描述的电力转换器和电力转换系统，尽管本公开内容的各 种构思并不限制于任何特定应用。 [0037]图1示出了示例性多电平电力转换器100,其分别具有第一直流输入101和第二直 流输入102、以及提供单相交流输出电压和相关联的输出电流iQUT以驱动负载(未示出）的交 流输出120。所示电力转换器100在本文中被称为嵌套中性点钳位(NNPC)电力转换器，并且 包括嵌套在NPC型逆变器电路110中的开关电容器(例如飞跨电容器）电路104。尽管在本文 中被称为NNPC电力转换器，但是NPC型逆变器电路110的中心节点119不需要连接至任何系 统“中性点”。通过端子101和102向电力转换器100提供来自直流源90的输入直流电能，其 中，图1示出了包括两个串联连接的电池的示例性输入配置，每个电池具有VDC/2的电压值从 而向电力转换器100提供具有值VDC的直流输入电压。此外，尽管不是对电力转换器100的所 有实施的严格要求，但是图1中所示的配置包括连接至直流输入源90的两个电池的连接点 的中性节点“N”。可以结合电力转换器100使用任何合适的直流源90,包括但不限制于一个 或更多个电池、有源和/或无源整流器等。另外，直流源90可以包括直流母线电容器、单个电 容器或任何串联和/或并联配置连接的多个电容器的任意组合。此外，如以下结合图18所示 的，NNPC转换器级100的某些实施方式可以包括在直流输入端子101与102之间连接的机载 电容。 [0038] 如图1所示，逆变器电路110包括在第一逆变器电路输入节点111与第二逆变器电 路输入节点112之间彼此串联连接的开关器件S2至S5、以及连接所述开关器件中的两个开 关器件S3和S4的逆变器输出节点116，其中，逆变器输出节点116直接或间接连接至转换器 100的交流输出端子120。另外，逆变器电路110可以包括在节点111与节点112之间彼此串联 连接的任何整数个开关器件S。在所示示例中，提供了四个器件S2至S5,输出节点116具有在 输出节点116与上输入节点111之间的两个开关器件S2和S3,以及在输出节点116与第二逆 变器输入节点112之间连接的两个开关S4和S5。此外，开关电容器电路104包括如所示在逆 变器输入111与对应的直流输入端子1 〇 1之间的附加开关S1以及在逆变器输入112与对应的 直流输入端子102之间的附加开关S6。可以在电力级100的电路104和110中使用任何合适类 型的开关器件S1至S6,包括但不限制于基于半导体的开关例如绝缘栅双极晶体管（IGBT)、 硅可控整流器(SCR)、门极可关断晶闸管(GTO)、集成门极换向晶闸管（IGCT)等。另外，如图1 所示，各个开关S1至S6包括用于当开关断开时导通在反向上的电流的二极管。 [0039] NNPC转换器100的逆变器电路110还包括具有第一钳位元件和第二钳位元件例如 彼此串联连接的二极管D1和D2的钳位电路，D1的阴极连接至第一内部节点114，D2的阳极连 接至第二内部节点118A2的阴极在第三内部节点119处接合至D1的阳极。在该配置中，D1提 供了从第三内部节点119到第一内部节点114的导通路径，D2提供了从第二内部节点118到 第三内部节点119的导通路径。可以在其他实施方式中使用有源钳位开关或其他钳位元件 代替如在附图中所示的钳位二极管。其中二极管或其他钳位元件在逆变器开关电路的第一 内部节点与第二内部节点之间彼此串联连接的其他配置也是可以的。另外，可以如所示地 使用单个二极管D1和D2,或可以使用多个二极管或其他钳位元件。例如，可以使用以在节点 119与节点114之间以任何合适的串联和/或并联配置互连的两个或更多个二极管来代替 D1，使用在节点118与节点119之间以任何合适的方式互连的两个或更多个二极管来代替 D2。另外，跨NNPC转换器100的开关器件S1至S6的二极管D1和D2和/或钳位二极管可替换地 可以为钳位开关(未示出）。还可以由有源开关代替钳位二极管D1和D2以实现有源中性点钳 位。 [0040] 开关电容器电路104包括在预期直流输入端子101和102与逆变器电路输入节点 111和112中的对应之一之间连接的开关S1和S6。此外，开关电容器电路104包括如所示分别 连接在第三内部节点119与对应的逆变器电路输入节点111之间的第一电容器C1以及连接 在第三内部节点119与对应的逆变器电路输入节点112之间的第二电容器C2。可以使用任何 适合类型和配置的电容器C1和C2,其中，各个电容器C1和C2可以为以任何合适的串联和/或 并联配置连接以提供节点111与节点119之间的第一电容C1以及节点119与节点112之间的 第二电容C2的单个电容器或多个电容器。另外，优选地C1和C2具有基本上相等的电容值，尽 管本公开内容未如此严格要求。 [0041] 还参照图2至图5,控制器122向各个逆变器开关器件S2至S5提供开关控制信号 124-2、124-3、124-4以及124-5,并且向开关电容器电路开关器件S1和S6提供开关控制信号 124-1和124-6。如果钳位器件D1和D2是有源器件，则控制器122还向有源钳位器件D1和D2提 供开关控制信号。控制器122还接受未在图中示出的反馈信号例如电压和/或电流。控制器 122可以被实施为转换器100的一部分和/或可以为分立的部件或系统，单个控制器122可以 向多个转换器级100提供信号124。可以使用任何合适的硬件、处理器执行软件或固件或上 述组合来实施转换器控制器122,其中，控制器122的示例性实施方式包括一个或更多个处 理元件例如微处理器、微控制器、FPGA、DSP、可编程逻辑电路等、以及电子存储器、程序存储 器以及信号调节驱动器电路元件，处理元件被编程或不然被配置成生成适于操作电力级 100的开关器件的逆变器开关控制信号124以及执行其他电机驱动操作任务以驱动负载。另 夕卜，计算机可读介质被设想具有用于实施所描述的电力转换器开关控制处理以及技术的计 算机可执行指令，该计算机可执行指令可以被存储在形成控制器122的一部分的或不然与 控制器122在操作上相关联的电子存储器中作为程序指令。 [0042] 最好由图2可见，将开关控制信号124以脉宽调制的形式提供给开关S1至S6、以提 供在逆变器输出节点116处的多电平输出电压(例如线与中性点间的电压Van)。在所示实施 方式中，例如，控制器122向开关S1至S6提供开关控制信号124以提供在四个不同的线与中 性点间的电压电平之一处的输出电压Van。图4中的曲线图210示出了相对于中性节点“N”在 逆变器输出节点116处的示例性四电平线与中性点间的电压波形212 (Vm)。另外，由图3可 见，三个不同的NNPC转换器级100可以连接至对应的直流源90以向电机相线路202提供交流 输出电压以驱动三相电机负载200，其中控制器122向每个NNPC级100提供开关控制信号124 的集合。图5示出了表示图3的系统中的示例性线间电压波形222的曲线图220，其中在相对 的相位角120 °处的三个NNPC级100的受控切换提供七电平线间电压波形222。 [0043]另外，在某些实施方式中，提供开关控制信号124操作以控制开关电容器C1和C2的 充电和放电，以将对应的电容器电压VC1和VC2调节成在第一直流输入101和第二直流输入 102处接收的直流输入电压Vdc的目标部分。另外，控制电容器电压Vci和Vc2便利了在各个开 关器件S1至S6处可见的电压的基本上均匀的分布，从而提供显著的优点。图2示出了表示与 NNPC开关器件S1至S6的不同开关状态对应的六个可能的开关矢量¥1、¥2、¥3、¥4、¥5和¥6以 及相对于输入直流电平Vdc的对应的线与中性点间的电压值的不例性开关状态表126，其中 “1”表示对应开关S“接通”或导通。在操作中，第一矢量VI提供+VDC/2的输出电压电平，第二 开关矢量V2与第三开关矢量V3相对于线与中性点间的输出电压彼此冗余，每个矢量获得+ Vdc/6的值。矢量V4与矢量V5也是冗余开关状态对，每个矢量提供-Vdc/6的输出值，最终开关 状态或矢量V6获得-VDC/2的输出电压。由图2可见，另外，通过冗余矢量选择来控制电容器C1 和C2的充电和放电，针对冗余开关状态对相应的电容器电压的作用可以不同、使得智能地 选择矢量以控制电容器充电和/或放电。例如，如果期望输出电压电平为Vdc/6,则当输出电 流Iolit为正(&gt;0)时可以选择矢量V2对C1进行充电，或当输出电流为负时可以选择矢量V2对 C1进行放电。可替代地选择冗余矢量V3针对正输出电流对C1和C2进行放电，当输出电流为 负时对这些电容器C1和C2进行充电。另外，由图2的表126中可见，可以当期望输出电压电平 为-Vdc/6时通过从冗余矢量V4和V5进行选择来进行相似的充电和/或放电选择。 [0044] 还参照图6和图7,可以在控制器122中使用任何合适形式的脉宽调制开关控制信 号生成技术。图6中的曲线图230示出了示例性基于载波的脉宽调制实施，其中相反极性的 调制信号231和232与电平移位三角形载波波形233、234和235—起使用用于生成用于六个 转换器开关S1至S6的开关控制信号124。在另一个可能的实施方式中，如图7的曲线图240所 示可以使用空间矢量调制，其中控制器122确定围绕如所示的参考矢量Vref的当前位置的三 个控制矢量V1、V2和V3的相对次数，其中参考矢量Vrrf具有相应的调制索引（M)和相应的相 位角9,并且根据在某些电机驱动器实施中的期望电机负载位置和扭矩贯穿空间矢量调制 图240进行旋转。 [0045] 参照图2和图8,在图8的流程图中示出了用于生成脉宽调制开关控制信号124的处 理250,该处理250可以在图1和图2的NNPC电力转换器控制器的控制器122中实施。以下以一 些列动作或事件的形式来说明和描述处理250,尽管本公开内容的各个方法并不受这样的 动作或事件的所示顺序的限制。关于此，除非在下文特别指出，一些动作或事件可以与除了 根据本公开内容在此说明和描述的动作或事件之外的其他动作或事件以不同顺序和/或同 时发生。还应当注意，并非所有说明的步骤需要实施根据本公开内容的处理或方法，可以将 一个或更多个这样的动作进行组合。本公开内容的所示方法250和其他方法可以以硬件、处 理器执行软件或其组合的形式例如在示例性控制器122中来实施，并且可以以存储在有形 非暂态计算机可读介质例如在一个示例中的与控制器122在操作上相关联的存储器中的计 算机可执行指令的形式来体现。 [0046] 在操作中，将开关控制信号124提供给NNPC开关S1至S6以生成多电平输出电压Van、 并控制电容器C1和C2的充电和放电。图8的示例是针对三相系统(例如以上的图3)的，其中 控制器122执行空间矢量调制以生成针对与电机相A、B和C相关联的三个NNPC转换器100中 的每个的开关控制信号124。在某些实施中，基于关于输出电流iQUT的一个或更多个反馈值 (例如针对三相示例的Ia、Ib、Ic)以及针对NNPC转换器100中的每个的开关电容器电压VC1和 VC2来完成对冗余开关矢量(例如来自图2的表126)的选择。由图8可见，所示处理250表示空 间矢量调制处理，其中根据接收到的调制索引“M”和相位角“0”来确定期望输出状态(例如 电机位置和扭矩）。在252处接收并使用期望输出状态以识别参考矢量Vrrf (图7)的位置。参 考矢量转而用于识别三个周围控制矢量Vi、V#PV3 (例如图7)，空间矢量调制处理用于确定 在图8中的252处的对应的“接通时间”持续时间间隔t、t2和t3。在254处，控制矢量和持续时 间间隔用于确定针对与周围矢量Vl、V2和V3中的一个、一部分或全部相关联的每个电机输出 相的冗余开关状态(如果存在的话）。例如，图2中的状态表126表示矢量开关状态V2与V3如 V4与V5—样彼此冗余。在256处接收针对输出电流Ia、Ib和Ic的反馈以及针对每个相的开关 电容器电压Vci和VC2。 [0047] 在图8的258处，控制器122评估关于每个电机相的可用冗余开关状态的成本函数 “J”，并且从冗余状态中选择使各个相的成本函数最小化的那些冗余状态。在所示示例中， 成本函数与电容器电压(Vci)例如以上图1中的VC1和VC2相关，函数使用根据其调节这些电 容器电压（图8中的Vcref)的期望或预定的参考值。根据本公开内容的某些方面，不像传统 的NPC电力转换器，在某些实施方式中的目标调节飞跨电容器电压值Vcref小于VDC/2。例如， 在图1的示例中，通过控制器122智能地选择冗余开关矢量将电容器电压VC1和VC2控制或调 节成VDC/3。在其他非限制性示例中，目标值Vcref可以为小于直流输入电压的一半的另一个 值例如Vdc/4 (以下图26)或Vdc/5 (图27)。 [0048] 使用针对三相中的每个相选择的开关矢量，在图8的260处由控制器122执行选通 信号生成以生成针对每个对应的NNPC转换器级100的开关器件S1至S6的开关控制信号124 的三个集合。以这种方式，控制器122操作以使得将适当的输出电压提供给电机负载200 (图 3)并且还对每个NNPC电力级100的电容器C1和C2上的电压进行调节。这种对开关电容器电 压VC1和VC2的仔细调节转而便利NNPC转换器100的操作以提供在基本上等间隔输出电平处 的输出电压(例如图2中的Van)。例如，在图2的示例中，在以VDC/ 3的步进间隔开的四个不同 电平处提供输出电压。因此，使用在所示NNPC转换器100中的经调节的较低的电容器电压电 平便利通过开关器件S1至S6可见的电压的均匀分布。因此，所有的开关器件S1至S6经历相 等的电压应力，任一个器件不需要太大。 [0049] 还参照图9至图12,图9示出了电力转换器300,其包括以在本文中被称为NNPC H桥 接(NNPCHB)的H桥接配置连接的结合图1和图2以上描述的两个NNPC级100A和100B。NNPCHB 转换器300包括如上所述从源90接收输入直流电压的直流输入端子301和302,如所示输入 端子301和302被连接至NNPC级100A和100B二者的直流输入。与图1的NNPC转换器级100相 似，图9中的第一级100A包括开关器件SA1、SA2、SA3、SA4、SA5和SA6、以及钳位开关或其他钳 位元件DA1和DA2、以及具有相应电压Vcai和Vca2(例如VDc/k，其中k&gt;2)的电容器CA1和CA2。相 似地，第二级100B包括SB1、SB2、SB3、SB4、SB5和SB6、以及钳位元件DB1和DB2、以及具有相应 电容器电压VCBdPVCB2 (例如VDC/k，其中k&gt;2)的电容器CB1和CB2。在附图中将开关器件DA1、 DA2、DB1和DB2示出为二极管，但是有源开关例如IGBT和IGCT也可以用作钳位元件。 [0050] 图9中的逆变器100A的逆变器输出节点116连接至系统中性节点306,第二多电平 电力转换器100B的逆变器输出节点116提供电力转换系统300的交流输出304。在这种情况 下，控制器122向第一NNPC转换器100A提供开关控制信号124A、以及向第二NNPC级100B提供 开关控制信号124B的集合。在一个非限制性实施方式中，控制器122通过选择给定的矢量VI 至V36根据在图10A至10D中所示的开关状态或矢量表310,来提供开关控制信号以提供在七 个可能的电平之一处的期望的线与中性点间的电压Van。另外，由图9还可见，可以与相应的 直流源90—起提供NNPCHB转换器300的三个集合，以提供用于驱动三相电机负载200的输出 电压，对应转换器300的控制器122根据表310提供开关控制信号124,在一个可能的实施中 对应电机相的输出电压被移位120 °。 [0051] 由图10A至图10D可见，对应的开关电容器被调节成VDC/3的电压，等间隔输出电压 电平(线与中性点间的）可能包括Vdc (矢量VI)、2VDC/3 (V2至V5)、VDC/3 (矢量V6至V13)、0伏特 (矢量V14至V23)、-Vdc/3 (矢量V24至V31)、-2Vdc/3 (矢量V32至V35)以及针对矢量V36的-VDC〇 此外，由表310中可见，电压输出步进都等于(VDC/3)。图11中的曲线图320示出了针对图9中 的NNPC H桥接电力转换器300的示例性七电平线与中性点间的输出电压波形322。另外，在 所示三相示例中，图12示出了具有示例性13电平线间电压输出波形332的曲线图330。 [0052] 此外，如以上描述的NNPC实施方式100，NNPCHB转换器300中的控制器122当可能时 有利地从冗余矢量中选择，以调节构成NNPC级100A和100B的电容器上的开关电容器电压。 例如，冗余矢量V2至V5 (图10A)基于针对输出电平2VDC/3的输出电流IA的极性、提供对NNPC 级100A和100B的组成电容器CA1、CA2、CB1和CB2进行选择性地充电或放电的能力，以及在表 310中所示的其他冗余矢量组使得控制器122将电容器电压V™、VCA2、VCB1和VCB2有利地调节 成期望电平。关于此，在某些实施方式中，可以在操作控制器300时、控制器122采用以上描 述的图8中的处理250。另外，可以采用空间矢量调制或基于载波的脉宽调制技术用于生成 NNPCHB转换器300中的开关控制信号124。 [0053] 还参照图13至图17,本公开内容的另外的方面提供了具有多个NNPC电力转换器 100和/或多个NNPCHB转换器300的多电平电力转换系统400、420、430、440和450。图13示出 了如下非限制性示例400,其包括通过可选滤波器402 (电感器L、电感电容器CL、LCL等)耦接 至交流输入电源的三个NNPC转换器100,所述三个NNPC转换器100操作以接收在相应交流输 入端子(例如以上图1中的端子120)处的输入交流电压，直流端子连接至正和负的直流母线 轨道，从而三个NNPC转换器100的第一集合提供三相有源整流器。这些整流器级的输出提供 如所示在直流母线电容Ca和Cb上的直流母线电压。在某些实施中，可以将可选输入滤波器 402的中性点连接至通过可选阻抗链接408接合直流母线电容器Ca与Cb的直流母线中点或 中心节点。将直流母线电压提供作为至三个NNPC级100的另一个集合的直流输入端子（以上 图1中的端子101和102)的输入，这些级100的逆变器输出通过可选滤波器404提供交流输出 电压以驱动负载406。此外，由图13可见，可以将直流母线的中点通过可选阻抗链接410可选 地连接至输出滤波器404的中性点。图14示出了与以上图13的三相系统相似的另一个三相 系统420,输入变压器412向NNPC转换器100的第一集合提供交流输入电力。在一个非限制性 示例中，可以使用图13和图14中的系统410和420,以使用针对总计36个开关和12个钳位二 极管的六个NNPC级100的背靠背（back-to-back)配置来提供期望输出电压例如2kV至 7.2kV，所述钳位二极管还可以为有源钳位开关，在图14中的示例420附加地提供了通过变 压器412的隔离。 [0054]图15示出了另一个多相系统430,其具有向三个整流器434的集合中的每个整流器 提供三相次级线圈、以提供电容器Ca、Cb和Cc上的直流母线的输入变压器432。将由此产生 的母线上的直流电压提供给其交流输出通过可选输出滤波器404驱动三相负载406的三个 NNPC级100的集合的直流输入端子。在某些实施方式中，整流器434可以为二极管整流器、 SCR整流器、双电平、NPC三电平或NNPC四电平IGBT/IGCT整流器。整流器432和整流器433还 可以具有不同的脉冲个数，例如在一些实施方式中的6脉冲、12脉冲、24脉冲等。 [0055]图16示出了另一个三相电力转换系统440,其具有如下相移输入变压器432:通过 初级线圈32接收来自交流源20的电力、并提供在示例性角度25°、15°、5°、-5°、-15°和-25° 处的六个不同的三相次级线圈，每个次级线圈驱动如上所述的相应整流器434,由整流器 434中的两个分别驱动三个NNPCHB级300的集合(例如以上图9)，以提供通过可选输出滤波 器404的交流输出以驱动三相电机负载406。在本示例中，从而使用36脉冲变压器432提供 NNPC H桥接多相整流器系统440以实现期望输出电压例如10kV至15kV。在一个可能的替选 实施中，可以提供两个18脉冲变压器，或针对某些脉冲个数的相移角度的其他组合也是可 以的，或使用串联的不同个数的直流源也是可以的。 [0056]图17示出了使用再次结合图16以上描述的36脉冲变压器432的具有针对期望的输 出电压例如1 OkV至15kV的多脉冲整流器的级联NNPCHB系统。在这种情况下，通过由变压器 432的对应次级线圈驱动的对应整流器434来对每个NNPC H桥接级300进行供电，其中每个 级300包括如图9上述连接的一对NNPC级100。关于此，由一对NNPC H桥接级300驱动每个输 出相，第一级300的交流输出连接至电机相(通过可选输出滤波器404)，级300的中性点连接 至第二级300的交流输出，第二级300的中性端子连接至系统中性点N。变压器次级绕组和直 流整流器的个数、变压器次级绕组之间的相移角度以及其他设计参数可以针对该级联 NNPCHB的类型而变化。 [0057] 还参照图18至图22,图18示出了具有连接在直流输入端子101和102上的集成式电 容器C3的另一个NNPC电力转换器级实施方式500 (NNPC’）。图19示出了采用两个这样的 NNPC’级500用于通过输出电感器502提供相输出的示例性系统510,将正直流电压施加给第 一级500的交流端子120,第一级500的较低的直流端子102连接至电感器502的一端。电感器 502的较低端连接至第二级500的交流端子120,第二级500的较低的直流端子102连接至直 流源的较低（负)端子。电感器502的中心抽头连接提供了相输出㈧，多个这样的配置510可 以用于对多相负载(未示出)进行供电。图20示出了基于NNPC的模块化多电平系统520,其中 如上所述连接整数个NNPC’级500,级500的第一集合连接在上直流线路与电感器502的上端 之间，级500的第二集合连接在下电感器端子与下直流线路之间。图21提供了表示针对图19 的系统510 (使用两个NNPC’级500)的示例性线与中性点间的电压输出波形532的曲线图 530,提供了七电平线与中性点间的输出电压。此外，图22中的曲线图540表示提供13电压电 平的相应多相线间电压输出波形542。 [0058] 还参照图23至图25,图23示出了使用两个NNPC单元或级100的级联NNPC配置以及 对应的直流源90的另一个示例性系统600的单相。使用以相似方式连接的不止两个的NNPC 单元100的其他配置也是可以的。由图23的示例可见，系统中性点“N”连接至第一单元100的 直流输入源90的中点，第一单元100的交流输出连接至上（第二)单元100的直流源90的中 点。第二单元100的交流输出转而提供针对由系统600驱动的相的输出电压。在该配置中，控 制器122的操作提供了如图24的曲线图610中所示的七电平线与中性点间的输出电压波形 612、以及用于多相实施的图25的曲线图620中的13电平线间输出波形622。 [0059] 图26示出了另一个示例性NNPC电力转换器实施100,其中，控制器122根据所示开 关状态表700提供开关控制信号124用于操作开关S1至S6以提供在逆变器输出节点（交流） 处的多电平输出电压，以及控制开关电容器C1和C2的充电和放电。然而，在该实施中，控制 器122的操作将电容器电压VC1、VC2调节成直流母线电压电平的大约四分之一 (VDC/4)。另外， 图26中的所示相的输出(Van)具有VDC/4的等间隔步进。 [0060]图27示出了另一种可能的实施，其中控制器122根据状态表800进行操作提供开关 控制信号124,以生成在通过直流输入电压的大约五分之一 (Vdc/5)间隔开的六个不同的电 平之一处的多电平电压输出，控制器122操作以调节在直流输入电压电平的大约五分之一 处的电容器电压。 [0061] 图28示出了另一个NNPC电力转换器900,在这种情况下NNPC电力转换器包括关于 NPC核心电路110配置的多个开关电容器嵌套级。该嵌套电力转换器900包括逆变器电路 110、开关电容器电路104和控制器122。与图1的上述NNPC单元100—样，图28的转换器900中 的逆变器电路110包括在逆变器电路输入节点111与112之间彼此串联连接的开关器件S3至 S6,以及连接S4与S5的逆变器输出节点116。此外，逆变器电路110包括如所示与开关S4附近 的第一内部节点114与在开关S5附近的第二内部节点118彼此串联连接的钳位开关或其他 钳位元件D1和D2。钳位电路还包括接合钳位元件D1与D2的第三内部节点119。在附图中将钳 位器件表示为二极管。然而，为了钳位目的还可以使用有源开关例如IGBT和IGCT。转换器 900还包括双重嵌套的开关电容器电路104,其中第一开关S1连接在第一直流输入101与第 四内部节点106之间，第二开关S2连接在节点106与第一逆变器输入节点111之间。此外，第 三开关S7连接在第二逆变器电路输入节点112与第五内部节点108之间，第四开关S8连接在 第五内部节点108与第二直流输入102之间。 [0062] 在图28中提供了两电平的串联连接的开关电容器C1/C2和C3/C4，C1连接在节点 111与119之间，C2连接在节点119与112之间，C3连接在节点106与第六内部节点113之间、以 及C4连接在节点113与108之间。在某些实施中，可以接合节点113与119,尽管在所有实施方 式中未如此要求。控制器122提供开关控制信号124以操作逆变器开关S3至S6以及电容器开 关器件S1、S2、S7和S8以提供在逆变器输出节点116处的多电平输出电压、并例如使用如上 所述选择的冗余开关矢量来控制电容器C1至C4的充电和放电。 [0063]图29示出了另一个多相电力转换系统1000,其包括变压器432和三个串联连接的 输入整流器434以生成直流母线，与以上图15的系统430相似（图29中未单独示出控制器 122)，三个NNPC级100提供交流输出电压波形通过可选输出滤波器404以驱动三相负载406。 此外，图29的系统1000包括向六个附加整流器434提供交流输入的辅助变压器432’（或主变 压器432的辅助次级绕组），每个整流器434的由此产生的直流输出连接在NNPC级100的开关 电容器C1、C2中的相应一个上。在操作中，辅助变压器或次级线圈432’被选择性地供电，以 例如在整体系统1000上电时通过干预整流器434对每个所述级100的开关电容器C1和C2进 行预充电，之后当系统1000达到稳态操作时可以断电。 [0064] 以上示例仅说明了本公开内容的各个方面的若干可能的实施方式，其中当阅读并 理解本说明书和附图时、对本领域的技术人员会出现等同变化和/或修改。特别关于通过上 述部件(组件、器件、系统、电路等)执行的各种功能，用于描述这样的部件的术语(包括引用 的“装置”）除非特别指出意在与执行所描述部件的指定功能（即功能上等价)的任何部件例 如硬件、处理器执行软件或上述组合对应，即使所述部件与执行在本公开内容的所说明的 实施中的功能的所公开的结构在结构上不等价。此外，尽管可以相对于若干个实施中的仅 一个实施公开本公开内容的特定特征，但是这样的特征可以与针对任何给定或特定应用可 能期望并有利的一个或更多个其他特征或其他实施进行组合。此外，到术语“包括”、“包含” “具有”或其变型用于详细描述和/或权利要求中的程度，这样的术语意在以与术语“包括” 相似的方式为包容性的。 [0065] 本发明还可以通过以下方案来实现，包括但不限制于： [0066] 1. 一种多电平电力转换器，包括： [0067] 逆变器电路，所述逆变器电路包括： [0068] 逆变器开关电路，所述逆变器开关电路包括:在第一逆变器电路输入节点与第二 逆变器电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器 开关器件中的两个逆变器开关器件的逆变器输出节点，以及 [0069] 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部 节点之间彼此串联的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所述第 二钳位元件的第三内部节点； [0070] 开关电容器电路，所述开关电容器电路包括： [0071] 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流 输入与相应的逆变器电路输入节点之间，以及 [0072] 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器 电路输入节点中的相应一个与所述第三内部节点之间；以及 [0073] 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器 件提供开关控制信号，以提供在所述逆变器输出节点处的多电平输出电压并控制所述第一 电容器和所述第二电容器的充电和放电。 [0074] 2•根据1所述的多电平电力转换器， [0075] 其中，所述逆变器开关电路包括： [0076] 第一逆变器开关器件，所述第一逆变器开关器件具有连接至所述第一逆变器电路 输入节点的第一端子和连接至所述第一内部节点的第二端子， [0077] 第二逆变器开关器件，所述第二逆变器开关器件具有连接至所述第一内部节点的 第一端子和连接至所述逆变器输出节点的第二端子， [0078] 第三逆变器开关器件，所述第三逆变器开关器件具有连接至所述逆变器输出节点 的第一端子和连接至所述第二内部节点的第二端子，以及 [0079] 第四逆变器开关器件，所述第四逆变器开关器件具有连接至所述第二内部节点的 第一端子和连接至所述第二逆变器电路输入节点的第二端子； [0080] 其中，所述第一钳位元件包括连接至所述第三内部节点的第一端子和连接至所述 第一内部节点的第二端子； [0081] 其中，所述第二钳位元件包括连接至所述第二内部节点的第一端子和连接至所述 第三内部节点的第二端子； [0082] 其中，所述开关电容器电路包括： [0083] 第一开关电容器电路开关器件，所述第一开关电容器电路开关器件具有连接至第 一直流输入的第一端子和连接至所述第一逆变器电路输入节点的第二端子，以及 [0084] 第二开关电容器电路开关器件，所述第二开关电容器电路开关器件具有连接至所 述第二逆变器电路输入节点的第一端子和连接至第二直流输入的第二端子； [0085] 其中，所述第一电容器包括连接至所述第一逆变器电路输入节点的第一端子和连 接至所述第三内部节点的第二端子;以及 [0086] 其中，所述第二电容器包括连接至所述第三内部节点的第一端子和连接至所述第 二逆变器电路输入节点的第二端子。 [0087] 3.根据2所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件以及 所述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同电平之一处的输 出电压。 [0088] 4.根据3所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控制 所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二电容 器电压调节成小于在所述第一直流输入与所述第二直流输入之间的直流输入电压的一半。 [0089] 5.根据4所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的三分之一。 [0090] 6.根据4所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的四分之一。 [0091] 7.根据4所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的五分之一。 [0092] 8.根据1所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件和所 述开关电容器电路开关器件提供所述开关控制信号，以提供在四个不同电平之一处的输出 电压。 [0093] 9.根据8所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控制 所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二电容 器电压调节成小于在所述第一直流输入与所述第二直流输入之间的直流输入电压的一半。 [0094] 10.根据9所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的三分之一。 [0095] 11.根据9所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的四分之一。 [0096] 12.根据9所述的多电平电力转换器，其中，所述控制器在提供所述开关控制信号 时、从针对所述四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以 控制所述第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二 电容器电压调节成所述直流输入电压的五分之一。 [0097] 13.根据9所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件和 所述开关电容器电路开关器件提供所述开关控制信号，以提供在基本上等间隔步进的四个 不同电平之一处的输出电压。 [0098] 14.根据1所述的多电平电力转换器，其中，所述控制器向所述逆变器开关器件和 所述开关电容器电路开关器件提供所述开关控制信号，以提供在基本上等间隔步进的多个 不同电平之一处的输出电压。 [0099] 15•—种多电平电力转换器，包括： [0100] 逆变器电路，所述逆变器电路包括： [0101] 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆 变器电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开 关器件中的两个逆变器开关器件的逆变器输出节点，以及 [0102] 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部 节点之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所 述第二钳位元件的第三内部节点； [0103] 开关电容器电路，所述开关电容器电路包括： [0104] 第一开关电容器电路开关器件，所述第一开关电容器电路开关器件具有连接至第 一直流输入的第一端子和连接至第四内部节点的第二端子， [0105] 第二开关电容器电路开关器件，所述第二开关电容器电路开关器件具有连接至所 述第四内部节点的第一端子和连接至所述第一逆变器电路输入节点的第二端子， [0106] 第三开关电容器电路开关器件，所述第三开关电容器电路开关器件具有连接至所 述第二逆变器电路输入节点的第一端子和连接至第五内部节点的第二端子， [0107] 第四开关电容器电路开关器件，所述第四开关电容器电路开关器件具有连接至所 述第五内部节点的第一端子和连接至第二直流输入的第二端子， [0108] 第一电容器，所述第一电容器包括连接至所述第一逆变器电路输入节点的第一端 子和连接至所述第三内部节点的第二端子， [0109] 第二电容器，所述第二电容器包括连接至所述第三内部节点的第一端子和连接至 所述第二逆变器电路输入节点的第二端子， [0110] 第三电容器，所述第三电容器包括连接至所述第四内部节点的第一端子和连接至 第六内部节点的第二端子，以及 [0111] 第四电容器，所述第四电容器包括连接至所述第六内部节点的第一端子和连接至 所述第五内部节点的第二端子;以及 [0112] 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器 件提供开关控制信号，以提供在所述逆变器输出节点处的多电平输出电压并控制所述第一 电容器、所述第二电容器、所述第三电容器和所述第四电容器的充电和放电。 [0113] 16 •—种电力转换系统，包括多个多电平电力转换器，各个多电平电力转换器包 括： [0114] 逆变器电路，所述逆变器电路包括： [0115] 逆变器开关电路，所述逆变器开关电路包括在第一逆变器电路输入节点与第二逆 变器电路输入节点之间彼此串联连接的多个逆变器开关器件、以及连接所述多个逆变器开 关器件中的两个逆变器开关器件的逆变器输出节点，以及 [0116] 钳位电路，所述钳位电路包括在所述逆变器开关电路的第一内部节点与第二内部 节点之间彼此串联连接的第一钳位元件和第二钳位元件、以及接合所述第一钳位元件与所 述第二钳位元件的第三内部节点； [0117] 开关电容器电路，所述开关电容器电路包括： [0118] 开关电容器电路开关器件，所述开关电容器电路开关器件各自连接在相应的直流 输入与相应的逆变器电路输入节点之间，以及 [0119] 第一电容器和第二电容器，所述第一电容器和第二电容器各自连接在所述逆变器 电路输入节点中的相应一个与所述第三内部节点之间；以及 [0120] 控制器，所述控制器向所述多个逆变器开关器件以及所述开关电容器电路开关器 件提供开关控制信号，以提供在所逆变器输出节点处的多电平输出电压并控制所述第一电 容器和所述第二电容器的充电和放电。 [0121] 17.根据16所述的电力转换系统，包括： [0122] 第一多电平电力转换器；以及 [0123] 第二多电平电力转换器； [0124] 其中，所述第一多电平电力转换器与所述第二多电平电力转换器的直流输入被连 接在一起； [0125] 其中，所述第一多电平电力转换器的逆变器输出节点连接至系统中性节点；以及 [0126] 其中，所述第二多电平电力转换器的逆变器输出节点提供用于所述电力转换系统 的交流输出。 [0127] 18.根据16所述的电力转换系统，其中，所述控制器向所述逆变器开关器件和所述 开关电容器电路开关器件提供所述开关控制信号，以提供在至少四个不同电平之一处的每 个多电平电力转换器的输出电压。 [0128] 19.根据18所述的电力转换系统，其中，所述控制器在提供所述开关控制信号时、 从针对四个不同输出电压电平中的至少一个的多个冗余开关状态中进行选择，以控制所述 第一电容器和所述第二电容器的充电和放电、以将相应的第一电容器电压和第二电容器电 压调节成小于在所述第一直流输入与所述第二直流输入之间的直流输入电压的一半。 [0129] 20.根据16所述的电力转换系统，其中，所述多电平电力转换器的至少一个提供针 对所述电力转换系统的多个输出相的每个相的输出电压。 [0130] 部件列表 [0131] [0132] [0133] [0134] [EN EP2816719B1]: BACKGROUND Power converters are used to convert input electrical energy from one form to another for driving a load. One form of power conversion system is a motor drive, which may be employed for variable speed operation of an electric motor load. For applications requiring fairly large output voltages, so-called multilevel voltage source converter architectures have been developed, including flying capacitor designs, neutral point clamped (NPC) designs, as well as cascaded and hybrid typologies. NPC designs include a pair of capacitors connected across a DC input providing a neutral node, with each capacitor being charged to half the DC input value. A series of switches are connected across the DC bus, with a pair of diodes connecting intermediate switch nodes to the neutral point. The NPC converter advantageously provides a relatively simple circuit structure, but increasing the number of output levels in an NPC converter increases switching and diode conduction losses and leads to increased reverse recovery current flow. Moreover, high output level NPC converters suffer from uneven distribution of switching device losses thereby limiting the maximum power rating, output current and switching frequency for a given switch type. In addition, the number of clamping diodes increases substantially as the number of output levels increases. Flying capacitor designs utilize one or more capacitors that are selectively interconnected to provide the output voltage. This type of multilevel converter, however, suffers from the need for high switching frequencies to keep the capacitors properly balanced, and the voltages on the flying capacitors must be initialized. Cascaded H-bridge (CHB) topologies may be used to achieve significantly high output voltage levels and high output power ratings, while allowing the use of relatively low switching frequencies and low voltage components. However, CHB designs require a significantly higher number of components to achieve regenerative operation, and a CHB converter typically requires a phase-shifting transformer, leading to higher cost. Moreover, the CHB approach requires a large number of isolated DC sources. Accordingly, a need remains for improved multilevel power converters and system designs capable of providing multilevel inverter output capability for driving the load at variable speeds and torques. JP 2013 102674 A discloses a multilevel power converter which reduces the number of necessary semiconductor elements. The multilevel power converter comprises: a direct current power source; capacitors C3 and C4 connected in series between positive and negative electrode ends of the power source; switching elements S5 and S6, capacitors C1 and C2 and switching elements S7 and S8 which are sequentially connected in series between the positive and negative electrode ends of the power source; switching elements S1 to S4 connected in series between a common connection point between S6 and C1 and a common connection point between C2 and S7; diodes D1 and D2 connected in series between a common connection point between S1 and S2 and a common connection point between S3 and S4; and D3 and S11, and D4 and S12 connected in series between a common connection point NP' between C1 and C2 and a common connection point NP between C3 and C4. The common connection point between the elements S2 and S3 and the common connection point between C3 and C4 serve as AC output ends at a plurality of voltage levels. US 2013/148390 A1 discloses an electric circuit wherein a multi-phase bridge is connected in series with a plurality of single-phase bridges. The multi-phase bridge is composed of a plurality of 3-level diode clamped legs, while the single-phase bridges each is composed of two 3-level diode clamped legs. Moreover, also a control strategy is disclosed for synthesizing multi-level voltage waveforms from output voltages of the multi-phase bridge and the plurality of single-phase bridges. SUMMARY It is the object of the present invention to provide an improved system for converting electrical energy from one form to another. This object is solved by the subject matter of the independent claims. Preferred embodiments are defined by the dependent claims. Various aspects of the present disclosure are now summarized to facilitate a basic understanding of the disclosure, wherein this summary is not an extensive overview of the disclosure, and is intended neither to identify certain elements of the disclosure, nor to delineate the scope thereof. Rather, the primary purpose of this summary is to present various concepts of the disclosure in a simplified form prior to the more detailed description that is presented hereinafter. The present disclosure provides multilevel power converter stages as well as power conversion systems employing two or more such multilevel converters connected in a variety of configurations. The multilevel power converter includes an NPC type inverter circuit nested in a switched capacitor circuit to form a nested NPC (NNPC) power converter, with a controller that operates the switches of the inverter and switched capacitor circuit to provide a multilevel output voltage. The controller in certain embodiments employs selective choice of redundant switching states to control the charging and discharging of the switched capacitors to achieve a predetermined target capacitor voltage value. In certain implementations, the switching control and capacitor voltage regulation advantageously ensure switched capacitor voltages of less than half the DC input voltage value, and facilitate provision of the converter output voltage at one of multiple distinct levels of substantially equally spaced steps, thereby balancing the voltage seen by the individual switching devices. In certain embodiments, the inverter circuit includes two or more inverter switches connected in series between inverter circuit input nodes, with an inverter output node connecting two of the inverter switching devices. The inverter further includes a clamping circuit with first and second clamping elements, such as clamping switches or diodes, connected in series between first and second internal nodes of the inverter switching circuit, with a third internal node joining the first and second clamping elements. The switched capacitor circuit includes two or more switches individually connected between one of the inverter circuit input nodes and a corresponding DC input, as well as first and second capacitors individually connected between a corresponding one of the inverter circuit input nodes and the third internal node. The controller provides switching control signals to the inverter switches and to the switched capacitor circuit switching devices to provide multilevel output at the inverter output node and to control charging and discharging of the first and second capacitors. In accordance with further aspects of the disclosure, power conversion systems are provided, which include two or more of the nested NPC converter stages or modules. In certain embodiments, the DC inputs of two NNPC modules are connected together, with the inverter output of the first converter stage connected to a system neutral node, and the inverter output of the second stage providing an AC output for the system. In this manner, an NNPC H-bridge configuration can be achieved, and two or more such configurations can be cascaded or connected in series to achieve a variety of output power levels and output voltages. In addition, the power conversion systems can be constructed using multiple sets of such modules or groups thereof to provide the multiphase outputs for driving a load. In these multi-stage systems, moreover, the switching control can be provided to select from various redundant overall switching states in order to achieve control over the charging and discharging of the individual switched capacitors, and may facilitate balancing of voltages seen by individual switching devices and advantageously provide output voltages at any suitable number of distinct levels of substantially equally spaced steps. BRIEF DESCRIPTION OF THE DRAWINGS The following description and drawings set forth certain illustrative implementations of the disclosure in detail, which are indicative of several exemplary ways in which the various principles of the disclosure may be carried out. The illustrated examples, however, are not exhaustive of the many possible embodiments of the disclosure. Other objects, advantages and novel features of the disclosure will be set forth in the following detailed description when considered in conjunction with the drawings, in which: Fig. 1 is a schematic diagram illustrating an exemplary nested neutral point clamped (NNPC) multilevel power converter including an inverter circuit and a switched capacitor circuit with a controller using redundant switch state selection to control charging and discharging of first and second flying capacitors to provide multilevel output voltage and to regulate the flying capacitors to one third of the DC input voltage level in accordance with one or more aspects of the present disclosure;Fig. 2 is a partial schematic diagram illustrating an exemplary set of switching states for the NNPC power converter of Fig. 1 to provide a four-level voltage output with substantially equally spaced steps;Fig. 3 is a schematic diagram illustrating three NNPC power converters and associated DC supplies for providing a three-phase voltage output to drive a motor load;Fig. 4 is a graph showing a four-level line-to-neutral voltage output waveform for the NNPC power converter of Figs. 1 and 2;Fig. 5 is a graph illustrating a seven-level line-to-line voltage output waveform for the three-phase motor drive implementation of Fig. 3;Fig. 6 is a graph illustrating an exemplary level shifted pulse width modulation implementation in the NNPC power converter controller of Figs. 1 and 2;Fig. 7 is a graph illustrating an exemplary space vector modulation technique for providing pulse width modulated switching control signals in the NNPC power converter controller of Figs. 1 and 2;Fig. 8 is a flow diagram illustrating an exemplary pulse width modulation process in the NNPC power converter controller of Figs. 1 and 2 to provide switching control signals to one or more NNPC power converters to provide a multilevel output voltage at the inverter output node a
[EN US2021242797A1]: POWER CIRCUITS FOR MODULAR MULTI-LEVEL CONVERTERS (MMC) AND MODULAR MULTI-LEVEL CONVERTERS [FR EP3788711A1]: CIRCUITS DE PUISSANCE POUR CONVERTISSEURS MULTI-NIVEAUX MODULAIRES (MMC) ET CONVERTISSEURS MULTI-NIVEAUX MODULAIRES [DE EP3788711A1]: LEISTUNGSSCHALTUNGEN FÜR MODULARE MEHRSTUFENUMRICHTER (MMC) SOWIE MODULARE MEHRSTUFENUMRICHTER | [EN US2021242797A1]: The present invention relates to electronic power circuits and their use in power converters and in modular multi-level converters (MMCs) comprising such power converters. [FR WO2019210918A1]: La présente invention concerne des circuits de puissance électroniques et leur utilisation dans des convertisseurs de puissance et dans des convertisseurs multiniveaux modulaires (MMCs) comprenant de tels convertisseurs de puissance. | WO2019210918A1 | 2019-11-07 | DK2019050113W | 2019-04-10 | DKPA201870270A, 2018-05-04 | WO2019210918A1: 2019-11-07 EP3788711A1: 2021-03-10 US2021242797A1: 2021-08-05 | UNIV AALBORG | MUNK-NIELSEN STIG | H02M7/483: I H02M3/335: I | H02M3/33576: I H02M7/483: I H02M7/4835: I H02M3/33584: I | US2014268888A1 |  | [EN US2021242797A1]: 1. A power circuit arranged to receive a DC electric input signal at a first and a second connection terminals, and to output an AC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a third electrically controllable bidirectional two-quadrant switch, the fourth connection terminal being connected to a fourth electrically controllable bidirectional two-quadrant switch, the first, second, third and fourth switches being connected to a first node connected through a first node in such a way that the switches are connected between the first node and the respective first, second, third, and fourth connection terminals, a first capacitor being connected between the first and second connection terminals, a second capacitor being connected between the third and fourth connection terminals, and wherein one of the first and second connection terminals is connected to one of the third and fourth connection terminals through at least one electrically controllable bidirectional switch. 2. The power circuit according to claim 1, wherein the first connection terminal is connected to the third connection terminal through an electrically controllable bidirectional switch. 3. The power circuit according to claim 2, wherein the switch connecting the first and third connection terminals comprises a series connection of two electrically controllable switches. 4. The power circuit according to claim 1, wherein the second connection terminal is connected to the fourth connection terminal through an electrically controllable bidirectional switch. 5. The power circuit according to claim 4, wherein the switch connecting the second and fourth connection terminals comprises a series connection of two electrically controllable switches. 6. A power circuit arranged to receive a DC electric input signal at first and second connection terminals, and to output an AC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a third electrically controllable bidirectional two-quadrant switch, the fourth connection terminal being connected to a fourth electrically controllable bidirectional two-quadrant switch, the first switch, the second switch, the third switch and the fourth switch being connected to a first node in such a way that the switches are connected between the first node and the respective first, second, third, and fourth connection terminals, a first electronic component being connected to the first connection terminal, a second electronic component being connected to the second connection terminal, a third electronic component being connected to a second node, the second node, the first and third electronic component and the first connection terminal being connected, a fourth electronic component being connected to a third node, the third node, the second and fourth electronic component and the second connection terminal being connected, a first capacitor being connected to the second and third node, the first, second, third and fourth electronic components being connected to a first coupled inductor in such a way that: the first electronic component is connected between the first coupled inductor and the first connection terminal, the second electronic component is connected between the first coupled inductor and the second connection terminal, the third electronic component is connected between the first coupled inductor and the second node, and the fourth electronic component is connected between the first coupled inductor and the third node, wherein further: a fifth electronic component is connected to the third connection terminal, a sixth electronic component is connected to the fourth connection terminal, a seventh electronic component connected to a fourth node, the fourth node, the fifth and seventh electronic component and the third connection terminal being connected, an eighth electronic component is connected to a fifth node, the fifth node, the sixth and eighth electronic component and the fourth connection terminal being connected, a second capacitor is connected to the fourth and fifth node, the fifth, sixth, seventh and eighth electronic components, are connected to a second coupled inductor in such a way that: the fifth electronic component is connected between the second coupled inductor and the third connection terminal, the sixth electronic component is connected between the second coupled inductor and the fourth connection terminal, the seventh electronic component is connected between the second coupled inductor and the fourth node, and the eighth electronic component is connected between the second coupled inductor and the fifth node, and wherein the first, second, third, fourth, fifth, sixth, seventh and eighth electronic components are selected from the group consisting of an electrically controllable switch, a capacitor and a diode. 7. (canceled) 8. (canceled) 9. (canceled) 10. (canceled) 11. A power circuit arranged to receive a DC electric input signal at first and second connection terminals, and to output an AC or DC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a first electronic component, the fourth connection terminal being connected to a second electronic component, the first switch and the second switch being connected to a first node in such a way that the switches are connected between the first node and the respective first and second connection terminals, a third electronic component being connected to the first connection terminal, a fourth electronic component being connected to the second connection terminal, a third electrically controllable bidirectional two-quadrant switch being connected to a second node, the second node, the third electronic component the third electrically controllable bidirectional two-quadrant switch and the first connection terminal being connected, a fourth electrically controllable bidirectional two-quadrant switch being connected to a third node, the third node, the fourth electronic component, the fourth electrically controllable bidirectional two-quadrant switch and the second connection terminal being connected, a first capacitor being connected to the second and third node, the third electronic component, the fourth electronic component, the third electrically controllable bidirectional two-quadrant switch and the fourth electrically controllable bidirectional two-quadrant switch being connected to a first coupled inductor in such a way that: the third electronic component is connected between the first coupled inductor and the first connection terminal, the fourth electronic component is connected between the first coupled inductor and the second connection terminal, the third electrically controllable bidirectional two-quadrant switch is connected between the first coupled inductor and the second node, and the fourth electrically controllable bidirectional two-quadrant switch is connected between the first coupled inductor and the third node, wherein further: a fifth electronic component connected to a fourth node, the fourth node, the first and fifth electronic component and the third connection terminal being connected, a sixth electronic component is connected to a fifth node, the fifth node, the second and sixth electronic component and the fourth connection terminal being connected, a second capacitor is connected to the fourth and fifth node, the first, second, fifth and sixth electronic component are connected to a second coupled inductor in such a way that: the first electronic component is connected between the second coupled inductor and the third connection terminal, the second electronic component connected between the second coupled inductor and the fourth connection terminal, the fifth electronic component is connected between the second coupled inductor and the fourth node, and the sixth electronic component is connected between the second coupled inductor and the fifth node, and wherein: the first, second, fifth and sixth electronic component are diodes, or the first and second electronic component are diodes and the fifth and sixth electronic components are capacitors, or the first and second electronic component are capacitors and the fifth and sixth electronic components are diodes, and wherein further: the third and fourth electronic components are electrically controllable switches and the first node is connected to the fourth connection terminal, or the third and fourth electronic components are capacitors and the first node is connected to the fourth connection terminal, or the first and second electronic components are capacitors and the first node is connected to the third connection terminal. 12. The power circuit according to claim 1, wherein the electrically controllable switches comprise IGBT or MOSFET transistors with diode function enabling bi-directional current flow. 13. (canceled) 14. The power converter circuit comprising a power circuit according to claim 1. 15. The power converter circuit comprising two or more power circuits according to claim 1, wherein the two or more power circuits are connected in parallel. 16. A power converter comprising two or more power converter circuits according to claim 14, wherein the two or more power converter circuits are connected in series. 17. The power converter according to claim 16, wherein the power converter circuits are configured such that each power converter circuit experiences approximately the same power, when the power converter is in use. 18. The power converter according to claim 16, wherein the power converter circuits are connected in series with a half bridge circuit. 19. The power converter according to claim 16, wherein the power converter is arranged to receive a DC input voltage of 1 V-1.5 kV. 20. The power converter according to claim 16, wherein the power converter is arranged to output an AC voltage of 100 V-100 kV. 21. The power converter according to claim 16, wherein the power converter is arranged to convert electric power of 1-100 W, 100 W-1 kW, 1 kW-100 kW, 100 kW-1 MW, 1 MW-10 MW or above 10 MW. 22. A device comprising a power converter according to claim 16. 23. A modular multi-level converter comprising a power converter according to claim 16 and further comprising a control circuit to control the switches. 24. The modular multi-level converter according to claim 23, wherein the MMC operates at a fundamental frequency within the range from 1 Hz to 20 MHz. 25. A method for controlling a modular multi-level converter according to claim 23, the method comprising: providing an MMC according to claim 23; controlling the electrically controllable switches such that output voltage states generate an alternating voltage causing a current of controllable amplitude and frequency controlling the load connected to the MMC. | [EN US2021242797A1]: FIELD OF THE INVENTION The present invention relates to electronic power circuits and their use in power converters and in modular multi-level converters (MMCs) comprising such power converters. BACKGROUND OF THE INVENTION Modular multi-level converters (MMCs) are a type of voltage-source converters, which may be used to convert one kind of voltage-source to another kind of voltage-source, such as e.g. converting a DC source to an AC source or AC to AC with a different voltage. MMCs comprise a number of independent converter submodules, referred to herein as power converter circuits, each comprising a number of power circuits and each acting as an independent multi-level converter generating a voltage. With a suitable number of submodules connected in series, the power converter can create a stepped voltage waveform which can approximate very closely to a sine-wave and contains very low levels of harmonic distortion. Advantages of MMCs include scalability, simple construction and low losses. A disadvantage of current MMCs is that the submodule capacitors themselves are large and bulky. Hence, an improved MMC with a high efficiency compared to existing solutions would be advantageous, and in particular a more efficient and/or less bulky MMC would be advantageous. OBJECT OF THE INVENTION It is an object of the present invention to provide power circuits suitable for use in power converter circuits. The topology of the power circuits allows for advanced control and operation of the power circuits and thereby any power converter circuit or power converter comprised of the power circuits in the present invention. The advanced control and operation of the power circuits advantageously allows for a reduction in the size of the capacitor in the power circuit when compared to prior art. This results from the charge of the capacitor having more degrees of freedom when compared to MMC power circuits in prior art. The advanced operation is particularly useful when clock operated switching ensures a better charge of the capacitor. The power circuits advantageously behave as a DC/AC transformer converting DC voltage up to n-level times higher AC voltage. The circuit can replace a system of conventional power converter and conventional transformer, however without the galvanic isolation provided by the transformer. It is another object of the present invention to provide power converter circuits for use in power converters. The power converter circuits are comprised of power circuits as disclosed herein and thus share the advantageous possibility of advanced control and operation of the power circuits. It is another object of the present invention to provide a power converter, such as e.g. a modular multi-level converter (MMC), comprising power converter circuits as disclosed herein. The power converter is comprised of power converter circuits as disclosed herein and thus share the advantages listed for those. It is another object of the present invention to provide a method for controlling a modular multi-level converter (MMC) as disclosed herein. It is a further object of the present invention to provide an alternative to the prior art. In particular, it may be seen as an object of the present invention to provide a modular multi-level converter comprising power converter circuits that solve the above mentioned problems of the submodule capacitors being large and bulky in the prior art. SUMMARY OF THE INVENTION Thus, the above described object and several other objects are intended to be obtained in a first aspect of the invention by providing a power circuit arranged to receive a DC electric input signal at a first and a second connection terminals, and to output an AC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a third electrically controllable bidirectional two-quadrant switch, the fourth connection terminal being connected to a fourth electrically controllable bidirectional two-quadrant switch, the first, second, third and fourth switches being connected to a first node connected through a first node in such a way that the switches are connected between the first node and the respective first, second, third, and fourth connection terminals, a first capacitor being connected between the first and second connection terminals, a second capacitor being connected between the third and fourth connection terminals, and wherein one of the first and second connection terminals may be connected to one of the third and fourth connection terminals through at least one electrically controllable bidirectional switch. Here and in the following “connected” means electrically connected. By “output an AC electric output signal” is meant that the power circuit outputs a stepped voltage waveform which can approximate an AC signal. In an embodiment of the invention the first connection terminal may be connected to the third connection terminal through an electrically controllable bidirectional switch. In another embodiment of the invention the switch connecting the first and third connection terminals may comprise a series connection of two electrically controllable switches. In an embodiment of the invention the second connection terminal may be connected to the fourth connection terminal through an electrically controllable bidirectional switch. In another embodiment of the invention the switch connecting the second and fourth connection terminals may comprise a series connection of two electrically controllable switches. In an embodiment the electrically controllable switches may comprise IGBT, Bipolar and Schottky Diodes, MCT, GTO, SCR, HEMT or MOSFET transistors with diode function enabling bi-directional current flow. In a further embodiment the power circuit may be implemented in a monolithic IC, in one single package configuration or comprised of discrete transistors with diode function. The embodiments of the first aspect may be combined in ways that make sense. For example, the first connection terminal may be connected to the third connection terminal through an electrically controllable bidirectional switch and the second connection terminal may, in the same circuit, be connected to the fourth connection terminal through an electrically controllable bidirectional switch. To obtain a power circuit for use in a power converter, it would also be possible to connect a first inductor between the first connection terminal and the third connection terminal and a second inductor between the second connection terminal and the fourth connection terminal and having the first and second inductor be magnetically coupled. This magnetic coupling will, however, also include a magnetization inductance, which will affect the circuit with a current. The magnetization current can be reduced by impedance, which will be frequency dependent. Thus, such a design must ensure a sufficient value of magnetization impedance to reduce the magnetization current to an acceptable level. The magnetically coupled inductors constitute a common mode transformer and for a common mode transformer the weight is large due to the dependency on the load frequency. Further, if the frequency decreases, the weight goes up. Thus, a magnetically coupled power circuit as described above will, while using a very low number of components, be too heavy for the use intended in the present invention. The second aspect of the invention provides power circuits comprising magnetically coupled inductors, which overcome the weight problem described above by introducing an electronic commutator. The purpose of the commutator is to control the frequency seen by the coupled inductors, in this way making the circuit independent of the AC load frequency, making the circuit able to generate voltages from DC (0 Hz) and making the size of the magnetics dependent on the commutator frequency. In a second aspect is provided a power circuit arranged to receive a DC electric input signal at first and second connection terminals, and to output an AC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a third electrically controllable bidirectional two-quadrant switch, the fourth connection terminal being connected to a fourth electrically controllable bidirectional two-quadrant switch, the first switch, the second switch, the third switch and the fourth switch being connected to a first node in such a way that the switches are connected between the first node and the respective first, second, third, and fourth connection terminals, a first electronic component being connected to the first connection terminal, a second electronic component being connected to the second connection terminal, a third electronic component being connected to a second node, the second node, the first and third electronic component and the first connection terminal being connected, a fourth electronic component being connected to a third node, the third node, the second and fourth electronic component and the second connection terminal being connected, a first capacitor being connected to the second and third node, the first, second, third and fourth electronic components being connected to a first coupled inductor in such a way that: the first electronic component is connected between the first coupled inductor and the first connection terminal, the second electronic component is connected between the first coupled inductor and the second connection terminal, the third electronic component is connected between the first coupled inductor and the second node, and the fourth electronic component is connected between the first coupled inductor and the third node, wherein further: a fifth electronic component is connected to the third connection terminal, a sixth electronic component is connected to the fourth connection terminal, a seventh electronic component is connected to a fourth node, the fourth node, the fifth and seventh electronic component and the third connection terminal being connected, an eighth electronic component is connected to a fifth node, the fifth node, the sixth and eighth electronic component and the fourth connection terminal being connected, a second capacitor is connected to the fourth and fifth node, the fifth, sixth, seventh and eighth electronic components, are connected to a second coupled inductor in such a way that: the fifth electronic component is connected between the second coupled inductor and the third connection terminal, the sixth electronic component is connected between the second coupled inductor and the fourth connection terminal, the seventh electronic component is connected between the second coupled inductor and the fourth node, and the eighth electronic component is connected between the second coupled inductor and the fifth node, and wherein the first, second, third, fourth, fifth, sixth, seventh and eighth electronic components are selected from the group consisting of an electrically controllable switch, a capacitor and a diode. In a first embodiment of the second aspect of the invention the first, second, third, fourth, fifth, sixth, seventh and eighth electronic components may be electrically controllable switches. In a second embodiment of the second aspect of the invention the first, second, seventh and eighth electronic components may be electrically controllable switches and the third, fourth, fifth and sixth electronic components may be capacitors. In a third embodiment of the second aspect of the invention the first, second, third and fourth electronic components may be electrically controllable switches and the fifth, sixth, seventh and eighth electronic components may be diodes. In a fourth embodiment of the second aspect of the invention the first and second electronic components may be capacitors, the third and fourth electronic components may be electrically controllable switches and the fifth, sixth, seventh and eighth electronic components may be diodes. In an embodiment, which may be combined with any of the first, second, third and fourth embodiments of the second aspect, the electrically controllable switches may comprise IGBT, MCT, GTO, SCR, HEMT or MOSFET transistors with diode function enabling bi-directional current flow. In a further embodiment, which may be combined with any of the first, second, third and fourth embodiments of the second aspect, the power circuit may be implemented in one single package configuration or comprised of discrete transistors with diode function. The power circuits presented in the first and second aspect are all 3-level circuits, which means that 3 voltage levels can be output by each circuit. In a third aspect is provided power circuits, which can output 2 voltage levels, i.e. 2-level circuits. In a third aspect is provided a power circuit arranged to receive a DC electric input signal at first and second connection terminals, and to output an AC or DC electric output signal at a third and a fourth connection terminals, the first connection terminal being connected to a first electrically controllable bidirectional two-quadrant switch, the second connection terminal being connected to a second electrically controllable bidirectional two-quadrant switch, the third connection terminal being connected to a first electronic component, the fourth connection terminal being connected to a second electronic component, the first switch and the second switch being connected to a first node in such a way that the switches are connected between the first node and the respective first and second connection terminals, a third electronic component being connected to the first connection terminal, a fourth electronic component being connected to the second connection terminal, a third electrically controllable bidirectional two-quadrant switch being connected to a second node, the second node, the third electronic component, the third electrically controllable bidirectional two-quadrant switch and the first connection terminal being connected, a fourth electrically controllable bidirectional two-quadrant switch being connected to a third node, the third node, the fourth electronic component, the fourth electrically controllable bidirectional two-quadrant switch and the second connection terminal being connected, a first capacitor being connected to the second and third node, the third electronic component, the fourth electronic component, the third electrically controllable bidirectional two-quadrant switch and the fourth electrically controllable bidirectional two-quadrant switch being connected to a first coupled inductor in such a way that: the third electronic component is connected between the first coupled inductor and the first connection terminal, the fourth electronic component is connected between the first coupled inductor and the second connection terminal, the third electrically controllable bidirectional two-quadrant switch is connected between the first coupled inductor and the second node, and the fourth electrically controllable bidirectional two-quadrant switch is connected between the first coupled inductor and the third node, wherein further: a fifth electronic component is connected to a fourth node, the fourth node, the first and fifth electronic component and the third connection terminal being connected, a sixth electronic component is connected to a fifth node, the fifth node, the second and sixth electronic component and the fourth connection terminal being connected, a second capacitor is connected to the fourth and fifth node, the first, second, fifth and sixth electronic component are connected to a second coupled inductor in such a way that: the first electronic component is connected between the second coupled inductor and the third connection terminal, the second electronic component is connected between the second coupled inductor and the fourth connection terminal, the fifth electronic component is connected between the second coupled inductor and the fourth node, and the sixth electronic component is connected between the second coupled inductor and the fifth node, and wherein: the first, second, fifth and sixth electronic component are diodes, or the first and second electronic component are diodes and the fifth and sixth electronic components are capacitors, or the first and second electronic component are capacitors and the fifth and sixth electronic components are diodes, and wherein further: the third and fourth electronic components are electrically controllable switches and the first node is connected to the fourth connection terminal, or the third and fourth electronic components are capacitors and the first node is connected to the fourth connection terminal, or the first and second electronic components are capacitors and the first node is connected to the third connection terminal. An example of a use for the 2-level circuits provided in the third aspect is flue gas cleaning systems installed in chimneys at power plants, where the system at its core has a DC voltage of approximately 100,000 V. For a DC system 3-level circuits has more functionality (more switches) than needed and so to produce the high DC voltage, 2-level circuits are used. 2-level power circuits can be used to make an AC voltage, but there will always be a DC voltage present. Mostly this DC voltage will not result in a flow of current and is therefore sometimes ignored. However, the DC voltage is there and electrical motors coupled to a 2-level power converter will have electrically insulated windings to prevent a current from running due to the DC voltage. Most electrical drives, by far, are 2-level even when considering drives ranging in power from e.g. MW wind turbines to washing machines (W). 2-level power circuits are widely used partly due to reduced cost when compared with 3-level power circuits. To make an AC voltage with an amplitude of e.g. 325 V requires that the switches in a 2-level power converter can tolerate twice the voltage, i.e. 650 V, as the 2-level power converter only has to voltage levels, in this case 0 V and 650 V. A 3-level power circuit for producing an AC voltage of 325 V will have three voltage levels: −325 V, 0 V and 325 V. However, the higher tolerance required of the switches does not result in a significantly higher cost, so when an AC voltage of 325 V (rms=230 V) is needed, a 2-level power converter is almost always chosen. In the rarer cases, where the higher tolerance switches cannot be used or the voltage is so high that no switch can handle it, it is necessary to couple either switches or circuits in series. This will be the case for the flue gas cleaning systems mentioned in which 100,000 V DC voltage is needed. In an embodiment the electrically controllable switches may comprise IGBT, MCT, GTO, SCR, HEMT or MOSFET transistors with diode function enabling bi-directional current flow. In a further embodiment the power circuit may be implemented in one single package configuration or comprised of discrete transistors with diode function. The power circuits provided in the first, second and third aspect of the invention may be used in combination with each other. In a fourth aspect is provided a power converter circuit comprising a power circuit according to the first, second or third aspect or a power converter circuit comprising two or more power circuits according to the first, second or third aspect, wherein the two or more power circuits are connected in parallel. The parallel coupling of the power circuits makes it easy to scale the power converter circuit as needed. In a fifth aspect is provided a power converter comprising two or more power converter circuits according to the fourth aspect, wherein the two or more power converter circuits are connected in series. E.g. a plurality of power converter circuits each designed for a maximum voltage handling of such as first voltage, such as 100-1000V, can be series connected to provide a maximum voltage handling of such as 1000V-100 kV, such as 33 kV. In power converter embodiments, the use of two energy storage elements, e.g. two capacitors, can be connected by inductors, e.g. two inductors. Specifically, the inductors may be magnetically coupled. Specifically, pulse voltages may be used. Specifically, the switches involved may be soft-switched. The power converter may be used to step up voltage or step down voltage at large voltage ratios with low power losses. In some systems this is done by a grid side power converter and transformer and in such systems a power converter as provided in the fifth aspect may eliminate the need for the heavy and bulky transformer. The power circuits provided by the first, second and third aspect of the present invention may be thought of as a “variable gearbox” when compared to a transformer. In such an analogy the transformer is a gearbox with one gear. The power converter may also conceivably replace other transformers. An advantage of the power converter of the present invention is a reduction in the number of power electronics components needed. In an embodiment the power converter circuits may be configured such that each power converter circuit experiences approximately the same power, when the power converter is in use. In a further embodiment the power converter circuits may be connected in series with a half bridge circuit. A half bridge circuit, also called a half-H bridge, is a well-known type of circuit. In another embodiment the power converter may be arranged to receive a DC input voltage of 1 V-1.5 kV, such as 1000 V. In an embodiment the power converter may be arranged to output an AC voltage of 100 V-100 kV, such as 690 V or 33 kV or 66 kV. In a further embodiment the power converter may be arranged to convert electric power of 1-100 W, 100 W-1 kW, 1 kW-100 kW, 100 kW-1 MW, 1 MW-10 MW or above 10 MW. In a sixth aspect is provided a device comprising a power converter according to the fifth aspect, such as a device further comprising a DC power electric generator. In a seventh aspect is provided a modular multi-level converter (MMC) comprising a power converter according to the fifth aspect and further comprising a control circuit to control the switches. In an embodiment the MMC may operate at a fundamental frequency within the range from 1 Hz to 20 MHz. In an eighth aspect is provided a method for controlling a modular multi-level converter (MMC) according to the seventh aspect, the method comprising: providing an MMC as disclosed herein; controlling the electrically controllable switches such that output voltage states generate an alternating voltage causing a current of controllable amplitude and frequency controlling the load connected to the MMC. By “MMC as disclosed herein” is meant a modular multi-level converter (MMC) obtainable from the disclosure herein, i.e. an MMC comprising power converter circuits as disclosed herein and where the power converter circuits comprise power circuits as also disclosed herein. The first, second and third aspect of the present invention may each be combined with each other by connecting power circuits to each other as long as the connections makes sense. These and other aspects of the invention will be apparent from and elucidated with reference to the embodiments described hereinafter. BRIEF DESCRIPTION OF THE FIGURES The present invention and in particular preferred embodiments thereof will now be disclosed in more detail with regard to the accompanying figures. The FIGS. show ways of implementing the present invention and are not to be construed as being limiting to other possible embodiments falling within the scope of the attached claim set. FIG. 1 illustrate schematically a power circuit. FIGS. 2-7 illustrate schematically a power circuit as provided in the first aspect. FIGS. 8-12 illustrate schematically a power circuit as provided in the second aspect. FIGS. 13-17 illustrates schematically 2-level power circuits as provided in the third aspect. FIG. 18 illustrates schematically a power converter. FIG. 19 illustrates schematically a power converter comprising three power converter circuits connected in series. FIG. 20 illustrates schematically a power converter circuit connected in series with a half bridge circuit as an illustration of claim 18. FIG. 21 illustrates schematically a device comprising a power converter. FIG. 22 illustrates schematically a modular multi-level converter (MMC) comprising a power converter and further comprising a control circuit to control the switches. FIG. 23 is an illustration of claim 25. FIG. 24A illustrates schematically a prior art solution. FIG. 24B illustrates schematically a simpler solution to the prior art shown in FIG. 24A. FIGS. 25-28 illustrate yet further power converter circuit embodiments. DETAILED DESCRIPTION OF AN EMBODIMENT FIG. 1 shows a basic power circuit. The power circuit is arranged to receive a DC electric input signal at a first and a second connection terminals A, B and to output an AC electric output signal at a third and a fourth connection terminals C, D. The first connection terminal A is connected to a first electrically controllable bidirectional two-quadrant switch s1, the second connection terminal B is connected to a second electrically controllable bidirectional two-quadrant switch s2, the third connection terminal C is connected to a third electrically controllable bidirectional two-quadrant switch s3, and the fourth connection terminal D is connected to a fourth electrically controllable bidirectional two-quadrant switch s4. Additionally, the first, second, third and fourth switches s1, s2, s3, s4 are connected to a first node 1 connected through a first node 1 in such a way that the switches s1, s2, s3, s4 are connected between the first node 1 and the respective first, second, third, and fourth connection terminals A, B, C, D. Further, a first capacitor CAP1 is connected between the first and second connection terminals A, B, while a second capacitor CAP2 is connected between the third and fourth connection terminals C, D. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIGS. 2-7 show power circuits according to embodiments of the first aspect of the present invention, wherein the circuits have the same connections as the circuit shown in FIG. 1 and where, additionally, one of the first and second connection terminals A, B is connected to one of the third and fourth connection terminals C, D through at least one electrically controllable bidirectional switch sa, sb, s5, s6, s7, s8. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 2 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 1 and where, additionally, the first connection terminal A is connected to the third connection terminal C through an electrically controllable bidirectional switch sa. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 3 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 2 and where, additionally, the switch sa connecting the first and third connection terminals A, C comprises a series connection of two electrically controllable switches s5, s6. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 4 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 1 and where, additionally, the second connection terminal B is connected to the fourth connection terminal D through an electrically controllable bidirectional switch sb. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 5 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 3 and where, additionally, the switch sb connecting the second and fourth connection terminals B, D comprises a series connection of two electrically controllable switches s7, s8. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 6 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 1 and where, additionally, the first connection terminal A is connected to the third connection terminal C through an electrically controllable bidirectional switch sa and the second connection terminal B is connected to the fourth connection terminal D through an electrically controllable bidirectional switch sb. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 7 shows a power circuit according to an embodiment of the present invention, wherein the circuit has the same components and connections as the circuit shown in FIG. 6 and where, additionally, the switch sa connecting the first and third connection terminals A, C comprises a series connection of two electrically controllable switches s5, s6 and the switch sb connecting the second and fourth connection terminals B, D comprises a series connection of two electrically controllable switches s7, s8. As electrically controllable switches one may use IGBT or MOSFET transistors with diode function enabling bi-directional current flow. FIG. 8 shows a power circuit, which forms the basis for the power circuits according to the second aspect of the present invention. The power circuit is arranged to receive a DC electric input signal at the first and second connection terminals C1, D1, and to output an AC electric output signal at a third and a fourth connection terminals A2, B2. The first connection terminal C1 is connected to a first electrically controllable bidirectional two-quadrant switch S1, the second connection terminal D1 is connected to a second electrically controllable bidirectional two-quadrant switch S2, the third connection terminal A2 is connected to a third electrically controllable bidirectional two-quadrant switch S3, and the fourth connection terminal B2 is connected to a fourth electrically controllable bidirectional two-quadrant switch S4. The first switch S1, the second switch Sz, the third switch S3 and the fourth switch S4 are connected to a first node 1 in such a way that the switches s1, s2, s3, s4 are connected between the first node 1 and the respective first, second, third, and fourth connection terminals C1, D1, A2, B2. A first electronic component EC1 is connected to the first connection terminal C1 and a second electronic component EC2 is connected to the second connection terminal D1. A third electronic component EC3 i
[ZH CN109167507B]: 一种多电平换流器子模块冗余供能电路及控制方法 [EN CN109167507B]: Redundant power supply circuit and control method for sub-modules of multi-level converter | [ZH CN109167507B]: 本发明公开的是一种多电平换流器子模块冗余供能电路及控制方法。多电平换流器子模块包括至少一个功率半导体单元、子模块电容CM、旁路开关KB、电源板卡以及控制板卡。所述冗余供能电路，由第一电阻R1、第二电阻R2，连接模块以及电压变换电路构成。本发明方案在电源板卡故障后，利用均压电阻分压和电压变换电路实现了旁路开关储能电容充电以及控制板卡供电，保证在电源板卡故障后，旁路开关的可靠合闸和子模块状态上送，避免系统停运和旁路开关状态未知下的带故障运行，提高了系统的安全性和可靠性。本发明方案利用子模块均压电阻回路能量，没有额外增加系统的损耗，提高了系统运行经济性，结构简单可靠，具备可实施性，成本低廉。 [EN CN109167507B]: The invention discloses a redundant power supply circuit and a control method of a multi-level converter sub-module. A sub-module of that multilevel convert includes at least one power semiconductor unit, a sub-module capacitor CM, a bypass switch KB, a power board and a control board. The redundant power supply circuit comprises a first resistor R1, a second resistor R2, a connection module and avoltage conversion circuit. As that power board card fails, The voltage dividing circuit and voltage converting circuit are used to charge the energy storage capacitor of the bypass switch and the power supply of the control board, which ensures the reliable closing of the bypass switch and the uplink of the sub-module state after the fault of the power board, avoids the system shutdown and the operation with fault when the state of the bypass switch is unknown, and improves the safety and reliability of the system. As that energy of the voltage equalize resistor loop of the sub-module is utilized, the loss of the system is not increased additionally, the system operation economy is improved, the structure is simple and reliable, and the system has the advantages of practicability and lowcost. | CN109167507B | 2019-01-08 2020-12-18 | CN201811153654A | 2018-09-30 2018-09-30 | CN201811153654A, 2018-09-30 CN201811153654A, 2018-09-30 | CN109167507B: 2020-12-18 | NARI RELAYS ELECTRIC CO LTD NANJING NARI RELAYS ENG TECH 南京南瑞继保电气有限公司 南京南瑞继保工程技术有限公司 | YU XIAOYANG WANG TAO LI LELE LUO RENSONG WEN JIFENG CAO DONGMING | H02M1/16: I H02M1/32: I | H02M1/16: I H02M1/32: I H02M1/325: A | CN103001242A CN105281545A US2016226247A1 CN106374767A CN106849635A CN107147305A CN108111007A CN102097926A | CN111049367A CN111049367 111049367 CN112583242A CN112583242 112583242 | [ZH CN109167507B]: 1 .一种多电平换流器子模块冗余供能电路，所述多电平换流器子模块包括功率半导体 单元、子模块电容Cm、旁路开关KB、旁路开关储能电容CB、可控开关Qb、控制线圈、电源板卡以 及控制板卡，其特征在于:所述多电平换流器子模块冗余供能电路由第一电阻R1、第二电阻 R2、连接模块以及电压变换电路构成;所述连接模块是二极管、机械开关、继电器、电子开关 或半导体可控器件； 所述电压变换电路是将输入电压转换成其它电压输出的电路;所述第一电阻R1一端与 子模块电容Cm正极相连，第一电阻R1另一端与第二电阻R2一端相连，第二电阻R2另一端与 子模块电容Cm负极相连； 所述连接模块一端连接至第一电阻R1与第二电阻R2的连接点，另一端连接至旁路开关 储能电容Cb正极，旁路开关储能电容Cb负极连接至子模块电容Cm负极； 所述电压变换电路输入正端连接至第一电阻R1与第二电阻R2的连接点，电压变换电路 输入负端连接至子模块电容Cm负极，电压变换电路输出连接至控制板卡； 所述电源板卡给所述控制板卡供电，所述电源板卡的输出正端连接所述旁路开关储能 电容Cb的正极、输出负端连接所述旁路开关储能电容Cb的负极;所述控制线圈的一端连接至 所述旁路开关储能电容Cb的正极，另一端连接至所述可控开关Qb的正极，所述可控开关Qb的 负极连接至所述旁路开关储能电容Cb的负极。 2 .如权利要求1所述的多电平换流器子模块冗余供能电路，其特征在于:所述控制板卡 包含通讯单元、旁路触发单元以及检测保护单元。 3 .如权利要求1所述的多电平换流器子模块冗余供能电路，其特征在于:所述第一电阻 R1和第二电阻R2分别是单个电阻或多个电阻串、并联的结构。 4 .如权利要求1所述的多电平换流器子模块冗余供能电路，其特征在于:所述电压变换 电路是开关电源模块、线性电源或者稳压电路。 5 .如权利要求1所述的多电平换流器子模块冗余供能电路，其特征在于:所述功率半导 体单元包括至少包含两个功率半导体器件的半桥连接方式和至少包含四个功率半导体器 件的全桥连接方式。 6 .如权利要求1-5中所述的任意一种多电平换流器子模块冗余供能电路的控制方法， 其特征在于：当多电平换流器子模块启动前，电源板卡已经故障，旁路功能实施包含如下步 骤； 步骤1：多电平换流器子模块开始预充电，子模块电容Cm电压开始上升，电源板卡故障未 工作;冗余供能电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入，给旁路开关 储能电容Cb充电；电压变换电路输入欠压未启动； 步骤2：子模块电容Cm电压上升到电压变换电路的启动电压以上，电压变换电路正常工 作，控制板卡正常工作;旁路开关储能电容Cb继续充电； 步骤3：控制板卡检测保护单元检测到子模块存在故障，并向上级控制系统发送故障状 态信息，上级控制系统接收到故障状态信息后下发旁路命令； 步骤4：控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条件后，旁路触 发单元触发旁路开关Kb合闸，控制板卡通讯单元向上级控制系统发送旁路开关位置信号； 系统继续运行。 7 .如权利要求1-5中所述的任意一种多电平换流器子模块冗余供能电路的控制方法， 其特征在于：当多电平换流器子模块在运行过程中，发生故障，旁路功能实施包含如下步 骤； 步骤1：多电平换流器子模块开始预充电，子模块电容CM电压开始上升，电源板卡输入欠 压未启动;冗余供能电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入，给旁路 开关储能电容Cb充电；电压变换电路输入欠压未启动； 步骤2：子模块电容Cm电压上升到电源板卡启动电压以上，电源板卡正常工作，给旁路开 关储能电容Cb充电，给控制板卡供电；冗余供能电路从给旁路开关储能电容Cb充电状态自动 退出；电压变换电路输入欠压未启动； 步骤3： 情况①：控制板卡检测保护单元检测到子模块发生故障、电源板卡正常； 情况②：电源板卡发生故障，控制板卡失电，子模块电容Cm电压上升到电压变换电路的 启动电压以上，电压变换电路正常工作，控制板卡恢复工作；冗余供能电路的第一电阻R1、 第二电阻R2分压后通过连接模块自动投入给旁路开关储能电容Cb继续充电； 步骤4：控制板卡向上级控制系统发送故障状态信息;上级控制系统接收到故障状态信 息后下发旁路命令，控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条件， 旁路触发单元触发旁路开关Kb合闸，控制板卡上送旁路开关位置信号；系统继续运行。 [EN CN109167507B]: 1 A redundant power supply circuit for a multi-level converter sub-module, the multi-level converter sub-module includes a power semiconductor unit, a sub-module capacitor Cm, a bypass switch KB, a bypass switch energy storage capacitor CB, The controllable switch Qb, the control coil, the power board and the control board are characterized in that: the redundant power supply circuit of the multi-level converter sub-module is composed of a first resistor R1, a second resistor R2, a connection module, and a voltage Conversion circuit composition; the connection module is a diode, a mechanical switch, a relay, an electronic switch or a semiconductor controllable device; the voltage conversion circuit is a circuit that converts the input voltage into another voltage output; one end of the first resistor R1 is connected to the sub The module capacitor Cm is connected to the positive pole, the other end of the first resistor R1 is connected to one end of the second resistor R2, and the other end of the second resistor R2 is connected to the negative pole of the sub-module capacitor Cm; one end of the connecting module is connected to the first resistor R1 and the second resistor R2 The other end is connected to the positive pole of the bypass switch energy storage capacitor Cb, the negative pole of the bypass switch energy storage capacitor Cb is connected to the negative pole of the sub-module capacitor Cm; the positive input terminal of the voltage conversion circuit is connected to the first resistor R1 and the second resistor R1 At the connection point of the resistor R2, the negative input terminal of the voltage conversion circuit is connected to the negative terminal of the sub-module capacitor Cm, and the output of the voltage conversion circuit is connected to the control board; the power board supplies power to the control board, and the output of the power board The positive terminal is connected to the bypass switch for energy storage The positive and negative output ends of the capacitor Cb are connected to the negative electrode of the bypass switch energy storage capacitor Cb; one end of the control coil is connected to the positive electrode of the bypass switch energy storage capacitor Cb, and the other end is connected to the controllable switch The positive pole of Qb, and the negative pole of the controllable switch Qb is connected to the negative pole of the energy storage capacitor Cb of the bypass switch. 2 The multi-level converter sub-module redundant power supply circuit according to claim 1, wherein the control board includes a communication unit, a bypass trigger unit, and a detection and protection unit. 3 The multi-level converter sub-module redundant power supply circuit according to claim 1, wherein: the first resistor R1 and the second resistor R2 are respectively a single resistor or a multiple resistor string, parallel structure . 4 The multi-level converter sub-module redundant power supply circuit of claim 1, wherein the voltage conversion circuit is a switching power supply module, a linear power supply or a voltage stabilizing circuit. 5 The multi-level converter sub-module redundant power supply circuit according to claim 1, wherein the power semiconductor unit includes a half-bridge connection method including at least two power semiconductor devices and at least four power semiconductor devices. Full bridge connection of semiconductor devices. 6 The method for controlling redundant power supply circuits of any multi-level converter sub-module as claimed in claims 1-5, characterized in that: before the multi-level converter sub-module is activated, the power supply board It has failed, the implementation of the bypass function includes the following steps; Step 1: The multi-level converter sub-module starts to pre-charge, the voltage of the sub-module capacitor Cm starts to rise, the power board fails and does not work; the first resistance of the redundant power supply circuit After R1 and the second resistor R2 are divided into voltage, they are automatically turned on through the connection module to charge the energy storage capacitor Cb of the bypass switch; the input voltage of the voltage conversion circuit is not activated; Step 2: The voltage of the sub-module capacitor Cm rises to the starting voltage of the voltage conversion circuit Above, the voltage conversion circuit works normally, and the control board works normally; the bypass switch energy storage capacitor Cb continues to charge; Step 3: The control board detection and protection unit detects a fault in the sub-module, and sends fault status information to the higher-level control system. The upper-level control system issues a bypass command after receiving the fault status information; Step 4: After the control board card detection and protection unit detects that the voltage of the bypass switch energy storage capacitor Cb meets the closing conditions, the bypass trigger unit triggers the bypass switch Kb to close , The control board communication unit sends the bypass switch position signal to the superior control system; the system continues to run. 7 . The control method of any one of the redundant power supply circuits of multi-level converter sub-modules as described in claims 1-5, It is characterized in that: when the multi-level converter sub-module fails during operation, the implementation of the bypass function includes the following steps; Step 1: The multi-level converter sub-module starts pre-charging, and the sub-module capacitor CM voltage starts Rising, the input undervoltage of the power supply board is not activated; the first resistor R1 and the second resistor R2 of the redundant power supply circuit are divided into voltage and then automatically turned on through the connection module to charge the energy storage capacitor Cb of the bypass switch; the input of the voltage conversion circuit is undervoltage Step 2: The voltage of the sub-module capacitor Cm rises above the startup voltage of the power supply board, and the power supply board works normally. Charge the bypass switch energy storage capacitor Cb and supply power to the control board; the redundant power supply circuit The charging state of the energy storage capacitor Cb of the bypass switch is automatically exited; the input voltage of the voltage conversion circuit is not activated; Step 3: Case 1: The control board detection and protection unit detects that the sub-module is faulty and the power board is normal; Case 2: The power board The card fails, the control board card loses power, the voltage of the sub-module capacitor Cm rises above the starting voltage of the voltage conversion circuit, the voltage conversion circuit works normally, and the control board resumes work; the first resistor R1 and the second resistor of the redundant power supply circuit After the resistor R2 is divided into voltage, it is automatically put into the bypass switch energy storage capacitor Cb through the connection module to continue charging; Step 4: The control board sends the fault status information to the upper control system; the upper control system sends the bypass command after receiving the fault status information , The control board card detection protection unit detects that the bypass switch energy storage capacitor Cb voltage meets the closing conditions, The bypass trigger unit triggers the bypass switch Kb to close, and the control board sends the bypass switch position signal; the system continues to run. | [ZH CN109167507B]: 一种多电平换流器子模块冗余供能电路及控制方法 技术领域 [0001]本发明公布了一种多电平换流器子模块冗余供能电路及控制方法，涉及柔性交直 流输电领域，尤其涉及功率单元模块的取能技术。 背景技术 [0002]级联多电平换流器在特高压交直流输电、无功补偿、直流配电网等电力、轨道交通 以及新能源场合广泛应用。为了保证级联多电平换流器的安全稳定运行，多电平换流器子 模块均要求设计故障旁路功能，当子模块内部出现故障后，旁路功能会将故障模块旁路，避 免故障扩大，维持系统继续运行，避免造成经济损失。 [0003]但是，电源板卡作为多电平换流器子模块内部所有控制保护功能实现的能量来 源，由于器件的寿命限制、老化、失效以及其他外部原因，存在一定的故障概率。特别是在系 统启动前，电源板卡已经发生故障的工况，旁路开关不具备合闸所需的能量，子模块控制板 也无法正常发出指令，那么旁路功能就无法实现，因此会导致整个系统的停运。发明专利 CN201710228027 .X提出了 一种多电平换流器子模块旁路开关自触发电路，利用功率模块单 元交流侧能量给旁路开关储能电容充电，但是如果在系统启动前，电源板已经故障，由于旁 路开关合闸线圈电阻比较小，旁路开关储能电容被短路，无法完成充电，因此旁路开关无法 完成合闸动作。发明专利CN108111007A公开了一种功率模块冗余供能电路及控制方法，在 电源板卡故障后，第一电容电压超过某一门槛后击穿第一稳压管给旁路开关储能电容充 电，并在第一电容电压超过另一门槛后击穿第二稳压管触发第二开关合闸，然后触发旁路 开关合闸。但是，该发明引入了多个高压稳压管，会造成发热严重，可靠性差;旁路开关储能 电容的容量都在几百微法数量级以上，只有当第一电容电压击穿第一稳压管后，才能给旁 路开关储能电容充电，浪费了击穿前的充电时间；并且稳压管的引入限制了充电回路的电 流，影响充电速度;而且稳压管稳压离散性大、温漂大，对保护精度会造成较大影响；此外， 该发明还引入了多个高压开关，需要隔离控制，控制复杂，工程可实施性差;更重要的是，该 发明仅为实现旁路开关的可靠旁路做了努力，但是如果出现旁路开关本体拒动或更恶劣的 情况，上级控制系统无法获知故障模块的状态，如果在旁路失败情况下继续运行，会导致故 障进一步扩大，造成更严重的损失。 [0004]基于以上分析，本发明人提出了一种多电平换流器子模块冗余供能电路及控制方 法，实现旁路开关和子模块控制板卡的冗余供能，本案由此产生。 发明内容 [0005]发明目的 [0006]本发明所要解决的技术问题是:多电平换流器子模块在电源板卡故障后无法执行 旁路而导致系统停运，以及旁路状态未知下的可能带故障运行，提出了一种多电平换流器 子模块冗余供能电路及控制方法。当子模块电源板卡出现故障时，本发明通过冗余供能电 路，给旁路开关提供合闸所需能量，给子模块控制板卡供电，保证旁路开关可靠合闸，避免 系统停运，并上送故障模块的状态，避免系统带故障运行，提高了系统运行的安全性和可靠 性。 [0007] 技术方案 [0008] 一种多电平换流器子模块冗余供能电路，所述多电平换流器子模块至少包括功率 半导体单元、子模块电容Cm、旁路开关Kb、旁路开关储能电容Cb、可控开关Qb、控制线圈、电源 板卡以及控制板卡;所述多电平换流器子模块冗余供能电路由第一电阻R1、第二电阻R2、连 接模块以及电压变换电路构成;所述连接模块是二极管、机械开关、继电器、电子开关或半 导体可控器件;所述电压变换电路是将输入电压转换成其它电压输出的电路;所述第一电 阻R1一端与子模块电容Cm正极相连，第一电阻R1另一端与第二电阻R2一端相连，第二电阻 R2另一端与子模块电容Cm负极相连;所述连接模块一端连接至第一电阻R1与第二电阻R2的 连接点，另一端连接至旁路开关储能电容Cb正极，旁路开关储能电容Cb负极连接至子模块电 容Cm负极;所述电压变换电路输入正端连接至第一电阻R1与第二电阻R2的连接点，电压变 换电路输入负端连接至子模块电容Cm负极，电压变换电路输出连接至控制板卡;所述电源 板卡给所述控制板卡供电，所述电源板卡的输出正端连接所述旁路开关储能电容Cb的正 极、输出负端连接所述旁路开关储能电容Cb的负极;所述控制线圈的一端连接至所述旁路 开关储能电容Cb的正极，另一端连接至所述可控开关Qb的正极，所述可控开关Qb的负极连接 至所述旁路开关储能电容Cb的负极。 [0009]进一步地，所述多电平换流器子模块的控制板卡包含通讯单元、旁路触发单元以 及检测保护单元。通讯单元负责接收上级控制系统的指令、发送子模块的状态信息;旁路触 发单元负责执行旁路触发命令;检测保护单元负责检测子模块的状态，监视点电压电流采 样以及子模块本体的主动保护功能。 [0010]进一步地，所述多电平换流器子模块的子模块电容Cm两端均会并联均压电阻，达 到预充电过程中模块均压作用。因此，第一电阻R1、第二电阻R2在起分压供能的同时，也可 以充当子模块的均压电阻，没有额外增加系统的损耗。第一电阻R1、第二电阻R2既可以是单 个电阻，也可以是电阻串、并联结构，提高回路的冗余度。 [0011]进一步地，所述多电平换流器子模块冗余供能电路的电压变换电路可以是开关电 源模块、线性电源或者稳压电路。 [0012]进一步地，所述功率半导体单元包括至少包含两个功率半导体器件的半桥连接方 式和至少包含四个功率半导体器件的全桥连接方式。 [0013] 本发明还公开了一种多电平换流器子模块冗余供电电路的控制方法，如下所示： [0014] (1)当多电平换流器子模块启动前，电源板卡已经故障，旁路功能实施的步骤如 下： [0015]步骤1 ：多电平换流器子模块开始预充电，子模块电容Cm电压开始上升；冗余供能 电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入，给旁路开关储能电容Cb充 电；电压变换电路输入欠压未启动； [0016]步骤2：子模块电容Cm电压上升到电压变换电路的启动电压以上，电压变换电路正 常工作，控制板卡正常工作;旁路开关储能电容Cb继续充电； [0017] 步骤3：控制板卡检测保护单元检测到子模块存在故障，并向上级控制系统发送故 障状态信息，上级控制系统接收到故障状态信息后下发旁路命令； [0018]步骤4：控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条件后，旁 路触发单元触发旁路开关Kb合闸，控制板卡通讯单元向上级控制系统发送旁路开关位置信 号;系统继续运行。 [0019] ⑵当多电平换流器子模块在运行过程中，发生故障，旁路功能实施的步骤如下： [0020]步骤1 ：多电平换流器子模块开始预充电，子模块电容Cm电压开始上升，电源板卡 输入欠压未启动;冗余供能电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入， 给旁路开关储能电容Cb充电；电压变换电路输入欠压未启动； [0021]步骤2：子模块电容Cm电压上升到电源板卡启动电压以上，电源板卡正常工作，给 旁路开关储能电容Cb充电，给控制板卡供电;冗余供能电路从给旁路开关储能电容Cb充电状 态自动退出；电压变换电路输入欠压未启动； [0022]步骤3： [0023]情况①：控制板卡检测保护单元检测到子模块发生故障、电源板卡正常； [0024]情况②：电源板卡发生故障，控制板卡失电，子模块电容Cm电压上升到电压变换电 路的启动电压以上，电压变换电路正常工作，控制板卡恢复工作;冗余供能电路的第一电阻 R1、第二电阻R2分压后通过连接模块自动投入给旁路开关储能电容Cb继续充电； [0025] 步骤4：控制板卡向上级控制系统发送故障状态信息；上级控制系统接收到故障状 态信息后下发旁路命令，控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条 件，旁路触发单元触发旁路开关Kb合闸，控制板卡上送旁路开关位置信号；系统继续运行。 [0026] 有益效果 [0027]采用本发明所述的多电平换流器子模块冗余供能电路，解决了子模块电源板卡故 障后的旁路开关储能电容取能以及子模块控制板卡的供电问题，与现有技术相比，具有以 下有益效果： [0028] ⑴利用简单的无源分压电路，实现了旁路开关储能电容的冗余供能;保证了旁路 开关合闸动作的能量来源； [0029] (2)利用简单的无源分压电路，在电阻分压降压端口，引入电压变换电路，实现了 子模块控制冗余供电问题;保障了保护触发功能和状态上送功能；避免因为旁路开关本体 拒动或更恶劣工况导致故障扩大； [0030] ⑶利用控制板的数字采样以及高精度基准芯片，保护精度高； [0031] (4)利用了子模块原有的均压电阻回路能量，没有额外增加系统损耗；具有经济 性； [0032] (5)电路结构简单可靠，无需额外增加控制，工程可实施性高，成本低廉。 附图说明 [0033]图1为本发明多电平换流器子模块冗余供能电路原理图。 [0034]图2为本发明多电平换流器子模块冗余供能电路实施例原理图。 [0035]图3为本发明多电平换流器子模块冗余供能电路的控制方法逻辑图。 具体实施方式 [0036]下面结合附图对技术方案的实施作进一步的详细描述。 [0037] 冗余取能实施例： [0038]参考图1,本发明保护的多电平换流器子模块冗余供能电路，所述的多电平换流器 子模块至少包括功率半导体单元、子模块电容Cm、旁路开关Kb、旁路开关储能电容Cb、可控开 关Qb、控制线圈、电源板卡以及控制板卡;所述多电平换流器子模块冗余供能电路由第一电 阻R1、第二电阻R2、连接模块以及电压变换电路构成;所述连接模块是二极管、机械开关、继 电器、电子开关或半导体可控器件;所述电压变换电路是将输入电压转换成其它电压输出 的电路;所述第一电阻R1一端与子模块电容Cm正极相连，第一电阻R1另一端与第二电阻R2 一端相连，第二电阻R2另一端与子模块电容Cm负极相连;所述连接模块一端连接至第一电 阻R1与第二电阻R2的连接点，另一端连接至旁路开关储能电容Cb正极，旁路开关储能电容Cb 负极连接至子模块电容Cm负极;所述电压变换电路输入正端连接至第一电阻R1与第二电阻 R2的连接点，电压变换电路输入负端连接至子模块电容Cm负极，电压变换电路输出连接至 控制板卡;所述电源板卡给所述控制板卡供电，所述电源板卡的输出正端连接所述旁路开 关储能电容Cb的正极、输出负端连接所述旁路开关储能电容Cb的负极;所述控制线圈的一端 连接至所述旁路开关储能电容Cb的正极，另一端连接至所述可控开关Qb的正极，所述可控开 关Qb的负极连接至所述旁路开关储能电容Cb的负极。 [0039]作为优选方案，如图2所示，所述多电平换流器子模块冗余供能电路的连接模块应 选用二极管或二极管串并联组合，二极管阳极连接至第一电阻R1与第二电阻R2的连接点， 二极管阴极连接至旁路开关储能电容Cb正极。当电源板卡正常工作，且子模块电容Cm电压未 达到过压点时，旁路电源输出高于第一电阻R1、第二电阻R2的分压值，二极管D1处于反向阻 断状态，可以避免冗余供能电路对电源板卡的影响；当子模块电容Cm电压超过过压点，可能 出现冗余供能电路供电，电源板卡内部的二极管可以阻断冗余供能电路对电源板卡的影 响；当电源板卡故障时，电源板卡内部的二极管处于反向阻断状态，避免影响冗余供能电 路。 [0040]作为优选方案，如图2所示，多电平换流器子模块冗余供能电路的电压变换电路应 选用DC/DC电源模块。DC/DC电源模块具有宽输入范围、输出电压稳定、转换效率高的优点， 减小对旁路开关储能电容充电速度的影响。DC/DC电源模块输出可以设置串联二极管，阻断 与电源板卡输出之间的相互影响。 [0041] 控制方法实施例： [0042]参考图3,本发明公布了一种多电平换流器子模块冗余供能电路的控制方法， [0043] (1)当多电平换流器子模块启动前，电源板卡已经故障，旁路功能实施的步骤如 下： [0044]步骤1 ：多电平换流器子模块开始预充电，子模块电容Cm电压开始上升；冗余供能 电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入，给旁路开关储能电容Cb充 电；电压变换电路输入欠压未启动； [0045]步骤2：子模块电容Cm电压上升到电压变换电路的启动电压以上，电压变换电路正 常工作，控制板卡正常工作;旁路开关储能电容Cb继续充电； [0046] 步骤3：控制板卡检测保护单元检测到子模块存在故障，并向上级控制系统发送故 障状态信息，上级控制系统接收到故障状态信息后下发旁路命令； [0047]步骤4：控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条件后，旁 路触发单元触发旁路开关Kb合闸，控制板卡通讯单元向上级控制系统发送旁路开关位置信 号;系统继续运行。 [0048] ⑵当多电平换流器子模块在运行过程中，发生故障，旁路功能实施的步骤如下： [0049]步骤1 ：多电平换流器子模块开始预充电，子模块电容Cm电压开始上升，电源板卡 输入欠压未启动;冗余供能电路的第一电阻R1、第二电阻R2分压后通过连接模块自动投入， 给旁路开关储能电容Cb充电；电压变换电路输入欠压未启动； [0050]步骤2：子模块电容Cm电压上升到电源板卡启动电压以上，电源板卡正常工作，给 旁路开关储能电容Cb充电，给控制板卡供电;冗余供能电路从给旁路开关储能电容Cb充电状 态自动退出；电压变换电路输入欠压未启动； [0051] [0052] [0053] 步骤3： 情况①:控制板卡检测保护单元检测到子模块发生故障、电源板卡正常； 情况②：电源板卡发生故障，控制板卡失电，子模块电容Cm电压上升到电压变换电 路的启动电压以上，电压变换电路正常工作，控制板卡恢复工作;冗余供能电路的第一电阻 R1、第二电阻R2分压后通过连接模块自动投入给旁路开关储能电容Cb继续充电； [0054] 步骤4：控制板卡向上级控制系统发送故障状态信息；上级控制系统接收到故障状 态信息后下发旁路命令，控制板卡检测保护单元检测旁路开关储能电容Cb电压满足合闸条 件，旁路触发单元触发旁路开关Kb合闸，控制板卡上送旁路开关位置信号；系统继续运行。 [0055]以上实施例仅用于说明本发明的技术方案而非对其限制，参照上述实施例进行的 各种形式修改或变更均在本发明的保护范围之内。 [EN CN109167507B]: A multi-level converter sub-module redundant energy supply circuit and control method technical field [0001] The present invention discloses a redundant power supply circuit and a control method for a multi-level converter sub-module, which relates to the field of flexible AC and DC power transmission, and in particular to the energy acquisition technology of power unit modules. Background technique [0002] Cascaded multilevel converters are widely used in UHV AC and DC transmission, reactive power compensation, DC distribution networks and other power, rail transit and new energy applications. In order to ensure the safe and stable operation of the cascaded multilevel converter, the sub-modules of the multi-level converter are required to design a fail-by-pass function. When a fault occurs in the sub-module, the bypass function will bypass the faulty module to avoid The failure is enlarged to keep the system running and avoid economic losses. [0003] However, as the energy source for the realization of all control and protection functions within the multi-level converter sub-module, the power board card has a certain probability of failure due to the life limitation, aging, failure and other external reasons of the device. Especially before the system is started, the power supply board has failed working conditions, the bypass switch does not have the energy required for closing, and the sub-module control board cannot send instructions normally, so the bypass function cannot be realized, which will lead to The shutdown of the entire system. The invention patent CN201710228027.X proposes a self-triggering circuit for the bypass switch of the multi-level converter sub-module, which uses the energy of the AC side of the power module unit to charge the energy storage capacitor of the bypass switch, but if the power board has been activated before the system is started Fault, because the bypass switch closing coil resistance is relatively small, the bypass switch energy storage capacitor is short-circuited, and the charging cannot be completed, so the bypass switch cannot complete the closing action. The invention patent CN108111007A discloses a power module redundant energy supply circuit and control method. After the power board fails, the voltage of the first capacitor exceeds a certain threshold and the first voltage regulator tube is broken down to charge the energy storage capacitor of the bypass switch. And after the voltage of the first capacitor exceeds another threshold, the second voltage regulator tube is broken down to trigger the closing of the second switch, and then the bypass switch is triggered to close. However, the invention introduces multiple high-voltage regulator tubes, which will cause serious heat generation and poor reliability; the bypass switch stores energy The capacitance of the capacitors is on the order of hundreds of microfarads or more. Only when the voltage of the first capacitor breaks down the first voltage regulator tube, can the energy storage capacitor of the bypass switch be charged, which wastes the charging time before breakdown; and the voltage regulator tube The introduction of the charging circuit limits the current of the charging circuit and affects the charging speed; moreover, the voltage regulator tube has a large voltage regulation dispersion and a large temperature drift, which will have a greater impact on the protection accuracy; in addition, the invention also introduces multiple high-voltage switches, which need to be isolated The control and control are complex, and the project can be implemented poorly; more importantly, the invention only makes efforts to realize the reliable bypass of the bypass switch, but if the bypass switch body refuses to move or worse, the superior control system cannot Knowing the status of the faulty module, if it continues to run in the case of bypass failure, it will cause the fault to expand further and cause more serious losses. [0004] Based on the above analysis, the inventor proposed a multi-level converter sub-module redundant power supply circuit and control method to realize the redundant power supply of the bypass switch and the sub-module control board. This case resulted from this . Summary of the invention [0005] Purpose of the invention [0006] The technical problem to be solved by the present invention is: the multi-level converter sub-module fails to perform the bypass after the power board fails, resulting in the system shutdown, and the possible operation with failure when the bypass state is unknown. A redundant power supply circuit and control method for sub-modules of a multi-level converter. When the sub-module power supply board fails, the present invention provides the bypass switch with the energy required for closing through the redundant power supply circuit, and supplies power to the sub-module control board to ensure reliable closing of the bypass switch and avoid The system is shut down, and the status of the faulty module is uploaded to prevent the system from running with a fault and improve the safety and reliability of the system's operation. [0007] Technical Solution [0008] A multi-level converter sub-module redundant power supply circuit, the multi-level converter sub-module at least includes a power semiconductor unit, a sub-module capacitor Cm, a bypass switch Kb, bypass switch energy storage The capacitor Cb, the controllable switch Qb, the control coil, the power supply board and the control board card; the redundant power supply circuit of the multi-level converter sub-module is composed of a first resistor R1, a second resistor R2, a connection module, and a voltage conversion Circuit composition; the connection module is a diode, a mechanical switch, a relay, an electronic switch or a semiconductor controllable device; the voltage conversion circuit is a circuit that converts the input voltage into other voltage outputs; one end of the first resistor R1 is connected to the submodule The capacitor Cm is connected to the positive pole, the other end of the first resistor R1 is connected to one end of the second resistor R2, and the other end of the second resistor R2 is connected to the negative pole of the sub-module capacitor Cm; one end of the connecting module is connected to the first resistor R1 and the second resistor R2. The other end of the connection point is connected to the positive electrode of the bypass switch energy storage capacitor Cb, the negative electrode of the bypass switch energy storage capacitor Cb is connected to the negative electrode of the sub-module capacitor Cm; the positive input terminal of the voltage conversion circuit is connected to the first resistor R1 and the second resistor At the connection point of R2, the negative input terminal of the voltage conversion circuit is connected to the negative terminal of the sub-module capacitor Cm, and the output of the voltage conversion circuit is connected to the control board; the power board supplies power to the control board, and the output of the power board is positive Terminal connected to the positive side of the bypass switch energy storage capacitor Cb The output negative terminal is connected to the negative electrode of the bypass switch energy storage capacitor Cb; one end of the control coil is connected to the positive electrode of the bypass switch energy storage capacitor Cb, and the other end is connected to the positive electrode of the controllable switch Qb , The negative electrode of the controllable switch Qb is connected to the negative electrode of the energy storage capacitor Cb of the bypass switch. [0009] Further, the control board of the multi-level converter sub-module includes a communication unit, a bypass trigger unit, and a detection and protection unit. The communication unit is responsible for receiving instructions from the upper-level control system and sending the status information of the submodule; the bypass trigger unit is responsible for executing the bypass trigger command; the detection protection unit is responsible for detecting the status of the submodule, monitoring point voltage and current sampling and the active protection of the submodule body Features. [0010] Further, both ends of the sub-module capacitor Cm of the multi-level converter sub-module are connected in parallel with voltage equalizing resistors to achieve the voltage equalizing function of the module in the pre-charging process. Therefore, the first resistor R1 and the second resistor R2 can also serve as voltage-sharing resistors of the sub-modules while supplying energy by dividing the voltage, without additional loss of the system. The first resistor R1 and the second resistor R2 may be a single resistor, or a resistor string or parallel structure, which improves the redundancy of the loop. [0011] Further, the voltage conversion circuit of the redundant power supply circuit of the multi-level converter sub-module may be a switching power supply module, a linear power supply or a voltage stabilizing circuit. [0012] Further, the power semiconductor unit includes a half-bridge connection method including at least two power semiconductor devices and a full-bridge connection method including at least four power semiconductor devices. [0013] The present invention also discloses a control method for the redundant power supply circuit of the sub-module of the multi-level converter, as shown below: [0014] (1) Before the sub-module of the multi-level converter is started, the power supply board The card has failed, the steps to implement the bypass function are as follows: [0015] Step 1: The multi-level converter sub-module starts to be precharged, and the voltage of the sub-module capacitor Cm starts to rise; the first resistor R1 and the second resistor R2 of the redundant power supply circuit are divided by voltage and then automatically put into operation through the connection module, Charge the energy storage capacitor Cb of the bypass switch; the input voltage of the voltage conversion circuit is not activated; [0016] Step 2: The voltage of the sub-module capacitor Cm rises above the starting voltage of the voltage conversion circuit, the voltage conversion circuit works normally, and the control board works normally; the bypass switch energy storage capacitor Cb continues to charge; [0017] Step 3: The control board detection and protection unit detects that the submodule has a fault, and sends the fault status information to the upper control system, and the upper control system issues a bypass command after receiving the fault status information; [0018] Step 4: After the control board detection protection unit detects that the voltage of the bypass switch energy storage capacitor Cb meets the closing conditions, the bypass trigger unit triggers the bypass switch Kb to close, and the control board communication unit sends a bypass to the superior control system Road switch position signal; the system continues to run. [0019] When the multi-level converter sub-module fails during operation, the steps for implementing the bypass function are as follows: [0020] Step 1: The multi-level converter sub-module starts to pre-charge, the voltage of the sub-module capacitor Cm starts to rise, and the input undervoltage of the power supply board is not activated; the first resistor R1 and the second resistor R2 of the redundant power supply circuit After the voltage is divided, it is automatically turned on through the connection module to charge the energy storage capacitor Cb of the bypass switch; the input voltage of the voltage conversion circuit is not activated; [0021] Step 2: The voltage of the sub-module capacitor Cm rises above the startup voltage of the power supply board, the power supply board works normally, and the bypass switch energy storage capacitor Cb is charged to supply power to the control board; the redundant power supply circuit is from the side The charging state of the energy storage capacitor Cb of the circuit switch is automatically exited; the input voltage of the voltage conversion circuit is not activated; [0022] Step 3: [0023] Situation 1: The control board detection and protection unit detects that the sub-module is faulty and the power board is normal; [0024] Situation 2: the power board fails, the control board loses power, the voltage of the sub-module capacitor Cm rises above the starting voltage of the voltage conversion circuit, the voltage conversion circuit works normally, and the control board resumes work; redundant power supply circuit After the first resistor R1 and the second resistor R2 are divided into voltage, the connection module is automatically put into the bypass switch energy storage capacitor Cb to continue charging; [0025] Step 4: The control board sends fault status information to the higher-level control system; the upper-level control system issues a bypass command after receiving the fault status information, and the control board detection and protection unit detects that the voltage of the bypass switch energy storage capacitor Cb meets the requirements. Under brake condition, the bypass trigger unit triggers the bypass switch Kb to close, and the control board sends the bypass switch position signal; the system continues to run. [0026] Benefits [0027] The use of the multi-level converter sub-module redundant power supply circuit of the present invention solves the power supply problems of the bypass switch energy storage capacitor and the sub-module control board after the sub-module power board fails. Compared with the prior art, it has the following beneficial effects: [0028] Using a simple passive voltage divider circuit, the redundant energy supply of the energy storage capacitor of the bypass switch is realized; the energy source for the closing action of the bypass switch is guaranteed; [0029] (2) A simple passive voltage divider circuit is used to introduce a voltage conversion circuit at the resistor divider and step-down port to realize the sub-module control redundant power supply problem; to ensure the protection trigger function and the status upload function; to avoid Failure to expand due to the refusal of the bypass switch or more severe working conditions; [0030] Using the digital sampling of the control board and the high-precision reference chip, the protection accuracy is high; [0031] (4) Utilizing the original voltage-balancing resistor loop energy of the sub-module without additional system loss; it is economical; [0032] (5) The circuit structure is simple and reliable, no additional control is needed, the engineering feasibility is high, and the cost is low. Description of the drawings [0033] FIG. 1 is a schematic diagram of a redundant power supply circuit for a sub-module of a multi-level converter of the present invention. [0034] FIG. 2 is a schematic diagram of an embodiment of a redundant power supply circuit for a sub-module of a multi-level converter of the present invention. [0035] FIG. 3 is a logic diagram of the control method of the redundant power supply circuit of the sub-module of the multi-level converter of the present invention. Detailed ways [0036] The implementation of the technical solution will be described in further detail below in conjunction with the accompanying drawings. [0037] Redundant energy acquisition embodiment: [0038] Referring to FIG. 1, the multi-level converter sub-module redundant power supply circuit protected by the present invention, the multi-level converter sub-module at least includes a power semiconductor unit, a sub-module capacitor Cm, a bypass switch Kb, bypass switch energy storage capacitor Cb, controllable switch Qb, control coil, power supply board and control board card; the redundant power supply circuit of the multi-level converter sub-module is composed of a first resistor R1 and a second resistor R2, a connection module and a voltage conversion circuit composition; the connection module is a diode, a mechanical switch, a relay, an electronic switch or a semiconductor controllable device; the voltage conversion circuit is a circuit that converts the input voltage into other voltage outputs; the first One end of a resistor R1 is connected to the positive pole of the sub-module capacitor Cm, the other end of the first resistor R1 is connected to one end of the second resistor R2, and the other end of the second resistor R2 is connected to the negative pole of the sub-module capacitor Cm; one end of the connecting module is connected to the first resistor The connection point of R1 and the second resistor R2, the other end is connected to the positive pole of the bypass switch energy storage capacitor Cb, the negative pole of the bypass switch energy storage capacitor Cb is connected to the negative pole of the sub-module capacitor Cm; the positive input terminal of the voltage conversion circuit is connected to the first A connection point of a resistor R1 and a second resistor R2, the negative input terminal of the voltage conversion circuit is connected to the negative terminal of the sub-module capacitor Cm, and the output of the voltage conversion circuit is connected to the control board; the power board supplies power to the control board, so The positive output terminal of the power board is connected to the bypass switch The positive and negative output ends of the energy storage capacitor Cb are connected to the negative electrode of the bypass switch energy storage capacitor Cb; one end of the control coil is connected to the positive electrode of the bypass switch energy storage capacitor Cb, and the other end is connected to the The positive electrode of the controllable switch Qb is connected to the negative electrode of the energy storage capacitor Cb of the bypass switch. [0039] As a preferred solution, as shown in FIG. 2, the connection module of the redundant power supply circuit of the multi-level converter sub-module should use a diode or a combination of diode series and parallel, and the diode anode is connected to the first resistor R1 and the first resistor R1 and the first resistor R1. At the junction of the two resistors R2, the cathode of the diode is connected to the anode of the energy storage capacitor Cb of the bypass switch. When the power board is working normally and the voltage of the sub-module capacitor Cm has not reached the overvoltage point, the bypass power supply output is higher than the voltage division value of the first resistor R1 and the second resistor R2, and the diode D1 is in the reverse blocking state. Avoid the influence of redundant energy supply circuit on the power supply board; when the voltage of the sub-module capacitor Cm exceeds the overvoltage point, redundant energy supply circuit power may occur. The diode inside the power supply board can block the redundant energy supply circuit from affecting the power supply board. The influence of the card: When the power board fails, the diode inside the power board is in a reverse blocking state to avoid affecting the redundant power supply circuit. [0040] As a preferred solution, as shown in FIG. 2, the voltage conversion circuit of the redundant power supply circuit of the multi-level converter sub-module should be a DC/DC power supply module. The DC/DC power module has the advantages of wide input range, stable output voltage, and high conversion efficiency, reducing the impact on the charging speed of the energy storage capacitor of the bypass switch. The output of the DC/DC power module can be set with a series diode to block the mutual influence with the output of the power board. [0041] Control method embodiment: [0042] Referring to FIG. 3, the present invention discloses a control method of a redundant power supply circuit for a sub-module of a multi-level converter, [0043] (1) Before the multi-level converter sub-module is started, the power board has failed, and the steps for implementing the bypass function are as follows: [0044] Step 1: The multi-level converter sub-module starts to be precharged, and the voltage of the sub-module capacitor Cm starts to rise; the first resistor R1 and the second resistor R2 of the redundant power supply circuit are divided by voltage and then automatically put into operation through the connecting module, Charge the energy storage capacitor Cb of the bypass switch; the input voltage of the voltage conversion circuit is not activated; [0045] Step 2: The voltage of the sub-module capacitor Cm rises above the starting voltage of the voltage conversion circuit, the voltage conversion circuit works normally, and the control board works normally; the bypass switch energy storage capacitor Cb continues to charge; [0046] Step 3: The control board detection and protection unit detects that the submodule has a fault, and sends the fault status information to the upper control system, and the upper control system issues a bypass command after receiving the fault status information; [0047] Step 4: After the control board card detection protection unit detects that the voltage of the bypass switch energy storage capacitor Cb meets the closing conditions, The circuit trigger unit triggers the bypass switch Kb to close, and the control board communication unit sends the bypass switch position signal to the superior control system; the system continues to run. [0048] (2) When the multi-level converter sub-module fails during operation, the steps for implementing the bypass function are as follows: [0049] Step 1: The multi-level converter sub-module starts to pre-charge, the voltage of the sub-module capacitor Cm starts to rise, and the input undervoltage of the power board is not activated; the first resistor R1 and the second resistor R2 of the redundant power supply circuit After the voltage is divided, it is automatically turned on through the connection module to charge the energy storage capacitor Cb of the bypass switch; the input voltage of the voltage conversion circuit is not activated; [0050] Step 2: The voltage of the sub-module capacitor Cm rises above the startup voltage of the power supply board, the power supply board is working normally, charge the bypass switch energy storage capacitor Cb, and supply power to the control board; the redundant power supply circuit is from the side The charging state of the energy storage capacitor Cb of the circuit switch is automatically exited; the input voltage of the voltage conversion circuit is not activated; [0051] [0052] [0053] Step 3: Case 1: The control board card detection and protection unit detects that the sub-module is faulty and the power board is normal; Case 2: The power board fails, the control board loses power, and the voltage of the sub-module capacitor Cm rises to voltage Above the starting voltage of the conversion circuit, the voltage conversion circuit works normally, and the control board resumes work; the first resistor R1 and the second resistor R2 of the redundant power supply circuit are divided into voltage and then automatically put into the bypass switch energy storage capacitor Cb through the connection module. Continue charging [0054] Step 4: The control board sends fault status information to the higher-level control system; the upper-level control system issues a bypass command after receiving the fault status information, and the control board detection and protection unit detects that the voltage of the bypass switch energy storage capacitor Cb meets the requirements. Under the condition of brake, the bypass trigger unit triggers the bypass switch Kb to close, and the control board sends the bypass switch position signal; the system continues to run. [0055] The above embodiments are only used to illustrate the technical solutions of the present invention rather than to limit it. Various modifications or changes made with reference to the above embodiments are all within the protection scope of the present invention.
[EN EP3878011A1]: POWER ELECTRONICS SYSTEM [FR EP3878011A1]: SYSTÈME ÉLECTRONIQUE DE PUISSANCE [ZH CN113261100A]: 电力电子系统 [DE EP3878011A1]: LEISTUNGSELEKTRONIKSYSTEM | [EN WO2020094663A1]: The invention relates to an electronic system comprising a plurality of adjacent, elementary power electronics modules connected to one another by an electrical module connection, each elementary module comprising at least one power component integrated on a printed circuit inserted between two electrical conductive heat sinks. Advantageously, the electrical module connection is provided by means of the heat sinks at the side and/or central connection surfaces thereof. [FR FR3088137B1]: L'invention a pour objet un système électronique comprenant une pluralité de modules électroniques de puissance élémentaires adjacents et connectés entre eux par une connexion électrique de modules, chaque module élémentaire comprenant au moins un composant de puissance intégré sur un circuit imprimé intercalé entre deux dissipateurs thermiques conducteurs électriques. Avantageusement, la connexion électrique de modules se fait par l'intermédiaire desdits dissipateurs thermiques au niveau de leurs surfaces de connexion latérales et/ou centrales. [ZH CN113261100A]: 本发明涉及一种电子系统，包括多个通过电模块连接彼此连接的相邻的基本电力电子模块，每个基本模块包括集成在印刷电路上的至少一个功率器件，印刷电路插入两个导电散热器之间。有利地，电模块连接是通过在其侧面和/或中心连接表面处的散热器提供的。 | FR3088137B1 | 2020-05-08 2020-11-27 | FR1860229A | 2018-11-06 2018-11-06 | FR1860229A, 2018-11-06 FR1860229A, 2018-11-06 | FR3088137B1: 2020-11-27 WO2020094663A1: 2020-05-14 CN113261100A: 2021-08-13 EP3878011A1: 2021-09-15 | INST POLYTECHNIQUE GRENOBLE 格勒诺布尔理工学院 | AVENAS YVAN | H01L23/36: I H02M1/00: I H01L25/11: I H01L23/13: I H01L23/34: I H01L23/367: I H01L23/40: I H01L23/48: I H01L23/538: I H01L23/58: I H01L25/07: I H01L25/18: I | H01L23/13: I H01L23/36: I H01L23/3677: A H01L23/5389: I H01L23/58: I H01L25/072: I H01L25/115: I H01L25/18: I H01L2023/4087: A H01L2224/24137: A | WO2018189468A1 US5424919A US2015179611A1 |  | [EN EP3878011A1]: CLAIMS 1. Electronic system comprising at least one electronic cell (CO), said at least one electronic cell (CO) comprising: - A first electronic module of elementary power (1), said first elementary module (1), A second electronic module of elementary power (2), said second elementary module (2), Said first and second elementary modules (1, 2) being adjacent and connected together by an electrical connection of modules, each of these first and second elementary modules (1, 2) comprising: at least one power component (100, 200), preferably integrated on or in a printed circuit (10), a first electrically conductive heat sink (11, 21), called an anode sink, connected to a first electrode called an anode of the component power (100, 200), and a second electrically conductive heat sink (12, 22), called cathode heat sink, connected to a second electrode called cathode of the power component (100, 200), said electronic system being characterized in that: each cathode sink (12, 22) has a first connection surface (120) called the cathode central surface and at least a second connection surface (121, 122, 222) called the cathode side surface, and each anode sink (1 1, 21 ) has a first connection surface (1 10, 210) called anodic central surface and at least a second connection surface (1 1 1, 112, 212) called anodic side surface, and in that: the electrical connection of modules between the first and second adjacent elementary modules (1, 2) comprises at least one lateral conductive electrical connection (1121c, 1222c) between: at least one of the anode and cathode side surfaces (1 1 1, 121) of the first elementary module (1), and at least one of the anode and cathode side surfaces (212, 222) of the second elementary module (2). 2. System according to the preceding claim, in which the electrical connection of modules between the first and second elementary modules (1, 2) adjacent further comprises one of a capacitive lateral electrical connection (1222cp) and an insulating lateral electrical connection (1221 i) Between : at least one other among the anode and cathode side surfaces (1 11, 121) of the first elementary module (1), and at least one other among the anode and cathode side surfaces (212, 222) of the second elementary module (2). 3. System according to the preceding claim, in which at least one anodic lateral surface (11 1) of the first elementary module (1) is connected to at least one cathodic lateral surface (222) of the second elementary module (2) by a conductive lateral electrical connection ( 1,122c) and at least one cathode lateral surface (121) of the first elementary module (1) is connected to at least one anodic lateral surface (212) of the second elementary module (2) by a connection electrical selected from a capacitive lateral electrical connection (1221cp) and an insulating lateral electrical connection (1221 i). 4. System according to the preceding claim, in which the at least one power component (100) of the first elementary module (1) is one of a first power transistor and a first power diode, and the at least one component of power (200) of the second elementary module (2) is one of a second power transistor and a second power diode, so that the electronic cell forms a switching cell (C10). 5. System according to any one of the preceding claims, comprising a plurality of adjacent electronic cells and connected to each other, an electronic cell (C1, C1 ') of the plurality of electronic cells being connected to at least one adjacent electronic cell (C2, C2' ) by an electrical connection of cells, said electrical connection of cells comprising at least one of a conductive central electrical connection (1231c, 1242c), a capacitive central electrical connection and an insulating central electrical connection (2142Î) between: at least one of the anodic and cathodic central surfaces of the cell (C1, C1 '), and at least one of the anodic and cathodic central surfaces of the at least one cell adjacent (C2, C2 ') to said cell (C1, C1'). 6. System according to the preceding claim, in which at least one central cathode surface (120) of the cell (C1) is connected to at least one central anode surface (310) of the adjacent cell (C2) by a central conductive electrical connection (1231 c ) and at least one anode central surface (210) of the cell (C1) is connected to at least one cathode central surface (420) of the adjacent cell (C2) by an insulating central electrical connection (2142i). 7. System according to the preceding claim and claim 4, in which each electronic cell (C1, C2, C3) of the plurality of electronic cells is a switching cell (C10), so that the system forms a subset of a converter multi-level power. 8. The system of claim 5 wherein the electrical connection of cells further comprises at least one lateral conductive electrical connection (1252c, 2161 c) between: at least one of the anode and cathode side surfaces of the cell (C1 '), and at least one of the anode and cathode side surfaces of at least one other cell adjacent (C3') to said cell (C1 '). 9. System according to the preceding claim and claim 4 comprising a first electronic cell (C1 '), a second electronic cell (C2'), a third electronic cell (C3 '), a fourth electronic cell (C4'), said first, second , third, fourth electronic cells (C1 ', C2', C3 ', C4') being switching cells (C10), in which: The anodic and cathodic central surfaces of the anodic (21) and cathodic (12) heat sinks connected together by a capacitive lateral electrical connection (1221 cp) of the first cell (C1 ') are respectively connected to the anodic and cathodic central surfaces of the dissipators anodic (31) and cathodic (42) thermal interconnected by a capacitive lateral electrical connection (4231 cp) of the second cell (C2 '), by central conductive electrical connections (2131 c, 1242c), The anodic and cathodic central surfaces of the anodic (61) and cathodic (52) heatsinks linked together by a capacitive lateral electrical connection (5261 cp) of the third cell (C3 ') are respectively connected to the anodic and cathodic central surfaces of the heatsinks anodic (71) and cathodic (82) thermal interconnected by a capacitive lateral electrical connection (8271cp) of the fourth cell (C4 '), by central conductive electrical connections (6171 c, 5282c), The anode and cathode side surfaces of the anode (11) and cathode heat sinks (22) connected together by a conductive side electrical connection (1122c), located on the same side of the first cell (C1 ') are respectively connected to the anode and cathode side surfaces of the anode (51) and cathode (62) heat sinks connected together by a conductive lateral electrical connection (5162c), located on a same side of the third cell (C3 '), by lateral electrical insulating connections (1151 i, 2262i), The anodic and cathodic lateral surfaces of the anodic (21) and cathodic (12) heat sinks linked together by a capacitive lateral electrical connection (1221cp), located on the same side of the first cell (C1 ') are respectively connected to the lateral surfaces anodic and cathodic anodic (61) and cathodic (52) heat sinks linked together by a capacitive lateral electrical connection (5261 cp), located on the same side of the third cell (C3 '), by lateral conductive electrical connections (2161c, 1252c), The anode and cathode side surfaces of the anode (31) and cathode heat sinks (42) connected together by a connection electric lateral capacitive (4231 cp), located on the same side of the second cell (C2 ') are respectively connected to the anode and cathode side surfaces of the anode (71) and cathode (81) heat sinks connected together by a capacitive lateral electrical connection (8271cp), located on a same side of the fourth cell (C4 '), by lateral conductive electrical connections (3171c, 4282c), The anode and cathode side surfaces of the anode (41) and cathode (32) heat sinks connected together by a conductive lateral electrical connection (4132c), located on the same side of the second cell (C2 ') are respectively connected to the side surfaces anodic and cathodic anodic (81) and cathodic (72) heat sinks connected together by a lateral conductive electrical connection (8172c), located on the same side of the fourth cell (C4 '), by lateral electrical insulating connections (4181 i, 3272i), so that the system forms a power converter of interlaced chopper type. 10. System according to any one of the preceding claims, in which each dissipator (1 1, 12, 21, 22) comprises at least one of a fin and a finger. 1 1. System according to any one of the preceding claims except for claims 1, 5 and 9 in which at least one of the lateral capacitive electrical connection (1221cp, 221 1cp, 6251 cp, 4231 cp) and the connection electric capacitive power plant includes at least one capacitor (10cp). 12. A system according to any one of the preceding claims further comprising a cooling device (2000) configured to cool each anode and cathode heatsink (1 1, 12, 21, 22). 13. System according to any one of the preceding claims, further comprising at least one elementary inductance module (9) comprising: A conductive coil (900) embedded in a magnetic matrix (903) having a first face and a second face opposite to the first face, a first heat sink (91) electrically conductive on the first face and connected to said conductive coil (900) , and a second heat sink (92) electrically conductive on the second face and connected to said conductive coil (900). [FR EP3878011A1]: REVENDICATIONS1. Système électronique comprenant au moins une cellule électronique (CO), ladite au moins une cellule électronique (CO) comprenant : - Un premier module électronique de puissance élémentaire (1 ), dit premier module élémentaire (1 ), Un deuxième module électronique de puissance élémentaire (2), dit deuxième module élémentaire (2), Lesdits premier et deuxième modules élémentaires (1 , 2) étant adjacents et connectés entre eux par une connexion électrique de modules, chacun de ces premier et deuxième modules élémentaires (1 , 2) comprenant : au moins un composant de puissance (100, 200), de préférence intégré sur ou dans un circuit imprimé (10), un premier dissipateur thermique conducteur électrique (11 , 21 ), dit dissipateur anodique, relié à une première électrode dite anode du composant de puissance (100, 200), et un deuxième dissipateur thermique conducteur électrique (12, 22), dit dissipateur cathodique, relié à une deuxième électrode dite cathode du composant de puissance (100, 200), ledit système électronique étant caractérisé en ce que : chaque dissipateur cathodique (12, 22) présente une première surface de connexion (120) dite surface centrale cathodique et au moins une deuxième surface de connexion (121 , 122, 222) dite surface latérale cathodique, et chaque dissipateur anodique (1 1 , 21 ) présente une première surface de connexion (1 10, 210) dite surface centrale anodique et au moins une deuxième surface de connexion (1 1 1 , 112, 212) dite surface latérale anodique, et en ce que : la connexion électrique de modules entre les premier et deuxième modules élémentaires (1 , 2) adjacents comprend au moins une connexion électrique latérale conductrice (1 121c, 1222c) entre : au moins une parmi les surfaces latérales anodique et cathodique (1 1 1 , 121 ) du premier module élémentaire (1 ), et au moins une parmi les surfaces latérales anodique et cathodique (212, 222) du deuxième module élémentaire (2). 2. Système selon la revendication précédente dans lequel la connexion électrique de modules entre les premier et deuxième modules élémentaires (1 , 2) adjacents comprend en outre l’une parmi une connexion électrique latérale capacitive (1222cp) et une connexion électrique latérale isolante (1221 i) entre : au moins une autre parmi les surfaces latérales anodique et cathodique (1 11 , 121 ) du premier module élémentaire (1 ), et au moins une autre parmi les surfaces latérales anodique et cathodique (212, 222) du deuxième module élémentaire (2). 3. Système selon la revendication précédente dans lequel au moins une surface latérale anodique (11 1 ) du premier module élémentaire (1 ) est connectée à au moins une surface latérale cathodique (222) du deuxième module élémentaire (2) par une connexion électrique latérale conductrice (1 122c) et au moins une surface latérale cathodique (121 ) du premier module élémentaire (1 ) est connectée à au moins une surface latérale anodique (212) du deuxième module élémentaire (2) par une connexion électrique choisie parmi une connexion électrique latérale capacitive (1221cp) et une connexion électrique latérale isolante (1221 i). 4. Système selon la revendication précédente dans lequel l’au moins un composant de puissance (100) du premier module élémentaire (1 ) est l’un parmi un premier transistor de puissance et une première diode de puissance, et l’au moins un composant de puissance (200) du deuxième module élémentaire (2) est l’un parmi un deuxième transistor de puissance et une deuxième diode de puissance, de sorte que la cellule électronique forme une cellule de commutation (C10). 5. Système selon l’une quelconque des revendications précédentes comprenant une pluralité de cellules électroniques adjacentes et connectées entre elles, une cellule électronique (C1 , C1’) de la pluralité de cellules électroniques étant connectée à au moins une cellule électronique adjacente (C2, C2’) par une connexion électrique de cellules, ladite connexion électrique de cellules comprenant au moins l’une parmi une connexion électrique centrale conductrice (1231c, 1242c), une connexion électrique centrale capacitive et une connexion électrique centrale isolante (2142Î) entre : au moins une parmi les surfaces centrales anodique et cathodique de la cellule (C1 , C1’), et au moins une parmi les surfaces centrales anodique et cathodique de l’au moins une cellule adjacente (C2, C2’) à ladite cellule (C1 , C1’). 6. Système selon la revendication précédente dans lequel au moins une surface centrale cathodique (120) de la cellule (C1 ) est connectée à au moins une surface centrale anodique (310) de la cellule adjacente (C2) par une connexion électrique centrale conductrice (1231 c) et au moins une surface centrale anodique (210) de la cellule (C1 ) est connectée à au moins une surface centrale cathodique (420) de la cellule adjacente (C2) par une connexion électrique centrale isolante (2142i). 7. Système selon la revendication précédente et la revendication 4 dans lequel chaque cellule électronique (C1 , C2, C3) de la pluralité de cellules électroniques est une cellule de commutation (C10), de sorte que le système forme un sous-ensemble d’un convertisseur de puissance multiniveaux. 8. Système selon la revendication 5 dans lequel la connexion électrique de cellules comprend en outre au moins une connexion électrique latérale conductrice (1252c, 2161 c) entre : au moins une parmi les surfaces latérales anodique et cathodique de la cellule (C1’), et au moins une parmi les surfaces latérales anodique et cathodique d’au moins une autre cellule adjacente (C3’) à ladite cellule (C1’). 9. Système selon la revendication précédente et la revendication 4 comprenant une première cellule électronique (C1’), une deuxième cellule électronique (C2’), une troisième cellule électronique (C3’), une quatrième cellule électronique (C4’), lesdites première, deuxième, troisième, quatrième cellules électroniques (C1’, C2’, C3’, C4’) étant des cellules de commutation (C10), dans lequel : Les surfaces centrales anodique et cathodique des dissipateurs thermiques anodique (21 ) et cathodique (12) reliés entre eux par une connexion électrique latérale capacitive (1221 cp) de la première cellule (C1’) sont respectivement connectées aux surfaces centrales anodique et cathodique des dissipateurs thermiques anodique (31 ) et cathodique (42) reliés entre eux par une connexion électrique latérale capacitive (4231 cp) de la deuxième cellule (C2’), par des connexions électriques centrales conductrices (2131 c, 1242c), Les surfaces centrales anodique et cathodique des dissipateurs thermiques anodique (61 ) et cathodique (52) reliés entre eux par une connexion électrique latérale capacitive (5261 cp) de la troisième cellule (C3’) sont respectivement connectées aux surfaces centrales anodique et cathodique des dissipateurs thermiques anodique (71 ) et cathodique (82) reliés entre eux par une connexion électrique latérale capacitive (8271cp) de la quatrième cellule (C4’), par des connexions électriques centrales conductrices (6171 c, 5282c), Les surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (11 ) et cathodique (22) reliés entre eux par une connexion électrique latérale conductrice (1 122c), situées sur un même côté de la première cellule (C1’) sont respectivement connectées aux surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (51 ) et cathodique (62) reliés entre eux par une connexion électrique latérale conductrice (5162c), situées sur un même côté de la troisième cellule (C3’), par des connexions électriques latérales isolantes (1151 i, 2262i), Les surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (21 ) et cathodique (12) reliés entre eux par une connexion électrique latérale capacitive (1221cp), situées sur un même côté de la première cellule (C1’) sont respectivement connectées aux surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (61 ) et cathodique (52) reliés entre eux par une connexion électrique latérale capacitive (5261 cp), situées sur un même côté de la troisième cellule (C3’), par des connexions électriques latérales conductrices (2161c, 1252c), Les surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (31 ) et cathodique (42) reliés entre eux par une connexion électrique latérale capacitive (4231 cp), situées sur un même côté de la deuxième cellule (C2’) sont respectivement connectées aux surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (71 ) et cathodique (82) reliés entre eux par une connexion électrique latérale capacitive (8271cp), situées sur un même côté de la quatrième cellule (C4’), par des connexions électriques latérales conductrices (3171c, 4282c), Les surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (41 ) et cathodique (32) reliés entre eux par une connexion électrique latérale conductrice (4132c), situées sur un même côté de la deuxième cellule (C2’) sont respectivement connectées aux surfaces latérales anodique et cathodique des dissipateurs thermiques anodique (81 ) et cathodique (72) reliés entre eux par une connexion électrique latérale conductrice (8172c), situées sur un même côté de la quatrième cellule (C4’), par des connexions électriques latérales isolantes (4181 i , 3272i), de sorte que le système forme un convertisseur de puissance de type hacheur entrelacé. 10. Système selon l’une quelconque des revendications précédentes dans lequel chaque dissipateur (1 1 , 12, 21 , 22) comprend au moins l’un parmi une ailette et un doigt. 1 1. Système selon l’une quelconque des revendications précédentes à l’exception des revendications 1 , 5 et 9 dans lequel l’une au moins parmi la connexion électrique latérale capacitive (1221cp, 221 1cp, 6251 cp, 4231 cp) et la connexion électrique centrale capacitive comprend au moins un condensateur (10cp). 12. Système selon l’une quelconque des revendications précédentes comprenant en outre un dispositif de refroidissement (2000) configuré pour refroidir chaque dissipateur thermique anodique et cathodique (1 1 , 12, 21 , 22). 13. Système selon l’une quelconque des revendications précédentes comprenant en outre au moins un module d’inductance élémentaire (9) comprenant : Une bobine conductrice (900) noyée dans une matrice magnétique (903) présentant une première face et une deuxième face opposée à la première face, un premier dissipateur thermique (91 ) conducteur électrique sur la première face et relié à ladite bobine conductrice (900), et un deuxième dissipateur thermique (92) conducteur électrique sur la deuxième face et relié à ladite bobine conductrice (900). [ZH CN113261100A]: 1 .一种电子系统，包括至少一个电子单元(C0),所述至少一个电子单元(C0)包括： - 称为第一基本模块⑴的第一基本电力电子模块(1)， - 称为第二基本模块⑵的第二基本电力电子模块(2)， 所述第一和第二基本模块(1，2)相邻并且通过电模块连接件彼此连接， 所述第一和第二基本模块(1，2)中的每一个都包括： - 至少一个功率器件(100，200)，优选地集成在印刷电路(10)上或印刷电路(10)中， - 称为阳极散热器的第一导电散热器(11，21)，所述阳极散热器连接到功率器件(100， 200)的称为阳极的第一电极，以及 - 称为阴极散热器的第二导电散热器(12,22)，所述阴极散热器连接到功率器件(100， 200)的称为阴极的第二电极， 所述电子系统的特征在于： 每个阴极散热器(12,22)都具有称为中心阴极表面的第一连接表面(120)和至少一个 称为阴极侧表面的第二连接表面(121，122,222)，以及 每个阳极散热器(11，21)具有称为中心阳极表面的第一连接表面(110，210)和至少一 个称为阳极侧表面的第二连接表面(111，112,212)，其中： 相邻的第一和第二基本模块(1，2)之间的电模块连接件包括： 第一基本模块⑴的阳极和阴极侧表面(111，121)中的至少一个，与 第二基本模块⑵的阳极和阴极侧表面(212,222)中的至少一个 之间的至少一个导电侧电连接件(1121c，1222c)。 2 .根据权利要求1所述的系统，其中，在相邻的第一和第二基本模块(1，2)之间的电模 块连接件还包括： 第一基本模块⑴的阳极和阴极侧表面(111，121)中的至少另一个，与 第二基本模块⑵的阳极和阴极侧表面(212,222)中的至少另一个 之间的电容性侧电连接件(1222cp)和绝缘侧电连接件(1221i)中的一个。 3 .根据权利要求2所述的系统，其中，第一基本模块⑴的至少一个阳极侧表面(111)通 过导电侧电连接件(1122c)连接到第二基本模块⑵的至少一个阴极侧表面(222)，并且第 一基本模块⑴的至少一个阴极侧表面(121)通过选自电容性侧电连接件(1221cp)和绝缘 侧电连接件(1221i)的电连接件连接到第二基本模块⑵的至少一个阳极侧表面(212)。 4 .根据权利要求3所述的系统，其中，第一基本模块⑴的至少一个功率器件(100)是第 一功率晶体管和第一功率二极管中的一个，并且第二基本模块⑵的至少一个功率器件 (200)是第二功率晶体管和第二功率二极管中的一个,使得电子单元形成开关单元(C10)。 5 .根据前述权利要求1-4中的任一项所述的系统，包括多个相邻的彼此连接的电子单 元，所述多个电子单元中的一个电子单元(C1，C1')通过这些单元的电连接件连接到至少一 个相邻的电子单元(C2，C2')，所述单元的电连接件包括位于： 单元(C1，C1')的中心阳极和阴极表面中的至少一个，与 与所述单元(C1，C1')相邻的至少一个单元(C2，C2')的中心阳极表面和阴极表面中的 至少一个 之间的导电中心电连接件(1231c，1242c)、电容性中心电连接件以及中心绝缘电连接 件(2142。中的一个。 6 .根据权利要求5所述的系统，其中，单元(C1)的至少一个中心阴极表面(120)通过导 电中心电连接件(1231c)连接到相邻的单元(C2)的至少一个中心阳极表面(310)，并且单元 (C1)的至少一个中心阳极表面(210)通过中心绝缘电连接件(2142i)连接到相邻的单元 (C2)的至少一个中心阴极表面(420)。 7 .根据权利要求6和权利要求4所述的系统，其中，所述多个电子单元中的每个电子单 元(C1，C2，C3)是开关单元(C10)，使得所述系统形成多电平功率变换器的子组件。 8 .根据权利要求5所述的系统，其中，所述单元的电连接件还包括： 单元(C1')的阳极和阴极侧表面中的至少一个，以及 与所述单元(C1,)相邻的至少一个其他单元(C3')的阳极和阴极侧表面中的至少一个 之间的至少一个导电侧电连接件(1252c，2161c)。 9 .根据权利要求8和权利要求4所述的系统，包括第一电子单元(C1')、第二电子单元 (C2')、第三电子单元(C3')、第四电子单元(C4')，所述第一、第二、第三、第四电子单元 (C1'，C2'，C3'，C4')是开关单元(C10)，其中： 阳极散热器(61)和阴极散热器(52)的中心阳极表面和中心阴极表面通过导电中心电 连接件(2131c，1242c)分别连接到阳极散热器(31)和阴极散热器(42)的中心阳极表面和中 心阴极表面，其中阳极散热器(61)和阴极散热器(52)的中心阳极表面和中心阴极表面通过 第一单元(C1')的电容性侧电连接件(1221cp)彼此连接，并且阳极散热器(31)和阴极散热 器(42)的中心阳极表面和中心阴极表面通过第二单元(C2')的电容性侧电连接件(4231cp) 彼此连接， 阳极散热器(61)和阴极散热器(52)的中心阳极表面和中心阴极表面通过导电中心电 连接件(6171c，5282c)分别连接到阳极散热器(71)和阴极散热器(82)的中心阳极表面和中 心阴极表面，其中阳极散热器(61)和阴极散热器(52)的中心阳极表面和中心阴极表面通过 第三单元(C3')的电容性侧电连接件(5261cp)彼此连接，并且阳极散热器(71)和阴极散热 器(82)的中心阳极表面和中心阴极表面通过第四单元(C4')的电容性侧电连接件(8271cp) 彼此连接， 位于第一单元(C1')的同一侧上的阳极散热器(11)和阴极散热器(22)其阳极侧表面和 阴极侧表面通过绝缘侧电连接件(1151i，2262i)分别连接到位于第三单元(C3')同一侧上 的阳极散热器(51)和阴极散热器(62)的阳极侧表面和阴极侧表面，其中位于第一单元 (C1')的同一侧上的阳极散热器(11)和阴极散热器(22)其阳极侧表面和阴极侧表面通过导 电侧电连接件(1122c)彼此连接，并且位于第三单元(C3')同一侧上的阳极散热器(51)和阴 极散热器(62)其阳极侧表面和阴极侧表面通过导电侧电连接件(5162c)彼此连接， 位于第一单元(C1')同一侧上的阳极散热器(21)和阴极散热器(12)其阳极侧表面和阴 极侧表面通过导电侧电连接件(2161c，1252c)分别连接到位于第三单元(C3')同一侧上的 阳极散热器(61)和阴极散热器(52)的阳极侧表面和阴极侧表面，其中位于第一单元(C1') 同一侧上的阳极散热器(21)和阴极散热器(12)其阳极侧表面和阴极侧表面通过电容性侧 电连接件(1221cp)彼此连接，并且位于第三单元(C3')同一侧上的阳极散热器(61)和阴极 散热器(52)其阳极侧表面和阴极侧表面通过电容性侧电连接件(5261cp)彼此连接， 位于第二单元(C2')同一侧上的阳极散热器(31)和阴极散热器(42)其阳极侧表面和阴 极侧表面通过导电侧电连接件(3171c，4282c)分别连接到位于第四单元(C4')同一侧上的 阳极散热器(71)和阴极散热器(82)的阳极侧表面和阴极侧表面，其中位于第二单元(C2') 同一侧上的阳极散热器(31)和阴极散热器(42)其阳极侧表面和阴极侧表面通过电容性侧 电连接件(4231cp)彼此连接，并且位于第四单元(C4')同一侧上的阳极散热器(71)和阴极 散热器(82)其阳极侧表面和阴极侧表面通过电容性侧电连接件(8271cp)彼此连接， 位于第二单元(C2')同一侧上的阳极散热器(41)和阴极散热器(32)其阳极侧表面和阴 极侧表面通过绝缘侧电连接件(4181i，3272i)分别连接到位于第四单元(C4')同一侧上的 阳极散热器(81)和阴极散热器(72)的阳极侧表面和阴极侧表面，其中位于第二单元(C2') 同一侧上的阳极散热器(41)和阴极散热器(32)其阳极侧表面和阴极侧表面通过导电侧电 连接件(4132c)彼此连接，并且位于第四单元(C4')同一侧上的阳极散热器(81)和阴极散热 器(72)其阳极侧表面和阴极侧表面通过导电侧电连接件(8172c)彼此连接， 使得系统形成交错斩波型功率变换器。 10 .根据前述权利要求中任一项所述的系统，其中，每个散热器(11，12,21，22)包括翅 片和指状件中的至少一个。 11 .根据前述权利要求中除了权利要求1、5和9之外的任一项所述的系统，其中，电容性 侧电连接件(1221cp，2211cp，6251cp，4231cp)和电容性中心电连接件中的至少一个包括至 少一个电容器(10cp)。 12 .根据前述权利要求中任一项所述的系统，还包括冷却装置(2000)，所述冷却装置 (2000)配置为冷却每个阳极和阴极散热器(11，12，21，22)。 13 .根据前述权利要求中任一项所述的系统，还包括至少一个基本电感模块(9)，所述 基本电感模块⑼包括： 「嵌入在磁性矩阵(903)中的导电线圈(900)，磁性矩阵(903)具有第一面和与第一面相 反的第二面， 「在第一面上并且连接到所述导电线圈(900)的第一导电散热器(91)，以及 「在第二面上并且连接到所述导电线圈(900)的第二导电散热器(92)。 | [EN EP3878011A1]: "Electronic power system" TECHNICAL FIELD OF THE INVENTION The invention relates to electronic power systems. It finds at least one particularly advantageous application in the field of static power converters. STATE OF THE ART An electronic power converter generally comprises elementary power modules connected to each other. Each elementary power module comprises power components, such as transistors (for example bipolar transistors with an IGBT insulated gate, from English “Insulated Gâte Bipolar Transistor”) and diodes, assembled in the form of a chip in order to ensure a elementary function, for example an electronic switch function. The heat produced by the power components of the elementary power modules must be dissipated. The elementary power modules are generally transferred to a cooling or heat dissipation system. An air cooling system comprising for example metal fins welded to an aluminum base mounted on the rear face of the chip holder is a standard solution for power electronics. The effectiveness of such a system is however not optimal. Its size and mass are relatively large. Another solution consists in using a liquid cooling system in order to improve the heat exchanges between the power module and the surrounding fluid. Such a system, however, requires hydraulic circuits generating a higher cost than the air cooling system, and more complex maintenance. Another solution consists in cooling the two faces of the component within the power module. The power component is then interposed between a first heat sink facing its first face, and a second heat sink facing its second face, opposite the first face, as illustrated in FIG. 1. The first heat sink can also be connected to a first electrode, for example the anode, of the power component, so as to provide a first electrical connection, for example anodic, to the power component. The second heat sink can also be connected to a second electrode, for example the cathode, of the power component, so as to provide a second electrical connection, for example cathodic, to the power component. This solution advantageously makes it possible to functionalize the heat sinks of the power module. It is therefore possible to assemble several power modules in a so-called “press-pack” configuration, in the form of a stack of said power modules, in order to produce electronic cells comprising at least two power modules interconnected by the through their heat sinks. However, such an assembly requires exerting a very high external pressure in order to limit the thermal resistance of contact between the heat sinks and the ceramic case of the interconnected power modules. This type of press-pack assembly therefore includes a press or a pressure device around the power modules. This pressure device is generally bulky. Consequently, a “press-pack” assembly makes it possible to put two power modules in series, but is not suitable for paralleling the power modules. This assembly also induces large parasitic inductances which are not very compatible with the use of electronic cells comprising fast switching power components. An object of the present invention is to at least partially overcome some of the drawbacks mentioned above. According to a particular aspect, an object of the present invention is to provide an electronic system comprising power modules in parallel and / or in series having a simple and efficient cooling system. Another object of the present invention is to provide an electronic system comprising an assembly of power modules limiting parasitic inductances. The other objects, characteristics and advantages of the present invention will appear on examining the following description and the accompanying drawings. It is understood that other advantages can be incorporated. SUMMARY OF THE INVENTION To achieve this objective, a first aspect of the invention relates to an electronic system comprising at least one electronic cell, said at least one electronic cell comprising: - A first electronic module of elementary power, called first elementary module, - A second electronic module of elementary power, called second elementary module, Said first and second elementary modules being adjacent and connected to each other. Each of these first and second elementary modules includes: - at least one power component, preferably integrated on or in a printed circuit, - A first electrically conductive heat sink, called an anode sink, connected to a first electrode called an anode of the power component, and - a second electrically conductive heat sink, said an cathode sink, connected to a second electrode called a cathode of the power component. Advantageously, the cathode heatsinks each have a first connection surface called the cathode central surface and at least a second connection surface called the cathode lateral surface. In addition, the anode dissipators each have a first connection surface called the anode central surface and at least a second connection surface called the anode side surface. Advantageously, the connection of the first and second adjacent elementary modules comprises at least one lateral conductive electrical connection between: at least one of the anode and cathode side surfaces of the first elementary module, and at least one of the anode and cathode side surfaces of the second elementary module. According to the invention and in a particularly advantageous manner, the power modules can be connected laterally by the lateral connection surfaces of their heat sinks. This first configuration makes it possible to simply connect power modules in parallel or anti-parallel. This first configuration also makes it possible to connect power modules in series, for example by turning 180 ° one of the power modules to be connected. The power modules can also be connected vertically via the central connection surfaces of their heat sinks. This second configuration allows simple connection of power modules in series. This second configuration also makes it possible to connect power modules in parallel or in anti-parallel mode, for example by turning 180 ° one of the power modules to be connected. Such an electronic system comprising electronic modules connected according to the first and / or second above-mentioned configurations advantageously makes it possible to produce various structures in the field of power electronics, such as switching cells, choppers, or inverters, possibly with multilevel or interleaved configurations. Each elementary power module being equipped with two heat sinks, the overall cooling efficiency of the electronic system is improved. BRIEF DESCRIPTION OF THE FIGURES The aims, objects, as well as the characteristics and advantages of the invention will emerge more clearly from the detailed description of embodiments of the latter which are illustrated by the following accompanying drawings in which: - FIGURE 1 shows a physical embodiment diagram of an electronic module of elementary power according to the prior art; - FIGURE 2A shows an electronic diagram of an electronic cell comprising two power components in series; - FIGURE 2B shows a physical embodiment diagram of the electronic cell illustrated in Figure 2A according to the prior art; - FIGURE 3A shows an electronic diagram of an electronic cell comprising two power components in parallel; - FIGURE 3B shows a physical embodiment of the electronic cell illustrated in Figure 3A according to an embodiment of the present invention; - FIGURE 3C shows a physical embodiment of the electronic cell illustrated in Figure 3A according to another embodiment of the present invention; - FIGURE 3D shows a physical embodiment of the electronic cell illustrated in Figure 3A according to another embodiment of the present invention; - FIGURE 4A shows an electronic diagram of a switching cell; - FIGURE 4B shows a physical embodiment of the switching cell illustrated in Figure 4A according to an embodiment of the present invention; - FIGURE 4C shows a physical embodiment of the switching cell illustrated in Figure 4A according to another embodiment of the present invention; - FIGURE 4D shows a physical embodiment of the switching cell illustrated in Figure 4A according to another embodiment of the present invention; - FIGURE 5A shows an electronic diagram of part of an electronic multilevel conversion system corresponding to a series of switching cells; - FIGURE 5B shows a physical embodiment diagram of the part of the electronic multilevel conversion system illustrated in FIG. 5A according to an embodiment of the present invention; FIGURE 6A shows an electronic diagram of an electronic power conversion system of the interlaced chopper type, corresponding to a switching cells paralleling; - FIGURE 6B shows a physical embodiment diagram of the electronic power conversion system of the interlaced chopper type illustrated in FIG. 6A according to an embodiment of the present invention; - FIGURE 7A shows a physical embodiment diagram of an electronic elementary power module according to an embodiment of the present invention; - FIGURE 7B shows a physical embodiment of an electronic module of elementary power according to another embodiment of the present invention; - FIGURE 8A shows an electronic diagram of a switching cell coupled to a load via an inductor; - FIGURE 8B shows a physical embodiment of the inductor illustrated in Figure 8A according to an embodiment of the present invention; - FIGURE 9A shows a physical embodiment diagram of a heat sink according to an embodiment of the present invention; - FIGURE 9B shows a physical embodiment of a heat sink according to another embodiment of the present invention; - FIGURE 10A shows a physical embodiment diagram of a capacitive lateral electrical connection according to an embodiment of the present invention; - FIGURE 10B shows a physical embodiment of a lateral capacitive electrical connection according to another embodiment of the present invention; - FIGURE 11A shows a physical diagram of an electronic system according to an embodiment of the present invention; - FIGURE 11 B shows a physical embodiment diagram in cross section along the plane AA indicated in FIGURE 1 1A of the electronic system according to the embodiment of the present invention illustrated in FIGURE 1 1A; - FIGURE 12 illustrates a thermal simulation result carried out on an electronic half-module of elementary power according to an embodiment of the present invention. The drawings are given by way of examples and are not limitative of the invention. They constitute schematic representations of principle intended to facilitate the understanding of the invention and are not necessarily on the scale of practical applications. In particular, the thicknesses and dimensions of the different layers and portions of the printed circuits, heat sinks and illustrated electrical connections are not representative of reality. In this patent application, the following notations are used: For an electronic module of elementary power X, we will note: X0 the printed circuit of this module, XI, X2 the first and second heat sinks of this module, X10, X20 the central connection surfaces of the first and second heat sinks, XI I, X12 of the lateral connection surfaces of the first heat sink, X21, X22 of the lateral connection surfaces of the second heat sink, X00, X00AT, X00B the electronic components of this module. In the present patent application, a conductive electrical connection between a heat sink Xi (i = 1, 2) of a first module X and a heat sink Yj (j = 1, 2) of a second module Y, is noted : XiYjc In the present patent application, a capacitive electrical connection between a heat sink Xi (i = 1, 2) of a first module X and a heat sink Yj (j = 1, 2) of a second module Y, is noted : XiYjcp In the present patent application, an insulating electrical connection between a heat sink Xi (i = 1, 2) of a first module X and a heat sink Yj (j = 1, 2) of a second module Y, is noted: XiYji Reading on the connection direction sheet is done from left to right, from bottom to top and from front to back. An electronic cell is denoted Cnot. All the references of each electronic elementary power module and / or of each electronic cell are not necessarily given in the drawings for the sake of clarity. The references of the elements not explicitly referenced on the drawings can nevertheless be easily deduced from the notations explained above and from the detailed description which follows. DETAILED DESCRIPTION OF THE INVENTION Before starting a detailed review of embodiments of the invention, it is recalled that the invention according to its first aspect notably includes the following optional characteristics which can be used in combination or alternatively: According to one embodiment, the electrical connection of modules between the first and second adjacent elementary modules further comprises one of a capacitive lateral electrical connection and an insulating lateral electrical connection between: at least one other among the anode and cathode side surfaces of the first elementary module, and o at least one other among the anode and cathode side surfaces of the second elementary module. According to one embodiment, at least one anode side surface of the first elementary module is connected to at least one cathode side surface of the second elementary module by a conductive lateral electrical connection and at least one cathode side surface of the first elementary module is connected to at least one anode side surface of the second elementary module by an electrical connection from a lateral capacitive electrical connection and an insulating lateral electrical connection. According to one embodiment, the at least one power component of the first elementary module is one of a first power transistor and a first power diode, for example of the IGBT type, and the at least one power component of the second elementary module is one of a second power transistor and a second power diode, so that the electronic cell forms a switching cell. According to one embodiment, the system comprises a plurality of adjacent electronic cells and connected to each other, an electronic cell of the plurality of electronic cells being connected to at least one adjacent electronic cell by an electrical connection of cells, said electrical connection of cells comprising at least one of a conductive central electrical connection, a capacitive central electrical connection and an insulating central electrical connection between: o at least one of the central anodic and cathodic surfaces of said cell, and o at least one of the anodic and cathodic central surfaces of the at least one cell adjacent to said cell. According to one embodiment, the electrical connection of cells comprises a central conductive electrical connection between: o at least one of the central anodic and cathodic surfaces of said cell, and at least one of the anodic and cathodic central surfaces of the at least one cell adjacent to said cell, and one of a capacitive central electrical connection and an insulating central electrical connection between: o at least one other among the anodic and cathodic central surfaces of the cell, and o at least one other among the anodic and cathodic central surfaces of the at least one cell adjacent to said cell. According to one embodiment, at least one cathode central surface of the cell is connected to at least one anodic central surface of the adjacent cell by a conductive central electrical connection and at least one anodic central surface of the cell is connected to at least one cathodic central surface of the adjacent cell by an insulating central electrical connection. According to one embodiment, each electronic cell of the plurality of electronic cells is a switching cell, so that the system forms a subset of a multilevel power converter. According to one embodiment, the electrical connection of cells further comprises at least one lateral conductive electrical connection between: o at least one of the anode and cathode side surfaces of the cell, and o at least one of the anode and cathode side surfaces of at least one other cell adjacent to said cell. According to one embodiment, the system comprises a first electronic cell, a second electronic cell, a third electronic cell, a fourth electronic cell, said first, second, third, fourth electronic cells being switching cells, and: o The anodic and cathodic central surfaces of the anodic and cathodic heat sinks connected together by a capacitive lateral electrical connection of the first cell are respectively connected to the anodic and cathodic central surfaces of the anodic and cathodic heat sinks connected to each other by a capacitive lateral electrical connection of the second cell, by central conductive electrical connections, o The anodic and cathodic central surfaces of the anodic and cathodic heat sinks linked together by a capacitive lateral electrical connection of the third cell are respectively connected to the anodic and cathodic central surfaces of the anodic and cathodic heat sinks connected to each other by a capacitive lateral electrical connection of the fourth cell, by central conductive electrical connections, o The anode and cathode side surfaces of the anode and cathode heat sinks linked together by a conductive lateral electrical connection, located on the same side of the first cell are respectively connected to the anode and cathode side surfaces of the anode and cathode heat sinks connected together by a conductive lateral electrical connection, located on the same side of the third cell, by insulating lateral electrical connections, o The anode and cathode side surfaces of the anode and cathode heat sinks linked together by a capacitive lateral electrical connection, located on the same side of the first cell are respectively connected to the anode and cathode side surfaces of the anode and cathode heat sinks connected together by a capacitive lateral electrical connection, located on the same side of the third cell, by conductive lateral electrical connections, o The anode and cathode side surfaces of the anode and cathode heat sinks connected to each other by a capacitive lateral electrical connection, situated on the same side of the second cell are respectively connected to the anode and cathode side surfaces of the anode and cathode heat sinks connected to each other by a capacitive lateral electrical connection, located on the same side of the fourth cell, by conductive lateral electrical connections, o The anode and cathode side surfaces of the anode and cathode heat sinks linked together by a conductive lateral electrical connection, located on the same side of the second cell are respectively connected to the anode and cathode side surfaces of the anode and cathode heat sinks connected together by a conductive lateral electrical connection, located on the same side of the fourth cell, by insulating lateral electrical connections, so that the system forms an interlaced chopper-type power converter. According to one embodiment, each dissipator comprises at least one of a fin, a pin and a finger. According to one embodiment, at least one of the lateral capacitive electrical connection and the central capacitive electrical connection comprises at least one capacitor. According to one embodiment, the system further comprises a cooling device, such as a ventilation or pumping device, configured to cool each anode and cathode heat sink. According to one embodiment, the system further comprises at least one elementary inductance module comprising: a conductive coil embedded in a magnetic matrix having a first face and a second face opposite the first face, a first electrically conductive heat sink on the first face and connected to said conductive coil, and o a second electrically conductive heat sink on the second face and connected to said conductive coil. According to one embodiment, the first heat sinks of the first and second adjacent elementary modules form one and the same first cell heat sink. The conductive lateral electrical connection between the first heat sinks of the first and second adjacent elementary modules therefore corresponds to an intermediate part of said first cell heat sink. This intermediate part can be located between a first part of said first cell heat sink, said first part being associated with the first elementary module, and a second part of said first cell heat sink, said second part being associated with the second elementary module. According to this embodiment, the conductive lateral electrical connection between the first heat sinks of the first and second adjacent elementary modules has material continuity with said first heat sinks, so that it is inseparable from said first heat sinks. According to one embodiment, the second heat sinks of the first and second adjacent elementary modules form one and the same second cell heat sink. The conductive lateral electrical connection between the second heat sinks of the first and second adjacent elementary modules therefore corresponds to an intermediate part of said second cell heat sink. This intermediate part can be located between a first part of said second cell heat sink, said first part being associated with the first elementary module, and a second part of said second cell heat sink, said second part being associated with the second elementary module. According to this embodiment, the conductive lateral electrical connection between the second heat sinks of the first and second adjacent elementary modules has material continuity with said second heat sinks, so that it is inseparable from said second heat sinks. According to one embodiment, the first heat sink of the first elementary module and the second heat sink of the second elementary module form one and the same main cell heat sink. The conductive lateral electrical connection between the first heat sink of the first elementary module and the second heat sink of the second elementary module therefore corresponds to an intermediate part of said main cell heat sink. This intermediate part can be located between a first part of said main cell heat sink, said first part being associated with the first elementary module, and a second part of said main cell heat sink, said second part being associated with the second elementary module. According to this embodiment, the conductive lateral electrical connection between the first heat sink of the first elementary module and the second heat sink of the second elementary module has a continuity of material with said first and second heat sinks, so that it is inseparable said first and second heat sinks. According to one embodiment, the first printed circuit of the first elementary module and the second printed circuit of the second elementary module form one and the same main printed circuit. In this embodiment, the main printed circuit includes first and second power components. In the present invention, the first and second heat sinks are said to be anodic or cathodic for the sake of clarity. This designation is not limitative of the invention. The anode and cathode heatsinks form electrodes. These electrodes can be an anode, a cathode, an emitter, a collector, a source, a drain, etc. These electrodes can be inverted according to the passing direction of the electronic component for example. In general in the present invention, the anode sink preferably has a higher electrical potential than the cathode sink when the corresponding electronic switch is open (blocked state). In the present invention, the term “IGBT type transistor” is understood to mean an insulated gate bipolar transistor (IGBT, from the English term “Insulated Gâte Bipolar Transistor”). Other transistor architectures can be used, for example, but not limited to: a “HEMT type transistor”, which is a field effect transistor with high electron mobility, sometimes also designated by the term heterostructure field effect transistor, an insulated gate field effect transistor more commonly known as MOSFET (acronym for “Metal Oxide Semiconductor Field Effect Transistor”). Other components, such as thyristors, trigger-extinguishing thyristors (thyristor GTO or more simply GTO, from the English “Gate Turn-Off” Thyristor), can also be used. These transistors and components are well known and commonly used in the field of power electronics, in particular for static power converters. The term “electronic system” in the field of power electronics is understood to mean systems preferably operating with electric currents having intensities between 10 A and 1000 A, and / or electrical voltages between 10 V and 10000 V, preferably between 10 V and 5000 V, and preferably between 10 V and 1000 V. The function of power converters is to convert an electrical signal into another electrical signal. There are, for example, converters intended to convert an alternating current into another alternating current (AC / AC converters called dimmers), converters intended to convert a direct current into another direct current (DC / DC converters called choppers), converters intended to convert an alternating current into a direct current (AC / DC converters called rectifiers), and converters intended to convert a direct current into an alternating current (DC / AC converters called inverters). The chopper is an electronic system in the field of power electronics using one or more controlled electronic switches. It allows in particular to modify the value of the average voltage of a DC voltage source with a high efficiency. It is therefore connected on the one hand to a DC voltage source and on the other hand to one or more resistive or inductive loads. These connections are made at the level of a half-bridge or bridge arm. A chopper can consist of one or more bridge arms. The bridge arm can consist of one or more switching cells. Each switching cell is formed of a pair of switches (controlled such as transistors and / or uncontrolled such as diodes) linked together. By playing with the switching of these switches, the chopper periodically changes the interconnection of the voltage source and the load. The switching cubicle must comply with the basic rules for interconnection of the following sources: A voltage source must not be short-circuited, but it can be opened. A power source must not be opened, but it can be short-circuited. The state of the switches in the switching cell must therefore be complementary so as to comply with the interconnection rules. To ensure this additional switching, the switches can each be controlled by a control circuit or "driver feeder" according to English terminology. The switching speed of these electronic switches can however be limited by the parasitic inductances and / or the parasitic capacitances of the electronic system. The switching frequency of the electronic system can therefore be limited. According to the invention, the electronic system consists of several elementary modules each comprising power components ensuring in particular one or more functions of electronic switch. The system is therefore advantageously modular and makes it possible to produce numerous structures of static converters, such as a switching cell, a multilevel converter, an interlaced chopper. The principle of modularity of the electronic system according to the invention is illustrated in Figures 2B and 3B. Each elementary module 1, 2 comprises at least one power component 100, 200 preferably integrated on a printed circuit 10, 20, a first heat sink 1 1, 21 and a second heat sink 12, 22. The following description of an elementary module 1 as illustrated in FIG. 1 is valid for the other elementary modules of the electronic system according to the invention. As illustrated in more detail in FIGS. 7A, 7B, the printed circuit 10, or PCB (from the acronym “Printed Circuit Board”), advantageously makes it possible to provide connectors 101, 102, 103 for various semiconductor electronic components. 100, 100A, 100B, such as transistors 100, 100A, diodes, control circuits 100B etc. It also makes it possible to arrange these components by optimizing the distribution of the electric field around these components. The integration on a same PCB 10 of different components 100A, 100B can allow good cooling of all of these components. The use of a PCB 10 is however not compulsory. Other supports can be envisaged. The printed circuit 10 preferably has a first face and a second face opposite the first face. The first heat sink 11 is assembled at the first face of the integrated circuit 10, and the second heat sink 12 is assembled at the second face of the integrated circuit 10. The assemblies of the first and second heatsinks 1 1, 12 on the first and second faces of the integrated circuit 10 can be produced by soldering, welding or by sintering. Such assemblies advantageously make it possible to limit the thermal resistances of contact between the semiconductor component (s) 100, 100A, 100B of the PCB 10 and the heat sink (s) 11, 12. Such assemblies do not require clamping pressure such that required for press-pack assembly. They also make it possible to limit the number of thermal interfaces between the semiconductor component (s) of the PCB 10 and the heat sink (s) 11, 12. The efficiency of the heat dissipation is therefore improved. The compactness of module 1 can thus be optimized. The first and second heatsinks 1 1, 12 are necessarily electrically conductive. The first heat sink 1 1 electrical conductor, said anode sink, is preferably connected to a first electrode, called anode, of the power component 100. The second electrically conductive heat sink 12, called the cathode heat sink, is preferably connected to a second electrode, called the cathode, of the power component 100. The first and second heatsinks 1 1, 12 can be made of aluminum in order to reduce the total weight of the elementary module 1. They may include flat or wavy fins, as shown in Figure 9A, or pins or fingers as shown in Figure 9B, to improve heat transfer and optimize heat dissipation of or 100 power components. In the case of the fingers illustrated in FIG. 9B, the cooling fluid can advantageously circulate in several directions. The installation of a fluid circulation device is therefore facilitated. The coolant can be air or an insulating liquid. According to the invention, the heatsinks of an elementary module make it possible to ensure at least one electrical connection with the heatsinks of an adjacent elementary module of the electronic system. Each dissipator preferably has a central connection surface and, for an elementary module of square or rectangular cross section in the plane of the integrated circuit, four lateral connection surfaces. The electrical connection at these connection surfaces can be conductive, capacitive or insulating. By insulating electrical connection is meant an electrically insulating or electrically insulated connection. The conductive, capacitive or insulating electrical connection can be made respectively via a conductive, capacitive or insulating element. It can be done alternately without an intermediate element, directly at the interface between the connection surfaces. A conductive element XiYjvs for example solid or in the form of foam can improve the electrical contact between the dissipators if necessary. A XiYj capacitive elementCp as illustrated in FIGS. 10A, 10B is preferably used for the capacitive electrical connection. It can advantageously provide a decoupling capacitor function. The surface of such an element is pr
[EN US2021067057A1]: VOLTAGE LEVEL MULTIPLIER MODULE FOR MULTILEVEL POWER CONVERTERS [FR EP3785363A1]: MODULE MULTIPLICATEUR DE NIVEAU DE TENSION POUR CONVERTISSEURS DE PUISSANCE MULTINIVEAUX [DE EP3785363A1]: SPANNUNGSNIVEAU-MULTIPLIKATORMODUL FÜR MEHRPEGELWANDLER | [EN US2021067057A1]: Generalized circuit topology of voltage level multiplier modules (VLMMs) for use with multilevel inverters (MLIs) and power converter circuits comprising at least one VLMM and a MLI are described herein. The VLMM is configured to receive a first output voltage from the MLI having a first number of voltage levels and to generate a second output voltage having a second number of voltage levels. If the first number of voltage levels is M, and the VLMM is N-fold voltage level multiplier, then second number of voltage levels is M×N+1. Switching pattern generators for use with the VLMM and modulation methods for controlling switching elements of the VLMM are also described herein. [FR EP3785363A1]: L'invention concerne une topologie de circuit généralisée de modules multiplicateurs de niveau de tension (VLMMs) destinés à être utilisés avec des onduleurs multiniveaux (MLIs) et des circuits convertisseurs de puissance comprenant au moins un VLMM et un MLI. Le VLMM est conçu pour recevoir une première tension de sortie du MLI ayant un premier nombre de niveaux de tension et pour générer une seconde tension de sortie ayant un second nombre de niveaux de tension. Si le premier nombre de niveaux de tension est M, et le VLMM est un multiplicateur de niveau de tension à N fois, alors le second nombre de niveaux de tension est MxN+1. L'invention concerne également des générateurs de motifs de commutation destinés à être utilisés avec les VLMM et des procédés de modulation pour commander des éléments de commutation du VLMM. | WO2019204935A1 | 2019-10-31 | CA2019050531W | 2019-04-25 | US201862662389P, 2018-04-25 | WO2019204935A1: 2019-10-31 EP3785363A1: 2021-03-03 US2021067057A1: 2021-03-04 | ECOLE TECHNOLOGIE SUPERIEURE | ABARZADEH MOSTAFA AL-HADDAD KAMAL | H02M7/44: I H02M7/501: I H02M7/5387: I H02M1/084: I | H02M7/483: I H02M7/487: I H02M7/49: I H02M7/5387: I H02M7/5395: I H02M1/0025: A H02M1/0095: I H02M7/4833: I H02M7/4835: I H02M7/4837: I H02M1/084: I H02M7/53875: I |  | US10924031B2 US10924031 10924031 US2019363644A1 US2019363644 US20190363644A1 WO2021119850A1 WO2021119850 2021/119850 WO2021/119850A1 EP3820041A1 EP3820041 3820041 WO2021159219A1 WO2021159219 2021/159219 WO2021/159219A1 US11114948B1 US11114948 11114948 | [EN US2021067057A1]: 1. A power converter circuit, comprising: a multilevel inverter providing at an output thereof a first output voltage having M voltage levels; andat least one N-fold voltage level multiplier module electrically connected to the output of the multilevel inverter and comprising a plurality of circuit elements configured to provide at least five voltage levels, the at least one voltage level multiplier module configured to receive the first output voltage from the multilevel inverter and to generate a second output voltage having M×N+1 voltage levels, where N is at least four. 2-13. (canceled) 14. The power converter circuit of claim 1, wherein the multilevel inverter is configured to provide three output voltages, each of the three output voltages being phase shifted by 2π/3 and having the M voltage levels, three of the at least one voltage level multiplier module being connected to receive a respective one of the three output voltages and being configured to each generate the second output voltage at a corresponding phase. 15. The power converter circuit of claim 1, further comprising an output filter connected to an output of the voltage level multiplier module, the output filter comprising an inductor and a capacitor, wherein the inductor has an inductance value of L = V DC 8 × ( n - 1 ) × Δ   I L × f 1  st   SW   Harmonic and the capacitor has a capacitance value of C= 4 ( 2  π × f 1  st   SW   Harmonic ) 2 × L , where n is the number of output voltage levels, ΔIL is the desired output current ripple, f1st SW Harmonic is the first switching harmonic cluster frequency and VDC is the DC-link voltage. 16. (canceled) 17. (canceled) 18. A voltage level multiplier module, comprising: an input for connecting to a multilevel inverter and for receiving therefrom a first output voltage having M voltage levels;an output; anda plurality of circuit elements connected between the input and the output, the plurality of circuit elements configured to provide at least five voltage levels and configured for providing a second output voltage having M×N+1 voltage levels, where N is at least four. 19. The voltage level multiplier module of claim 18, wherein the voltage level multiplier module is connectable in series and is adapted to generate a converter output voltage of M×Nm+Σk=0m−1Nk voltage levels, where k is an index of each of the series-connected voltage level multiplier modules ranging from 1 to m and m is the number of series-connected voltage level multiplier modules. 20. The voltage level multiplier module of claim 19, wherein the multilevel inverter comprises a first power source operating at a DC voltage level E and wherein the plurality of circuit elements comprise an additional power source operating at a voltage level of E/(N(k−1)×(M−1)k), for each kth series-connected voltage level multiplier module. 21. The voltage level multiplier module of claim 19, wherein the plurality of circuit elements comprise two low frequency switches operating at the E/(N(k−1)×(M−1)k) voltage level, for each kth series-connected voltage level multiplier module. 22. The voltage level multiplier module of claim 21, wherein the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors each having a capacitor voltage of ((n−b)×E)/(n×N(k−1)×(M−1)k) where b is an index of each of the n−1 capacitors, b ranging from 1 to n−1, the high frequency switches operating at a voltage of E/(n×N(k−1)×(M−1)k), for each kth series-connected voltage level multiplier module. 23. The voltage level multiplier module of claim 22, wherein the two low frequency switches and the 2×n high frequency switches are controlled to provide sensor-less voltage balancing to the n−1 capacitors. 24. The voltage level multiplier module of claim 18, wherein the multilevel inverter is selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter, a voltage level multiplier module, and a packed U-cell converter. 25. The voltage level multiplier module of claim 18 wherein the voltage level multiplier module comprises a plurality of circuit elements configured as a converter selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter, a voltage level multiplier module and a packed U-cell converter. 26. A switching pattern generator connected to the voltage level multiplier module of claim 18, the plurality of circuit elements comprising a plurality of switching elements, the switching pattern generator configured to provide a plurality of switching signals each for controlling a given one of the plurality of switching elements based on phase disposition pulse width modulation. 27. The switching pattern generator of claim 26, configured to generate the plurality of switching signals based on comparing a reference voltage signal to a group of triangular carrier signals. 28. The switching pattern generator of claim 27, wherein the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors and wherein the group of triangular carrier signals are n phase-shifted triangular carrier signals that are shifted by 2×π/n. 29. The switching pattern generator of claim 28, wherein the plurality of switching signals provide sensor-less voltage balancing to the n−1 capacitors. 30. A method for controlling a plurality of switching elements of a voltage level multiplier module configured to provide at least five voltage levels, the method comprising: generating a first reference signal having staircase voltage levels based on level detection of a sinusoidal input reference signal;generating a second reference signal by subtracting the first reference signal from the sinusoidal input reference signal;comparing the second reference signal to a plurality of triangular carrier signals to generate comparison results;processing the comparison results to generate a plurality of switching signals; andproviding the plurality of switching signals to the voltage level multiplier module, each of the plurality of switching signals for controlling a given one of the plurality of switching elements. 31. The method of claim 30 wherein the plurality of triangular carrier signals are phase-shifted triangular carrier signals. 32. (canceled) 33. The method of claim 31 wherein the plurality of triangular carrier signals are n triangular carrier signals that are shifted by 2π/n, where the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors. 34. The method of claim 30 further comprising comparing the second reference signal to a zero value by applying a zero-crossing comparator to generate comparison results for two low-frequency switching elements of the plurality of circuit elements. 35. (canceled) 36. The method of claim 30 further comprising sensor-less balancing a voltage of n−1 capacitors according to the switching signals, where the plurality of circuit elements comprise n−1 capacitors. | [EN US2021067057A1]: CROSS-REFERENCE TO RELATED APPLICATIONS The present application claims priority to U.S. Provisional Patent Application bearing Ser. No. 62/662,389 filed on Apr. 25, 2018, the contents of which are hereby incorporated by reference. TECHNICAL FIELD The present disclosure relates generally to power converter circuits, and, more particularly, to voltage level multiplier modules for use with multilevel inverters. BACKGROUND OF THE ART Multilevel inverters (MLIs) are used as power converters for energy conversion systems in many industrial applications. Applications for MLIs include renewable energy conversion systems, grid connected inverters, transportation, electrical vehicles, aerospace and other industrial plant applications, to name a few. A multilevel inverter (MLI) produces a staircase type of output voltage which provides improved harmonic content, reduced dV/dt, lower switching frequency and losses, higher efficiency, decreased electromagnetic interference (EMI) and fault-tolerant capabilities. These advantages enable MLIs to be used in high-power applications. MLIs are typically classified under three major topologies: neutral-point-clamped (NPC) converters, cascaded H-bridge (CHB) converters and flying capacitor (FC) converters. FC MLIs have a sub-topology referred to as stacked multi-cell (SM) converters. It is desirable to increase the number of voltage levels in MLs, for example, to fulfill relevant standards. However, to achieve a higher number of voltage levels in MLIs requires an excessive increase in the number of isolated direct current (DC) power supplies in CHB converters, of DC-link capacitors and clamping diodes in NPC converters, and of flying capacitors in FC and SM converters. In addition, increasing the output voltage levels in the aforementioned topologies, increases not only the number of components but also the complexity of the DC-link capacitors voltage control in NPC converters and of flying capacitors voltage balancing in FC converters. In order to overcome the aforementioned drawbacks, new configurations of multilevel converters such as hybrid multilevel converters have been proposed. For example, a hybrid cascaded multilevel inverter (HCMLI) which consists of improved 4-level submodules and a full-bridge converter has been proposed. Optimized topologies for symmetrical cascaded multilevel (SCM) and asymmetrical cascaded multilevel (ASCM) converters have also been proposed. A three-stage 18-level hybrid inverter circuit which comprises three hybrid high, medium, and low voltage inverter stages as well as its modulation method have been proposed. However, by increasing the number of output voltage levels, these hybrid configurations require numerous isolated DC-power supplies with various voltages. Hence, the HCMLI, SCM, and ASCM configurations lead to an increase cost and size, and also a decrease in modularity of the mentioned converters. A hybrid multicell converter (HMC) based on the combination of FC and CHB converters has also been proposed. The nominal voltage of the HMC converter is set to be equal to the blocking voltage of the semiconductors of augmented CHB. Hence, this configuration is not applicable for high voltage MLIs. Moreover, even though the suggested hybrid configuration consists of fewer isolated DC power supplies, they require numerous bulky and costly FCs in order to achieve a large number of voltage levels. This leads to increased cost, size, and complexity of control and modulation while decreasing modularity. As such, there is a need for improved MLs and associated power electronic circuits and/or modules. SUMMARY In one aspect, there is provided a power converter circuit. The power convert circuit comprises a multilevel inverter providing at an output thereof a first output voltage having M voltage levels, and at least one N-fold voltage level multiplier module electrically connected to the output of the multilevel inverter and comprising a plurality of circuit elements configured to provide at least five voltage levels, the at least one voltage level multiplier module configured to receive the first output voltage from the multilevel inverter and to generate a second output voltage having M×N+1 voltage levels, where N is at least four. In some embodiments, the at least one N-fold voltage level multiplier module comprise m series-connected N-fold voltage level multiplier modules generating a converter output voltage of M×Nm+Σk=0m−1Nk voltage levels, where k is an index of each of the series-connected N-fold voltage level multiplier modules, k ranging from 1 to m. In some embodiments, the multilevel inverter comprises a first power source operating at a DC voltage level E and where the plurality of circuit elements comprise an additional power source operating at a voltage level of E/(N(k−1)×(M−1)k), for each kth series-connected N-fold voltage level multiplier module. In some embodiments, the plurality of circuit elements comprise two low frequency switches operating at the E/(N(k−1)×(M−1)k) voltage level, for each kth series-connected N-fold voltage level multiplier module. In some embodiments, the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors each having a capacitor voltage of ((n−b)×E)/(n×N(k−1)×(M−1)k) where b is an index of each of the n−1 capacitors, b ranging from 1 to n−1, the high frequency switches operating at a voltage of E/(n×N(k−1)×(M−1)k), for each kth series-connected N-fold voltage level multiplier module. In some embodiments, the power converter circuit further comprises a switching pattern generator connected to the at least one voltage level multiplier module, the plurality of circuit elements comprise a plurality of switching elements, the switching pattern generator configured to provide a plurality of switching signals each for controlling a given one of the plurality of switching elements based on comparing a voltage level multiplier module (VLMM) reference signal to n phase-shifted triangular carrier signals. In some embodiments, the plurality of switching signals provide sensor-less voltage balancing to n−1 capacitors. In some embodiments, the power converter circuit further comprises a switching pattern generator connected to the at least one voltage level multiplier module, the plurality of circuit elements comprise a plurality of switching elements, the switching pattern generator configured to provide a plurality of switching signals each for controlling a given one of the plurality of switching elements based on phase disposition pulse width modulation. In some embodiments, the switching pattern generator is configured to generate the plurality of switching signals based on comparing a voltage level multiplier module (VLMM) reference signal to four level-shifted triangular carrier signals, when N=4. In some embodiments, two of the four level-shifted triangular carrier signals are phase-shifted. In some embodiments, the power converter circuit further comprises a reference signal generator for generating a multilevel inverter (MLI) reference signal, the MLI reference signal being generated according to a modulation of an input reference signal. In some embodiments, the reference signal generator is further adapted to generate a voltage level multiplier module (VLMM) reference signal, the VLMM reference signal being generated according to the input reference signal to which the MLI reference signal is subtracted. In some embodiments, the power converter circuit further comprises a MLI switching pattern generator connected to the multilevel inverter, the switching pattern generator configured to provide a plurality of switching signals for controlling switches of the multilevel inverter according to a pulse width modulation of the MLI reference signal. In some embodiments, the multilevel inverter is configured to provide three output voltages, each of the three output voltages being phase shifted by 2π/3 and having the M voltage levels, three of the at least one voltage level multiplier module being connected to receive a respective one of the three output voltages and being configured to each generate the second output voltage at a corresponding phase. In some embodiments, the power converter circuit further comprises an output filter connected to an output of the voltage level multiplier module, the output filter comprising an inductor and a capacitor, wherein the inductor has an inductance value of L = V D  C 8 × ( n - 1 ) × Δ   I L × f 1  s  t  S  WHarmon  i  c and the capacitor has a capacitance value of C = 4 ( 2  π × f 1  s  t  S  W  H  a  r  m  o  n  i  c ) 2 × L , where n is the number of output voltage levels, ΔIL is the desired output current ripple, f1st SW Harmonic is the first switching harmonic cluster frequency and VDC is the DC-link voltage. In some embodiments, the multilevel inverter is selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter and a packed U-cell converter. In some embodiments, the at least one voltage level multiplier module comprises a plurality of circuit elements configured as a converter selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter, a voltage level multiplier module and a packed U-cell converter. In accordance with one aspect, there is provided a voltage level multiplier module. The voltage level multiplier module comprises an input for connecting to a multilevel inverter and for receiving therefrom a first output voltage having M voltage levels, an output, and a plurality of circuit elements connected between the input and the output, the plurality of circuit elements configured to provide at least five voltage levels and configured for providing a second output voltage having M×N+1 voltage levels, where N is at least four. In some embodiments, the voltage level multiplier module is connectable in series and is adapted to generate a converter output voltage of M×Nm+Σk=0m−1Nk voltage levels, where k is an index of each of the series-connected voltage level multiplier modules ranging from 1 to m and m is the number of series-connected voltage level multiplier modules. In some embodiments, the multilevel inverter comprises a first power source operating at a DC voltage level E and wherein the plurality of circuit elements comprise an additional power source operating at a voltage level of E/(N(k−1)×(M−1)k), for each kth series-connected voltage level multiplier module. In some embodiments, the plurality of circuit elements comprise two low frequency switches operating at the E/(N(k−1)×(M−1)k) voltage level, for each kth series-connected voltage level multiplier module. In some embodiments, the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors each having a capacitor voltage of ((n−b)×E)/(n×N(k−1)×(M−1)k) where b is an index of each of the n−1 capacitors ranging from 1 to n−1, the high frequency switches operating at a voltage of E/(n×N(k−1)×(M−1)k), for each kth series-connected voltage level multiplier module. In some embodiments, the two low frequency switches and the 2×n high frequency switches are controlled to provide sensor-less voltage balancing to n−1 capacitors. In some embodiments, the multilevel inverter is selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter, a voltage level multiplier module, and a packed U-cell converter. In some embodiments, the voltage level multiplier module comprises a plurality of circuit elements configured as a converter selected from the group consisting of a neutral point clamped converter, a cascaded H-bridge converter, a flying capacitor multi-cell converter, a stacked multi-cell converter, an active neutral point clamped converter, a voltage level multiplier module and a packed U-cell converter. In some embodiments, a switching pattern generator is connected to the voltage level multiplier module, the plurality of circuit elements comprise a plurality of switching elements, the switching pattern generator configured to provide a plurality of switching signals each for controlling a given one of the plurality of switching elements based on phase disposition pulse width modulation. In some embodiments, the switching pattern generator is configured to generate the plurality of switching signals based on comparing a reference voltage signal to a group of triangular carrier signals. In some embodiments, the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors and wherein the group of triangular carrier signals are n phase-shifted triangular carrier signals that are shifted by 2×π/n. In some embodiments, the plurality of switching signals provide sensor-less voltage balancing to the n−1 capacitors. In accordance with one aspect, there is provided a method for controlling a plurality of switching elements of a voltage level multiplier module configured to provide at least five voltage levels. The method comprises generating a first reference signal having staircase voltage levels based on level detection of a sinusoidal input reference signal, generating a second reference signal by subtracting the first reference signal from the sinusoidal input reference signal, comparing the second reference signal to a plurality of triangular carrier signals to generate comparison results, processing the comparison results to generate a plurality of switching signals, and providing the plurality of switching signals to the voltage level multiplier module, each of the plurality of switching signals for controlling a given one of the plurality of switching elements. In some embodiments, the plurality of triangular carrier signals are phase-shifted triangular carrier signals. In some embodiments, the plurality of triangular carrier signals are level-shifted triangular carrier signals. In some embodiments, the plurality of triangular carrier signals are n triangular carrier signals that are shifted by 2π/n, where the plurality of circuit elements comprise 2×n high frequency switches and n−1 capacitors. In some embodiments, the method further comprises comparing the second reference signal to a zero value by applying a zero-crossing comparator to generate comparison results for two low-frequency switching elements of the plurality of circuit elements. In some embodiments, the second reference signal is a modified reference signal generated from the second reference signal. In some embodiments, the method further comprises sensor-less balancing a voltage of n−1 capacitors according to the switching signals, where the plurality of circuit elements comprise a number of n−1 capacitors. DESCRIPTION OF THE DRAWINGS Reference is now made to the accompanying figures in which: FIG. 1 is a schematic block diagram of an example power converter circuit comprising a voltage level multiplier module (VLMM) for use with a multilevel inverter (MLI) and being controlled by a VLMM switching pattern generator and a MLI switching pattern generator respectively, in accordance with an embodiment; FIG. 2 is a circuit diagram of an example voltage level multiplier module, in accordance with an embodiment; FIG. 3 is a circuit diagram of an example packed u-cell converter; FIG. 4A is a block diagram of a first switching pattern generator for use with the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 4B is a table presenting the switching states provided by the first switching pattern generator of FIG. 4A, in accordance with an embodiment; FIG. 5A is an example of a first reference signal for use by a switching pattern generator for a multilevel inverter; FIG. 5B is an example of a second reference signal for use by a switching pattern generator for a voltage level multiplier module; FIG. 5C is an example of an output voltage of the multilevel inverter with respect to a ground, in accordance with an embodiment; FIG. 5D is an example of a voltage between an input and output of the voltage level multiplier module, in accordance with an embodiment; FIG. 5E is an example of an output voltage of the converter of FIG. 1 with respect to a ground, in accordance with an embodiment; FIG. 6 is a block diagram of a second switching pattern generator for use with the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7A is a circuit diagram of an example power converter circuit comprising a neutral-point-clamped (NPC) converter and the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7B is a circuit diagram of an example power converter circuit comprising a cascaded H-bridge (CHB) converter and the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7C is a circuit diagram of an example power converter circuit comprising a stacked multi-cell (SM) converter and the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7D is a circuit diagram of an example power converter circuit comprising an active neutral-point-clamped (ANPC) converter and the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7E is a circuit diagram of an example power converter circuit comprising a packed U-cell (PUC) converter and a voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 7F is a circuit diagram of an example power converter circuit comprising an active neutral-point-clamped (ANPC) converter and another type of voltage level multiplier module, in accordance with an embodiment; FIG. 8 is an example of an example power converter circuit comprising two voltage level multiplier modules connected in series to a multilevel inverter; FIG. 9 is an example of a third switching pattern generator for use with the two voltage level multiplier modules of FIG. 8; FIG. 10 is a flowchart illustrating an example method for modulating the voltage level multiplier module of FIG. 2, in accordance with an embodiment; FIG. 11A is plot of output voltage of the voltage level multiplier module and the example multilevel inverter of FIG. 7E; FIG. 11B is a plot of output voltage of the power converter circuit of FIG. 7E; FIG. 11C is a plot of output voltage of the power converter circuit of FIG. 7E with a Fast Fourier Transform (FFT) analysis; FIG. 11D is a plot of output voltage and load current of the power converter circuit of FIG. 7E; FIG. 11E is a plot of output voltage of the multilevel inverter, voltage level multiplier module and the multilevel power converter of FIG. 7E with a plot of load current; FIG. 12A is an example of a main reference signal for use by a switching pattern generator for the multilevel inverter of FIG. 8; FIG. 12B is an example of a first reference signal for the first voltage level multiplier module of FIG. 8; FIG. 12C is an example of a second reference signal for the second voltage level multiplier module of FIG. 8; FIG. 13A is a plot of output voltage of the multilevel inverter of FIG. 8; FIG. 13B is a plot of output voltage of the first voltage level multiplier module of FIG. 8; FIG. 13C is a plot of output voltage of the second voltage level multiplier module of FIG. 8; FIG. 13D is plot of output voltage for the power converter circuit of FIG. 8; FIGS. 14A and 14B each illustrate an FFT analysis of the power converter circuit of FIG. 8; FIG. 15A is a circuit diagram of a six-fold voltage level multiplier module, according to one embodiment; FIG. 15B is a schematic block diagram of an example power converter circuit comprising the six-fold voltage level multiplier module of FIG. 15A for use with the multilevel inverter and being controlled by a VLMM switching pattern generator and a MLI switching pattern generator respectively, in accordance with an embodiment; FIG. 15C is a block diagram of a switching pattern generator for use with the six-fold voltage level multiplier module of FIG. 15A, in accordance with an embodiment; FIGS. 16A and 16B are graphs of a main MLI converter reference signal and a low-voltage six-fold VLMM reference signal, according to one embodiment; FIG. 17 is a circuit diagram of a six-fold VLMM connected to a five-level PUC converter, adapted to produce thirty-one voltage levels, according to one embodiment; FIG. 18 are graphs of the five-level PUC converter output voltage with respect to a ground, the voltage measured between the output and the input of the six-fold VLMM and the thirty-one voltage levels at the output of the six-fold VLMM connected to the five-level PUC of FIG. 17 with respect to a ground, according to one embodiment; FIG. 19 is a graph of a Fast Fourier Transform of the voltage generated at the output of the six-fold VLMM connected to the five-level PUC of FIG. 17 with respect to a ground, according to one embodiment; FIG. 20 is a circuit diagram of a prior art single-phase seven-level PUC (PUC7) converter as described in U.S. Pat. No. 9,331,599; FIG. 21 is a block diagram of the multilevel inverter connected to the voltage level multiplier module with their corresponding outputs, according to one embodiment; FIG. 22 presents various embodiments of the voltage level multiplier module each producing a respective voltage level multiplication, according to one embodiment; FIG. 23A presents a graph of a VLMM reference signal intersecting with various carrier signals of a VLMM switching pattern generator, according to one embodiment; FIG. 23B is a block diagram of a generalised sensor-less switching pattern generator for use with various voltage level multiplier modules, in accordance with an embodiment; FIG. 24 is a circuit diagram of a three phase converter having three voltage level multiplier modules each connected to a phase voltage output of a three phase H-Bridge inverter, according to one embodiment; FIG. 25 are graphs of the phase voltage and line voltage of the three phase converter of FIG. 24, according to one embodiment; FIG. 26 is a table presenting a component comparison between the three phase converter of FIG. 24 with various traditional topologies, according to one embodiment; FIG. 27 is a circuit diagram of a three phase converter having three voltage level multiplier modules each connected to a phase voltage output of a three phase NPC multilevel inverter, according to one embodiment; FIG. 28 are graphs of the phase voltage and line voltage of the three phase converter of FIG. 27, according to one embodiment; FIG. 29 is a table presenting a component comparison between the three phase converter of FIG. 27 with various traditional topologies, according to one embodiment; FIGS. 30 to 33 are circuit diagrams of three phase converters having three voltage level multiplier modules each connected to a phase voltage output of a three phase five-level multilevel inverters, according to various embodiments; and FIG. 34 is graph of a line voltage of the three phase converters of FIGS. 30 to 33, according to one embodiment. It will be noted that throughout the appended drawings, like features are identified by like reference numerals. DETAILED DESCRIPTION Voltage level multiplier modules (VLMMs) for use with multilevel inverters (MLIs) and power converter circuits comprising at least one voltage level multiplier module (VLMM) and a multilevel inverter (MLI) are described herein. Switching pattern generators for use with the VLMM are also described herein. A VLMM is described herein for use with any suitable MLI, such that the VLMM increases the number of voltage levels of the output voltage of the MLI. With reference to FIG. 1, an example power converter circuit 100 comprising a VLMM 110 for increasing the number of voltage levels of an output voltage of an MLI 120 is shown. In accordance with an embodiment, the power converter circuit 100 comprises the MLI 120. The MLI 120 has an output 122 for providing an alternating current (AC) output voltage having a number of voltage levels. The MLI 120 may be implemented according to any suitable configuration, including, but not limited to, a neutral point clamped (NPC) converter, a cascaded H-bridge (CHB) converter, a flying capacitor multi-cell (FMC) converter, a stacked multi-cell (SM) converter, an active neutral point clamped (ANPC) converter, and a packed U-cell (PUC) converter. In accordance with a specific and non-limiting example of implementation, the MLI 120 is a five-level MLI generating five output voltage levels. The number of output voltage levels may vary depending on practical implementation. The VLMM 110 has an input 112 and an output 114. To differentiate the output 122 of the MLI 120 from the output 114 of the VLMM 110, the output 122 of the MLI 120 may be referred to as an “MLI output” and the output 114 of the VLMM 110 may be referred to as a “VLMM output”. The input 112 of the VLMM 110 may be referred to as a “VLMM input”. In accordance with an embodiment, the MLI output 122 is electrically connected to the VLMM input 112. The VLMM 110 is configured such that the VLMM output 114 provides an AC voltage having an increased number of voltage levels compared to the number of voltage levels of the AC voltage at the VLMM input 112 (and MLI output 122). In other words, the VLMM 110 is configured to receive a first output voltage having a first number of voltage levels from the MLI 120 and to generate a second output voltage having a second number of voltage levels. In accordance with an embodiment, the second number of voltage levels are at least a quadruple of the first number of voltage levels. The VLMM 110 is configured to generate minor voltage levels between main voltage levels of the MLI 120. For example, in the case of a five-level MLI 120, the VLMM 110 may be configured to generate minor voltage levels between the five levels of the voltage levels of the MLI output 122 for a total of twenty-one (21) levels. The number of voltage levels at the VLMM output 114 may vary depending on practical implementation. The VLMM output 114 provides the output of the power converter circuit 100. In accordance with an embodiment, the power converter circuit 100 comprises an MLI switching pattern generator 130 for controlling the MLI 120. The MLI switching pattern generator 130 outputs an MLI switching pattern via an output 135 connected to switches (not shown) of the MLI 120. In accordance with an embodiment, the power converter circuit 100 comprises a VLMM switching pattern generator 140 for controlling the VLMM 110. The VLMM switching pattern generator 140 outputs a VLMM switching pattern via an output 145 connected to switches (not shown) of the VLMM 110. According to one embodiment, the MLI switching pattern generator 130 and the VLMM switching pattern generator 140 receive a respective reference signal Vref-MLI 152 and reference signal Vref-VLMM 154 generated by a reference signal generator 150. The MLI switching pattern is thereby generated according to the Vref-MLI 152 and the VLMM switching pattern is thereby generated according to the Vref-VLMM 154. The MLI switching pattern generator 130 and VLMM switching pattern generator 140 and reference signal generator 150 are described in further detail elsewhere in this document. With reference to FIG. 2, the VLMM 110 is shown in accordance with an embodiment. The VLMM 110 comprises a plurality of circuit elements 200 connected between the VLMM input 122 and the VLMM output 124. The plurality of circuit elements 200 comprises a plurality of switches 210, a capacitor 220 and a DC source 230. The plurality of switches 210 may be referred to as a plurality of switching elements. In the illustrated embodiment, the plurality of switches 210 comprises six power switches S1, S2, S3, S4, S5 and S6. The switches S1, S2, S3, S4, S5 and S6 may be metal-oxide-semiconductor field-effect transistors (MOSFETs), gate turn-off thyristors (GTOs), insulated-gate bipolar transistors (IGBTs) or any other suitable type of switches. In accordance with an embodiment, four of the six switches S2, S3, S5 and S6 are high-frequency switches and two of the six switches S1 and S4 are low-frequency switches. The switches S1, S2, S3, S4, S5 and S6 are complementary in operation and may be considered as complimentary pairs {S1, S4}, {S2, S5} and {S3, S6}. The DC source 230 provides a DC voltage. The DC source 230 may be a DC link capacitor adapted for connection to a separate independent DC source (e.g., a standard AC/DC converter, a solar photovoltaic module or the like). The DC source 230 may be an isolated DC source. The DC voltage of the DC source 230 may be referred to as a DC-link voltage. The capacitor 220 may be any suitable DC capacitor. In accordance with an embodiment, the capacitor voltage is regulated to half of the voltage level of the DC source 230 by th
[ZH CN110789360B]: 基于模块化多电平变流器的多流制牵引传动系统及方法 [EN CN110789360B]: Multi-stream traction transmission system and method based on modularized multi-level converter | [ZH CN110789360B]: 本发明公开了一种基于模块化多电平变流器的多流制牵引传动系统及方法，利用电力电子牵引变压器进行牵引电能传输。在交流牵引供电制式下，通过模块化多电平换流器与牵引供电接触网相连进行降压和升频，再通过中高频变压器进行隔离，输出绕组与整流器相连，整流器与牵引逆变器相连，逆变器输出三相交流电驱动电机运行；在直流牵引供电制式下，中高频变压器的输出绕组作为直流滤波电抗器使用，依次通过直流稳压电容、整流器和牵引逆变器驱动电机运行。通过设备复用以及替代工频牵引变压器，可有效降低系统体积、重量和成本，提升整体性能。 [EN CN110789360B]: The invention discloses a multi-flow traction transmission system and method based on a modular multilevel converter, which utilizes a power electronic traction transformer to carry out traction electric energy transmission. Under an AC traction power supply system, the modularized multilevel converter is connected with a traction power supply contact network for voltage reduction and frequency rise, then a middle high-frequency transformer is isolated, an output winding is connected with a rectifier, the rectifier is connected with a traction inverter, and the inverter outputs a three-phase alternating current to drive a motor to operate; and under a direct current traction power supply system, the output winding of the middle high-frequency transformer is used as a DC filter reactor, andthe motor is driven to operate through a direct-current voltage-stabilizing capacitor, the rectifier and the traction inverter in sequence. Through equipment multiplexing and replacement of a power frequency traction transformer, the system volume, weight and cost can be effectively reduced, and the overall performance is improved. | CN110789360B | 2020-02-14 2021-06-18 | CN201911053639A | 2019-10-31 2019-10-31 | CN201911053639A, 2019-10-31 CN201911053639A, 2019-10-31 | CN110789360B: 2021-06-18 | UNIV HUNAN 湖南大学 | XU JIAZHU XIANG JINWEN LIU YUXING | B60L15/00: I B60L50/53: I B61C3/00: I | B60L15/007: I B60L2210/20: A B61C3/00: I B60L50/53: I Y02T10/70: A Y02T10/72: A | US2012235607A1 CN103036451A EP2586646A2 CN103895534A CN104253548A CN104393614A CN104477054A |  | [ZH CN110789360B]: 1 .一种基于模块化多电平变流器的多流制牵引传动系统，其特征在于，包括牵引供电 接触网(1)、受电弓(2)、交流输入电抗器(3)、直流滤波电抗器(4)、轮轨(5)、交流电机(6)、 模块化多电平变流器(7)、中/高频变压器(8)、整流器单元⑼以及牵引逆变器(10)； 所述牵引供电接触网⑴与受电弓⑵相连，所述受电弓(2)与交流输入电抗器(3)一端 通过第一开关单元(13)相连，所述交流输入电抗器(3)的另一端与模块化多电平变流器的 输入上端口相连，模块化多电平变流器的输入下端口与所述轮轨(5)通过第三开关单元 (15)相连;所述受电弓(2)通过第四开关单元(16)与直流滤波电抗器(4)的一端相连，所述 直流滤波电抗器⑷的另一端与中/高频变压器⑻的输出绕组上端相连； 所述模块化多电平变流器(7)的输出端口与中/高频变压器(8)的单级输入绕组相连， 中/高频变压器的各级输出绕组分别与整流器单元(9)中的各级全桥整流器的输入端相连， 且上级输出绕组的尾端与下级输出绕组的首端之间串联有第五开关单元(17)，所述各级全 桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相连，所述三相桥式 逆变器的输出端与交流电机⑹相连； 所述模块化多电平变流器(7)包含左、右两个桥臂组，每个桥臂组的上桥臂的输入上端 口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由x个子模 块(10)以及一个桥臂电感(11)串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥 臂中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口； 每个子模块的输入上端口和输入下端口之间设置有第二开关单元(14)； x的取值范围为［4， 20］； 所述子模块(10)由四个带有反并联二极管的全控型器件构成全桥结构之后再与储能 电容并联组成； 中/高频变压器(8)为单级输入绕组和y级输出绕组的中频或高频变压器，其中，各级输 出绕组的首端和尾端之间设有第八开关单元(20)，且输入绕组的两端上分别设有第六开关 单元(18)和第七开关单元(19)，中/高频变压器⑻中最后一级绕组的尾端与整流器第一级 全桥整流器的输出侧首端之间设置第九开关单元(21)；y的取值范围为［4,6］； 整流器包含y级全桥整流器，其中，上下级的全桥整流器的输出侧的首端之间设有第十 一开关单元(23)、上下级全桥整流器的输出侧尾端之间设置有第十二开关单元(24)；第一 级全桥整流器的输出侧的尾端与轮轨之间设置有第十开关单元(22)。 2 .根据权利要求1所述的系统，其特征在于，中/高频变压器铁芯材料采用铁氧体、纳米 晶或非晶材料。 3 .根据权利要求1所述的系统，其特征在于，所述开关单元为断路器、隔离开关、接触 器、手动开关或自动开关中的任意一种。 4 .根据权利要求1-3任一项所述的系统，其特征在于，所述的牵引供电接触网包括交流 和直流供电制式，其中，交流供电制式至少包括:交流25kV/50Hz、25kV/60Hz、20kV/50Hz、 20kV/60Hz、15kV/16.7Hz、12.5kV/60Hz、12kV/25Hz ；直流供电制式至少包括直流3kV和 1.5kV。 5 .一种基于模块化多电平变流器的多流制牵引传动方法，其特征在于，利用牵引供电 接触网(1)与受电弓(2)相连，将受电弓(2)与交流输入电抗器(3)一端通过第一开关单元 (13)相连，将交流输入电抗器(3)的另一端与模块化多电平变流器的输入上端口相连，模块 化多电平变流器的输入下端口与轮轨⑸通过第三开关单元(15)相连； 所述模块化多电平变流器(7)的输出端口与中/高频变压器(8)的单级输入绕组相连， 中/高频变压器(8)的各级输出绕组分别与整流器单元(9)中的各级全桥整流器的输入端相 连，所述各级全桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相 连，所述三相桥式逆变器的输出端与交流电机⑹相连； 所述模块化多电平变流器(7)包含左、右两个桥臂组，每个桥臂组的上桥臂的输入上端 口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由x个子模 块(10)以及一个桥臂电感(11)串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥 臂中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口； 每个子模块的输入上端口和输入下端口之间设置有第三开关单元(15)； 所述子模块(10)由四个带有反并联二极管的全控型器件构成全桥结构之后再与储能 电容并联组成； 当牵引供电接触网为交流牵引供电制式时，连通第一开关单元(13)、第三开关单元 (15)，第六开关单元(18)，第七开关单元(19)，其中，第二开关单元(14)的连通数量根据交 流电压等级确定，形成交流牵引供电系统； 中/高频变压器(8)输出绕组的两端上分别串联有第六开关单元(18)和第七开关单元 (19)，子模块(10)的输入上端口和输入下端口与第二开关单元(14)的两端并联； 当牵引供电接触网为直流牵引供电制式时，连通第四开关单元(16)、第五开关单元 (17)，第九开关单元(21)，第十开关单元(22)、第十一开关单元(23)、第十二开关单元(24)， 其中，第八开关单元(20)的连通数量根据直流滤波电感需求确定，其余开关单元断开，系统 进入直流结构； 中/高频变压器⑻的输出绕组的首端和尾端之间并联有第八开关单元(20)，且上级输 出绕组的尾端与下级输出绕组的首端之间串联有第五开关单元(17)，中/高频变压器⑻中 最后一级绕组的尾端与整流器第一级全桥整流器的输出侧首端之间设置第九开关单元 (21)； 整流器的上下各级全桥整流器的输出侧的首端之间并联有第十一开关单元(23)、上下 级全桥整流器的输出侧尾端之间并联有第十二开关单元(24)；第一级全桥整流器的输出侧 的尾端与轮轨之间设置有第十开关单元(22)。 6 .根据权利要求5所述的方法，其特征在于，当牵引供电接触网为交流牵引供电制式 时，通过改变第二开关单元(14)的连通和关断数量，形成不同的交流电压等级。 7 .根据权利要求5所述的方法，其特征在于，当牵引供电接触网为直流牵引供电制式 时，通过改变第八开关单元(20)的连通和关断数量来获得所需的直流滤波电感量。 8 .根据权利要求5所述的方法，其特征在于，所述的牵引供电接触网包括交流和直流供 电制式，其中，交流供电制式至少包括:交流25kV/50Hz、25kV/60Hz、20kV/50Hz、20kV/60Hz、 15kV/16.7Hz,12.5kV/60Hz、12kV/25Hz ；直流供电制式至少包括直流3kV和 1.5kV。 [EN CN110789360B]: 1 A multi-stream traction drive system based on a modular multi-level converter, which is characterized by comprising a traction power supply contact network (1), a pantograph (2), an AC input reactor (3), and a DC filter Reactor (4), wheel rail (5), AC motor (6), modular multi-level converter (7), medium/high frequency transformer (8), rectifier unit , and traction inverter (10) The traction power supply catenary (1) is connected to the pantograph (2), and one end of the pantograph (2) and the AC input reactor (3) is connected through the first switch unit (13), and the AC input reactor (3) ) Is connected to the upper input port of the modular multilevel converter, and the lower input port of the modular multilevel converter is connected to the wheel rail (5) through a third switch unit (15); The pantograph (2) is connected to one end of the DC filter reactor (4) through the fourth switch unit (16), and the other end of the DC filter reactor (4) is connected to the upper end of the output winding of the medium/high frequency transformer ; The output port of the modular multilevel converter (7) is connected to the single-stage input winding of the medium/high frequency transformer (8), and the output windings of each stage of the medium/high frequency transformer are respectively connected to the rectifier unit (9). The input ends of the full-bridge rectifiers at all levels are connected, and a fifth switch unit (17) is connected in series between the tail end of the upper-level output winding and the head end of the lower-level output winding. The output ends of the bridge rectifier are respectively connected to the input ends of the three-phase bridge inverters at various levels in the traction inverter, and the output ends of the three-phase bridge inverter are connected to the AC motor ; The flattening converter (7) includes two bridge arm groups on the left and right. The upper input port of the upper bridge arm of each bridge arm group is connected in parallel, and the input lower port of the lower bridge arm is connected in parallel. Each bridge arm group contains upper and lower arm groups. Two bridge arms, each bridge arm is formed by cascading x sub-modules (10) and a bridge arm inductance (11) in series, the two bridge arm inductances in each bridge arm group are connected in series, and the upper bridge arm The lead wire at the junction of the bridge arm inductance of the lower bridge arm and the bridge arm inductance in the lower bridge arm is the output port of the modular multilevel converter; a second switch unit ( 14); The value range of x is [4, 20]; The sub-module (10) is composed of four fully-controlled devices with anti-parallel diodes forming a full bridge structure and then connected in parallel with an energy storage capacitor; The high-frequency transformer (8) is an intermediate-frequency or high-frequency transformer with a single-stage input winding and a y-stage output winding, wherein an eighth switch unit (20) is provided between the head end and the tail end of the output winding of each stage, and the input winding There are a sixth switch unit (18) and a seventh switch unit (19) on both ends of the rectifier. The tail end of the final winding in the medium/high frequency transformer and the output side head end of the first-stage full-bridge rectifier of the rectifier A ninth switch unit (21) is set in between; the value range of y is [4,6]; The rectifier includes a y-level full-bridge rectifier, wherein an eleventh switch unit (23) is provided between the output ends of the full-bridge rectifiers of the upper and lower levels, and a first switch unit (23) is provided between the output-side tail ends of the upper and lower full-bridge rectifiers. Twelve switch units (24); a tenth switch unit (22) is arranged between the tail end of the output side of the first-stage full-bridge rectifier and the wheel rail. 2 The system according to claim 1, wherein the core material of the medium/high frequency transformer adopts ferrite, nanocrystalline or amorphous materials. 3 The system according to claim 1, wherein the switch unit is any one of a circuit breaker, an isolating switch, a contactor, a manual switch, or an automatic switch. 4 The system according to any one of claims 1-3, wherein the traction power supply contact network includes AC and DC power supply systems, wherein the AC power supply system at least includes: AC 25kV/50Hz, 25kV/60Hz, 20kV/50Hz, 20kV/60Hz, 15kV/16.7Hz, 12.5kV/60Hz, 12kV/25Hz; DC power supply system includes at least DC 3kV and 1.5kV. 5 A multi-stream traction transmission method based on a modular multi-level converter, characterized in that the traction power supply catenary (1) is connected to the pantograph (2), and the pantograph (2) is connected to the AC One end of the input reactor (3) is connected through the first switch unit (13), and the other end of the AC input reactor (3) is connected to the input upper port of the modular multilevel converter, and the module The lower input port of the modular multilevel converter is connected to the wheel rail (5) through the third switch unit (15); the output port of the modular multilevel converter (7) is connected to the medium/high frequency transformer (8) The single-stage input windings of the medium/high frequency transformer (8) are connected to the input ends of the full-bridge rectifiers of all levels in the rectifier unit (9), and the output ends of the full-bridge rectifiers of the various levels are respectively It is connected to the input end of the three-phase bridge inverter at all levels in the traction inverter, and the output end of the three-phase bridge inverter is connected to the AC motor ; the modular multilevel converter (7 ) Contains two bridge arm groups on the left and right. The upper input port of the upper bridge arm of each bridge arm group is connected in parallel, and the input lower port of the lower bridge arm is connected in parallel. Each bridge arm group contains two upper and lower bridge arms. Each bridge arm is formed by cascading x sub-modules (10) and a bridge arm inductance (11) in series. The two bridge arm inductances in each bridge arm group are connected in series, and the bridge arm inductance in the upper bridge arm is connected to the lower bridge arm inductance in series. The lead wire at the junction of the bridge arm inductance in the bridge arm is the output port of the modular multilevel converter; a third switch unit (15) is provided between the input upper port and the input lower port of each submodule; The module (10) is composed of four fully controlled devices with anti-parallel diodes forming a full bridge structure and then connected in parallel with an energy storage capacitor; when the traction power supply catenary is an AC traction power supply system, it is connected to the first switch unit (13) , The third switch unit (15), the sixth switch unit (18), the seventh switch unit (19), wherein the number of connections of the second switch unit (14) is determined according to the AC voltage level to form an AC traction power supply system; medium/high frequency transformer ( 8) A sixth switch unit (18) and a seventh switch unit (19) are respectively connected in series on both ends of the output winding. The input upper port and the input lower port of the submodule (10) are connected to the two of the second switch unit (14). When the traction power supply catenary is in the DC traction power supply system, the fourth switch unit (16), the fifth switch unit (17), the ninth switch unit (21), the tenth switch unit (22), and the tenth switch unit are connected in parallel; A switch unit (23), a twelfth switch unit (24), wherein the number of connections of the eighth switch unit (20) is determined according to the requirements of the DC filter inductance, the other switch units are disconnected, and the system enters the DC structure; medium/high frequency An eighth switch unit (20) is connected in parallel between the head end and the tail end of the output winding of the transformer , and a fifth switch unit (17) is connected in series between the tail end of the upper-level output winding and the head end of the lower-level output winding. /The ninth switch unit (21) is set between the tail end of the last winding in the high-frequency transformer and the output side head end of the first-level full-bridge rectifier of the rectifier; the first end of the output side of the full-bridge rectifier at the upper and lower levels of the rectifier The eleventh switch unit (23), the upper and lower A twelfth switch unit (24) is connected in parallel between the output side tail ends of the first-level full-bridge rectifier; a tenth switch unit (22) is arranged between the output side tail end of the first-level full-bridge rectifier and the wheel rail. 6 The method according to claim 5, characterized in that when the traction power supply catenary is an AC traction power supply system, different AC voltage levels are formed by changing the number of connection and shutdown of the second switch unit (14). 7 The method according to claim 5, characterized in that, when the traction power supply catenary is a DC traction power supply system, the required DC filter inductance is obtained by changing the number of on and off of the eighth switch unit (20) . 8 The method according to claim 5, wherein the traction power supply contact network includes AC and DC power supply systems, wherein the AC power supply system at least includes: AC 25kV/50Hz, 25kV/60Hz, 20kV/50Hz, 20kV /60Hz, 15kV/16.7Hz, 12.5kV/60Hz, 12kV/25Hz; DC power supply system includes at least DC 3kV and 1.5kV. | [ZH CN110789360B]: 基于模块化多电平变流器的多流制牵引传动系统及方法 技术领域 [0001]本发明属于轨道交通牵引传动变流技术领域，特别涉及一种基于模块化多电平变 流器的多流制牵引传动系统及方法。 背景技术 [0002]牵引传动系统从牵引供电网获取电能并驱动机车运行，是电力机车的核心装备。 在轨道交通电气化发展过程中，由于技术历史和物理空间等因素，牵引供电网络存在多种 供电制式。目前世界范围内广泛采用的牵引供电制式包括25kV、15kV工频交流以及3kV、 1.5kV直流。多流制牵引传动系统能够适应上述两种及以上种供电制式的灵活切换，实现电 力机车的跨线运行。而电力电子牵引变压器因其灵活的控制性能成为多流制电力机车的理 想接口。 [0003]长期以来，我国的电力机车牵引供电系统采用单一的供电制式，其中干线铁路和 城际铁路采用25kV的工频交流牵引供电制式，而城市轨道交通采用1.5kV直流牵引供电制 式。但是，随着我国轨道交通的迅速发展，三种轨道交通互联的需求已经出现，研发能够跨 线运行的双流制电力机车成为有效途径。另外，世界各国因发展过程的不同存在多种供电 制式，中国电力机车制造企业要实现高端装备走向世界，急需研发适用于不同国情的多流 制牵引传动系统。 [0004]目前的多流制电力机车均采用工频牵引变压器，在交流供电制式下提供降压和隔 离的功能，在直流供电制式下变压器绕组作为直流滤波器使用。虽然通过设备复用，用一套 系统实现了多系统功能的集成，在很大程度上降低了空间、重量及成本，但是工频牵引变压 器的一些固有缺点使其难以适应未来轨道交通的发展需求。得益于电力电子器件以及软磁 材料的发展，电力电子牵引变压器应运而生。不仅能够进一步减小多流制牵引传动系统的 体积和重量、提高系统效率、提高电能质量，还具有潮流控制、故障限流、故障隔离等多功 能。 [0005]在众多电力电子牵引变压器方案中模块化多电平变流器技术方案具有突出优势。 模块化多电平换流器技术实现了电力电子设备在高压大容量场景的应用，已经展现出极其 重要的工程应用前景，具有以下优势：结构简单，冗余设计和维护方便；子模块的功能可替 代性强，系统容错率高，一个子模块故障，仅电压缺少一个电平，不影响整体工作；模块化设 计使换流器功能灵活，能适用各种电压功率水平;没有中间高压直流连接线，不需要低电感 母线，可直接采用普通电缆线；用更低的开关频率实现更高的电平数，从而降低损耗和谐波 含量。然而，在现有技术中，多应用于交直变换场景中，需要多级变换。 发明内容 [0006]本发明的目的是提供一种基于模块化多电平变流器的多流制牵引传动系统拓扑 及方法，为电力机车的跨线运行提供技术方案，并有效克服传统的多流制牵引传动系统的 上述不足，获得更高的功率密度，更高的整体效率以及更灵活的能量控制。 [0007] 一种基于模块化多电平变流器的多流制牵引传动系统，包括牵引供电接触网1、受 电弓2、交流输入电抗器3、直流滤波电抗器4、轮轨5、交流电机6、模块化多电平变流器7、中/ 高频变压器8、整流器单元9以及牵引逆变器10； [0008]所述牵引供电接触网1与受电弓2相连，所述受电弓2与交流输入电抗器3一端通过 第一开关单元13相连，所述交流输入电抗器3的另一端与模块化多电平变流器的输入上端 口相连，模块化多电平变流器的输入下端口与所述轮轨5通过第三开关单元15相连； [0009]所述模块化多电平变流器7的输出端口与中/高频变压器8的单级输入绕组相连， 中/高频变压器的各级输出绕组分别与整流器单元9中的各级全桥整流器的输入端相连，所 述各级全桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相连，所述 三相桥式逆变器的输出端与交流电机6相连； [0010] 所述模块化多电平变流器7包含左、右两个桥臂组，每个桥臂组的上桥臂的输入上 端口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由x个子 模块10以及一个桥臂电感11串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥臂 中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口；每 个子模块的输入上端口和输入下端口之间设置有第二开关单元14； x的取值范围为[4，20]； [0011]所述子模块10由四个带有反并联二极管的全控型器件构成全桥结构之后再与储 能电容并联组成。 [0012] x根据系统电压和采用器件电压等级两者决定的，具体取多少级是工程上根据实 际需要计算出来的； [0013] 全控型器件可以为IGBT、MOSFET或IGCT，器件材料可以为SiC或GaN； [0014]整流器单元中的各级全桥整流器和模块化多电平变流器的子模块结构部分相同， 在配置电容上有区别，整流单元可以是每个配一个电容也可能是多个并联后配一个电容； 子模块是每个子模块一个电容。 [0015]本方案中模块化多电平变流器的子模块采用全桥结构，可以实现直接从工频交流 到中高频交流的直接交交变换。与交直交变换相比省去了中间直流母线，在连接线的选型 方面省去了低电感母线，可直接采用普通电缆线;该方案采用模块化级联设计。方便进行冗 余设计，子模块故障后可以用冗余子模块替换，提高了系统的可靠性，维护方便;系统可以 容错运行；提高等效开关频率，降低开关损耗和谐波含量；通过子模块上并联的开关单元可 以调整子模块接入状态，开关接通则子模块被旁路，子模块退出运行；开关关断，则子模块 被串联进桥臂中工作;可以根据牵引网电压的等级调整每个桥臂上运行子模块的数量，实 现电压匹配;与其他电力电子牵引变压器方案相比，只需要单台中高频牵引变压器。 [0016]进一步地，中/高频变压器为单级输入绕组和y级输出绕组的中频或高频变压器， 其中，各级输出绕组的首端和尾端之间设有第八开关单元20，且输入绕组的两端上分别设 有第六开关单元18和第七开关单元19,中/高频变压器中最后一级绕组的尾端与整流器第 一级全桥整流器的输出侧首端之间设置第九开关单元21；y的取值范围为[4,6].y的取值根 据机车的类型、功率、动力分布型式等来确定； [0017] 进一步地，整流器包含y级全桥整流器，其中，上下级的全桥整流器的输出侧的首 端之间设有第十一开关单元23、上下级全桥整流器的输出侧尾端之间设置有第十二开关单 元24；第一级全桥整流器的输出侧的尾端与轮轨之间设置有第十开关单元22。 [0018]进一步地，中/高频变压器铁芯材料采用铁氧体、纳米晶或非晶材料。 [0019] 进一步地，所述开关单元为断路器、隔离开关、接触器、手动开关或自动开关中的 任意一种。 [0020]进一步地，所述的牵引供电接触网包括交流和直流供电制式，其中，交流供电制式 至少包括：交流25kV/50Hz、25kV/60Hz、20kV/50Hz、20kV/60Hz、15kV/16.7Hz、12.5kV/60Hz、 12kV/25Hz ；直流供电制式至少包括直流3kV和1.5kV。 [0021] 一种基于模块化多电平变流器的多流制牵引传动方法，利用牵引供电接触网1与 受电弓2相连，将受电弓2与交流输入电抗器3一端通过第一开关单元13相连，将交流输入电 抗器3的另一端与模块化多电平变流器的输入上端口相连，模块化多电平变流器的输入下 端口与轮轨5通过第三开关单元15相连； [0022]所述模块化多电平变流器7的输出端口与中/高频变压器8的单级输入绕组相连， 中/高频变压器的各级输出绕组分别与整流器单元9中的各级全桥整流器的输入端相连，所 述各级全桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相连，所述 三相桥式逆变器的输出端与交流电机6相连； [0023]所述模块化多电平变流器7包含左、右两个桥臂组，每个桥臂组的上桥臂的输入上 端口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由X个子 模块10以及一个桥臂电感11串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥臂 中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口；每 个子模块的输入上端口和输入下端口之间设置有第三开关单元15； [0024]所述子模块10由四个带有反并联二极管的全控型器件构成全桥结构之后再与储 能电容并联组成； [0025]当牵引供电接触网为交流牵引供电制式时，连通第一开关单元13、第三开关单元 15,第六开关单元18,第七开关单元19,其中，第二开关单元14的连通数量根据交流电压等 级确定，形成交流牵引供电系统； [0026]当牵引供电接触网为交流牵引供电制式时，牵引供电接触网的线频高压交流电通 过模块化多电平变流器的变频与降压作用，转换为电压等级相对较低的中频或高频方波交 流电，之后通过中/高频变压器将中高频方波交流电耦合到各级输出绕组并送到各级全桥 整流器，各级全桥整流器输出侧并联直流稳压电容并与牵引逆变器相连，牵引逆变器输出 三相交流电驱动交流牵引电机； [0027]当牵引供电接触网为直流牵引供电制式时，连通第四开关单元16、第五开关单元 17,第九开关单元21，第十开关单元22、第十一开关单元23、第十二开关单元24,其中，第八 开关单元20的连通数量根据直流滤波电感需求确定，其余开关单元断开，系统进入直流结 构； [0028]当牵引供电接触网为直流牵引供电制式时，中/高频变压器的输出绕组作为直流 滤波电抗器使用，牵引供电接触网提供的直流电通过直流滤波器与直流稳压电容并联，并 与牵引逆变器的输入侧并联，牵引逆变器输出三相交流电驱动交流牵引电机。 [0029]进一步地，当牵引供电接触网为交流牵引供电制式时，通过改变第二开关单元14 的连通和关断数量，形成不同的交流电压等级。 [0030]从而可以根据交流电压等级调整每个桥臂上投入运行的子模块数量，电压等级越 高，模块化多电平换流器投入的子模块数量越多，即关断的第二开关单元越多。 [0031]进一步地，当牵引供电接触网为直流牵引供电制式时，通过改变第八开关单元20 的连通和关断数量来获得所需的直流滤波电感量。 [0032]所需电感值越高，接入的输出绕组数量越多，即关断的第八开关单元20越多。 [0033]进一步地，所述的牵引供电接触网包括交流和直流供电制式，其中，交流供电制式 至少包括：交流25kV/50Hz、25kV/60Hz、20kV/50Hz、20kV/60Hz、15kV/16.7Hz、12.5kV/60Hz、 12kV/25Hz ；直流供电制式至少包括直流3kV和1.5kV。 [0034] 有益效果 [0035]本发明提供了一种基于模块化多电平变流器的多流制牵引传动系统拓扑及方法， 为电力机车的跨供电制式运行提供了一种新型优化技术方案。针对多流制机车应用时的特 殊需要进行了新的设计和优化，该模块化多电平变流器的子模块采用全桥结构，可以实现 从工频交流到中高频交流的直接“交-交”变换；相较于交直交变换，不需要每一级中间直流 母线，在连接线的选型方面省去了低电感母线，可直接采用普通电缆线，可节约成本;且子 模块的冗余设计，维护方便;通过开关单元可以调整子模块的数量，适应不同的供电电压等 级；该方案采用设备复用的思想，用一套牵引传动系统实现了可在多种供电制式下运行的 功能，大大减少了系统的设备数量，进而降低体积和重量，节约成本。用基于模块化多电平 换流器的电力电子牵引变压器取代了传统的工频牵引变压器，可进一步减小系统的体积和 重量、提高系统效率、提高电能质量、提高容错能力，还具有潮流控制、故障限流等多功能。 附图说明 [0036]图1为基于模块化多电平变流器的多流制牵引传动系统接线方案示意图； [0037] 标号说明：1-牵引供电接触网、2-受电弓、3-交流输入电抗器、4-直流滤波电抗器、 5-轮轨、6-交流电机、7-模块化多电平变流器、8-中/高频变压器、9-整流器、10-牵引逆变 器、11-桥臂电感、13-第一开关单元、14-第二开关单元、15-第三开关单元、16-第四开关单 元、17-第五开关单元、18-第六开关单元、19-第七开关单元、20-第八开关单元、21-第九开 关单元、22-第十开关单元、23-第十一开关单元、24-第十二开关单元。 具体实施方式 [0038]下面将结合附图和实施例对本发明做进一步的说明。 [0039]如图1所示，一种基于模块化多电平变流器的多流制牵引传动系统，包括牵引供电 接触网1、受电弓2、交流输入电抗器3、直流滤波电抗器4、轮轨5、交流电机6、模块化多电平 变流器7、中/高频变压器8、整流器单元9以及牵引逆变器10； [0040]所述牵引供电接触网1与受电弓2相连，所述受电弓2与交流输入电抗器3一端通过 第一开关单元13相连，所述交流输入电抗器3的另一端与模块化多电平变流器的输入上端 口相连，模块化多电平变流器的输入下端口与所述轮轨5通过第三开关单元15相连； [0041]所述模块化多电平变流器7的输出端口与中/高频变压器8的单级输入绕组相连， 中/高频变压器8的各级输出绕组分别与整流器单元9中的各级全桥整流器的输入端相连， 所述各级全桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相连，所 述三相桥式逆变器的输出端与交流电机6相连； [0042] 所述模块化多电平变流器7包含左、右两个桥臂组，每个桥臂组的上桥臂的输入上 端口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由x个子 模块10以及一个桥臂电感11串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥臂 中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口；每 个子模块的输入上端口和输入下端口之间设置有第二开关单元14；x的取值范围为[4,20]； x根据系统电压和采用器件电压等级两者决定的，具体取多少级是工程上根据实际需要计 算出来的；25kV牵引网电压，采用3.3kV IGBT,x=18；采用6.5kV IGBT,x = 9；15kV牵引网电 压，采用3.3kV IGBT,x = 12；采用6.5kV IGBT,x = 6； [0043]所述子模块10由四个带有反并联二极管的全控型器件构成全桥结构之后再与储 能电容并联组成。 [0044]中/高频变压器8为单级输入绕组和y级输出绕组的中频或高频变压器，其中，各级 输出绕组的首端和尾端之间设有第八开关单元20,且输入绕组的两端上分别设有第六开关 单元18和第七开关单元19,中/高频变压器8中最后一级绕组的尾端与整流器第一级全桥整 流器的输出侧首端之间设置第九开关单元21；y的取值范围为[4,6].y的取值根据机车的类 型、功率、动力分布型式等来确定，通常取4；中/高频变压器铁芯材料采用铁氧体、纳米晶或 非晶材料。 [0045]整流器包含y级全桥整流器，其中，上下级的全桥整流器的输出侧的首端之间设有 第十一开关单元23、上下级全桥整流器的输出侧尾端之间设置有第十二开关单元24；第一 级全桥整流器的输出侧的尾端与轮轨之间设置有第十开关单元22。 [0046] 其中，全控型器件可以为IGBT、MOSFET或IGCT,器件材料可以为SiC或GaN； [0047]整流器单元中的各级全桥整流器和模块化多电平变流器的子模块结构部分相同， 在配置电容上有区别，整流单元可以是每个配一个电容也可能是多个并联后配一个电容； 子模块是每个子模块一个电容。 [0048]在本实例中开关单元为断路器、隔离开关、接触器、手动开关或自动开关中的任意 一种。 [0049]所述的牵引供电接触网包括交流和直流供电制式，其中，交流供电制式至少包括: 交流25kV/50Hz、25kV/60Hz、20kV/50Hz、20kV/60Hz、15kV/16.7Hz、12.5kV/60Hz、12kV/ 25Hz ；直流供电制式至少包括直流3kV和1.5kV。 [0050] 一种基于模块化多电平变流器的多流制牵引传动方法，利用牵引供电接触网1与 受电弓2相连，将受电弓2与交流输入电抗器3一端通过第一开关单元13相连，将交流输入电 抗器3的另一端与模块化多电平变流器的输入上端口相连，模块化多电平变流器的输入下 端口与轮轨5通过第三开关单元15相连； [0051]所述模块化多电平变流器7的输出端口与中/高频变压器8的单级输入绕组相连， 中/高频变压器的各级输出绕组分别与整流器单元9中的各级全桥整流器的输入端相连，所 述各级全桥整流器的输出端分别与牵引逆变器中各级三相桥式逆变器的输入端相连，所述 三相桥式逆变器的输出端与交流电机6相连； [0052] 所述模块化多电平变流器7包含左、右两个桥臂组,每个桥臂组的上桥臂的输入上 端口并联，下桥臂的输入下端口并联，每个桥臂组包含上、下两个桥臂，每个桥臂均由x个子 模块10以及一个桥臂电感11串联级联而成，每个桥臂组中的两个桥臂电感串联，且上桥臂 中的桥臂电感与下桥臂中桥臂电感连接处的引出线为模块化多电平变流器的输出端口；每 个子模块的输入上端口和输入下端口之间设置有第三开关单元15； [0053]所述子模块10由四个带有反并联二极管的全控型器件构成全桥结构之后再与储 能电容并联组成； [0054]当牵引供电接触网为交流牵引供电制式时，连通第一开关单元13、第三开关单元 15,第六开关单元18,第七开关单元19,其中，第二开关单元14的连通数量根据交流电压等 级确定，形成交流牵引供电系统； [0055]当牵引供电接触网为交流牵引供电制式时，牵引供电接触网的线频高压交流电通 过模块化多电平变流器的变频与降压作用，转换为电压等级相对较低的中频或高频方波交 流电，，之后通过中/高频变压器将中高频方波交流电耦合到各级输出绕组并送到各级全桥 整流器，各级全桥整流器输出侧并联直流稳压电容并与牵引逆变器相连，牵引逆变器输出 三相交流电驱动交流牵引电机； [0056]当牵引供电接触网为直流牵引供电制式时，连通第四开关单元16、第五开关单元 17,第九开关单元21，第十开关单元22、第十一开关单元23、第十二开关单元24,其中，第八 开关单元20的连通数量根据直流滤波电感需求确定，其余开关单元断开，系统进入直流结 构； [0057]当牵引供电接触网为直流牵引供电制式时，中/高频变压器的输出绕组作为直流 滤波电抗器使用，牵引供电接触网提供的直流电通过直流滤波器与直流稳压电容并联，并 与牵引逆变器的输入侧并联，牵引逆变器输出三相交流电驱动交流牵引电机。 [0058]当牵引供电接触网为交流牵引供电制式时，通过改变第二开关单元14的连通和关 断数量，形成不同的交流电压等级。 [0059]从而可以根据交流电压等级调整每个桥臂上投入运行的子模块数量，电压等级越 高，模块化多电平换流器投入的子模块数量越多，即关断的第二开关单元越多。 [0060]当牵引供电接触网为直流牵引供电制式时，通过改变第八开关单元20的连通和关 断数量来获得所需的直流滤波电感量。 [0061]所需电感值越高，接入的输出绕组数量越多，即关断的第八开关单元20越多。 [0062]所述的牵引供电接触网包括交流和直流供电制式，其中，交流供电制式至少包括: 交流25kV/50Hz、25kV/60Hz、20kV/50Hz、20kV/60Hz、15kV/16.7Hz、12.5kV/60Hz、12kV/ 25Hz ；直流供电制式至少包括直流3kV和1.5kV。 [0063]以上仅是对本发明优选实施方式的描述，本发明的保护范围并不局限于上述实施 例，凡属于本发明思路下的技术方案均属于本发明的保护范围。本发明所属技术领域的技 术人员在不偏离本发明的精神和原理的情况下对所描述的具体实施例做各种修改或补充 或采用类似的方式替代，视为本发明的保护范围。 CN 110789360 Β [EN CN110789360B]: Multi-stream traction drive system and method based on modular multi-level converterTechnical field [0001] The present invention belongs to the technical field of rail transit traction drive conversion, and in particular relates to a multi-stream traction transmission system and method based on a modular multi-level converter. Background technique [0002] The traction drive system obtains electrical energy from the traction power supply network and drives the locomotive to run, and is the core equipment of the electric locomotive. In the process of electrification of rail transit, due to factors such as technological history and physical space, there are multiple power supply systems in the traction power supply network. At present, the traction power supply system widely used in the world includes 25kV, 15kV power frequency AC and 3kV, 1.5kV DC. The multi-stream traction drive system can adapt to the flexible switching of the above two or more power supply systems, and realize the cross-line operation of electric locomotives. The power electronic traction transformer has become an ideal interface for multi-stream electric locomotives due to its flexible control performance. [0003] For a long time, my country's electric locomotive traction power supply system has adopted a single power supply system, in which trunk railways and intercity railways have adopted a 25kV power frequency AC traction power supply system, while urban rail transit has adopted a 1.5kV DC traction power supply system. However, with the rapid development of rail transit in my country, the need for three kinds of rail transit interconnection has emerged, and the development of dual-stream electric locomotives that can run across lines has become an effective way. In addition, countries around the world have multiple power supply systems due to different development processes. To realize high-end equipment going global, Chinese electric locomotive manufacturers urgently need to develop multi-stream traction drive systems suitable for different national conditions. [0004] The current multi-stream electric locomotives all use power frequency traction transformers to provide voltage reduction and isolation functions under the AC power supply system, and the transformer windings are used as DC filters under the DC power supply system. Although the integration of multiple system functions is achieved through equipment reuse and a set of systems, which greatly reduces space, weight and cost, some inherent shortcomings of industrial frequency traction transformers make it difficult to adapt to the development needs of future rail transit. . Thanks to the development of power electronic devices and soft magnetic materials, power electronic traction transformers have emerged. Not only can it further reduce the volume and weight of the multi-flow traction drive system, improve system efficiency, and improve power quality, but it also has functions such as power flow control, fault current limiting, and fault isolation. [0005] Among many power electronic traction transformer solutions, the modular multilevel converter technical solution has outstanding advantages. Modular multi-level converter technology realizes the application of power electronic equipment in high-voltage and large-capacity scenarios, and has shown extremely important engineering application prospects. It has the following advantages: simple structure, redundant design and convenient maintenance; sub-module functions Strong replaceability, high system fault tolerance, one sub-module failure, only one voltage level is missing, does not affect the overall work; modular design makes the converter function flexible and can be applied to various voltage and power levels; there is no intermediate high voltage DC connection Line, do not need low inductance bus bar, can directly use ordinary cable line; use lower switching frequency to achieve higher level number, thereby reducing loss and harmonic content. However, in the prior art, it is mostly used in AC-DC conversion scenarios, and multi-level conversion is required. Summary of the invention [0006] The purpose of the present invention is to provide a multi-stream traction drive system topology and method based on a modular multi-level converter, to provide technical solutions for the cross-line operation of electric locomotives, and effectively overcome the traditional multi-stream system The above-mentioned shortcomings of the traction drive system result in higher power density, higher overall efficiency and more flexible energy control. [0007] A multi-stream traction drive system based on a modular multi-level converter, including a traction power supply contact network 1, a pantograph 2, an AC input reactor 3, a DC filter reactor 4, a wheel rail 5. AC motor 6, modular multilevel converter 7, medium/high frequency transformer 8, rectifier unit 9, and traction inverter 10; [0008] The traction power supply catenary 1 is connected to the pantograph 2, one end of the pantograph 2 and the AC input reactor 3 is connected through the first switch unit 13, and the other end of the AC input reactor 3 is connected to the module The upper input port of the modular multilevel converter is connected, and the lower input port of the modular multilevel converter is connected to the wheel rail 5 through a third switch unit 15; [0009] The output port of the modular multilevel converter 7 is connected to the single-stage input winding of the medium/high-frequency transformer 8, and the output windings of each stage of the medium/high-frequency transformer are respectively connected to each stage in the rectifier unit 9. The input ends of the full-bridge rectifier are connected, and the output ends of the full-bridge rectifiers at all levels are respectively connected to the input ends of the three-phase bridge inverters at all levels in the traction inverter. The output of the three-phase bridge inverter is The terminal is connected to the AC motor 6; [0010] The modular multilevel converter 7 includes two left and right bridge arm groups, each of which has an upper bridge arms input upper port in parallel, and a lower bridge arms input lower port in parallel, each The bridge arm group includes upper and lower bridge arms. Each bridge arm is formed by cascading x sub-modules 10 and a bridge arm inductor 11 in series. The two bridge arm inductors in each bridge arm group are connected in series, and the upper The lead wire at the junction of the bridge arm inductance in the bridge arm and the bridge arm inductance in the lower bridge arm is the output port of the modular multilevel converter; the second input port and the input lower port of each sub-module are provided The switch unit 14; the value range of x is [4, 20]; [0011] The sub-module 10 is composed of four fully-controlled devices with anti-parallel diodes forming a full bridge structure and then connected in parallel with an energy storage capacitor. [0012] x is determined according to both the system voltage and the voltage level of the adopted device, and the specific level is calculated according to actual needs in the project; [0013] The fully controlled device can be an IGBT, MOSFET or IGCT, and the device material can be SiC or GaN; [0014] The sub-modules of the full-bridge rectifiers and modular multilevel converters in the rectifier unit are the same in structure, and there are differences in the configuration of capacitors. The rectifier unit can be equipped with one capacitor for each capacitor or multiple in parallel. There is a capacitor after it; the sub-module is a capacitor for each sub-module. [0015] The sub-modules of the modular multi-level converter in this solution adopt a full-bridge structure, which can realize direct AC-to-AC conversion from power frequency AC to medium and high frequency AC. Compared with the AC-DC-AC conversion, the intermediate DC bus is omitted, and the low-inductance bus is omitted in the selection of the connecting line, and ordinary cable can be directly used; this scheme adopts a modular cascade design. It is convenient to carry out redundant design, and the sub-module can be replaced with redundant sub-modules after failure, which improves the reliability of the system and is convenient to maintain; the system can run fault-tolerant; improve the equivalent switching frequency and reduce the switching loss and harmonic content; through the sub-module The switch unit connected in parallel can adjust the access status of the sub-module. When the switch is turned on, the sub-module is bypassed and the sub-module exits operation; when the switch is turned off, the sub-module is connected in series into the bridge arm to work; it can be operated according to the voltage level of the traction network Adjust the number of running sub-modules on each bridge arm to achieve voltage matching; compared with other power electronic traction transformer solutions, only a single medium and high frequency traction transformer is required. [0016] Further, the medium/high-frequency transformer is an intermediate-frequency or high-frequency transformer with a single-stage input winding and a y-stage output winding, wherein an eighth switch unit 20 is provided between the head end and the tail end of the output winding of each stage, And a sixth switch unit 18 and a seventh switch unit 19 are respectively provided on both ends of the input winding, between the tail end of the last winding in the medium/high frequency transformer and the output side head end of the first-stage full-bridge rectifier of the rectifier Set the ninth switch unit 21; the value range of y is [4,6]. The value of y is determined according to the type, power, power distribution type, etc. of the locomotive; [0017] Further, the rectifier includes a y-level full-bridge rectifier, wherein an eleventh switch unit 23 is provided between the output side head ends of the upper and lower full bridge rectifiers, and one of the output side tail ends of the upper and lower full bridge rectifiers A twelfth switch unit 24 is provided in between; a tenth switch unit 22 is provided between the tail end of the output side of the first-stage full-bridge rectifier and the wheel rail. [0018] Further, the core material of the medium/high frequency transformer adopts ferrite, nanocrystalline or amorphous materials. [0019] Further, the switch unit is any one of a circuit breaker, an isolating switch, a contactor, a manual switch or an automatic switch. [0020] Further, the traction power supply contact network includes AC and DC power supply systems, where the AC power supply system at least includes: AC 25kV/50Hz, 25kV/60Hz, 20kV/50Hz, 20kV/60Hz, 15kV/16.7Hz, 12.5kV/60Hz, 12kV/25Hz; DC power supply system includes at least DC 3kV and 1.5kV. [0021] A multi-stream traction transmission method based on a modular multi-level converter. The traction power supply contact net 1 is connected to the pantograph 2, and one end of the pantograph 2 and the AC input reactor 3 is passed through the first The switch unit 13 is connected, and the other end of the AC input reactor 3 is connected to the upper input port of the modular multilevel converter, and the lower input port of the modular multilevel converter and the wheel rail 5 pass through the third switch unit 15 connected; [0022] The output port of the modular multilevel converter 7 is connected to the single-stage input winding of the medium/high-frequency transformer 8, and the output windings of each stage of the medium/high-frequency transformer are respectively connected to each stage in the rectifier unit 9. The input ends of the full-bridge rectifier are connected, and the output ends of the full-bridge rectifiers at all levels are respectively connected to the input ends of the three-phase bridge inverters at all levels in the traction inverter. The output of the three-phase bridge inverter is The terminal is connected to the AC motor 6; [0023] The modular multi-level converter 7 includes left and right two bridge arm groups, each of the upper bridge arm of the upper input port is connected in parallel, and the lower input port of the lower bridge arm is connected in parallel, each The bridge arm group includes upper and lower bridge arms. Each bridge arm is formed by cascading X sub-modules 10 and a bridge arm inductor 11 in series. The two bridge arm inductors in each bridge arm group are connected in series, and the upper The lead wire at the junction of the bridge arm inductance in the bridge arm and the bridge arm inductance in the lower bridge arm is the output port of the modular multilevel converter; a third input port is provided between the input upper port and the input lower port of each submodule. Switch unit 15; [0024] The sub-module 10 is composed of four fully-controlled devices with anti-parallel diodes forming a full bridge structure and then connected in parallel with an energy storage capacitor; [0025] When the traction power supply catenary is the AC traction power supply system, the first switch unit 13, the third switch unit 15, the sixth switch unit 18, and the seventh switch unit 19 are connected, wherein the number of the second switch units 14 is connected Determined according to the AC voltage level to form an AC traction power supply system; [0026] When the traction power supply catenary is an AC traction power supply system, the line-frequency high-voltage AC power of the traction power supply catenary is converted into a relatively low-voltage intermediate frequency or medium frequency through the frequency conversion and voltage reduction effect of the modular multi-level converter High frequency square wave alternating current, then through the medium/high frequency transformer, the medium and high frequency square wave alternating current is coupled to the output windings of each level and sent to the full bridge rectifiers of each level. The converter is connected, and the traction inverter outputs three-phase AC power to drive the AC traction motor; [0027] When the traction power supply contact network is a DC traction power supply system, the fourth switch unit 16, the fifth switch unit 17, the ninth switch unit 21, the tenth switch unit 22, the eleventh switch unit 23, and the twelfth switch unit are connected. The switch unit 24, wherein the number of connections of the eighth switch unit 20 is determined according to the requirement of the DC filter inductance, the other switch units are disconnected, and the system enters the DC structure; [0028] When the traction power supply catenary is the DC traction power supply system, the output winding of the medium/high-frequency transformer is used as a DC filter reactor, and the DC power provided by the traction power supply catenary is connected in parallel with the DC stabilized capacitor through the DC filter and The input side of the traction inverter is connected in parallel, and the traction inverter outputs three-phase AC power to drive the AC traction motor. [0029] Further, when the traction power supply catenary is an AC traction power supply system, by changing the number of connection and shutdown of the second switch unit 14, different AC voltage levels are formed. [0030] Thus, the number of sub-modules put into operation on each bridge arm can be adjusted according to the AC voltage level, the higher the voltage level High, the more the number of sub-modules invested in the modular multilevel converter, that is, the more second switch units that are turned off. [0031] Further, when the traction power supply catenary is a DC traction power supply system, the required DC filter inductance can be obtained by changing the number of on and off of the eighth switch unit 20. [0032] The higher the required inductance value, the more output windings are connected, that is, the more eighth switch units 20 are turned off. [0033] Further, the traction power supply contact network includes AC and DC power supply systems, where the AC power supply system at least includes: AC 25kV/50Hz, 25kV/60Hz, 20kV/50Hz, 20kV/60Hz, 15kV/16.7Hz, 12.5kV/60Hz, 12kV/25Hz; DC power supply system includes at least DC 3kV and 1.5kV. [0034] Benefits [0035] The present invention provides a multi-stream traction drive system topology and method based on a modular multi-level converter, and provides a new optimized technical solution for the operation of electric locomotives across power supply systems. New designs and optimizations have been made for the special needs of multi-stream locomotive applications. The sub-modules of this modular multi-level converter adopt a full-bridge structure, which can achieve direct "inter- Compared with the AC-DC-AC conversion, the intermediate DC bus of each level is not needed, and the low-inductance bus is omitted in the selection of the connection line. The ordinary cable can be directly used, which can save the cost; and the redundancy of the sub-module Additional design and easy maintenance; the number of sub-modules can be adjusted through the switch unit to adapt to different power supply voltage levels; the solution adopts the idea of equipment reuse, and uses a set of traction drive system to realize the function of running under multiple power supply systems , Which greatly reduces the number of equipment in the system, thereby reducing the volume and weight and saving costs. Replace the traditional power frequency traction transformer with a power electronic traction transformer based on a modular multilevel converter, which can further reduce the volume and weight of the system, improve system efficiency, improve power quality, improve fault tolerance, and also have power flow control , Multi-functions such as fault current limiting. Description of the drawings [0036] FIG. 1 is a schematic diagram of a wiring scheme for a multi-stream traction drive system based on a modular multi-level converter; [0037] Description of reference signs: 1-traction power supply contact net, 2-pantograph, 3-AC input reactor, 4-DC filter reactor, 5-wheel rail, 6-AC motor, 7-modular multilevel Converter, 8-medium/high frequency transformer, 9-rectifier, 10-traction inverter, 11-arm inductor, 13-first switching unit, 14-second switching unit, 15-third switching unit, 16-fourth switch unit, 17-fifth switch unit, 18-sixth switch unit, 19-seventh switch unit, 20-eighth switch unit, 21-ninth switch unit, 22-tenth switch unit, 23 -The eleventh switch unit, 24-the twelfth switch unit. Detailed ways [0038] The present invention will be further described below in conjunction with the accompanying drawings and embodiments. [0039] As shown in FIG. 1, a multi-stream traction drive system based on a modular multi-level converter includes a traction power supply contact network 1, a pantograph 2, an AC input reactor 3, and a DC filter reactor 4. Wheel and rail 5, AC motor 6, modular multi-level converter 7, medium/high frequency transformer 8, rectifier unit 9 and traction inverter 10; [0040] The traction power supply catenary 1 is connected to the pantograph 2, one end of the pantograph 2 and the AC input reactor 3 is connected through the first switch unit 13, and the other end of the AC input reactor 3 is connected to the module The upper input port of the modular multilevel converter is connected, and the lower input port of the modular multilevel converter is connected to the wheel rail 5 through a third switch unit 15; [0041] The output port of the modular multilevel converter 7 is connected to the single-stage input winding of the medium/high-frequency transformer 8. The output windings of each stage of the medium/high-frequency transformer 8 are connected to each of the rectifier units 9 respectively. The input ends of the three-stage full-bridge rectifier are connected, and the output ends of the full-bridge rectifiers at all levels are respectively connected to the input ends of the three-phase bridge inverters of each level in the traction inverter. The output end is connected to the AC motor 6; [0042] The modular multilevel converter 7 includes left and right two bridge arm groups, the upper input port of the upper bridge arm of each bridge arm group is connected in parallel, and the input lower port of the lower bridge arm is connected in parallel, each The bridge arm group includes upper and lower bridge arms. Each bridge arm is formed by cascading x sub-modules 10 and a bridge arm inductor 11 in series. The two bridge arm inductors in each bridge arm group are connected in series, and the upper The lead wire at the junction of the bridge arm inductance in the bridge arm and the bridge arm inductance in the lower bridge arm is the output port of the modular multilevel converter; the second input port and the input lower port of each sub-module are provided Switching unit 14; the value range of x is [4,20]; x is determined according to both the system voltage and the voltage level of the device used. The specific level is calculated according to actual needs in the project; 25kV traction network voltage is adopted 3.3kV IGBT, x=18; 6.5kV IGBT, x = 9; 15kV traction network voltage, 3.3kV IGBT, x = 12; 6.5kV IGBT, x = 6; [0043] The sub-module 10 is composed of four fully-controlled devices with anti-parallel diodes forming a full bridge structure and then connected in parallel with an energy storage capacitor. [0044] The intermediate/high frequency transformer 8 is an intermediate frequency or high frequency transformer with a single-stage input winding and a y-stage output winding, wherein an eighth switch unit 20 is provided between the head end and the tail end of the output winding of each stage, and the input A sixth switch unit 18 and a seventh switch unit 19 are respectively provided on both ends of the winding. The tail end of the final winding in the medium/high frequency transformer 8 and the output side head end of the first-stage full-bridge rectifier of the rectifier are arranged between The ninth switch unit 21; the value range of y is [4,6]. The value of y is determined according to the type, power, power distribution type, etc. of the locomotive, usually 4; the iron core material of the medium/high frequency transformer is iron Oxygen, nanocrystalline or amorphous materials. [0045] The rectifier includes a y-level full-bridge rectifier, wherein an eleventh switch unit 23 is provided between the output side head ends of the upper and lower full bridge rectifiers, and the output side tail ends of the upper and lower full bridge rectifiers are provided between The twelfth switch unit 24; a tenth switch unit 22 is provided between the tail end of the output side of the first-stage full-bridge rectifier and the wheel rail. [0046] Among them, the fully-controlled device may be an IGBT, MOSFET or IGCT, and the device material may be SiC or GaN; [0047] The sub-modules of the full-bridge rectifiers and the modular multilevel converters in the rectifier unit are the same in structure, and there are differences in the configuration of the capacitors. The rectifier unit can be equipped with one capacitor for each capacitor or multiple in parallel. There is a capacitor after it; the sub-module is a capacitor for each sub-module. [0048] In this example, the switch unit is any one of a circuit breaker, an isolating switch, a contactor, a manual switch, or an automatic switch. [0049] The traction power supply contact network includes AC and DC power supply systems, where the AC power supply system at least includes: AC 25kV/50Hz, 25kV/60Hz, 20kV/50Hz, 20kV/60Hz, 15kV/16.7Hz, 12.5kV/ 60Hz, 12kV/ 25Hz; DC power supply system includes at least DC 3kV and 1.5kV. [0050] A multi-stream traction transmission method based on a modular multi-level converter. The traction power supply contact net 1 is connected to the pantograph 2, and one end of the pantograph 2 and the AC input reactor 3 is passed through the first The switch unit 13 i
[ZH CN110729911B]: 适用于多电平变换器的热应力平衡预测控制方法及系统 [EN CN110729911B]: Thermal stress balance predictive control method and system suitable for multilevel converter | [ZH CN110729911B]: 本发明公开了一种适用于多电平变换器的热应力平衡预测控制方法及系统，涉及电力电子变换器控制技术。所述热应力平衡预测控制方法及系统，先根据控制变量参考值和控制变量输出预测值来构建代价函数，确定最优的输出总电平和电平增量，再根据电平增量确定能动作的模块，最后根据结温值设计开关分配函数，确定需要动作的模块，将电平增量分配到需要动作的模块，该控制方法中代价函数根据输出预测值来设计，且无修正，保证了输出精度；开关分配函数以用于反应各模块热应力的结温值为设计依据，通过开关分配函数确定模块的开关状态，达到了多模块热应力平衡的效果。 [EN CN110729911B]: The invention discloses a thermal stress balance predictive control method and system suitable for a multi-level converter, and relates to a power electronic converter control technology. The thermalstress balance predictive control method comprises the following steps: firstly, a cost function is constructed according to a control variable reference value and a control variable output predictionvalue, and an optimal total output level and a level increment are determined; secondly, modules capable of acting are determined according to the level increment; and finally, a switch distributionfunction is designed according to the junction temperature value, modules needing to act are determined, and the level increment is distributed to the modules needing to act. In the control method, the cost function is designed according to the output prediction value and is not corrected, and the output precision is ensured. The switch distribution function is designed based on the junction temperature value for reflecting the thermal stress of each module, the switching states of modules are determined through the switch distribution function, and an effect of multi-module thermal stress balance is achieved. | CN110729911A | 2021-06-11 2020-01-24 | CN201911010461A | 2019-10-23 2019-10-23 | CN201911010461A, 2019-10-23 CN201911010461A, 2019-10-23 | CN110729911B: 2021-06-11 | 湖南大学 UNIV HUNAN | LUO AN HAN RONG XU QIANMING DING HONGQI TANG CHENG WANG LIANG | H02M7/49: I | H02M7/49: I |  |  | [ZH CN110729911B]: L一种适用于多电平变换器的热应力平衡预测控制方法，其特征在于，包括以下步骤： 步骤1：采集多电平变换器在k时刻的控制变量输出瞬时值，由该控制变量输出瞬时值 得到k+Ι时刻不同开关状态组合下的控制变量输出预测值； 步骤2：设定k+Ι时刻控制变量参考值，根据k+Ι时刻控制变量参考值和步骤1的控制变 量输出预测值构建代价函数，在有限控制集的约束下，以代价函数最小对应的总电平作为k +1时刻的最优输出总电平,并得到k+Ι时刻最优状态下的电平增量； 步骤3：根据步骤2的电平增量选出k+Ι时刻能动作的模块； 步骤4：采集各功率器件的导通电压和电流，由所述导通电压和电流估算出各模块功率 器件的结温值； 步骤5：根据步骤4的结温值构建模块的开关分配函数，根据每个模块的开关分配函数 在步骤3能动作的模块中选出k+Ι时刻需要动作的模块； 步骤6：将步骤2的电平增量分配至需要动作的模块的具体桥臂，以实现多模块热应力 的平衡； 所述步骤5中，第i个模块的开关分配函数的具体表达式为 c^ky=c^iky+ac^k) 其中，q (k)为第i个模块在k时刻的开关分配函数，c：(外为第i个模块在ο到k时刻开关 的动作次数累计值，。汽左)为第i个模块在k时刻功率器件的结温值,α为分配因子。 2 .如权利要求1所述的热应力平衡预测控制方法，其特征在于，所述步骤2中，代价函数 的具体表达式为： 其中，g为多电平变换器的代价函数为k+Ι时刻第j个控制变量参考值,XjP(k+l) 为k+Ι时刻不同开关状态组合下的第j个控制变量的输出预测值,3为第j个控制变量对应 的权重系数,η为控制变量的数量。 3 .如权利要求1所述的热应力平衡预测控制方法，其特征在于，所述步骤2中，以k时刻 多电平变换器输出总电平H(k)前后邻近的Z个电平状态作为有限控制集,k+Ι时刻输出总电 平Η (k+Ι)在有限控制集的约束为： H (k+1) e {H(k) -Z,H(k) -Z+1,…，H(k)，…，H (k)+ZT ,H(k)+Z} 其中，H(k) =Q] (k) +---+Qi (k) +…+Qk) (k)为第i个模块在k时刻的输出电平,m为多 电平变换器的模块总数量,Qj (k) = 1,0, -1。 4 .如权利要求1所述的热应力平衡预测控制方法，其特征在于，所述步骤3中，k+Ι时刻 能动作的模块的选出方法为： 当电平增量AH〉O时，从当前输出电平Q (k)为或者0的模块中选出能动作的模块；当 电平增量AH〈O时，从当前输出电平Q (k)为1或者0的模块中选出能动作的模块；当电平增 量AH=O时，下一时刻输出电平必(k+Ι)与当前输出电平必(k)保持一致，各个模块中功率器 件在下一时刻的状态与在当前时刻的状态保持一致。 5 .如权利要求1所述的热应力平衡预测控制方法，其特征在于，所述步骤5中，需要动作 的模块的选出方法为： 步骤5.1：在每一控制周期，计算出所有能动作的模块的开关分配函数值； 步骤5.2:对计算出的开关分配函数值进行排序， 步骤5.3:从开关分配函数值序列的最大值开始，选取与开关分配函数值对应的） Δ H ¦ 个模块作为k+1时刻需要动作的模块，δη为k+1时刻的电平增量； 步骤5.4：将需要动作的模块对应的开关动作次数累计值清零，将不需要动作的模块对 应的开关动作次数累计值继续累加计数。 6 .如权利要求1所述的热应力平衡预测控制方法，其特征在于，所述步骤6中，电平增量 分配至需要动作的模块的具体桥臂的具体方法为:每个模块的桥臂包括左桥臂和右桥臂， 对第i个模块引入状态标志位flagi； 如果flagi = 1,则优先对第i个模块的左桥臂或右桥臂的开关状态进行判定，如果左桥 臂或右桥臂的开关能动作，则根据电平增量动作左桥臂或右桥臂，如果左桥臂或右桥臂的 开关不能动作，则根据电平增量动作右桥臂或左桥臂； 如果flagi = - 1,则优先对第i个模块的右桥臂或左桥臂的开关状态进行判定,如果右 桥臂或左桥臂的开关能动作，则根据电平增量动作右桥臂或左桥臂，如果右桥臂或左桥臂 的开关不能动作，则根据电平增量动作左桥臂或右桥臂； 右桥臂或左桥臂的开关每次动作后flagi取反，以平衡每个模块左桥臂和右桥臂开关 的动作次数。 7 .一种适用于多电平变换器的热应力平衡预测控制系统，用于实现权利要求1至6任一 所述的热应力平衡预测控制方法，其特征在于，包括： 输出预测模块，用于获取多电平变换器当前时刻的控制变量输出瞬时值，并根据所述 控制变量输出瞬时值得到下一时刻不同开关状态组合下的控制变量输出预测值； 有限集开关状态寻优模块，用于在有限控制集的约束下，根据给定的下一时刻的控制 变量参考值和所述控制变量输出预测值得到下一时刻的输出总电平和下一时刻的电平增 量； 电压电流采集模块，用于采集每个模块功率器件的导通电压和电流； 结温估算模块，用于根据每个模块功率器件的导通电压和电流估算出每个模块功率器 件的结温值； 开关分配函数计算模块，用于获取每个模块当前时刻的开关动作次数累计值，并根据 每个模块的功率器件结温值和开关动作次数累计值得到每个模块的开关分配函数值； 开关状态分配模块，用于将所有模块的开关分配函数值进行排序，并根据下一时刻的 电平增量从开关分配函数值的最大值开始选出下一时刻需要动作的模块； 开关动作桥臂分配模块，用于将下一时刻的电平增量分配至需要动作的模块的需要动 作的桥臂。 [EN CN110729911B]: L. A thermal stress balance predictive control method suitable for multi-level converters, which is characterized by including the following steps: Step 1: Collect the instantaneous value of the control variable output of the multi-level converter at time k, and output the control variable from the control variable. The instantaneous value obtains the predicted output value of the control variable under different switch state combinations at k+1; Step 2: Set the reference value of the control variable at k+1, and predict the output according to the reference value of the control variable at k+1 and the control variable in step 1 The cost function is constructed by the value of the finite control set, and the total level corresponding to the minimum cost function is taken as the optimal output total level at k +1, and the level increment in the optimal state at k+1 is obtained Step 3: Select the modules that can act at k+1 according to the level increment of Step 2. Step 4: Collect the conduction voltage and current of each power device, and estimate the power of each module from the conduction voltage and current The junction temperature value of the device; Step 5: Construct the switch distribution function of the module according to the junction temperature value of Step 4, and select the module that needs to act at k+1 according to the switch distribution function of each module from the active modules in Step 3; Step 6: Allocate the level increment of step 2 to the specific bridge arm of the module to be actuated to achieve the balance of the thermal stress of the multiple modules; in the step 5, the specific expression of the switch allocation function of the i-th module is c^ky=c^iky+ac^k) Among them, q (k) is the switch allocation function of the i-th module at time k, c: (outside is the switch of the i-th module at time ο to k The cumulative value of the number of actions,. Steam left) is the junction temperature value of the power device of the i-th module at time k, and α is the distribution factor. 2 The thermal stress balance predictive control method according to claim 1, wherein in the step 2, the specific expression of the cost function is: where g is the cost function of the multilevel converter at the time k+1 The reference value of the jth control variable, XjP(k+l) is the predicted output value of the jth control variable under different switch state combinations at k+1, 3 is the weight coefficient corresponding to the jth control variable, and η is the control The number of variables. 3 The thermal stress balance predictive control method according to claim 1, characterized in that, in the step 2, the Z level states before and after the total output level H(k) of the multilevel converter at time k are taken as For a finite control set, the total output level Η (k+1) at k+1 is restricted to the finite control set: H (k+1) e {H(k) -Z,H(k) -Z+1,..., H(k),..., H (k)+ZT ,H(k)+Z} where, H (k) =Q) (k) +---+Qi (k) +...+Qk) (k) is the output level of the i-th module at time k, m is the total number of modules of the multilevel converter, and Qj (k) = 1,0, -1. 4 The thermal stress balance predictive control method according to claim 1, characterized in that, in the step 3, the method for selecting the modules that can operate at k+1 is: when the level increment AH&gt;0, from The active module is selected from the modules with the current output level Q (k) of or 0; when the level increment AH&lt;0, the active module is selected from the modules with the current output level Q (k) of 1 or 0 Action module; when the level increment AH=O, the output level (k+1) at the next moment must be consistent with the current output level (k), and the state of the power devices in each module at the next moment is consistent with that at the next moment. The current state remains the same. 5 The thermal stress balance predictive control method of claim 1, wherein in step 5, actions are required The method for selecting the modules is: Step 5.1: In each control cycle, calculate the switch assignment function values of all modules that can act; Step 5.2: Sort the calculated switch assignment function values, Step 5.3: Assign from the switch Start with the maximum value of the function value sequence, and select the corresponding switch distribution function value) Δ H ¦ modules as the modules that need to be acted upon at k+1, and δη is the level increment at k+1; Step 5.4: Action will be required The cumulative value of the number of switching operations corresponding to the module is cleared to zero, and the cumulative value of the number of switching operations corresponding to the modules that do not need to be activated continues to be counted. 6 The thermal stress balance predictive control method according to claim 1, characterized in that, in the step 6, the specific method for allocating the level increment to the specific bridge arm of the module that needs to be operated is: the bridge arm of each module Including the left bridge arm and the right bridge arm, introduce the status flag flagi to the i-th module; if flagi = 1, the switch state of the left bridge arm or the right bridge arm of the i-th module is judged first, if the left bridge arm Or the switch of the right bridge arm can act, the left bridge arm or the right bridge arm is actuated according to the level increment, if the switch of the left bridge arm or the right bridge arm cannot act, the right bridge arm or the left bridge arm is actuated according to the level increment Arm; if flagi =-1, the switch state of the right or left bridge arm of the i-th module will be judged first. If the switch of the right bridge arm or the left bridge arm can act, the right bridge arm or left bridge arm can be actuated according to the level increment. For bridge arm or left bridge arm, if the switch of right bridge arm or left bridge arm cannot be operated, the left bridge arm or right bridge arm will be actuated according to the level increment; the switch of right bridge arm or left bridge arm will take flagi after each action On the contrary, in order to balance the number of actions of the left bridge arm and the right bridge arm switch of each module. 7 A thermal stress balance predictive control system suitable for multi-level converters for realizing the thermal stress balance predictive control method of any one of claims 1 to 6, characterized in that it comprises: an output predictive module for Obtain the control variable output instantaneous value of the multilevel converter at the current moment, and obtain the control variable output predicted value under different switch state combinations at the next moment according to the control variable output instantaneous value; a finite set switch state optimization module for Under the constraint of the limited control set, obtain the total output level at the next time and the level increment at the next time according to the given reference value of the control variable at the next time and the predicted output value of the control variable; voltage and current acquisition module , Used to collect the conduction voltage and current of each module power device; Junction temperature estimation module, used to estimate the junction temperature value of each module power device according to the conduction voltage and current of each module power device; Switch distribution function The calculation module is used to obtain the cumulative value of the switching operation times of each module at the current moment, and obtain the switch distribution function value of each module according to the power device junction temperature value of each module and the cumulative value of the switching operation times; the switching state distribution module, It is used to sort the switch distribution function values of all modules, and select the modules that need to act at the next moment from the maximum value of the switch distribution function value according to the level increment at the next moment; switch action bridge arm distribution module, use To allocate the level increment at the next moment to the bridge arm of the module that needs to be moved. | [ZH CN110729911B]: 适用于多电平变换器的热应力平衡预测控制方法及系统 技术领域 [0001]本发明属于电力电子变换器控制技术，尤其涉及一种适用于多电平变换器的热应 力平衡预测控制方法及系统。 背景技术 [0002]随着我国经济的逐渐发展，对中高压、大功率变流器的需求量逐渐增加，对其容量 的需求甚至达到了上百MVA。然而由于电力电子器件自身的耐压等级及容量有所限制，传统 的两电平变换器在很多情况下已经不能满足现有的工业需求。为了提高电力电子装置处理 较大功率的能力，多电平变换器受到学术界的广泛关注，各国学者开展了大量研究工作。多 电平变换器是一种从拓扑结构入手的新型高压大功率变流器，它不仅可以得到高质量的输 出波形，还能克服很多传统两电平变流器的不足，无需动态均压电路以及输出端变压器。多 电平变换器通过改变其自身的拓扑结构，将多个功率器件连接起来，输出更多台阶的阶梯 波，输出波形更加接近正弦波，可以实现中高压、大容量、高性能的需求。 [0003]多电平变换器具有良好的输出性能，除了输出性能之外，可靠性通常是变换器的 一个非常重要的设计标准，特别是对于接入环境受限的特殊应用场合，比如高温高压环境、 军舰和密闭舱等。关于可靠性，功率半导体是变换器中最敏感的部件之一，其寿命周期主要 是受热循环幅值和平均结温值影响的。然而，由于在复杂的输出任务下多电平变换器电气 参数和控制变量的不平衡，模块之间存在热不平衡的问题。长期处于高结温的模块损坏的 可能性更高，可能会导致整个装置甚至系统崩溃，严重降低系统运行可靠性。对设备的正常 运行造成了重大威胁，所以在多模块之间进行合理的热应力管理具有重要意义。 [0004]当前，考虑热应力的控制策略按照所处的运行层次可分为功率器件层、换流器调 制层、换流器控制层和系统控制层四类。功率器件层热应力控制主要是通过调整功率器件 开关轨迹和控制导通压降来降低热应力，比如改变驱动电压、驱动电阻、开通/关断延迟时 间等。目前已应用于减小并联器件热应力不均、抑制风电变流器结温波动等场合，虽然通用 性强，然而该方法通常需要增加额外的硬件电路。换流器调制层热应力控制是通过改变调 制方法来改变功率器件的开关序列，进而对器件损耗进行改善的方法，该方法借助换流器 特有的冗余开关状态实现热优化，无需增加额外电路，工程应用价值高，但是通常只能用于 特定拓扑。变换器控制层热应力控制是通过调整与结温相关的状态变量来对热应力进行优 化，比如开关频率，输出功率和直流侧电压等，但是其热控制目标与其他控制目标较难兼 容，热应力控制通常会影响输出效果。系统控制层热应力控制是利用系统中不同装置的互 补运行特性，协调各装置控制目标，在保证系统整体性能不变的前提下，优化换流器中器件 的热应力，该方法利用系统之间不同装置的互补特性，对系统整体成本和输出性能影响较 小，是一种理想的热控制策略，但是其通用性较差，难以应用于单独使用的变换器。 [0005]上述所提热应力控制策略多是基于损耗优化或结温平滑的方式，通过减少功率器 件的热应力或者减少热摆幅以改善热性能，对于多电平变换器模块之间热应力平衡问题的 研究相对较少。 CN 110729911 B 说明 书 发明内容 [0006]针对现有技术的不足，本发明提供一种适用于多电平变换器的热应力平衡预测控 制方法及系统，在保证输出精度的同时，平衡模块之间的热应力，均衡模块的老化速度，使 整个装置的寿命最大化。 [0007] 本发明是通过如下的技术方案来解决上述技术问题的：一种适用于多电平变换器 的热应力平衡预测控制方法，包括以下步骤： [0008]步骤1：采集多电平变换器在k时刻的控制变量输出瞬时值，由该控制变量输出瞬 时值得到k+Ι时刻不同开关状态组合下的控制变量输出预测值； [0009] 步骤2：设定k+Ι时刻控制变量参考值，根据k+Ι时刻控制变量参考值和步骤1的控 制变量输出预测值构建代价函数，在有限控制集的约束下，以代价函数最小对应的总电平 作为k+Ι时刻的最优输出总电平,并得到k+Ι时刻最优状态下的电平增量； [0010]步骤3：根据步骤2的电平增量选出k+Ι时刻能动作的模块； [0011]步骤4：采集各功率器件的导通电压和电流，由所述导通电压和电流估算出各模块 功率器件的结温值； [0012]步骤5：根据步骤4的结温值构建模块的开关分配函数，根据每个模块的开关分配 函数在步骤3能动作的模块中选出k+Ι时刻需要动作的模块； [0013]步骤6：将步骤2的电平增量分配至需要动作的模块的具体桥臂，以实现多模块热 应力的平衡。 [0014]本发明所述热应力平衡预测控制方法,先根据控制变量参考值和控制变量输出预 测值来构建代价函数，通过有限控制集来选择最优的输出总电平，并确定电平增量,然后根 据电平增量确定能动作的模块，实现模块的开关状态分配，最后根据结温值构建开关分配 函数，确定需要动作的模块;该控制方法中代价函数根据输出预测值来设计，且无修正，保 证了输出精度;开关分配函数以用于反应各模块热应力的结温值为设计依据，通过开关分 配函数确定模块的开关状态，达到了多模块热应力平衡的效果，减少了多电平变换器的损 耗,增加了可靠性和使用寿命,简化了散热设计难度。 [0015] 进一步地，所述步骤2中，代价函数的具体表达式为： [0016] g = £% 区(左+1)-χ/(及+1)¦ 7=1 [0017]其中，g为多电平变换器的代价函数，芯(左+1)为k+Ι时刻第j个控制变量参考值,XjP (k+1)为k+1时刻不同开关状态组合下的第j个控制变量的输出预测值,3为第j个控制变量 对应的权重系数,η为控制变量的数量。 [0018]该代价函数是根据控制变量参考值和控制变量输出预测值直接得到的，并无修 正,保证了多电平变换器的输出精度。 [0019] 进一步地，所述步骤2中，以k时刻多电平变换器输出总电平H (k)前后邻近的Ζ个电 平状态作为有限控制集,k+Ι时刻输出总电平Η(k+Ι)在有限控制集的约束为： [0020] H (k+1) e {H(k) -Z,H(k) -Z+l, ··· ,H (k) , ··· ,H (k)+Z-1 ,H (k)+Z) [0021] 其中，H(k) =Qjk)+…+Qjk)+…+Qk) ,Qj(k)为第i个模块在k时刻的输出电平,m 为多电平变换器的模块总数量,Qj (k) = 1,0, -1。 [0022] 进一步地，所述步骤3中，k+1时刻能动作的模块的选出方法为： [0023]当电平增量AH〉0时，从当前输出电平Q (k)为-1或者0的模块中选出能动作的模 块;当电平增量ΑΗ〈0时，从当前输出电平必(k)为1或者0的模块中选出能动作的模块；当电 平增量ΑΗ=0时，下一时刻输出电平必(k+1)与当前输出电平必(k)保持一致,各个模块中功 率器件在下一时刻的状态与在当前时刻的状态保持一致。 [0024]进一步地，所述步骤5中，第i个模块的开关分配函数的具体表达式为 [0025] = [0026]其中，q (k)为第i个模块在k时刻的开关分配函数，6(外为第i个模块在ο到k时 刻开关的动作次数累计值，为第i个模块在k时刻功率器件的结温值,α为分配因子。 [0027]模块的开关分配函数包括两个部分，一个部分是模块开关的动作次数累计值，反 映了模块的开关动作频率，保证了各模块开关动作频率均匀，另一个部分为与热应力相关 的结温值，通过结温值来进行多模块的开关分配，保证了各模块的热应力平衡;增加分配因 子α,使⑹和&amp;号⑹保持在同一数量级，以更好地反映(幻和C?⑹对多模块之间热 应力的平衡作用。 [0028]进一步地，所述步骤5中，需要动作的模块的选出方法为： [0029]步骤5.1：在每一控制周期,计算出所有能动作的模块的开关分配函数值； [0030]步骤5.2 :对计算出的开关分配函数值进行排序， [0031]步骤5.3：从开关分配函数值序列的最大值开始，选取与开关分配函数值对应的 AHI个模块作为k+Ι时刻需要动作的模块，ΑΗ为k+Ι时刻的电平增量； [0032]步骤5.4：将需要动作的模块对应的开关动作次数累计值清零，将不需要动作的模 块对应的开关动作次数累计值继续累加计数。 [0033]进一步地，所述步骤6中，电平增量分配至需要动作的模块的具体桥臂的具体方法 为:每个模块的桥臂包括左桥臂和右桥臂，对第i个模块引入状态标志位flagi ； [0034]如果flagi = 1,则优先对第i个模块的左桥臂或右桥臂的开关状态进行判定,如果 左桥臂或右桥臂的开关能动作，则根据电平增量动作左桥臂或右桥臂，如果左桥臂或右桥 臂的开关不能动作，则根据电平增量动作右桥臂或左桥臂； [0035]如果flagi = - 1,则优先对第i个模块的右桥臂或左桥臂的开关状态进行判定,如 果右桥臂或左桥臂的开关能动作，则根据电平增量动作右桥臂或左桥臂，如果右桥臂或左 桥臂的开关不能动作，则根据电平增量动作左桥臂或右桥臂； [0036]右桥臂或左桥臂的开关每次动作后flagi取反，以平衡每个模块左桥臂和右桥臂 开关的动作次数。 [0037]相应的，一种适用于多电平变换器的热应力平衡预测控制系统，用于实现所述热 应力平衡预测控制方法,包括： [0038]输出预测模块，用于获取多电平变换器当前时刻的控制变量输出瞬时值,并根据 所述控制变量输出瞬时值得到下一时刻不同开关状态组合下的控制变量输出预测值； [0039]有限集开关状态寻优模块，用于在有限控制集的约束下，根据给定的下一时刻的 控制变量参考值和所述控制变量输出预测值得到下一时刻的输出总电平和下一时刻的电 平增量； [0040]电压电流采集模块,用于采集每个模块功率器件的导通电压和电流； [0041]结温估算模块，用于根据每个模块功率器件的导通电压和电流估算出每个模块功 率器件的结温值； [0042]开关分配函数计算模块，用于获取每个模块当前时刻的开关动作次数累计值，并 根据每个模块的功率器件结温值和开关动作次数累计值得到每个模块的开关分配函数值； [0043]开关状态分配模块，用于将所有模块的开关分配函数值进行排序,并根据下一时 刻的电平增量从开关分配函数值的最大值开始选出下一时刻需要动作的模块； [0044]开关动作桥臂分配模块,用于将下一时刻的电平增量分配至需要动作的模块的需 要动作的桥臂。 [0045] 有益效果 [0046]与现有技术相比，本发明提出的一种适用于多电平变换器的热应力平衡预测控制 方法,先根据控制变量参考值和控制变量输出预测值来构建代价函数，通过有限控制集来 选择最优的输出总电平，并确定电平增量，然后根据电平增量确定能动作的模块，实现模块 的状态分配，最后根据结温值设计开关分配函数,确定需要动作的模块，将电平增量分配到 需要动作的模块;该控制方法中代价函数根据输出预测值来设计，且无修正,保证了输出精 度;开关分配函数以用于反应各模块热应力的结温值为设计依据，通过开关分配函数确定 模块的开关状态，达到了多模块热应力平衡的效果，均衡各模块的老化速度,减少了多电平 变换器各模块的损耗，增加了可靠性和使用寿命,简化了散热设计难度。 附图说明 [0047]为了更清楚地说明本发明的技术方案,下面将对实施例描述中所需要使用的附图 作简单地介绍，显而易见地，下面描述中的附图仅仅是本发明的一个实施例，对于本领域普 通技术人员来说，在不付出创造性劳动的前提下，还可以根据这些附图获得其他的附图。 [0048]图1是本发明实施例中热应力平衡预测控制方法的流程图； [0049]图2是本发明实施例中多电平变换器模块的四种输出电平状态； [0050]图3是本发明实施例中热应力平衡预测控制系统的控制原理图。 具体实施方式 [0051]下面结合本发明实施例中的附图，对本发明中的技术方案进行清楚、完整地描述, 显然，所描述的实施例仅仅是本发明一部分实施例,而不是全部的实施例。基于本发明中的 实施例，本领域普通技术人员在没有作出创造性劳动的前提下所获得的所有其他实施例， 都属于本发明保护的范围。 [0052]如图1所示，本发明所提供的一种适用于多电平变换器的热应力平衡预测控制方 法，包括以下步骤： [0053] 1、采集多电平变换器在k时刻的第j个控制变量输出瞬时值xjk），根据多电平变 换器的数学模型，由Xj （k）得到k+1时刻不同开关状态组合下的第j个控制变量输出预测值 疗（什1）。 [0054]如图2所示，每个模块有四种不同开关状态，单个桥臂上、下两个功率器件只有一 个可以导通，其中，上管导通、下管关断表示该桥臂状态为1,下管导通、上管关断表示该桥 臂状态为0。多电平变换器由多个模块组成,则对应有多种不同的开关状态组合，在不同开 关状态组合下，多电平变换器的输出总电平不同。 [0055]设第i个模块的左半桥状态记为一，右半桥状态记为B2J第i个模块的输出电平 为必,则具有η个模块的多电平变换器的输出总电平Η为： [0056] H=Q1+Q2+---+0/1) [0057]其中， , ^H-ί ~ 1，Β ° [0058] - - 0, B2U - B2i ¢2) -1, %.产0且=1 [0059]不同类型的多电平变换器的数学模型是不同的，多电平变换器的数学模型的构建 方法为现有技术，例如，级联Η桥型多电平变换器的数学模型的构建方法可以参考:丁红旗. 模块化多电平功率放大器的研究及装置研制[D].湖南大学,2018。 [0060] 2、设k+Ι时刻的第j个控制变量参考值为X； (k+1)，由x：(计1)和XjP(k+l)构建多电 平变换器的代价函数，在有限控制集的约束下，以代价函数最小对应的总电平作为k+Ι时刻 的最优输出总电平,并得到k+Ι时刻最优状态下的电平增量。 [0061]代价函数的具体表达式为： [0062]且=汽%卜；(左+1)-吃«左+1)¦ (3) [0063]其中，g为多电平变换器的代价函数，¥依+D为k+Ι时刻第j个控制变量的参考值， XjP (k+Ι)为k+Ι时刻不同开关状态组合下的第j个控制变量的输出预测值为第j个控制变 量对应的权重系数(3根据经验来设置)，η为控制变量的数量。该代价函数是根据控制变量 参考值和控制变量输出预测值直接得到的，并无修正,保证了多电平变换器的输出精度。 [0064]以k时刻多电平变换器输出总电平H(k)前后邻近的Ζ个电平状态作为有限控制集， k+Ι时刻输出总电平Η (k+Ι)在有限控制集的约束为： [0065] H(k+1) e {H(k)-Z,H(k)-Z+1,…，H(k),…，H(k)+ZT,H(k)+Z} (4) [0066] 其中，H(k) =Qjk)+…+Qjk)+…+Qk) ,Qj(k)为第i个模块在k时刻的输出电平,m 为多电平变换器的模块总数量,Qj (k) = 1,0, -1。 [0067]在有限控制集的约束下，以代价函数g最小为优化目标,代价函数最小值对应的总 电平作为k+Ι时刻的输出总电平Η (k+Ι),根据Η (k+Ι)和口(女)得至以+1时刻的电平增量八出Δ H=H(k+l) -H(k),且 ΑΗ© (-Ζ,Ζ)。 [0068] 3、根据电平增量A Η选出k+1时刻能动作的模块。 [0069]当电平增量ΑΗ〉0时，此时当前输出电平Q (k)为1的模块不能再增加电平了，从当 前输出电平必(k)为或者0的模块中选出能动作的模块；当电平增量ΑΗ〈0时，此时当前输 出电平必(k)为-1的模块不能再减小电平了，从当前输出电平必(k)为1或者0的模块中选出 能动作的模块;当电平增量ΑΗ=0时，下一时刻输出电平必(k+Ι)与当前输出电平Qj(k)保持 一致，各个模块中功率器件在下一时刻的状态与在当前时刻的状态保持一致。 [0070] 4、采集各模块功率器件的导通电压和电流，由导通电压和电流估算出各模块功率 器件的结温值。 [0071]功率器件的结温值与热应力相关，反映了各模块的平均结温，通过功率器件的结 温值来构建开关分配函数，再根据开关分配函数来进行各模块开关状态的分配，保证了各 模块之间的热应力平衡。功率器件的结温值的估算为现有技术，可参考Ahmed Μ M R, Putrus G A.Amethod for predicting IGBT junction temperature under transient condition[C]//Conference of the IEEE Industrial Electronics Society. IEEE, 2008o [0072] 5、获取各模块当前时刻的开关动作次数累计值，根据开关动作次数累计值和功率 器件的结温值构建每个模块的开关分配函数，根据每个模块的开关分配函数在能动作的模 块中选出k+Ι时刻需要动作的模块，且需要动作的模块的数量等于电平增量的绝对值。第i 个模块的开关分配函数的具体表达式为 [0073] G㈤=c}㈤+如方㈤ （5 ） [0074]其中，q （k）为第i个模块在k时刻的开关分配函数，CT（行为第i个模块在ο到k时 刻开关的动作次数累计值，为第i个模块在k时刻功率器件的结温值,α为分配因子。分 配因子α采用试错法或根据经验来设置，采用试错法来确定的具体过程为：令α的初值为 £。“（专）/ C汽q ,观察热应力平衡的效果，如果效果较差,则换为α初值的邻近值，直到热应力 平衡的效果较好位置。 [0075]每个模块的开关分配函数均包括两个部分,一个部分是模块开关的动作次数累计 值Ch（左），反映了模块的开关动作频率，保证了各模块开关动作频率均匀，另一个部分为与 热应力相关的结温值G7体），通过结温值来进行多模块的开关分配,保证了各模块的热应 力平衡；增加的分配因子α,使CT （外和保持在同一数量级，以更好地反映和 C?（行对多模块之间热应力的平衡作用。 [0076]需要动作的模块的选出方法为： [0077] 5.1：在每一控制周期,计算出所有能动作的模块的开关分配函数值； [0078] 5.2 ：对计算出的开关分配函数值进行从大到小排序， [0079] 5.3：从开关分配函数值序列的最大值开始，选取与开关分配函数值对应的¦ AH 个模块作为k+Ι时刻需要动作的模块，A Η为k+Ι时刻的电平增量； [0080] 5.4：将需要动作的模块对应的开关动作次数累计值印（左） 清零，将不需要动作的 模块对应的开关动作次数累计值继续累加计数。 [0081] 6、将电平增量A Η分配至需要动作的模块的具体桥臂，以实现多模块热应力的平 衡。每个模块的桥臂包括左桥臂和右桥臂，对第i个模块引入状态标志位flagi,通过状态标 志位判断优先对模块的哪个桥臂进行开关状态判定： [0082]如果flagi = 1,则优先对第i个模块的左桥臂的开关状态进行判定,如果左桥臂的 开关能动作，则根据电平增量动作左桥臂,如果左桥臂的开关不能动作，则根据电平增量动 作右桥臂；如果flagi = - 1,则优先对第i个模块的右桥臂的开关状态进行判定,如果右桥 臂的开关能动作,则根据电平增量动作右桥臂，如果右桥臂的开关不能动作,则根据电平增 量动作左桥臂。 [0083]或者：如果flagi = 1,则优先对第i个模块的右桥臂的开关状态进行判定,如果右 桥臂的开关能动作，则根据电平增量动作右桥臂,如果右桥臂的开关不能动作，则根据电平 增量动作左桥臂；如果flagi = - 1,则优先对第i个模块的左桥臂的开关状态进行判定,如 果左桥臂的开关能动作,则根据电平增量动作左桥臂,如果左桥臂的开关不能动作,则根据 电平增量动作右桥臂。 [0084]右桥臂或左桥臂的开关每次动作后flagi取反，以平衡每个模块左桥臂和右桥臂 开关的动作次数。 [0085]如图3所示，一种适用于多电平变换器的热应力平衡预测控制系统，用于实现所述 热应力平衡预测控制方法，包括： [0086]输出预测模块1,用于获取多电平变换器6当前时刻的第j个控制变量输出瞬时值 Xj (k),并根据第j个控制变量输出瞬时值Xj (k)得到下一时刻不同开关状态组合下的第j个 控制变量输出预测值XjP (k+1)； [0087]有限集开关状态寻优模块2,用于在有限控制集的约束下，根据给定的下一时刻的 第j个控制变量参考值为X； (k+Ι)和第j个控制变量输出预测值刈'(左+1)得到下一时刻的输 出总电平H (k+1)和下一时刻的电平增量A Η； [0088]电压电流采集模块3,用于采集每个模块功率器件的导通电压和电流； [0089]结温估算模块4,用于根据每个模块功率器件的导通电压和电流估算出每个模块 功率器件的结温值(左)； [0090]开关分配函数计算模块5,用于获取每个模块当前时刻的开关动作次数累计值 £“*/)，并根据每个模块的功率器件结温值£号(外和开关动作次数累计值。门(左)得到每个 模块的开关分配函数值q (k)； [0091]开关状态分配模块6，用于将所有模块的开关分配函数值J (k)进行排序,并根据 下一时刻的电平增量A Η从开关分配函数值的最大值开始选出下一时刻需要动作的模块； [0092]开关动作桥臂分配模块7,用于将下一时刻的电平增量ΑΗ分配至需要动作的模块 的需要动作的桥臂。 [0093]多电平变换器8根据下一时刻各模块左、右桥臂的动作情况来控制其功率器件的 动作而达到控制效果，整个控制系统为一个闭环控制，可以达到多模块热应力平衡的效果, R为负载,Xj为控制变量。 [0094]以上所揭露的仅为本发明的具体实施方式，但本发明的保护范围并不局限于此, 任何熟悉本技术领域的技术人员在本发明揭露的技术范围内，可轻易想到变化或变型，都 应涵盖在本发明的保护范围之内。 [EN CN110729911B]: Technical field of thermal stress balance predictive control method and system suitable for multilevel converter [0001] The present invention belongs to power electronic converter control technology, and in particular relates to a thermal stress balance predictive control method and system suitable for multilevel converters. Background technique [0002] With the gradual development of my country's economy, the demand for medium and high voltage and high power converters has gradually increased, and the demand for its capacity has even reached hundreds of MVA. However, due to the limitation of the withstand voltage level and capacity of the power electronic devices, the traditional two-level converters can no longer meet the existing industrial needs in many cases. In order to improve the ability of power electronic devices to handle larger power, multilevel converters have received extensive attention from the academic community, and scholars from various countries have carried out a lot of research work. The multi-level converter is a new type of high-voltage high-power converter starting from the topology. It can not only get high-quality output waveforms, but also overcome the shortcomings of many traditional two-level converters without the need for dynamic voltage equalization circuits. And the output transformer. The multi-level converter changes its topological structure to connect multiple power devices to output a step wave with more steps, and the output waveform is closer to a sine wave, which can meet the needs of medium and high voltage, large capacity, and high performance. [0003] Multilevel converters have good output performance. In addition to output performance, reliability is usually a very important design criterion for converters, especially for special applications where the access environment is limited, such as high temperature and high pressure. Environment, warships and airtight cabins, etc. Regarding reliability, the power semiconductor is one of the most sensitive components in the converter, and its life cycle is mainly affected by the thermal cycle amplitude and the average junction temperature. However, due to the imbalance of the electrical parameters and control variables of the multilevel converter under complex output tasks, there is a problem of thermal imbalance between the modules. Modules that have been at a high junction temperature for a long time are more likely to be damaged, which may cause the entire device or even the system to crash, and seriously reduce the reliability of system operation. It poses a major threat to the normal operation of the equipment, so it is of great significance to conduct reasonable thermal stress management among multiple modules. [0004] Currently, control strategies that consider thermal stress can be divided into four categories: power device layer, converter modulation layer, converter control layer, and system control layer according to the operating level. The thermal stress control of the power device layer mainly reduces the thermal stress by adjusting the switching trajectory of the power device and controlling the turn-on voltage drop, such as changing the driving voltage, driving resistance, and turn-on/turn-off delay time. At present, it has been applied to reduce the uneven thermal stress of parallel devices and suppress the fluctuation of the junction temperature of wind power converters. Although it has strong versatility, this method usually requires the addition of additional hardware circuits. The thermal stress control of the converter modulation layer is a method of changing the switching sequence of the power device by changing the modulation method, and then improving the device loss. This method uses the unique redundant switching state of the converter to achieve thermal optimization without adding additional circuits. , High engineering application value, but usually only used for specific topologies. The thermal stress control of the converter control layer optimizes the thermal stress by adjusting the state variables related to the junction temperature, such as switching frequency, output power, and DC side voltage. However, its thermal control target is difficult to be compatible with other control targets. Stress control usually affects the output effect. The thermal stress control of the system control layer uses the complementary operating characteristics of different devices in the system to coordinate the control objectives of each device, and optimizes the thermal stress of the components in the converter under the premise of ensuring the overall performance of the system. The complementary characteristics of different devices have a greater impact on the overall cost and output performance of the system. Small is an ideal thermal control strategy, but its versatility is poor and it is difficult to apply to a stand-alone converter. [0005] The thermal stress control strategies mentioned above are mostly based on loss optimization or junction temperature smoothing, which improves thermal performance by reducing the thermal stress of the power device or reducing the thermal swing. For the thermal stress between the multi-level converter modules There are relatively few studies on balance issues. CN 110729911 B Description of the invention [0006] In view of the shortcomings of the prior art, the present invention provides a thermal stress balance predictive control method and system suitable for multi-level converters. While ensuring the output accuracy, the thermal stress between modules is balanced and the modules thermal stress is balanced. The aging speed maximizes the life of the entire device. [0007] The present invention solves the above technical problems through the following technical solutions: a thermal stress balance predictive control method suitable for multi-level converters, including the following steps: [0008] Step 1: Collect the instantaneous value of the control variable output of the multilevel converter at time k, and obtain the predicted output value of the control variable under different switch state combinations at k+1 from the instantaneous value of the control variable output; [0009] Step 2: Set the reference value of the control variable at time k+1, construct a cost function based on the reference value of the control variable at time k+1 and the predicted value of the control variable output in step 1, and under the constraint of the limited control set, use the cost function The minimum corresponding total level is taken as the optimal output total level at k+1, and the level increment in the optimal state at k+1 is obtained; [0010] Step 3: According to the level increment of step 2, select the module that can act at k+1; [0011] Step 4: Collect the conduction voltage and current of each power device, and estimate the junction temperature value of each module power device from the conduction voltage and current; [0012] Step 5: Construct the switch allocation function of the module according to the junction temperature value of step 4, and select the module that needs to be acted at k+1 from the actionable modules in step 3 according to the switch allocation function of each module; [0013] Step 6: Allocate the level increment of step 2 to the specific bridge arms of the module that needs to be actuated to achieve the balance of the thermal stress of the multiple modules. [0014] The thermal stress balance predictive control method of the present invention first constructs a cost function according to the reference value of the control variable and the predicted value of the control variable output, selects the optimal total output level through a limited control set, and determines the level increase Then determine the active module according to the level increment, realize the switch state distribution of the module, and finally construct the switch distribution function according to the junction temperature value to determine the module that needs action; in the control method, the cost function is designed according to the output predicted value, And without correction, the output accuracy is guaranteed; the switch distribution function is based on the design basis of the junction temperature used to reflect the thermal stress of each module, and the switch state of the module is determined by the switch distribution function, which achieves the effect of multi-module thermal stress balance and reduces The loss of the multilevel converter increases the reliability and service life, and simplifies the difficulty of heat dissipation design. [0015] Further, in the step 2, the specific expression of the cost function is: [0016] g = £% area (left+1)-χ/(and +1)¦ 7=1 [0017] Among them, g is the cost function of the multilevel converter, core (left+1) is the reference value of the j-th control variable at k+1, and XjP (k+1) is the combination of different switch states at k+1 The output predicted value of the jth control variable below, 3 is the weight coefficient corresponding to the jth control variable, and η is the number of control variables. [0018] The cost function is directly obtained according to the reference value of the control variable and the predicted value of the output of the control variable without correction, which ensures the output accuracy of the multilevel converter. [0019] Further, in the step 2, the multilevel converter outputs the Z level states before and after the total level H (k) at the time k as the finite control set, and the total level H is output at the time k+1. (k+1) The constraints on the finite control set are: [0020] H (k+1) e {H(k) -Z,H(k) -Z+1, ··· ,H (k), ··· ,H (k)+Z-1 ,H (k)+Z) [0021] Among them, H(k)=Qjk)+...+Qjk)+...+Qk), Qj(k) is the output level of the i-th module at time k, and m is the total number of modules of the multilevel converter Quantity, Qj (k) = 1,0, -1. [0022] Further, in the step 3, the method for selecting modules that can operate at k+1 is: [0023] When the level increment AH&gt;0, select an actionable module from the modules whose current output level Q(k) is -1 or 0; when the level increment AH&lt;0, from the current output The actionable module must be selected from the modules whose level must (k) is 1 or 0; when the level increment ΑΗ=0, the output level at the next moment must be (k+1) and the current output level must be (k ) Is consistent, the state of the power devices in each module at the next moment is consistent with the state at the current moment. [0024] Further, in the step 5, the specific expression of the switch allocation function of the i-th module is [0025] = [0026] Among them, q (k) is the switch allocation function of the i-th module at time k, 6 (externally is the cumulative value of the number of switching actions of the i-th module at time o to k, and is the i-th module at time k The junction temperature of the power device, α is the distribution factor. [0027] The switch distribution function of the module includes two parts, one part is the cumulative value of the number of switch actions of the module, which reflects the switching frequency of the module and ensures that the switching frequency of each module is uniform, and the other part is related to thermal stress. The junction temperature value, through the junction temperature value to carry out the switch distribution of the multi-module, to ensure the thermal stress balance of each module; increase the distribution factor α, so that and &amp; sign remain at the same order of magnitude to better reflect (magic and C ?Balanced effect on thermal stress among multiple modules. [0028] Further, in the step 5, the method for selecting the module that needs action is: [0029] Step 5.1: In each control cycle, calculate the switch distribution function values of all the modules that can act; [0030] Step 5.2: Sort the calculated switch allocation function values, [0031] Step 5.3: Starting from the maximum value of the switch distribution function value sequence, select AHI modules corresponding to the switch distribution function value as the modules that need to act at k+1, and AH is the level increment at k+1; [0032] Step 5.4: Clear the cumulative value of the number of switching operations corresponding to the module that needs to be operated, and continue the cumulative count of the cumulative value of the number of switching operations corresponding to the module that does not need to operate. [0033] Further, in the step 6, the specific method for allocating the level increment to the specific bridge arm of the module that needs to be acted is: the bridge arm of each module includes the left bridge arm and the right bridge arm, for the i-th bridge arm, The module introduces the status flag flagi; [0034] If flagi=1, the switch state of the left bridge arm or the right bridge arm of the i-th module is judged first. If the switch of the left bridge arm or the right bridge arm can operate, the left bridge arm or the right bridge arm can be operated according to the level increment. Bridge arm or right bridge arm, if the switch of the left bridge arm or right bridge arm cannot be moved, the right bridge arm or left bridge arm will be actuated according to the level increment; [0035] If flagi=1, the switch state of the right bridge arm or left bridge arm of the i-th module is judged first, and if the switch of the right bridge arm or left bridge arm can operate, it will act according to the level increment. Right bridge arm or left bridge arm, if the switch of the right bridge arm or left bridge arm cannot be operated, the left bridge arm or right bridge arm will be actuated according to the level increment; [0036] The flagi is reversed after each action of the switch of the right bridge arm or the left bridge arm to balance the number of actions of the left bridge arm and the right bridge arm switch of each module. [0037] Correspondingly, a thermal stress balance predictive control system suitable for multi-level converters is used to implement the thermal stress balance predictive control method, including: [0038] The output prediction module is used to obtain the instantaneous value of the control variable output of the multilevel converter at the current moment, and obtain the predicted value of the control variable output under different switch state combinations at the next moment according to the instantaneous value of the control variable output; 0039] The finite set switch state optimization module is used to obtain the total output level of the next moment and the next moment according to the given reference value of the control variable at the next moment and the predicted value of the control variable output under the constraints of the finite control set. The level increment at a moment; [0040] The voltage and current acquisition module is used to acquire the conduction voltage and current of the power device of each module; [0041] The junction temperature estimation module is used to estimate the junction temperature value of each module power device according to the conduction voltage and current of each module power device; [0042] The switch distribution function calculation module is used to obtain the cumulative value of the switching operation times of each module at the current moment, and obtain the switch distribution function value of each module according to the power device junction temperature value of each module and the cumulative value of the switching operation times [0043] The switch state distribution module is used to sort the switch distribution function values of all modules, and select the module that needs action at the next moment from the maximum value of the switch distribution function value according to the level increment at the next moment ; [0044] The switch-action bridge arm distribution module is used to distribute the level increment at the next moment to the bridge arms that need to be operated by the module that needs to be operated. [0045] Benefits [0046] Compared with the prior art, the present invention proposes a thermal stress balance predictive control method suitable for multi-level converters. First, the cost function is constructed according to the control variable reference value and the control variable output prediction value, and the cost function is limited by The control set selects the optimal total output level, and determines the level increment, and then determines the actionable module according to the level increment, realizes the state distribution of the module, and finally designs the switch distribution function according to the junction temperature value to determine the required action Module, the level increment is allocated to the module that needs action; the cost function in this control method is designed according to the output predicted value, and there is no correction to ensure the output accuracy; the switch distribution function is used to reflect the thermal stress of each module The temperature value is the design basis. The switch state of the module is determined by the switch distribution function, which achieves the effect of multi-module thermal stress balance, balances the aging speed of each module, reduces the loss of each module of the multi-level converter, and increases the reliability and The service life simplifies the difficulty of heat dissipation design. Description of the drawings [0047] In order to explain the technical solution of the present invention more clearly, the following will briefly introduce the drawings needed in the description of the embodiments. Obviously, the drawings in the following description are only one embodiment of the present invention. For those of ordinary skill in the art, without creative work, other drawings can be obtained based on these drawings. [0048] FIG. 1 is a flowchart of a thermal stress balance predictive control method in an embodiment of the present invention; [0049] FIG. 2 is the four output level states of the multilevel converter module in the embodiment of the present invention; [0050] FIG. 3 is a control principle diagram of a thermal stress balance predictive control system in an embodiment of the present invention. Detailed ways [0051] The following describes the technical solutions of the present invention clearly and completely with reference to the accompanying drawings in the embodiments of the present invention. Obviously, the described embodiments are only a part of the embodiments of the present invention, rather than all the embodiments. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0052] As shown in FIG. 1, a thermal stress balance predictive control method suitable for multilevel converters provided by the present invention includes the following steps: [0053] 1. Collect the output instantaneous value xjk of the j-th control variable of the multilevel converter at time k, and obtain the combination of different switch states at k+1 from Xj(k) according to the mathematical model of the multilevel converter The next j-th control variable outputs the predicted value of treatment (even 1). [0054] As shown in FIG. 2, each module has four different switching states. Only one of the upper and lower power devices of a single bridge arm can be turned on. Among them, the upper tube is on and the lower tube is off means that the bridge arm is turned on. The state is 1, the lower tube is on and the upper tube is off, which means that the state of the bridge arm is 0. The multilevel converter is composed of multiple modules, corresponding to a variety of different switch state combinations, In the off state combination, the total output level of the multilevel converter is different. [0055] Assuming that the left half-bridge state of the i-th module is denoted as one, and the right half-bridge state is denoted as B2J. The output level of the i-th module is necessary, then the total output power of the multilevel converter with n modules Ping Η is: [0056] H=Q1+Q2+---+0/1) [0057] Wherein, ^H-ί ~ 1, Β ° [0058]--0, B2U -B2i ¢2) -1, %. produces 0 and =1 [0059] The mathematical models of different types of multilevel converters are different, and the method for constructing the mathematical model of the multilevel converter is based on the prior art, for example, the mathematical model of the cascaded H-bridge multilevel converter The construction method can refer to: Ding Hongqi. Research and device development of modular multi-level power amplifier[D]. Hunan University, 2018. 2. Suppose the reference value of the j-th control variable at k+1 time is X; (k+1), the cost function of the multilevel converter is constructed by x: (counting 1) and XjP(k+1) Under the constraint of the finite control set, the total level corresponding to the minimum cost function is taken as the optimal output total level at k+1, and the level increment in the optimal state at k+1 is obtained. [0061] The specific expression of the cost function is: [0062] And = steam% BU; (Left+1)-Eat «Left+1)¦ (3) [0063] Wherein, g is the cost function of the multilevel converter, ¥+D is the reference value of the j-th control variable at time k+1, and XjP (k+1) is the combination of different switch states at time k+1 The predicted output value of the jth control variable is the weight coefficient corresponding to the jth control variable (3 is set according to experience), and η is the number of control variables. The cost function is directly obtained based on the reference value of the control variable and the predicted value of the control variable output, without correction, which ensures the output accuracy of the multilevel converter. [0064] At time k, the multilevel converter outputs the Z level states before and after the total level H(k) as the finite control set, and the output total level H(k+1) at the time k+1 is in the finite control set. The constraints are: [0065] H(k+1) e {H(k)-Z, H(k)-Z+1,..., H(k),..., H(k)+ZT, H(k)+Z} (4) [0066] Among them, H(k)=Qjk)+...+Qjk)+...+Qk), Qj(k) is the output level of the i-th module at time k, and m is the total number of modules of the multilevel converter Quantity, Qj (k) = 1,0, -1. [0067] Under the constraints of the finite control set, the minimum cost function g is taken as the optimization objective, and the total level corresponding to the minimum cost function is taken as the total output level H (k+1) at the time k+1, according to H (k +Ι) and the mouth (female) get ΔH=H(k+1) -H(k) with the level increment at time +1, and ΑΗ© (-Ζ,Ζ). [0068] 3. According to the level increment A Η, a module that can operate at k+1 is selected. [0069] When the level increment AH&gt;0, the module whose current output level Q (k) is 1 can no longer increase the level. Choose from mod
[DE EP3815228A1]: MEHRPHASIGER MEHRSTUFENSTROMRICHTER MIT EINER ANSTEUERUNG UND EINEM PASSIVEN FREQUENZFILTER UND VERFAHREN ZUR ANSTEUERUNG DES MEHRPHASIGEN MEHRSTUFENSTROMRICHTERS [EN US2021249970A1]: MULTIPHASE MULTILEVEL POWER CONVERTER HAVING A DRIVE AND A PASSIVE FREQUENCY FILTER, AND METHOD FOR DRIVING THE MULTIPHASE MULTILEVEL POWER CONVERTER [FR EP3815228A1]: CONVERTISSEUR MULTI-ÉTAGÉ POLYPHASÉ MUNI D'UN DISPOSITIF D'ACTIVATION ET D'UN FILTRE DE FRÉQUENCE PASSIF ET PROCÉDÉ D'ACTIVATION DU CONVERTISSEUR MULTI-ÉTAGÉ POLYPHASÉ [ZH CN112640280A]: 具有控制装置和无源频率滤波器的多相多级变流器以及用于控制多相多级装置变流器的方法 | [DE WO2020043263A1]: Mehrphasiger Mehrstufenstromrichter mit einer Ansteuerung und einem passiven Frequenzfilter und Verfahren zur Ansteuerung des mehrphasigen Mehrstufenstromrichters Die Erfindung betrifft einen mehrphasigen Mehrstufenstromrichter (MMC) mit einem Phasenmodul (210), das aus mehreren Submodulen (610) gebildet ist, die einen Energiespeicher (1020) aufweisen, wobei die Energiespeicher-Spannung (Uzk) als Submodul-Spannung (UDC) zwischen den beiden Submodul-Polen (ACP1, ACP2) zu- und abschaltbar ist und wobei zur Dämpfung von höherfrequenten Anteilen der Anschlussspannung (21) je Phasenmodul (210) ein passives Frequenzfilter (F) vorgesehen ist, dessen Resonanzfrequenz (fr) oberhalb einer Abtastfrequenz (ft) einer digitalen Regelung (15a) liegt, welche zu jeweils aufeinanderfolgenden Abtastzeitpunkten (ti) abgeschaltete Submodul-Spannungen (UDC) zuschaltet und zugeschaltete Submodul-Spannungen (UDC) abschaltet. Um keine Anregung der Resonanzstelle des Frequenzfilters (F) zu bewirken, wird vorgeschlagen, dass die Ansteuerung (15) eine Steuerung (15b) aufweist, welche innerhalb eines Abtastintervalls (Ti) der Regelung (15a) jeweils zu einer von der Regelung (15a) zugeschalteten Submodul-Spannung (UDC) zumindest eine der abgeschalteten Submodul-Spannungen (UDC) zumindest eimal kurzzeitig zu- und wieder abschaltet. Weiter gehört zu der Erfindung ein Verfahren zur Ansteuerung des mehrphasigen Mehrstufenstromrichters (MMC). [EN US2021249970A1]: A multiphase multilevel power converter includes a phase module having submodules with an energy storage device. An energy storage device voltage is connectable and disconnectiable as a submodule voltage between two submodule poles. To attenuate higher-frequency components of the connection voltage, a passive frequency filter is provided for each phase module, having a resonant frequency above a sampling frequency of a digital regulating system connecting disconnected submodule voltages and disconnecting connected submodule voltages at successive sampling times. To avoid exciting the point of resonance of the frequency filter, the drive has a controller briefly connecting and again disconnecting at least one of the disconnected submodule voltages at least once within a sampling interval of the regulating system for a submodule voltage connected by the regulating system. A method for driving the multiphase multilevel power converter is also provided. [FR WO2020043263A1]: Convertisseur multi-étagé polyphasé muni d'un dispositif d'activation et d'un filtre de fréquence passif et procédé d'activation du convertisseur multi-étagé polyphasé. L'invention concerne un convertisseur multi-étagé polyphasé (MMC) muni d'un module de phase (210) constitué de plusieurs sous-modules (610) qui présentent un accumulateur d'énergie (1020), la tension (Uzk) de l'accumulateur d'énergie pouvant être activée et désactivée en tant que tension (UDC) de sous-module entre les deux pôles (ACP1, ACP2) de sous-modules. Pour l'amortissement de parts haute fréquence de la tension de raccordement (21), le convertisseur comprend, par module de phase (210), un filtre de fréquence passif (F) dont la fréquence de résonance (fr) est supérieure à une fréquence d'échantillonnage (ft) d'une régulation numérique (15a) qui, à des instants d'échantillonnage (ti) respectifs, active les tensions (UDC) de sous-module désactivées et désactive les tensions (UDC) de sous-module activées. L'invention vise à ne pas provoquer d'excitation du point de résonance du filtre de fréquence (F). À cet effet, le dispositif d'activation (15) présente une commande (15b) qui, à l'intérieur d'un intervalle d'échantillonnage (Ti) de la régulation (15a) respectivement pour une tension (UDC) de sous-module activée par la régulation (15a), active au moins une fois brièvement au moins une des tensions (UDC) de sous-module désactivée, puis la désactive à nouveau. L'invention concerne par ailleurs un dispositif d'activation du convertisseur multi-étagé polyphasé (MMC). [ZH CN112640280A]: 具有控制装置和无源频率滤波器的多相多级变流器以及用于控制多相多级装置变流器的方法。本发明涉及一种多相多级变流器(MMC)，其具有相模块(210)，相模块由多个子模块(610)形成，子模块具有储能器(1020)，其中，能够作为两个子模块极(ACP1，ACP2)之间的子模块电压(UDC)来接通和断开储能器电压(Uzk)，并且其中，为了衰减连接电压(21)的高频分量，每个相模块(210)设置有无源频率滤波器(F)，其谐振频率(fr)高于数字调节器(15a)的采样频率(ft)，调节器在相应地连续的采样时间点(ti)，接通断开的子模块电压(UDC)，并且断开接通的子模块电压(UDC)。为了不引起频率滤波器(F)的谐振点的激励，提出，控制装置(15)具有控制器(15b)，其在调节器(15a)的采样间隔(Ti)内，相应地相对于由调节器(15a)接通的子模块电压(UDC)，短时间地接通断开的子模块电压(UDC)中的至少一个至少一次，并且再次将其断开。此外，本发明涉及一种用于控制多相多级变流器(MMC)的方法。 | WO2020043263A1 | 2020-03-05 | EP2018072960W | 2018-08-27 | EP2018072960W, 2018-08-27 | WO2020043263A1: 2020-03-05 CN112640280A: 2021-04-09 EP3815228A1: 2021-05-05 US2021249970A1: 2021-08-12 | SIEMENS AG SIEMENS ENERGY GLOBAL GMBH & CO KG | PIESCHEL MARTIN | H02M1/12: I H02M1/00: N H02M7/483: I H02M1/00: I | H02M1/126: I H02M1/0012: A H02M7/4835: I | US2009268490A1 US2016380556A1 WO2008086760A1 |  | [DE EP3815228A1]: Patentansprüche1. Mehrphasiger Mehrstufenstromrichter (MMC)mit einem Phasenmodul (210), das aus mehreren elektrisch in Reihe geschalteten zweipoligen Submodulen (610) gebildet ist, die jeweils mehrere Halbleiterschalter (810) und einen unipo lar aufladbaren Energiespeicher (1020) aufweisen, wobei die Energiespeicher-Spannung (Uzk) durch die Halbleiterschalter (810) als Submodul-Spannung (UDC) zwischen den beiden Submo- dul-Polen (ACPI, ACP2) zu- und abschaltbar ist,wobei die Summe der zugeschalteten Submodul-Spannungen (UDC) jeweils die Anschlussspannung (21) mit einer vorgegebenen Grundfrequenz bildet,wobei zur Dämpfung von gegenüber der Grundfrequenz höherfre- quenten Anteilen der Anschlussspannung (21) je Phasenmodul (210) ein passives Frequenzfilter (F) vorgesehen ist,wobei jeweils ein Teil der Submodule (610) zugeschaltete Sub- modul-Spannungen (UDC) und ein Teil der Submodule (610) abge schaltete Submodul-Spannungen (UDC) aufweisen,mit einer Ansteuerung (15), die eine digitale Regelung (15a) aufweist, welche die Abweichung der Anschlussspannung (21) von einer vorgegebenen Soll-Spannung ausregelt, indem sie entsprechend einer vorgegebenen Abtastfrequenz (ft) zu je weils aufeinanderfolgenden AbtastZeitpunkten (ti) abgeschal tete Submodul-Spannungen (UDC) zuschaltet und zugeschaltete Submodul-Spannungen (UDC) abschaltet, undwobei das Frequenzfilter (F) eine Resonanzfrequenz (fr) auf weist, die oberhalb der Abtastfrequenz (ft) liegt,d a d u r c h g e k e n n z e i c h n e t,dass die Ansteuerung (15) eine Steuerung (15b) aufweist, wel che innerhalb eines Abtastintervalls (Ti) der Regelung (15a) jeweils zu einer von der Regelung (15a) zugeschalteten Submo- dul-Spannung (UDC) für eine erste Zeitdauer (TI) zumindest eine der abgeschalteten Submodul-Spannungen (UDC) zumindest einmal zuschaltet und wieder abschaltet. 2. Mehrstufenstromrichter nach Anspruch 1,d a d u r c h g e k e n n z e i c h n e t, dass die Steuerung (15b) zu einer von der Regelung (15a) zu geschalteten Submodul-Spannung (UDC) mehrere der jeweils ab geschalteten Submodul-Spannungen (UDC) zeitlich beabstandet nacheinander zuschaltet und wieder abschaltet. 3. Mehrstufenstromrichter nach Anspruch 1,d a d u r c h g e k e n n z e i c h n e t,dass die Steuerung (15b) zu einer von der Regelung (15a) zu geschalteten Submodul-Spannung (UDC) eine der abgeschalteten Submodul-Spannungen (UDC) zeitlich beabstandet mehrmals zu schaltet und wieder abschaltet. 4. Mehrstufenstromrichter nach einem der Ansprüche 1 - 3, d a d u r c h g e k e n n z e i c h n e t,dass die erste Zeitdauer TI durch Tl=l/ (2*fr) mit fr gleich der Resonanzfrequenz gegeben ist. 5. Mehrstufenstromrichter nach einem der Ansprüche 1 - 4, d a d u r c h g e k e n n z e i c h n e t,dass ein Teil der jeweils abgeschalteten Submodul-Spannungen (UDC) eine kleinere Submodul-Spannung (UDC) als die übrigen abgeschalteten Submodul-Spannungen (UDC) aufweist und dass die Steuerung nur die kleineren (mittleren) Submodul- Spannungen (UDC) für die erste Zeitdauer TI jeweils zuschal tet und wieder abschaltet. 6. Mehrstufenstromrichter nach Anspruch 5,d a d u r c h g e k e n n z e i c h n e t,dass die kleinere Submodul-Spannung (UDC) halb so groß ist wie die übrigen abgeschalteten Submodul-Spannungen (UDC) . 7. Mehrstufenstromrichter nach einem der Ansprüche 1 - 6, d a d u r c h g e k e n n z e i c h n e t,dass die Steuerung (15b) zu einer von der Regelung (15a) zu geschalteten Submodul-Spannung (UDC) gleichzeitig mit dem Zu schalten dieser Submodul-Spannung (UDC) die kleinere Submo- dul-Spannung (UDC) für die erste Zeitdauer (TI) invertiert zuschaltet und anschließend wieder abschaltet. 8. Mehrstufenstromrichter nach Anspruch 1,d a d u r c h g e k e n n z e i c h n e t,dass alle Submodule (610) dieselbe Submodul-Spannung (UDC) aufweisen und die Steuerung (15b) jeweils zu einer von der Regelung (15a) zugeschalteten Submodul-Spannung (UDC) eine ungerade Anzahl für die erste Zeitdauer (TI) zuschaltet und wieder abschaltet, danach diese Submodul-Spannungen (UDC) für eine zweite Zeitdauer (T2) mit entgegengesetztem Vorzeichen zuschaltet und nach Ablauf der zweiten Zeitdauer (T2) alle von der Steuerung (15b) zugeschalteten Submodul-Spannungen (UDC) wieder abschaltet, wobei für die erste und zweite Zeit dauer (TI, T2) gilt: Tl=l/ (2*pi*fr) *arccos ( (4* (N*UDC) L2-2* (N*UDC) - UDCA2) / (4* (N*UDC) L2) ) und 9. Mehrstufenstromrichter nach Anspruch 8,d a d u r c h g e k e n n z e i c h n e t,dass die erste und zweite Zeitdauer (TI, T2) abhängig von der Anzahl im Verhältnis zu der Gesamtzahl der Submodule (610) ist . 10. Verfahren zur Ansteuerung eines mehrphasigen Mehrstufen stromrichters (MMC) , der ein Phasenmodul (210) aufweist, das aus mehreren elektrisch in Reihe geschalteten zweipoligen Submodulen (610) gebildet ist, die jeweils mehrere Halb leiterschalter (810) und einen unipolar aufladbaren Energie speicher (1020) aufweisen, wobei die Energiespeicher-Spannung (Uzk) durch die Halbleiterschalter (810) als Submodul- Spannung (UDC) zwischen den beiden Submodul-Polen (ACPI,ACP2) zu- und abschaltbar ist,wobei die Summe der zugeschalteten Submodul-Spannungen (UDC) jeweils die Anschlussspannung (21) mit einer vorgegebenen Grundfrequenz bildet,wobei zur Dämpfung von gegenüber der Grundfrequenz höherfre- quenten Anteilen der Anschlussspannung (21) je Phasenmodul (210) ein passives Frequenzfilter (F) vorgesehen ist,wobei jeweils ein Teil der Submodule zugeschaltete Submodul- Spannungen (UDC) und ein Teil der Submodule (610) abgeschal tete Submodul-Spannungen (UDC) aufweisen,wobei das Frequenzfilter (F) eine Resonanzfrequenz (fr) auf weist, die oberhalb einer vorgegebenen Abtastfrequenz (ft) liegt,bei dem durch eine digitale Regelung (15a) zu jeweils aufei nanderfolgenden AbtastZeitpunkten (tft) die Abweichungen der Anschlussspannung (21) von einer vorgegebenen Soll-Spannung erfasst werden und zumindest eine abgeschalteten Submodul- Spannungen (UDC) zugeschaltet oder zumindest eine der zuge schalteten Submodul-Spannungen (UDC) abschaltet wird,d a d u r c h g e k e n n z e i c h n e t,dass innerhalb eines Abtastintervalls (Ti) der Regelung (15a) jeweils zu einer von der Regelung (15a) zugeschalteten Submo- dul-Spannung (UDC) für eine erste Zeitdauer (TI, T2), die kleiner als das Abtastintervall (Ti) ist, zumindest eine der abgeschalteten Submodul-Spannungen (UDC) zumindest einmal zu schaltet und wieder abschaltet wird. [EN US2021249970A1]: 1-10. (canceled) 11. A multiphase multilevel power converter, comprising: a phase module formed of a plurality of two-pole submodules electrically connected in series, each of said two-pole submodules having two submodule poles, a plurality of semiconductor switches and an energy storage device chargeable in a unipolar manner, said semiconductor switches configured to switch an energy storage device voltage on and off as a submodule voltage between said two submodule poles;a sum of switched-on submodule voltages forming a connection voltage having a predefined fundamental frequency;a passive frequency filter associated with said phase module for damping components of the connection voltage being at a higher frequency than a fundamental frequency;a portion of said plurality of submodules having switched-on submodule voltages and a portion of said plurality of submodules having switched-off submodule voltages;a drive having a digital regulator correcting a deviation of the connection voltage from a predefined target voltage by switching on switched-off submodule voltages and switching off switched-on submodule voltages at respectively successive sampling instants in accordance with a predefined sampling frequency;said passive frequency filter having a resonant frequency above the predefined sampling frequency; andsaid drive having a controller configured to switch on and switch off again at least one of the switched-off submodule voltages at least once for a first time duration, within a sampling interval of said digital regulator relative to a submodule voltage switched on by said digital regulator. 12. The multilevel power converter according to claim 11, wherein said controller switches on and switches off again a plurality of the respectively switched-off submodule voltages successively in a temporally spaced-apart manner, relative to a submodule voltage switched on by said digital regulator. 13. The multilevel power converter according to claim 11, wherein said controller switches on and switches off again one of the switched-off submodule voltages repeatedly in a temporally spaced-apart manner, relative to a submodule voltage switched on by said digital regulator. 14. The multilevel power converter according to claim 11, wherein the first time duration is given by T1=1/(2*fr) where fr equals the resonant frequency. 15. The multilevel power converter according to claim 11, wherein a portion of the respectively switched-off submodule voltages has a smaller submodule voltage than other switched-off submodule voltages, and said controller only switches on and switches off again the smaller (average) submodule voltages for the first time duration. 16. The multilevel power converter according to claim 15, wherein a magnitude of the smaller submodule voltage is half of a magnitude of the other switched-off submodule voltages. 17. The multilevel power converter according to claim 11, wherein said controller switches on and subsequently switches off again the smaller submodule voltage in an inverted manner for the first time duration, simultaneously with the switching on of a submodule voltage switched on by said digital regulator. 18. The multilevel power converter according to claim 11, wherein: all of said plurality of submodules have an identical submodule voltage;said controller switches on and switches off again an odd number of said submodule voltages UDC for the first time duration T1, then switches on said submodule voltages with an opposite sign for a second time duration and, after the second time duration T2 has elapsed, switches off again all submodule voltages switched on by said controller, relative to a submodule voltage switched on by said regulator; andfor the first and second time durations: T1=1/(2*pr*fr)*arccos((4*(N*UDC)^2−2*(N*UDC)−UDC^2)/(4*(N*UDC)^2)) andT2=1/(2*pi*f_r)*a cos((2*(N*UDC)^2−2*(N*UDC)−UDC^2)/(2*(N+1)*UDC^2)). 19. The multilevel power converter according to claim 18, wherein the first and second time durations are dependent on a number relative to a total number of said plurality of submodules. 20. A method for driving a multiphase multilevel power converter, the method comprising: providing the multiphase multilevel power converter with a phase module formed of a plurality of two-pole submodules electrically connected in series, each of the two-pole submodules having a plurality of semiconductor switches and an energy storage device chargeable in a unipolar manner, the semiconductor switches configured to switch an energy storage device voltage on and off as a submodule voltage between two submodule poles;using a sum of the switched-on submodule voltages to form a connection voltage having a predefined fundamental frequency;using a passive frequency filter provided for each phase module to damp components of the connection voltage being at a higher frequency than a fundamental frequency;providing a portion of the submodules with switched-on submodule voltages and a portion of the submodules with switched-off submodule voltages;providing the frequency filter with a resonant frequency above a predefined sampling frequency;using a digital regulator, at respectively successive sampling instants, to detect deviations of the connection voltage from a predefined target voltage and to switch on at least one of the switched-off submodule voltages or switch off at least one of the switched-on submodule voltages; andwithin a sampling interval of the digital regulator, relative to a submodule voltage switched on by the digital regulator, switching on and switching off again at least one of the switched-off submodule voltages at least once for a first time duration being less than the sampling interval. [ZH CN112640280A]: 1 .一种多相多级变流器(MMC), 所述多相多级变流器具有相模块(210)，所述相模块由多个串联电连接的双极子模块 (610)形成，双极子模块分别具有单极能够充电的储能器(1020)和多个半导体开关(810)， 其中，通过半导体开关(810)，能够作为两个子模块极(ACP1，ACP2)之间的子模块电压 (UDC)，来接通和断开储能器电压(Uzk)， 其中，接通的子模块电压(UDC)的总和相应地形成具有预先给定的基频的连接电压 (21)， 其中，为了衰减相对于基频具有更高的频率的连接电压(21)的分量，每个相模块(210) 设置有无源频率滤波器(F)， 其中，相应地一部分子模块(610)具有接通的子模块电压(UDC)，并且一部分子模块 (610)具有断开的子模块电压(UDC)， 所述多相多级变流器具有控制装置(15)，所述控制装置具有数字调节器(15a)，所述数 字调节器调节连接电压(21)与预先给定的额定电压的偏差，方式是，所述数字调节器对应 于预先给定的采样频率(ft)，在相应地连续的采样时间点(ti)将断开的子模块电压(UDC) 接通，并且将接通的子模块电压(UDC)断开，以及 其中，所述频率滤波器(F)具有高于采样频率(ft)的谐振频率(fr)， 其特征在于， 所述控制装置(15)具有控制器(15b)，所述控制器在所述调节器(15a)的采样间隔(Ti) 内，相应地相对于由所述调节器(15a)接通的子模块电压(UDC)，在第一持续时间(T1)内，至 少一次接通断开的子模块电压(UDC)中的至少一个，并且再次将其断开。 2 .根据权利要求1所述的多级变流器， 其特征在于， 相对于由所述调节器(15a)接通的子模块电压(UDC)，所述控制器(15b)以在时间上间 隔开的方式依次接通相应地断开的子模块电压(UDC)中的多个，并且再次将其断开。 3 .根据权利要求1所述的多级变流器，其中， 其特征在于， 相对于由所述调节器(15a)接通的子模块电压(UDC)，所述控制器(15b)以在时间上间 隔开的方式多次接通断开的子模块电压(UDC)中的一个，并且再次将其断开。 4 .根据权利要求1至3中任一项所述的多级变流器， 其特征在于， 第一持续时间T1由T1 = 1/(2*fr)给出，其中，fr等于谐振频率。 5 .根据权利要求1至4中任一项所述的多级变流器， 其特征在于， 相应地断开的子模块电压(UDC)的一部分具有比其余断开的子模块电压(UDC)小的子 模块电压(UDC),并且所述控制器仅在第一持续时间T1内相应地接通较小的(平均)子模块 电压(UDC),并且再次将其断开。 6 .根据权利要求5所述的多级变流器，其中， 其特征在于， 较小的子模块电压(UDC)是其余断开的子模块电压(UDC)的一半大。 7 .根据权利要求1至6中任一项所述的多级变流器。 其特征在于， 相对于由所述调节器(15a)接通的子模块电压(UDC)，在接通该子模块电压(UDC)的同 时，所述控制器(15b)在第一持续时间(T1)内反转地接通较小的子模块电压(UDC)，随后再 次将其断开。 8 .根据权利要求1所述的多级变流器，其中， 其特征在于， 所有子模块(610)具有相同的子模块电压(UDC)，并且相应地相对于由调节器(15a)接 通的子模块电压(UDC)，所述控制器(15b)在第一持续时间(T1)内接通奇数数量的子模块电 压(UDC)，并且再次将其断开，之后在第二持续时间(T2)内以相反的符号接通这些子模块电 压(UDC)，并且在第二持续时间(T2)结束之后，再次断开所述控制器(15b)接通的所有子模 块电压(UDC)，其中，对于第一和第二持续时间(T1,T2),适用： T1 = 1/(2*pi*fr) *arccos((4* (N*UDC)2-2* (N*UDC) -UDC~2)/(4* (N*UDC)” 2)) 以及 T2 = 1/(2*pi*f_r) *acos((2* (N*UDC)2-2* (N*UDC) -UDC2)/(2* (N+1) *UDC ~2))„ 9 .根据权利要求8所述的多级变流器， 其特征在于， 第一和第二持续时间(T1,T2)取决于相对于子模块(610)的总数的数量。 10 .一种用于控制多相多级变流器(MMC)的方法，所述多相多级变流器(MMC)具有相模 块(210),所述相模块由多个串联电连接的双极子模块(610)形成，所述双极子模块分别具 有能够单极充电的储能器(1020)和多个半导体开关(810),其中，通过半导体开关(810),能 够作为两个子模块极(ACP1,ACP2)之间的子模块电压(UDC)来接通和断开储能器电压 (Uzk), 其中，接通的子模块电压(UDC)的总和相应地形成具有预先给定的基频的连接电压 (21), 其中，为了衰减相对于基频具有更高的频率的连接电压(21)的分量，每个相模块(210) 设置有无源频率滤波器(F), 其中，相应地一部分子模块具有接通的子模块电压(UDC)，并且一部分子模块(610)具 有断开的子模块电压(UDC), 其中，所述频率滤波器(F)具有处于预先给定的采样频率(ft)以上的谐振频率(fr), 在所述方法中，通过数字调节器(15a),在相应地连续的采样时间点(tft),采集连接电 压(21)与预先给定的额定电压的偏差，并且接通至少一个断开的子模块电压(UDC),或者断 开接通的子模块电压(UDC)中的至少一个， 其特征在于, 在调节器(15a)的采样间隔(Ti)内，相应地相对于由调节器(15a)接通的子模块电压 (UDC),在小于采样间隔(Ti)的第一持续时间(T1,T2)内，接通断开的子模块电压(UDC)中的 至少一个至少一次，并且再次将其断开。 | [DE EP3815228A1]: Beschreibung Mehrphasiger Mehrstufenstromrichter mit einer Ansteuerung und einem passiven Frequenzfilter und Verfahren zur Ansteuerung des mehrphasigen Mehrstufenstromrichters Die Erfindung betrifft einen mehrphasigen Mehrstufenstrom richter mit einer Ansteuerung und einem passiven Frequenzfil ter und ein Verfahren zur Ansteuerung des mehrphasigen Mehr stufenstromrichters gemäß dem Oberbegriff des Anspruchs 1 und des Anspruchs 10. Mehrphasige Mehrstufenstromrichter sind bekannt und bei spielsweise elektrisch mit einem dreiphasigen Wechselspan- nungs-Energieversorgungsnetz verbunden . Jeder Mehrstufenstromrichter weist mehrere Phasenmodule auf, die aus mehreren elektrisch in Reihe geschalteten zweipoligen Submodulen bestehen. Die Submodule verfügen über mehrere Halbleiterschalter und einen unipolar aufladbaren Energie speicher, wobei die vom Aufladungsgrad des Energiespeichers abhängige Energiespeicher-Spannung durch die Halbleiterschal ter als Submodul-Spannung zu- und abschaltbar ist, die je weils zwischen den beiden Submodul-Polen liegt. Mittels eines Stromsensors wird der durch den Mehrstufen stromrichter und damit durch die Phasenmodule fließende Ge samtstrom und mittels eines Messwandlers wird die Anschluss spannung gemessen. Die gemessenen Strom- und Spannungsmess werte werden zu einer Ansteuereinheit übertragen, die eine digitale Regelung umfasst, welche mit einer vorgegebenen Ab tastfrequenz zu jeweils aufeinanderfolgenden AbtastZeitpunk ten die Abweichung der Anschlussspannung von einer vorgegebe nen Soll-Spannung erfasst, die in Form von Sollwerten vorge geben ist, anhand der Sollwerte die Ansteuersignale für die Halbleiterschalter der Submodule berechnet und die Abweichung mittels der Ansteuersignale ausregelt. Die Ansteuersignale schalteten die Submodul-Spannungen entsprechend zu- und ab. D.h. ein Teil der Submodule und damit der Submodul-Spannungen ist jeweils zugeschaltet und ein Teil der Submodule und damit der Submodul-Spannungen ist jeweils nicht zugeschaltet (oder anders gesagt abgeschaltet) . Die Summe der zugeschalteten Submodul-Spannungen bildet jeweils die Anschlussspannung, al so die Ausgangsspannung des Mehrstufenstromrichters, die sich regelungsbedingt innerhalb eines Abtastintervalls , also in nerhalb des Zeitraums zwischen zwei unmittelbar aufeinander folgenden AbtastZeitpunkten, nicht wesentlich ändert. Dabei können zugeschaltete Submodul-Spannungen insbesondere auch über mehrere Abtastintervalle zugeschaltet bleiben. Zur Dämpfung von höherfrequenten Anteilen der Anschlussspan nung ist für jedes Phasenmodul ein passives Frequenzfilter vorgesehen, insbesondere als LCL-Passivfilter . Derartige Fre quenzfilter weisen eine Resonanzfrequenz auf, die zweckmäßi gerweise oberhalb der Abtastfrequenz liegt. Es ist bekannt, dass passive Frequenzfilter hochfrequente Störungen, die beim Schalten von mehrphasigen Mehrstufen stromrichtern auftreten können, sehr stark dämpfen. Diesem Vorteil steht eine sehr schwach gedämpfte Resonanzstelle ge genüber, welche durch das Schalten der einzelnen Submodule aufgrund von Schaltentscheidungen jedes Mal sprungförmig an geregt wird. Die Schaltentscheidungen werden beispielsweise mittels einer Pulsweitenmodulation oder der aus der WO 2008086760 bekannten Schaltheuristik getroffen. Ist die Resonanzstelle deutlich niederfrequenter als die Schaltfre quenz, kann die Anregung der Resonanzstelle mittels einer Ab- tastregelung ausreichend bedämpft werden. Die Absenkung der Resonanzstelle bedingt sehr große und damit teure Filterbau elemente. Liegt die Resonanzstelle oberhalb der Abtastfre quenz, so kann es bedingt durch Aliasingeffekte sogar zu ei ner weiteren Anregung der Resonanzstelle kommen. Die Aufgabe der Erfindung ist es, einen mehrphasigen Mehrstu fenstromrichter mit einem passiven Frequenzfilter nahe der Abtastfrequenz so anzusteuern, dass keine Anregung der Reso- nanzstelle des Frequenzfilters, insbesondere eines LCL- Passivfilters , erfolgt. Die Aufgabe wird durch die Merkmale des Anspruchs 1 gelöst; die Unteransprüche stellen vorteilhafte Ausgestaltungen dar. Die Lösung sieht bezogen auf den Mehrstufenstromrichter vor, dass die Ansteuerung eine Steuerung aufweist, welche inner halb eines Abtastintervalls der Regelung jeweils zu einer von der Regelung zugeschalteten Submodul-Spannung UDC für eine erste Zeitdauer TI, T2 zumindest eine der abgeschalteten Sub- modul-Spannungen UDC zumindest einmal (kurzzeitig) zuschaltet und wieder abschaltet. Insbesondere wird vorgeschlagen, dass die Steuerung zu einer von der Regelung zugeschalteten Submodul-Spannung UDC mehrere der jeweils abgeschalteten Submodul-Spannungen zeitlich beab- standet nacheinander (kurzzeitig) zuschaltet und wieder ab schaltet . Weiter wird vorgeschlagen, dass die Steuerung zu einer von der Regelung zugeschalteten Submodul-Spannung UDC eine der abgeschalteten Submodul-Spannungen UDC zeitlich beabstandet mehrmals (kurzzeitig) zuschaltet und wieder abschaltet. Zweckmäßigerweise ist die erste Zeitdauer TI durch Tl=l/ (2*fr) mit fr gleich der Resonanzfrequenz gegeben. Mit Vorteil wird vorgeschlagen, dass ein Teil der jeweils ab geschalteten Submodul-Spannungen UDC eine kleinere (mittlere) Submodul-Spannung UDC als die übrigen abgeschalteten Submo- dul-Spannungen UDC aufweist (mit einer kleineren Submodul- Spannung UDC betrieben wird) und dass die Steuerung nur die kleineren (mittleren) Submodul-Spannungen UDC für die erste Zeitdauer TI jeweils (kurzzeitig) zuschaltet und wieder ab schaltet . Zweckmäßig ist es dabei, wenn die kleinere Submodul-Spannung UDC halb so groß ist wie die übrigen abgeschalteten Submodul- Spannungen UDC . Bei vier Halbleiterschaltern je Submodul lässt sich die Dämp fung dadurch weiter verbessern, dass die Steuerung zu einer von der Regelung zugeschalteten Submodul-Spannung UDC gleich zeitig mit dem Zuschalten dieser Submodul-Spannung UDC (durch die Regelung) die kleinere Submodul-Spannung UDC für die ers te Zeitdauer TI (kurzzeitig) invertiert zuschaltet und an schließend wieder abschaltet. Alternativ ist es von Vorteil, wenn alle Submodule dieselbe (mittlere) Submodul-Spannung UDC aufweisen und die Steuerung jeweils zu einer von der Regelung zugeschalteten Submodul- Spannung eine ungerade Anzahl N-l für die erste Zeitdauer zu schaltet und wieder abschaltet, danach diese Submodul- Spannungen UDC (dieser Submodule) für eine zweite Zeitdauer mit entgegengesetztem Vorzeichen (invertiert) zuschaltet und wieder abschaltet und nach Ablauf der zweiten Zeitdauer alle von der Steuerung (zusätzlich) zugeschalteten Submodul- Spannungen UDC wieder abschaltet, wobei für die erste und zweite Zeitdauer TI, T2 gelten: Tl=l/ (2*pi*fr) *arccos ( (4* (N*UDC) L2-2* (N*UDC) - UDCA2 ) / (4* (N*UDC) L2) ) und Zweckmäßigerweise wird die erste und zweite Zeitdauer TI, T2 abhängig von der Gesamtzahl der Submodule gewählt. Die Lösung sieht zur Ansteuerung des mehrphasigen Mehrstufen stromrichters vor, dass innerhalb eines Abtastintervalls der Regelung jeweils zu einer von der Regelung zugeschalteten Submodul-Spannung UDC für eine erste Zeitdauer TI, die klei ner als das Abtastintervall ist, zumindest eine der abge- schalteten Submodul-Spannungen UDC zumindest einmal (kurzzei tig) zuschaltet und wieder abschaltet wird. Die Lösungen bezogen auf den Mehrstufenstromrichter und das Verfahren weisen eine deutlich geringere Anregung des passi ven Frequenzfilters und eine wirksamere Dämpfung von Störun gen auf. Außerdem ist die Komponentenbelastung insbesondere bei einem LCL-Filter geringer. Der Kern der Lösungen ist das zeitversetzte Schalten der ge stuften Submodul-Spannungen, so dass die Resonanzstelle ins besondere bei einem LCL-Filter kaum angeregt wird. Hinzu kommt ein besseres Störabstrahlverhalten des Mehrstu fenstromrichters. Außerdem ist das Projektrisiko in Bezug auf die EMV-Akzeptanz geringer. Die Erfindung wird nachfolgend anhand eines Ausführungsbei spiels näher beschrieben. Es zeigen: Fig. 1 eine Anordnung mit einem modularen Mehrstufen stromrichter, Fig . 2 einen Mehrstufenstromrichter mit drei Phasen modulen, Fig . 3 einen Mehrstufenstromrichter mit sechs Phasen modulen, Fig. 4 ein Phasenmodul, Fig . 5 ein zweipoliges Submodul, Fig . 6 eine Leistungshalbleiterschaltung mit vier HalbleiterSchaltern, Fig. 7 eine Leistungshalbleiterschaltung mit zwei HalbleiterSchaltern, Fig. 8 einen Energiespeicher in Form eines Kondensa tormoduls, Fig. 9 einen Mehrstufenstromrichter mit drei Phasen modulen in Sternschaltung, Fig. 10 ein einphasig an ein Energieversorgungsnetz anschließbares Phasenmodul. Fig . 11 den zeitlichen Verlauf einer von der Regelung des Mehrstufenstromrichters zugeschalteten Submodul-Spannung und einer von einer Steue rung kurzzeitig zusätzlich zugeschalteten Sub modul-Spannung, Fig. 12 zwei von der Steuerung zusätzlich kurzzeitig zugeschaltete Submodul-Spannungen, Fig. 13 zwei von der Steuerung zusätzlich kurzzeitig zugeschaltete Submodul-Spannungen mit halbem Spannungswert, Fig . 14 eine von der Steuerung zusätzlich kurzzeitig zugeschaltete Submodul-Spannung mit invertier tem halben Spannungswert und Fig. 15 drei zusätzlich kurzzeitig zugeschaltete Sub- modul-Spannungen . In Fig. 1 ist eine Anordnung 1 mit einem modularen Mehrstu fenstromrichter MMC (Modular Multilevel Converter) darge stellt. Der modulare Mehrstufenstromrichter MMC ist dreipha sig über eine Anschlussschiene 5 und einen Transformator 5a mit einem Energieversorgungsnetz 7 elektrisch verbunden. Das Energieversorgungsnetz 7 ist im Ausführungsbeispiel ein drei phasiges Wechselspannungs-Energieversorgungsnetz . Mittels ei nes Stromsensors 10 wird der durch den Mehrstufenstromrichter MMC fließende Strom gemessen. Die Strommesswerte 13 werden zu einer Ansteuereinheit 15 für den modularen Mehrstufenstrom richter MMC übertragen. Weiterhin wird mittels eines Span nungssensors 18 (der hier als ein Messwandler ausgeführt ist) die an der Anschlussschiene 5 anliegende Spannung, die An schlussspannung, gemessen. Diese Spannung entspricht im We sentlichen der an dem modularen Mehrstufenstromrichter MMC anliegenden Spannung. Die Spannungswerte der Anschlussspan nung 21 werden zu der Ansteuereinheit 15 übertragen. Die Ansteuereinheit 15 umfasst eine digitale Regelung 15a und eine Steuerung 15b. Anhand von vorgegebenen Sollwerten 25 berechnet die Regelung 15a der Ansteuereinheit 15 Ansteuersignale 28a, die zum modu laren Mehrstufenstromrichter MMC übertragen werden. Mittels dieser Ansteuersignale 28a wird der Mehrstufenstromrichter MMC derart angesteuert, dass sich an der Anschlussschiene 5 die gewünschte Anschlussspannung einstellt. Die Regelung 15a der Ansteuereinheit 15 kontrolliert auf diese Weise den Mehr stufenstromrichter MMC. In Fig. 2 ist ein Ausführungsbeispiel eines Mehrstufenstrom richters MMC dargestellt, welcher drei Phasenmodule 210 auf weist. Die drei Phasenmodule 210 sind in Dreiecksschaltung mit Netzdrosseln L und Filterkapazitäten C geschaltet und mit drei Phasen LI, L2 und L3 des Energieversorgungsnetzes 7 ver bunden. Der Aufbau der Phasenmodule 210 ist in Fig. 4 ge zeigt . In Fig. 3 ist ein Ausführungsbeispiel eines Mehrstufenstrom richters MMC dargestellt, welcher sechs Phasenmodule 210 auf weist. Die sechs Phasenmodule 210 sind in einer Brückenschal tung (hier: in einer B6-Brückenschaltung) wiederum mit Netz drosseln L und Filterkapazitäten C angeordnet. Dabei sind je weils ein Anschluss eines ersten Phasenmoduls und ein An schluss eines zweiten Phasenmoduls miteinander elektrisch verbunden und bilden einen Wechselspannungsanschluss 302, 304 oder 306. In Fig. 4 ist ein Ausführungsbeispiel des Phasenmoduls 210 näher dargestellt. Das Phasenmodul 210 weist einen ersten An schluss AC1 sowie einen zweiten Anschluss AC2 auf. Der erste Anschluss AC1 ist über einen Stromsensor 608 mit einem ersten zweipoligen Submodul 610 elektrisch verbunden. Das erste Sub modul 610 ist elektrisch in Reihe geschaltet mit weiteren zweipoligen Submodulen 610; insgesamt weist das Phasenmodul 210 hier beispielhaft 18 Submodule 610 auf. Das letzte der 18 zweipoligen Submodule 610 ist über eine Koppelinduktivität 612 elektrisch mit dem zweiten Anschluss AC2 verbunden. Mit tels des Stromsensors 608 wird der durch das Phasenmodul 210 fließende Strom IP gemessen. Der erste Anschluss AC1 und der zweite Anschluss AC2 können jeweils mit einer Phase des Wech- selspannungs-Energieversorgungsnetzes 7 verbunden sein. In Fig. 5 ist ein Ausführungsbeispiel eines zweipoligen Sub moduls 610 im Detail dargestellt. Das zweipolige Submodul 610 weist einen ersten Submodulpol ACPI und einen zweiten Submo dulpol ACP2 auf. Die beiden Submodulpole ACPI und ACP2 sind mit einer Leistungshalbleiterschaltung 710 verbunden (genauer gesagt mit einem Wechselspannungsanschluss der Leistungshalb leiterschaltung 710). Ein Gleichspannungsanschluss der Leis tungshalbleiterschaltung 710 ist über einen Gleichspannungs- zwischenkreis 714 mit einem Energiespeicher 724 verbunden. In dem Gleichspannungszwischenkreis 714 ist die Energiespeicher- Spannung Uzk vorhanden, die als Submodul-Spannung UDC zu- und abschaltbar ist und nach Zuschaltung als zugeschaltete Submo- dul-Spannung UDC zwischen den beiden Submodul-Polen liegt. Nach Abschaltung Submodul-Spannung UDC liegt keine Spannung (oder eine Nullspannung) zwischen den beiden Submodul-Polen an. Die Leistungshalbleiterschaltung 710 wird auch als „Powermodul" bezeichnet. In Fig. 6 ist ein Ausführungsbeispiel der Leistungshalb leiterschaltung 710 dargestellt. Die Leistungshalbleiter schaltung 710 weist vier Halbleiterschalter 810 auf, die ein- und ausschaltbar sind. Jeder der Halbleiterschalter 810 weist ein Leistungshalbleiterbauelement mit einer antiparallel ge schalteten Diode auf. Im Ausführungsbeispiel der Fig. 8 ist das Leistungshalbleiterbauelement ein IGBT (Insulated Gate Bipolar Transistor) . In anderen Ausführungsbeispielen kann das Halbleiterbauelement jedoch auch anders ausgestaltet sein, zum Beispiel als IGCT (Integrated Gate-Commutated Thy ristor), IEGT ( Inj ection-Enhanced Gate Transistor) oder als MOSFET (Metal-Oxide-Semiconductor Field-Effect Transistor) . Die vier Halbleiterschalter 810 bilden im Ausführungsbeispiel der Fig. 8 eine Vollbrückenschaltung. Dadurch kann die Pola rität der zwischen den Submodulpolen ACPI und ACP2 anliegen den Submodul-Spannung UDC umgekehrt werden. In Fig. 7 ist ein weitere Ausführungsbeispiel einer Leis tungshalbleiterschaltung 710' dargestellt, welche lediglich zwei Leistungshalbleiterschalter 810 aufweist und auch nur für einen Mehrstufenstromrichter MMC gemäß Fig. 3 geeignet ist. Die beiden Leistungshalbleiterschalter 810 bilden im Ausführungsbeispiel der Fig. 9 eine Halbbrückenschaltung. Dadurch kann zwischen den Submodulpolen ACPI und ACP2 nur ei ne Submodul-Spannung UDC einer Polarität (und eine Nullspan nung) ausgegeben werden. In Fig. 8 ist der Energiespeicher 724 in Form eines Kondensa tormoduls 724a dargestellt, das hier aus einem Kondensator C als Energiespeicher 1020 und einer parallelgeschalteten Span nungsmesseinrichtung 1020a besteht, wobei am Kondensator C die Energiespeicher-Spannung Uzk als Kondensatorspannung UC anliegt und von diesem gepuffert wird. Fig. 9 zeigt ein Ausführungsbeispiel eines modularen Mehrstu fenstromrichters MMC, bei dem drei Phasenmodule 210 in Stern schaltung mit Netzdrosseln L und Filterkapazitäten C geschal tet sind. Dabei sind Anschlüsse der drei Phasenmodule 210 miteinander elektrisch verbunden und bilden einen Sternpunkt 410. Der Sternpunkt 410 ist mit einem Rückleiter N des Ener gieversorgungsnetzes 7 verbunden. Die jeweils drei anderen Anschlüsse der Phasenmodule 210 sind jeweils mit einer Phase LI, L2 oder L3 des Energieversorgungsnetzes 7 verbunden. In Fig. 10 ist noch ein einzelnes Phasenmodul 210 darge stellt, welches einphasig an ein Energieversorgungsnetz ange schlossen werden kann. Dabei kann dieses Phasenmodul 210 zwi schen einer Phase L und dem Rückleiter N des Energieversor gungsnetzes angeschlossen werden, wie in Fig. 10 dargestellt ist . Der mehrphasige Mehrstufenstromrichter MMC weist also Phasen module 210 auf, die jeweils aus mehreren elektrisch in Reihe geschalteten zweipoligen Submodulen 610 gebildet sind. Jedes Submodul 610 verfügt jeweils über mehrere Halbleiterschalter 810 und einen unipolar aufladbaren Kondensator C als Energie speicher 1020, wobei die vom Aufladungsgrad des Energiespei chers 1020 abhängige Energiespeicher-Spannung Uzk durch die Halbleiterschalter 810 bei entsprechendem Schaltzustand der Halbleiterschalter 810 als Submodul-Spannung UDC zwischen den beiden Submodul-Polen ACPI, ACP2 zu- und abschaltbar ist. Da bei bildet die Summe der zugeschalteten Submodul-Spannungen UDC jeweils die Anschlussspannung 21 mit einer vorgegebenen Grundfrequenz. Zur Dämpfung von gegenüber der Grundfrequenz höherfrequenten Anteilen der Anschlussspannung 21 ist je Pha senmodul 210 ein passives Frequenzfilter F vorgesehen. Ein Teil der Submodule 610 weist dabei jeweils zugeschaltete Sub- modul-Spannungen UDC und ein Teil der Submodule 610 abge schaltete (also nicht zugeschaltete) Submodul-Spannungen UDC auf. Die Ansteuerung (Ansteuereinheit 15) verfügt eine digi tale Regelung 15b, welche die Abweichung der Anschlussspan nung (Spannungssensors 18) von einer vorgegebenen Soll- Spannung ausregelt, indem sie mit einer vorgegebenen Abtast frequenz (1/Ti) zu jeweils aufeinanderfolgenden Abtastzeit punkten ti abgeschaltete Submodul-Spannungen UDC zuschaltet und zugeschaltete Submodul-Spannungen UDC abschaltet (und insbesondere zugeschaltete Submodul-Spannungen UDC zugeschal tet lässt) . Die Resonanzfrequenz fr des Frequenzfilters F liegt oberhalb der Abtastfrequenz (1/Ti). Zusätzlich zur Re gelung 15a gehört die Steuerung 15b zur Ansteuerung (Ansteu ereinheit 15) . Fig. 11 zeigt beispielhaft den zeitlichen Verlauf der Submo- dul-Spannungen UDC von mehreren Submodulen 610, insbesondere eine zum Zeitpinkt ti von der Regelung 15a zugeschaltete Sub- modul-Spannung UDC eines Submoduls 610m. Die Steuerung 15b schaltet dann innerhalb des Abtastintervalls Ti der Regelung 15a zu der von der Regelung 15a zugeschalteten Submodul- Spannung UDC des Submoduls 610m die Submodul-Spannung UDC ei nes der unmittelbar davor abgeschalteten Submodule, hier des Submoduls 610n, für eine erste Zeitdauer TI einmal kurzzeitig (zeitlich kürzer als das Abtastintervall Ti) zu und wieder ab . Fig. 12 zeigt wie Fig. 11 den zeitlichen Verlauf der zum Zeitpinkt ti von der Regelung 15a zugeschaltete Submodul- Spannung UDC des Submoduls 610m. Die Steuerung 15b schaltet dann aber zwei der unmittelbar davor abgeschalteten Submodul- Spannungen UDC, hier die der Submodule 610n, 610o, zeitlich beabstandet nacheinander kurzzeitig (für eine Zeitdauer TI) zu und wieder ab. Dabei ist es auch möglich, dass die Steuerung 15b zu der von der Regelung 15a zugeschalteten Submodul-Spannung UDC des Submoduls 610m eine der abgeschalteten Submodul-Spannungen UDC (hier die des Submoduls 610n oder des Submoduls 610o) in nerhalb eines Abtastintervalls Ti zeitlich beabstandet mehr mals kurzzeitig zuschaltet und wieder abschaltet. Die erste Zeitdauer TI ist durch Tl=l/ (2*fr) mit fr gleich der Resonanzfrequenz gegeben. Fig. 13 zeigt beispielhaft, dass ein Teil der jeweils unmit telbar vor dem Zeitpunkt ti abgeschalteten Submodul-Spannun gen UDC (zu denen hier die beiden Submodul-Spannungen UDC der Submodule 610n, 610o gehören) eine kleinere Submodul-Spannung UDC als die übrigen abgeschalteten Submodul-Spannungen UDC aufweist, also mit einer kleineren Submodul-Spannung UDC be trieben wird, und dass die Steuerung 15 nur die kleineren Submodul-Spannungen UDC (hier die der Submodule 610n, 610o) für eine erste Zeitdauer TI jeweils nacheinander (kurzzeitig) zuschaltet und wieder abschaltet. Beispielsweise kann die kleinere Submodul-Spannung UDC halb so groß sein wie die üb rigen abgeschalteten Submodul-Spannungen UDC, wie in Fig. 13 beispielhaft dargestellt. Fig. 14 zeigt wieder beispielhaft den zeitlichen Verlauf der zum Zeitpinkt ti von der Regelung 15a zugeschalteten Submo- dul-Spannung UDC des Submoduls 610m. Die Steuerung 15b schal- tet dann zu der von der Regelung 15a zugeschalteten Submodul- Spannung UDC des Submoduls 610m gleichzeitig mit dem Zuschal ten dieser Submodul-Spannung UDC die kleinere Submodul-Span nung UDC des Submoduls 610n für die erste Zeitdauer TI (kurz zeitig) invertiert zu und anschließend wieder ab. Eine Inver tierung der Submodul-Spannung UDC setzt schaltungstechnisch voraus, dass vier Halbleiterschaltern 810 je Submodul 610 vorhanden sind. Fig. 15 zeigt: Für den Fall, dass alle Submodule 610 dieselbe (mittlere) Submodul-Spannung UDC aufweisen, kann die Steue rung 15a jeweils zu einer von der Regelung 15a zugeschalteten Submodul-Spannung UDC des Submoduls 610m eine ungerade Anzahl N-l (hier z.B. drei) Submodul-Spannungen UDC (hier der Submo dule 610n, 610o, 610p) für die erste Zeitdauer TI zu- und wieder abschalten, danach diese Submodul-Spannungen UDC (hier der Submodule 610n, 610o, 610p) für eine zweite Zeitdauer T2 mit entgegengesetztem Vorzeichen (also invertiert) zuschalten und wieder abschalten und nach Ablauf der zweiten Zeitdauer T2 alle von der Steuerung 15b (zusätzlich) zugeschalteten Submodul-Spannungen UDC (hier der Submodule 610n, 610o, 610p) wieder abschalten. Für die erste und zweite Zeitdauer TI, T2 muss dann gelten (mit L2 entspricht hoch 2 entspricht also zum Quadrat) : Tl=l/ (2*pi*fr) *arccos ( (4* (N*UDC) L2-2* (N*UDC) - UDCA2 ) / (4* (N*UDC) L2) ) und Die erste und zweite Zeitdauer TI, T2 ist dabei abhängig von dieser Anzahl N-l im Verhältnis zu der Gesamtzahl M der Sub module 610 zu wählen. Wie in Fig. 11 - Fig. 15 quasi dargestellt, wird verfahrens mäßig innerhalb eines Abtastintervalls Ti der Regelung 15a jeweils zu einer von der Regelung 15a zugeschalteten Submo- dul-Spannung UDC (in Fig. 11 - Fig. 15 das Submodul 610m) für eine Zeitdauer TI, T2, die kleiner als das Abtastintervall Ti ist, zumindest eine der abgeschalteten Submodul-Spannungen UDC (in Fig. 11 - Fig. 15 des Submoduls 610n oder der Submo- dule 610n und 610o oder der Submodule 610n und 610o und 610p) zumindest einmal (kurzzeitig) zuschaltet und wieder abschal tet . Bei den Submodul-Spannungen UDC handelt es sich jeweils um mittlere Submodul-Spannungen UDC. [EN US2021249970A1]: Multiphase multilevel power converter having a drive and a passive frequency filter, and method for driving the multiphase multilevel power converter The invention relates to a multiphase multilevel power converter having a drive and a passive frequency filter and to a method for driving the multiphase multilevel power converter according to the preamble of claim 1 and of claim 10. Multiphase multilevel power converters are known and for example are electrically connected to a three-phase AC voltage power supply system. Each multilevel power converter has a plurality of phase modules consisting of a plurality of two-pole submodules electrically connected in series. The submodules have a plurality of semiconductor switches and an energy store that is chargeable in a unipolar manner, wherein the energy store voltage dependent on the degree of charging of the energy store is able to be switched on and off as a submodule voltage by the semiconductor switches, said submodule voltage being present in each case between the two submodule poles. The total current flowing through the multilevel power converter and thus through the phase modules is measured by means of a current sensor and the connection voltage is measured by means of a measuring transducer. The measured current and voltage measurement values are transmitted to a drive unit comprising a digital regulator, which, at respectively successive sampling instants with a predefined sampling frequency, detects the deviation of the connection voltage from a predefined target voltage, which is predefined in the form of target values, calculates the drive signals for the semiconductor switches of the submodules on the basis of the target values and corrects the deviation by means of the drive signals. The drive signals correspondingly switch the submodule voltages on and off. That is to say that a portion of the submodules and thus of the submodule voltages is in each case switched on and a portion of the submodules and thus of the submodule voltages is in each case not switched on (or, to put it another way, switched off). The sum of the switched-on submodule voltages forms in each case the connection voltage, that is to say the output voltage of the multilevel power converter, which does not change significantly owing to the dictates of regulation within a sampling interval, that is to say within the time period between two directly successive sampling instants. In this case, switched-on submodule voltages can in particular also remain switched on over a plurality of sampling intervals. In order to damp higher-frequency components of the connection voltage, a passive frequency filter, in particular in the form of an LCL passive filter, is provided for each phase module. Frequency filters of this type have a resonant frequency that is expediently above the sampling frequency. It is known that high-frequency disturbances that may occur during the switching of multiphase multilevel power converters are damped to a very great extent by passive frequency filters. Conflicting with this advantage is a very weakly damped resonance point that is excited in sudden jumps each time as a result of the switching of the individual submodules on the basis of switching decisions. The switching decisions are taken for example by means of a pulse width modulation or the switching heuristic known from WO 2008086760. If the resonance point is at significantly lower frequency than the switching frequency, the excitation of the resonance point can be sufficiently damped by means of sampling regulation. The reduction of the resonance point necessitates very large and thus expensive filter components. If the resonance point is above the sampling frequency, then a further excitation of the resonance point may even occur owing to aliasing effects. The object of the invention is to drive a multiphase multilevel power converter comprising a passive frequency filter close to the sampling frequency such that the resonance point of the frequency filter, in particular of an LCL passive filter, is not excited. The object is achieved by means of the features of claim 1; the dependent claims present advantageous configurations. The solution relating to the multilevel power converter provides for the drive to have a controller, which, within a sampling interval of the regulator, in each case with respect to a submodule voltage UDC switched on by the regulator, (briefly) switches on and switches off again at least one of the switched-off submodule voltages UDC at least once for a first time duration T1, T2. In particular, it is proposed that with respect to a submodule voltage UDC switched on by the regulator, the controller (briefly) switches on and switches off again a plurality of the respectively switched-off submodule voltages successively in a temporally spaced-apart manner. Furthermore, it is proposed that with respect to a submodule voltage UDC switched on by the regulator, the controller (briefly) switches on and switches off again one of the switched-off submodule voltages UDC repeatedly in a temporally spaced-apart manner. Expediently, the first time duration T1 is given by T1=1/(2*fr) where fr equals the resonant frequency. Advantageously, it is proposed that a portion of the respectively switched-off submodule voltages UDC has a smaller (average) submodule voltage UDC than the other switched-off submodule voltages UDC (is operated with a smaller submodule voltage UDC), and that the controller (briefly) switches on and switches off again in each case only the smaller (average) submodule voltages UDC for the first time duration T1. It is expedient here if the magnitude of the smaller submodule voltage UDC is half that of the other switched-off submodule voltages UDC. Given four semiconductor switches per submodule, the damping can be further improved by virtue of the fact that with respect to a submodule voltage UDC switched on by the regulator, simultaneously with the switching on of this submodule voltage UDC (by the regulator), the controller (briefly) switches on and subsequently switches off again the smaller submodule voltage UDC in an inverted manner for the first time duration T1. Alternatively, it is advantageous if all submodules have the same (average) submodule voltage UDC and, in each case with respect to a submodule voltage switched on by the regulator, the controller switches on and switches off again an odd number N−1 for the first time duration, then switches on these submodule voltages UDC (of these submodules) with an opposite sign (in an inverted manner) for a second time duration and, after the second time duration has elapsed, switches off again all submodule voltages UDC switched on (additionally) by the controller, wherein the following holds true for the first and second time durations T1, T2: T1=1/(2*pi*fr)*arccos((4*(N*UDC)^2−2*(N*UDC)−UDC^2)/(4*(N*UDC)^2)) and T2=1/(2*pi*fr)*a cos((2*(N*UDC)^2−2*(N*UDC)−UDC^2)/(2*(N+1)*UDC^2)). Expediently, the first and second time durations T1, T2 are chosen in a manner dependent on the total number of submodules. The solution for driving the multiphase multilevel power converter provides that, within a sampling interval of the regulator, in each case with respect to a submodule voltage UDC switched on by the regulator, at least one of the switched-off submodule voltages UDC is (briefly) switched on and switched off again at least once for a first time duration T1 that is less than the sampling interval. The solutions relating to the multilevel power converter and the method exhibit a significantly smaller excitation of the passive frequency filter and a more effective damping of disturbances. Moreover, the component loading is lower particularly in the case of an LCL filter. The essence of the solutions is the time-staggered switching of the stepped submodule voltages, such that the resonance point is hardly excited particularly in the case of an LCL filter. An additional factor is a better noise emission behavior of the multilevel power converter. Moreover, the project risk with regard to EMC acceptance is lower. The invention is described in greater detail below on the basis of an exemplary embodiment. In the figures: FIG. 1 shows an arrangement comprising a modular multilevel power converter, FIG. 2 shows a multilevel power converter comprising three phase modules, FIG. 3 shows a multilevel power converter comprising six phase modules, FIG. 4 shows a phase module, FIG. 5 shows a two-pole submodule, FIG. 6 shows a power semiconductor circuit comprising four semiconductor switches, FIG. 7 shows a power semiconductor circuit comprising two semiconductor switches, FIG. 8 shows an energy store in the form of a capacitor module, FIG. 9 shows a multilevel power converter comprising three phase modules in a star connection, FIG. 10 shows a phase module that is connectable to a power supply system in a single-phase manner. FIG. 11 shows the temporal profile of a submodule voltage switched on by the regulator of the multilevel power converter and of a submodule voltage briefly switched on additionally by a controller, FIG. 12 shows two submodule voltages briefly switched on additionally by the controller, FIG. 13 shows two submodule voltages briefly switched on additionally by the controller with a half-magnitude voltage value, FIG. 14 shows a submodule voltage briefly switched on additionally by the controller with an inverted half-magnitude voltage value, and FIG. 15 shows three submodule voltages briefly switched on additionally. FIG. 1 illustrates an arrangement 1 comprising a modular mu
[JA JP6784089B2]: マルチレベル電力変換装置のユニット制御装置 [EN JP6784089B2]: Unit control device for multi-level power converter | [JA JP6784089B2]: 【課題】マルチレベルインバータでは、ユニット間に個体差があると横流電流が発生して電流責務がばらついてしまう。【解決手段】横流電流抑制制御手段の前段に電圧指令値補正手段を設ける。電圧指令値補正手段は、電圧指令値に対して閾値を設け、電圧指令値の零への接近を抑制する第１のスイッチ手段と、三角キャリア波形の傾きが正の時に、圧指令値の負から正の値への変化を禁止する第２のスイッチ手段と、三角キャリア波形の傾きが負の時に、圧指令値の正から負の値への変化を禁止する第３のスイッチ手段を備え、この電圧指令値補正手段により補正された電圧指令値を横流電流抑制制御手段への電圧指令値とする。【選択図】 図１ [EN JP6784089B2]: PROBLEM TO BE SOLVED: To solve the problem that, in a multilevel inverter, if there is an individual difference between units, a cross-flow current may be generated, thereby varying a current duty.SOLUTION: Voltage command value correction means is provided on a prestage of cross-flow current suppression control means. The voltage command value correction means includes: first switch means for suppressing an approach of a voltage command value to zero by providing a threshold with respect to the voltage command value; second switching means for inhibiting a change of the voltage command value from a negative value to a positive value when an inclination of a triangular carrier waveform is positive; and third switch means for inhibiting a change of the voltage command value from a positive value to a negative value when the inclination of the triangular carrier waveform is negative. The voltage command value that is corrected by the voltage command value correction means is defined as a voltage command value to the cross-flow current suppression control means.SELECTED DRAWING: Figure 1 | JP6784089B2 | 2018-02-08 2020-11-11 | JP2016151687A | 2016-08-02 2016-08-02 | JP2016151687A, 2016-08-02 JP2016151687A, 2016-08-02 | JP6784089B2: 2020-11-11 | MEIDENSHA ELECTRIC MFG CO LTD 株式会社明電舎 | OI KAZUNOBU | H02M7/487: I H02M7/493: I |  | WO2014123199A1 JPH05336754A JP2013255350A JP2013240252A JPH06153518A US2005047182A1 |  | [JA JP6784089B2]: 3レベル以上のマルチインバータユニットを並列に接続し、横流電流抑制制御手段によりインバータユニット間の横流責務の均等化を図りながら電圧指令値とキャリア三角波を比較し、インバータ内のスイッチング素子のオン・オフ信号を生成する制御装置において、 前記横流電流抑制制御手段の前段に電圧指令値補正手段を設け、 電圧指令値補正手段は、電圧指令値Vrefに対して閾値(禁止帯)-Vth~Vthを設け、電圧指令値Vrefの零への接近を抑制する第1のスイッチ手段と、 前記キャリア三角波の傾きが正の時に、電圧指令値Vrefの負から正の値への変化を禁止する第2のスイッチ手段と、 前記キャリア三角波の傾きが負の時に、電圧指令値Vrefの正から負の値への変化を禁止する第3のスイッチ手段を備え、 電圧指令値補正手段により補正された電圧指令値を、前記横流電流抑制制御手段への電圧指令値としたことを特徴としたマルチレベル電力変換装置のユニット制御装置。 前記第1のスイッチ手段は、電圧指令値Vrefが前記閾値Vth未満であることを検出する第1の比較器と、電圧指令値Vrefが前記閾値-Vthを越えることを検出する第2の比較器を有し、電圧指令値Vrefが閾値-Vth~Vthの範囲外時には電圧指令値Vrefを出力し、閾値-Vth~Vthの範囲内時には前回の出力値をホールドする機能を備え、 前記第2のスイッチ手段は、第1のスイッチ手段の出力が正の値であることを検出する第3の比較器と、ホールドされた前回の出力値が負の値であることを検出する第4の比較器と、前記キャリア三角波の微分値の傾きが正の値であることを検出する第5の比較器を有し、第3~第5の各比較器からの出力信号「1」でホールドされた前回の出力値を出力し、出力信号「1」でない時に、前記第1のスイッチ手段から出力する機能を備え、 前記第3のスイッチ手段は、第2のスイッチ手段の出力が負の値であることを検出する第6の比較器と、ホールドされた前回の出力値が正の値であることを検出する第7の比較器を有し、第6,第7の各比較器からの出力信号「1」で、且つ前記キャリア三角波の微分値の傾きが負の値のときにホールドされた前回の出力値を補正した電圧指令値Vref ́として出力し、キャリア三角波の微分値の傾きが正の時に、前記第2のスイッチ手段の出力を出力する機能を備えたことを特徴とした請求項1記載のマルチレベル電力変換装置のユニット制御装置。 前記マルチインバータユニットを三相とし、三相の電圧指令値Vrefを、前記電圧指令値補正手段により補正された電圧指令値Vref ́からそれぞれ減算器を介して各別に減算し、得られた算出値の総和値を三相の電圧指令値Vrefに各別に加算して新たに補正された三相の各電圧指令値Vref*とし、電圧指令値Vref*を前記横流電流抑制制御手段に対する電圧指令値としたことを特徴とした請求項1又は2記載のマルチレベル電力変換装置のユニット制御装置。 前記電圧指令値補正手段をN-2段直列に接続し、2段目以降の電圧指令値補正手段の入力を前段の電圧指令値補正手段の出力とし、直列に接続したn段目の電圧指令値補正手段では、入力(各段の電圧指令値Vref-n)が閾値2n/(N-1)-1-Vth&lt;Vref-n&lt;2n/(N-1)-1+Vthの範囲内であるか否かに基づいて、各段の電圧指令値補正手段の出力を生成することを特徴とした請求項1乃至3の何れか1項に記載のマルチレベル電力変換装置のユニット制御装置。ただし、Nはインバータのマルチレベル数、N≧4、n=1...N-2 [EN JP6784089B2]: Multi-inverter units of 3 levels or higher are connected in parallel, and the voltage command value and carrier triangular wave are compared while the cross current suppression control means is used to equalize the cross flow responsibilities between the inverter units, and the switching element in the inverter is turned on and off. In the control device that generates a signal, a voltage command value correction means is provided in front of the cross current suppression control means, and the voltage command value correction means provides a threshold (prohibited band) -Vth to Vth for the voltage command value Vref. , The first switch means for suppressing the approach of the voltage command value Vref to zero, and the second switch for prohibiting the change of the voltage command value Vref from a negative value to a positive value when the inclination of the carrier triangular wave is positive. A means and a third switch means for prohibiting a change of the voltage command value Vref from a positive value to a negative value when the inclination of the carrier triangular wave is negative, and the voltage command value corrected by the voltage command value correction means can be used. , A unit control device for a multi-level power conversion device, characterized in that the voltage command value is set to the cross current suppression control means. The first switching means is a first comparator that detects that the voltage command value Vref is less than the threshold Vth, and a second comparator that detects that the voltage command value Vref exceeds the threshold -Vth. When the voltage command value Vref is out of the range of the threshold -Vth to Vth, the voltage command value Vref is output, and when the voltage command value Vref is within the range of the threshold -Vth to Vth, it has a function of holding the previous output value. The switching means are a third comparator that detects that the output of the first switching means is a positive value, and a fourth comparator that detects that the previous output value held is a negative value. And the previous time, which has a fifth comparator that detects that the gradient of the differential value of the carrier triangular wave is a positive value, and is held by the output signal "1" from each of the third to fifth comparators. The output value of is output, and when the output signal is not "1", it has a function to output from the first switch means. The third switching means has a sixth comparator that detects that the output of the second switching means has a negative value, and a third that detects that the previous output value held is a positive value. It has 7 comparators, and the previous output value held when the output signal "1" from each of the 6th and 7th comparators and the gradient of the differential value of the carrier triangle wave is a negative value is used. The multi-level according to claim 1, wherein the output is output as a corrected voltage command value Vref ́, and the output of the second switch means is output when the gradient of the differential value of the carrier triangle wave is positive. A unit controller for a power converter. The multiIIntertaunitIs three-phase, and the voltage command value Vref of the three phases is subtracted from the voltage command value Vref ́ corrected by the voltage command value correction means separately via a subtractor, and the total value of the obtained calculated values is calculated. Each of the three-phase voltage command values Vref is newly corrected by adding each to the three-phase voltage command value Vref.*And the voltage command value Vref*The unit control device of the multi-level power conversion device according to claim 1 or 2, wherein the voltage command value for the cross current suppression control means is used. The voltage command value correction means is connected in series in N-2 stages, the input of the voltage command value correction means in the second and subsequent stages is used as the output of the voltage command value correction means in the previous stage, and the voltage command in the nth stage connected in series. In the value correction means, the input (voltage command value Vref-n of each stage) is within the range of the threshold 2n / (N-1) -1-Vth &lt;Vref-n &lt;2n / (N-1) -1 + Vth. The unit control device for a multi-level power conversion device according to any one of claims 1 to 3, wherein the output of the voltage command value correction means of each stage is generated based on the presence or absence. However, N is the number of multi-level inverters, N 4, n = 1 ... N-2 | [JA JP6784089B2]: 本発明は、マルチレベル電力変換装置のユニット並列制御装置に係わり、特に各インバータユニット間の電流責務の均等化を図った制御装置に関するものである。 マルチレベル電力変換装置の構成例として、3レベルインバータや5レベルインバータがあるが、図7(a)はNPC型3レベルインバータの1相分を示したものである。相電圧は、インバータ内のIGBT等のスイッチング素子T1~T4のON/OFF動作によって生成される。また、各スイッチング素子のON/OFF信号は、電圧指令値とキャリア三角波とを比較するPWM変調によって生成する方法(三角波比較PWM方法)が一般的である。 3レベルインバータの種類として、図7(a)のNPC型の他には図7(b)のT型、図7(c)のフライングキャパシタ(以下FCという)型がある。特許文献1にはFC型の3レベルインバータの例が記載されている。表1は図7(c)のFC型3レベルインバータのスイッチングパターンを示したものである。N端子を基準とした零電圧を出力端子Oに出力するときは、T1,T3をON、またはT2,T4をONすることでFCを導通させる。なお、コンデンサC1の印加電圧とコンデンサC2の印加電圧は等しく、VCF=Vdc1/2とする。 このようなインバータユニットを複数台並列にして電力変換装置を構成し大容量化に対応する場合がある。図8はFC型3レベルインバータを並列にした例である。このとき、インバータユニット間に個体差があると各インバータ間で出力電流に差が生じ(横流電流が発生)、電流責務がばらついてしまう。これにより特定のインバータに発熱が集中し寿命が短くなる。最悪の場合には、過電流や過熱でスイッチング素子が破壊されてしまう、といった問題が発生する。対策として各インバータに横流抑制リアクトルを接続するが、コストや重量、損失の増加などの新たな問題が生じる。この問題の解決のため、できる限り横流抑制リアクトルを小さくし、制御により横流を抑制する手法が検討されている。 特許文献2には、スイッチング素子のゲートタイミング(ON/OFF信号のタイミング)を調整して横流を抑制する手法が記載され、その実施例9(段落[0139])では、NPC型やT型の3レベルインバータの並列構成における横流電流の抑制制御が提案されている。 特開2008-92651 WO2014/123199 特開2015-8566 特許文献2の手法では、スイッチング時に横流電流を制御するために長期間スイッチングが行われないと横流電流が拡大してしまう問題点がある。図9は3レベルインバータの並列構成において、一時的に周波数が低下した場合の動作状態を示したものである。電圧指令値Vrefが零クロスするときにキャリア三角波(図9のキャリア1とキャリア2)と交差しないため、区間Aではキャリア1周期以上、区間Bでは1.5周期以上にわたりスイッチングが行われない。3レベルインバータでは電圧指令値Vrefが零クロスするときにキャリア三角波と交差しない場合があり、そのたびに横流電流が拡大する恐れがある。 また、最近では特許文献3に示す5レベルインバータなど、3レベルを超えるマルチレベルインバータが提案されている。このインバータをPWM変調する場合、図6のように4つのキャリア三角波を用いる。そのため、電圧指令値Vrefの零クロスだけでなく±0.5を通過する際も図3と同様の問題が発生する。3レベルを超えるマルチレベルインバータを並列構成とする場合、3レベルよりも横流電流の増加が頻繁に発生してしまう。 よって、本発明は上記問題点の解決を目的として、一定期間内に電圧指令値とキャリア三角波とを確実に交差させスイッチングが行われるように電圧指令値を補正することで横流電流を抑制させるマルチレベル電力変換装置のユニット制御装置を提供することにある。 本発明は、3レベル以上のマルチインバータユニットを並列に接続し、横流電流抑制制御手段によりインバータユニット間の横流責務の均等化を図りながら電圧指令値とキャリア三角波を比較し、インバータ内のスイッチング素子のオン・オフ信号を生成する制御装置において、前記横流電流抑制制御手段の前段に電圧指令値補正手段を設け、電圧指令値補正手段は、電圧指令値Vrefに対して閾値(禁止帯)-Vth~Vthを設け、電圧指令値Vrefの零への接近を抑制する第1のスイッチ手段と、前記キャリア三角波の傾きが正の時に、電圧指令値Vrefの負から正の値への変化を禁止する第2のスイッチ手段と、前記キャリア三角波の傾きが負の時に、電圧指令値Vrefの正から負の値への変化を禁止する第3のスイッチ手段を備え、電圧指令値補正手段により補正された電圧指令値を、前記横流電流抑制制御手段への電圧指令値としたものである。 本発明の第1のスイッチ手段は、電圧指令値Vrefが前記閾値Vth未満であることを検出する第1の比較器と、電圧指令値Vrefが前記閾値-Vthを越えることを検出する第2の比較器を有し、電圧指令値Vrefが閾値-Vth~Vthの範囲外時には電圧指令値Vrefを出力し、閾値-Vth~Vthの範囲内時には前回の出力値をホールドする機能を備え、第2のスイッチ手段は、第1のスイッチ手段の出力が正の値であることを検出する第3の比較器と、ホールドされた前回の出力値が負の値であることを検出する第4の比較器と、前記キャリア三角波の微分値の傾きが正の値であることを検出する第5の比較器を有し、第3~第5の各比較器からの出力信号「1」でホールドされた前回の出力値を出力し、出力信号「1」でない時に、前記第1のスイッチ手段から出力する機能を備え、第3のスイッチ手段は、第2のスイッチ手段の出力が負の値であることを検出する第6の比較器と、ホールドされた前回の出力値が正の値であることを検出する第7の比較器を有し、第6,第7の各比較器からの出力信号「1」で、且つ前記キャリア三角波の微分値の傾きが負の値のときにホールドされた前回の出力値を補正した電圧指令値Vref ́として出力し、キャリア三角波の微分値の傾きが正の時に、前記第2のスイッチ手段の出力を出力する機能を備えたものである。 また、本発明は、マルチインバータユニットを三相とし、三相の電圧指令値Vrefを、前記電圧指令値補正手段により補正された電圧指令値Vref ́からそれぞれ減算器を介して各別に減算し、得られた算出値の総和値を三相の電圧指令値Vrefに各別に加算して新たに補正された三相の各電圧指令値Vref*とし、電圧指令値Vref*を前記横流電流抑制制御手段に対する電圧指令値としたものである。 更に、本発明は、電圧指令値補正手段をN-2段直列に接続し、2段目以降の電圧指令値補正手段の入力を前段の電圧指令値補正手段の出力とし、直列に接続したn段目の電圧指令値補正手段では、入力(各段の電圧指令値Vref-n)が閾値2n/(N-1)-1-Vth&lt;Vref-n&lt;2n/(N-1)-1+Vthの範囲内であるか否かに基づいて、各段の電圧指令値補正手段の出力を生成するものである。たたし、Nはインバータのマルチレベル数、N≧4、n=1...N-2 以上のとおり、本発明によれば、電圧指令値が零付近にあっても必ずキャリア三角波の頂点間で1回のスイッチングを発生させることで、横流電流抑制制御を行う機会を増やし、横流電流を小さくすることができる。 本発明の実施形態を示す電圧指令値補正ブロック図。 横流電流抑制制御ブロック図。 本発明の他の実施形態を示す電圧指令値補正ブロック図。 本発明の他の実施形態を示す電圧指令値補正ブロック図。 電圧指令値の補正波形図。 電圧指令値の補正波形図。 3レベルインバータの主回路構成図(1相分)で、(a)はNPC型、(b)はA- NPC型、(c)FC型。 FC型3レベルインバータのユニット並列構成図。 スイッチング周波数低下時の説明波形図。 実施例の説明に先立って、本発明が適用されるマルチレベル電力変換装置の横流電流抑制制御ブロックについて説明する。図2はインバータユニット1相あたりの横流電流抑制制御ブロックを示したもので、インバータユニットの各相にそれぞれ設置されている。なお、図2の制御ブロックは3レベルインバータに適用した例で、特許文献2の図12と同じであるが、本実施例では横流電流抑制制御ブロックに入力する電圧指令Vref ́を、図1で示す電圧指令値補正ブロックによって補正するものである。 図2において、PWM変調器21は入力された電圧指令値Vref ́とキャリア三角波Vcarryを基にゲート指令値Gref1,Gref2を生成する。ゲート指令値Gref1は例えば、図8で示すスイッチング素子TN1,TN3に対応するゲート指令値となり、ゲート指令値Gref2はスイッチング素子TN2,TN4に対応するゲート指令値になる。ゲート指令値Gref1,Gref2はそれぞれ対応する遅延付加器DelayU1,DelayD1,DelayU2,DelayD2を通してデッドタイム処理器24に入力されてデッドタイム処理が行われた後、ゲート信号G1N,G2N,G3N,G4Nが出力される。これらのゲート信号が、各スイッチング素子のオン・オフ信号となる。 ゲート遅延指令値演算ブロック23には、頂点検出器22を通して検出されたキャリア三角波Vcarryの頂点検出信号と、ゲート指令値Gref1,Gref2が入力される。ゲート遅延指令値演算ブロック23では、バッファ32a,32bによりゲート指令値Gref1,Gref2のキャリア三角波Vcarryの半周期前の値を保持する。I1~I8は積分アンプ、SW11,SW21,SW31,SW41,SW51,SW61,SW71,SW81は入力スイッチ、SW12,SW22,SW32,SW42,SW52,SW62,SW72,SW82は出力スイッチ、AND1~AND8はアンド回路で、アンド回路AND1~AND4には符号検出器25の出力信号が入力され、入力スイッチSW11,SW21,SW31,SW41が閉じる条件の1つとして、インバータユニットの出力電流検出値IinvUNdetが正であることとする。この時、符号検出器25の出力信号が「1」となる。また、アンド回路AND5~AND8には符号検出器25の反転出力信号が入力され、入力スイッチSW51,SW61,SW71,SW81が閉じる条件の1つとして、インバータユニットの出力電流検出値IinvUNdetが負であることとする。この時、符号検出器25の出力信号が「0」となる。 入力スイッチSW11,SW51が閉じる別の条件は、ゲート指令値Gref1が「1」、キャリア三角波Vcarryの半周期前のゲート指令値Gref1が「0」、およびキャリア三角波Vcarryの半周期前のゲート指令値Gref2が「1」の場合である。また、入力スイッチSW21,SW61が閉じる別の条件は、ゲート指令値Gref1が「0」、キャリア三角波Vcarryの半周期前のゲート指令値Gref1が「1」、およびキャリア三角波Vcarryの半周期前のゲート指令値Gref2が「1」の場合である。 入力スイッチSW31,SW71が閉じる別の条件は、ゲート指令値Gref2が「1」、キャリア三角波Vcarryの半周期前のゲート指令値Gref2が「0」、およびキャリア三角波Vcarryの半周期前のゲート指令値Gref1が「0」の場合である。また、入力スイッチSW41,SW81が閉じる別の条件は、ゲート指令値Gref2が「0」、キャリア三角波Vcarryの半周期前のゲート指令値Gref2が「1」、およびキャリア三角波Vcarryの半周期前のゲート指令値Gref1が「0」の場合である。 出力スイッチSW12,SW22,SW32,SW42が閉じる条件は、インバータユニットの出力電流検出値IinvUNdetが正であることとする。出力スイッチSW52,SW62,SW72,SW82が閉じる条件はインバータユニットの出力電流検出値IinvUNdetが負であることとする。 加算器add1は、比例アンプPと出力スイッチSW12,SW52の出力を加算し、加算器add1の加算結果を乗算器mul1において-1倍して符号を反転する。この乗算器mul1の出力がゲート指令値Gref1が「0」から「1」に立ち上がるタイミングのDelayU1となる。加算器add2は、比例アンプPと出力スイッチSW22,SW62の出力を加算し、加算器add2の加算結果がゲート指令値Gref1が「1」から「0」に立ち下がるタイミングのDelayD1となる。 加算器add3は、比例アンプPと出力スイッチSW32,SW72の出力を加算し、加算器add3の加算結果を乗算器mul2において-1倍して符号を反転する。この乗算器mul2の出力がゲート指令値Gref2が「0」から「1」に立ち上がるタイミングのDelayU2となる。加算器add4は、比例アンプPと出力スイッチSW42,SW82の出力を加算し、加算器add4の加算結果がゲート指令値Gref2が「1」から「0」に立ち下がるタイミングのDelayD2となる。 本発明は、図2で示す横流電流抑制制御ブロックに入力される電圧指令値Vref ́は、図1で示す電圧指令値補正ブロックによって補正された電圧指令値としたものである。図1において、電圧指令値Vrefは、電流制御インバータや電圧制御インバータならば制御アンプの出力であり、制御を適用せずにフィードフォワードで与えられる場合もある。この電圧指令値Vrefは、比較器cmpAとcmpBおよびスイッチSWAの端子aにそれぞれ入力される。 比較器cmpAは、電圧指令値Vrefが設定された閾値Vth未満であることを検出し、「1」を出力する。比較器cmpBは電圧指令値Vrefが閾値-Vthを越えることを検出し「1」を出力する。比較器cmpA,cmpBの出力はアンド回路AND11の入力端子に各別に入力される。閾値Vthは図5で示した禁止帯の上限値に相当し、閾値-Vthは図5で示した禁止帯の下限値に相当する。アンド回路AND11は比較器cmpA,cmpBが共に「1」を出力し、-Vth&lt;Vref&lt;Vthが成立したとき「1」を出力する。スイッチSWAは、アンド回路AND11の出力が「1」のときに端子b側に切り換わり、「0」のときに端子aに切り換わる。 スイッチSWAの出力を入力するバッファZ-1の出力は、スイッチSWAの端子b側に接続される。スイッチSWAは、電圧指令値Vrefが閾値-Vth~Vthの範囲外ならばそのままVrefを出力信号として出力し、電圧指令値Vrefが閾値-Vth~Vthの範囲内ならば、前回出力した値をホールドする。スイッチSWBの端子aにはスイッチSWAの出力が接続される。スイッチSWCの端子aにはスイッチSWBの出力が接続される。 スイッチSWBの出力を入力するバッファZ-1の出力は、スイッチSWBの端子b側に接続される。比較器cmpDはスイッチSWA出力が正の値であることを検出し、「1」を出力する。比較器cmpCはバッファの値が負の値であることを検出して、「1」を出力する。各検出値はアンド回路AND12に入力される。また、アンド回路AND12には、比較器cmpGにより検出されたキャリア三角波の傾き信号が入力される。この傾き信号は、キャリア三角波を微分器sTにより微分し、比較器cmpGにより微分値(傾き)が正の値であることを検出してアンド回路AND12に入力される。 よって、アンド回路AND12は、比較器cmpC,cmpD,cmpGが全て「1」を出力したとき「1」を出力し、スイッチSWBを端子b側に切換える。スイッチSWBの出力信号は、キャリア三角波の傾きが正の時に電圧指令値Vrefが負から正に変化しても前回の負の値を出力し続け、キャリア三角波の傾きが負ならば電圧指令値Vrefをそのまま出力する。 スイッチSWCの端子aには、スイッチSWBの出力が接続され、スイッチSWCの出力を入力とするバッファZ-1の出力は、スイッチSWCの端子bに接続される。比較器cmpFはスイッチSWB出力が負の値であることを検出し、「1」を出力する。比較器cmpEはバッファZ-1の値が正の値であることを検出、「1」を出力する。アンド回路AND13は、比較器cmpE,cmpFが全て「1」て、且つキャリア三角波の微分(傾き)が負の時に「1」を出力し、スイッチSWCを端子b側に切り換える。スイッチSWCの出力信号は、キャリア三角波の傾きが負の時に電圧指令値Vrefが正から負に変化しても前回の正の値を出力し続け、キャリア三角波の傾きが正ならば電圧指令値Vrefをそのまま出力する。このスイッチSWCの出力信号は、電圧指令値Vref ́として図2の横流電流抑制制御ブロックに入力される。 この実施例では、スイッチとその周辺回路により3個のスイッチ手段が構成される。スイッチSWAは、電圧指令値Vrefに対して禁止帯-Vth~Vthを設け、電圧指令値Vrefを零に近づけないようにしている。スイッチSWBは、キャリア三角波の傾きが正の時に電圧指令値Vrefの負から正の値への変化を禁止している。スイッチSWCは、キャリア三角波の傾きが負の時に電圧指令値Vrefの正から負の値への変化を禁止している。 図5は電圧指令値Vref(実線)とその補正後の電圧指令値Vref ́(点線)を示したものである。補正前の電圧指令値Vrefは、零付近ではキャリア三角波と交差しないためスイッチングしない期間が長くなっている。この間は横流電流を抑制する手段を失ってしまう。スイッチング素子の電圧降下にずれがある場合、図5のGref1、Gref2で示すスイッチングしない期間でずれの電圧が横流抑制リアクトルに印加され続け、横流電流が拡大してしまう。 一方、本実施例では、補正により電圧指令値Vref ́は零付近に禁止帯が設定され、さらにキャリア三角波の傾きが負の時は電圧指令値Vref ́の正から負への変化が禁止される。これにより電圧指令値Vref ́は図5のGref1 ́のように補正され、キャリア三角波の頂点間で最低1回のスイッチングが確実に行われる。 実施例1によれば、スイッチングしない期間を短くできるため、横流電流の拡大を防ぐことができる。禁止帯の閾値Vthは、スイッチング素子が出力できる最小ONパルス幅を満たすように設定する必要がある。なお、実施例1により電圧指令値の補正を行うと、電圧指令値の零付近でスイッチング回数が増加し、損失が増えてしまう。しかし電力変換装置の出力力率の高い用途に限定すれば、出力電圧と出力電流の位相がほぼ等しくなるため電圧指令値の零付近では出力電流の瞬時値も零に近くなり、電圧指令値の零付近でスイッチング回数が増加しても遮断する出力電流は小さくスイッチング損失が微小となるため、損失増加は微小となる。 図1で示す電圧指令補正ブロックを用いた横流電流抑制制御により電圧指令値を変更すると、出力電圧ひずみ、出力電流ひずみが発生するケースが考えられる。実施例2では、この問題点を解消するものである。図3で示す電圧指令補正ブロックは、3相3線式の3レベルインバータを対象にしたもので、VrefUはU相電圧指令値、VrefVはV相電圧指令値、VrefWはW相電圧指令値で、各相の電圧指令値VrefU,VrefV,VrefWに対して、図1で得られた補正後の電圧指令値VrefU ́,VrefV ́,VrefW ́を加減算することで、新たな電圧指令値VrefU*,VrefV*,VrefW*を得て図2で示す横流電流抑制制御ブロックへの電圧指令値Vref ́とするものである。 すなわち、図1で示す電圧指令補正ブロックでの補正後の電圧指令値VrefU ́を入力し、減算器sub1において補正後の電圧指令値VrefU ́からVrefUを減算してU相補正操作量を求め、減算器sub2において補正後の電圧指令値VrefV ́からVrefVを減算してV相補正操作量を求める。さらに減算器sub3において補正後の電圧指令値VrefW ́からVrefWを減算してW相補正操作量を求める。加算器add10では各相の補正操作量を全て加算し、加算結果と電圧指令値VrefU,VrefV,VrefWをそれぞれ加算器add11,add12,add13で加算して各相の新たな電圧指令値VrefU*,VrefV*,VrefW*を得る。 以上により得られた新たな電圧指令値VrefU*,VrefV*,VrefW*は、相電圧では補正操作によるひずみは重畳するが、線間電圧は補正の影響を受けない。3相3線式のインバータでは外部負荷への影響は線間電圧のみに依存するため、以上の操作を行うことで、補正により出力電圧ひずみ、出力電流ひずみが発生する問題を解決することができる。 図4で示す実施例は、実施例1を4レベル以上(Nレベル)のマルチレベルインバータに適用する場合の例である。図4は、図1で示す電圧指令補正ブロックをN-2段直列に接続した構成で、例として3段直列による5レベルインバータ向けの構成における1段あたりの構成図を示したものである。 電圧指令値Vrefは、最初の段(n=1)ならば実施例1と同様に制御アンプの出力やフィードフォワードで与えられ、2段目以降(n≧2)ならば前段の出力である。比較器cmpAnは、n段目の電圧指令値補正手段の電圧指令値Vref-nが閾値2n/(N-1)-1+Vth未満であることを検出する。比較器cmpBnは、電圧指令値Vrefが閾値2n/(N-1)-1-Vthを超えることを検出し「1」を出力する。ここで、閾値Vthは図6で示す禁止帯2の上限値に相当する。比較器cmpAn,cmpBnが共に「1」を出力し、2n/(N-1)-1-Vth&lt;Vref-n&lt;2n/(N-1)-1+Vthが成立するときにアンド回路AND1nは「1」を出力する。 スイッチSWAnは、アンド回路AND11nの出力「1」により端子b側に切り換わり、「0」時で端子a側に切り換わる。スイッチSWAnの出力を入力するバッファZ-1の出力は、スイッチSWAnの端子b側に接続される。スイッチSWAnは、電圧指令値Vref-nが閾値2n/(N-1)-1-Vth&lt;Vref-n&lt;2n/(N-1)-1+Vthの範囲外ならばそのままVrefを出力信号として出力し、電圧指令値Vref-nが2n/(N-1)-1-Vth&lt;Vref-n&lt;2n/(N-1)-1+Vthの範囲内ならば、前回出力した値をホールドする。スイッチSWBnの端子aにはスイッチSWAnの出力が接続される。スイッチSWCの端子aにはスイッチSWBの出力が接続される。 スイッチSWBnの出力を入力するバッファZ-1の出力は、スイッチSWBnの端子b側に接続される。比較器cmpDnはスイッチSWAn出力が2n/(N-1)-1よりも大きい値であることを検出し、「1」を出力する。比較器cmpCnはバッファの値が2n/(N-1)-1よりも小さな値であることを検出して、「1」を出力する。各検出値はアンド回路AND12nに入力される。また、アンド回路AND12nには、比較器cmpGnにより検出されたキャリア三角波の傾き信号が入力される。この傾き信号は、キャリア三角波を微分器sTにより微分し、比較器cmpGnにより微分値(傾き)が正の値であることを検出して「1」を出力し、アンド回路AND12nに入力される。 スイッチSWBnの出力信号は、キャリア三角波の傾きが正の時に電圧指令値Vrefが2n/(N-1)-1よりも大きい値に変化しても前回の2n/(N-1)-1よりも小さい値(正確には、2n/(N-1)-1-Vth)を出力し続け、キャリア三角波の傾きが負ならば電圧指令値Vrefをそのまま出力する。スイッチSWBnの出力信号はスイッチSWCnの端子aに入力される他、比較器cmpF1、バッファZ-1に入力される。 スイッチSWCnの出力を入力するバッファZ-1の出力は、スイッチSWCnの端子b側に接続される。比較器cmpFnはスイッチSWBnの出力が2n/(N-1)-1よりも小さい値であることを検出し、「1」を出力する。比較器cmpEnはバッファZ-1の値が2n/(N-1)-1よりも大きな値であることを検出して、「1」を出力する。各検出値はアンド回路AND13nに入力される。また、アンド回路AND13nには、比較器cmpGnにより検出されたキャリア三角波の傾き信号が入力される。比較器cmpGnは微分器sTによる微分信号の傾きが正であることを検出して「1」を出力し、論理を反転してアンド回路AND13nに入力される。 スイッチSWCnの出力信号は、キャリア三角波の傾きが負のときに電圧指令値Vrefが2n/(N-1)-1よりも小さい値に変化しても前回の2n/(N-1)-1よりも大きい値(正確には、2n/(N-1)-1-Vth)を出力し続け、キャリア三角波の傾きが正ならば電圧指令値Vrefをそのまま出力する。このスイッチSWCnの出力信号は、最終段(n=N-2)であれば電圧指令値Vref ́として図2の横流電流抑制制御ブロックに入力され、それ以外であれば、次の段の電圧指令値補正ブロックに入力される。図4は、1段目はn=1、2段目はn=2の例で示している。 上記のように動作する機能を設けた電圧指令値補正手段により、4レベル以上(Nレベル)のマルチレベルインバータに適用できる補正された電圧指令値の生成ができる。例として5レベルインバータにおける電圧指令値Vrefの補正の様子を図6に示す。5レベルインバータでは、キャリア三角波を4つ使用してPWM変調を行うため、図1の零(0)付近の他に+0.5、-0.5付近でも補正が必要となる。そこで本実施例では、図1で示すブロックを3段直列にして+0.5、-0.5付近の補正機能を追加したものである。 図6中のNはレベル数を表し、5レベルならばN=5である。これを図4の最上段のブロックB1に入力すると、2n/(N-1)-1=2/(5-1)-1=-0.5となり、最上段B1のスイッチSWA1では、電圧指令値Vrefに対して禁止帯-0.5-Vth~-0.5+Vthを設け、電圧指令値Vrefを-0.5に近づけない。図6で示す禁止帯3が、ここでの禁止帯に相当する。 スイッチSWB1では、キャリア三角波の傾きが正の時は、電圧指令値Vrefの-0.5よりも小さな値から-0.5よりも大きな値への変化を禁止する。スイッチSWC1では、キャリア三角波の傾きが負の時は、電圧指令値Vrefの-0.5よりも大きな値から-0.5よりも小さな値への変化を禁止する。ブロックB1は以上のように動作する。 中段のブロックB2は、2n/(N-1)-1=4/4-1=0となり、図1と同一の構成・動作となる。図6で示す禁止帯2が、ここでの禁止帯に相当する。 最下段のブロックB3は、n=3, N=5を代入して2n/(N-1)-1=0.5となり、0.5付近の電圧指令値Vrefの補正を行う。図6で示す禁止帯1が、ここでの禁止帯に相当する。 レベル数をNとおいて、n=1~N-2を代入し同様のブロックをN-2段直列にすることで、任意のレベル数に対応した電圧指令値の補正ブロックを構成することができる。ただし、レベル数を増加すると使用するスイッチング素子が増加するため、積分アンプの数がスイッチング素子数の2倍になるよう図2の横流電流抑制制御ブロックを拡張する必要がある。 また、実施例3は実施例2と組み合わせることができる。実施例2では対象を3レベルインバータにしているが、4レベル以上であっても適用することができる。その際、例えば5レベルの場合、0の他に0.5、-0.5でも補正が必要となり、すべての相で補正が必要となるタイミングが重ならないことを確認してから適用する必要がある。 実施例3によれば、4レベル以上のマルチレベルインバータを並列接続にした場合でも、必ずキャリア三角波の頂点間で1回のスイッチングを発生させることで、横流電流抑制制御を行う機会を増やし、横流電流を小さくすることができるものである。 copA~copG... 比較器 SWA~SWC... スイッチ AND11~AND13... アンド回路 sT... 微分器 Z-1... バッファ sub1~sub3... :減算器 add10~add13... 加算器 [EN JP6784089B2]: The present invention relates to a unit parallel control device of a multi-level power conversion device, and particularly relates to a control device for equalizing current responsibilities between each inverter unit. As a configuration example of the multi-level power converter, there are a 3-level inverter and a 5-level inverter, and Fig. 7 (a) shows one phase of the NPC type 3-level inverter. The phase voltage is generated by the ON / OFF operation of switching elements T1 to T4 such as IGBTs in the inverter. Further, the ON / OFF signal of each switching element is generally generated by PWM modulation that compares the voltage command value and the carrier triangular wave (triangle wave comparison PWM method). In addition to the NPC type shown in Fig. 7 (a), there are the T type shown in Fig. 7 (b) and the flying capacitor (hereinafter referred to as FC) type shown in Fig. 7 (c) as types of 3-level inverters. Patent Document 1 describes an example of an FC type 3-level inverter. Table 1 shows the switching pattern of the FC type 3-level inverter shown in Fig. 7 (c). When outputting a zero voltage with reference to the N terminal to the output terminal O, turn on T1 and T3, or turn on T2 and T4 to make FC conductive. The applied voltage of the capacitor C1 and the applied voltage of the capacitor C2 are equal, and VCF = Vdc1 / 2. In some cases, a plurality of such inverter units are arranged in parallel to form a power conversion device to support a large capacity. Figure 8 shows an example of FC type 3-level inverters arranged in parallel. At this time, if there is an individual difference between the inverter units, a difference in the output current will occur between the inverters (a cross current will be generated), and the current responsibility will vary. As a result, heat generation is concentrated on a specific inverter and the life is shortened. In the worst case, there is a problem that the switching element is destroyed by overcurrent or overheating. As a countermeasure, a cross flow suppression reactor is connected to each inverter, but new problems such as increased cost, weight, and loss arise. In order to solve this problem, a method of suppressing the cross flow by controlling the cross flow suppression reactor as small as possible is being studied. Patent Document 2 describes a method of suppressing cross current by adjusting the gate timing (ON / OFF signal timing) of the switching element, and in the ninth embodiment (paragraph [0139]), the NPC type and the T type are described. Suppression control of cross current in a parallel configuration of a 3-level inverter has been proposed. Japanese Patent Application Laid-Open No. 2008-92651 WO2014 / 123199 Japanese Patent Application Laid-Open No. 2015-8566 The method of Patent Document 2 has a problem that the cross current increases if switching is not performed for a long period of time in order to control the cross current during switching. Figure 9 shows the operating state when the frequency drops temporarily in the parallel configuration of the 3-level inverter. Since the carrier triangle wave (carrier 1 and carrier 2 in FIG. 9) does not intersect when the voltage command value Vref crosses zero, switching is not performed for one carrier cycle or more in section A and 1.5 cycles or more in section B. In a 3-level inverter, when the voltage command value Vref crosses zero, it may not intersect with the carrier triangle wave, and the cross current may increase each time. Recently, multi-level inverters exceeding 3 levels, such as the 5-level inverter shown in Patent Document 3, have been proposed. When this inverter is PWM modulated, four carrier triangle waves are used as shown in Fig. 6. Therefore, the same problem as in FIG. 3 occurs when passing ± 0.5 as well as the zero cross of the voltage command value Vref. When multi-level inverters with more than 3 levels are configured in parallel, the cross current increases more frequently than with 3 levels. Therefore, for the purpose of solving the above-mentioned problems, the present invention suppresses the cross current by correcting the voltage command value so that the voltage command value and the carrier triangular wave are surely intersected and switched within a certain period of time. The purpose is to provide a unit control device for a level power converter. In the present invention, multi-inverter units of 3 levels or more are connected in parallel, and the voltage command value and the carrier triangular wave are compared while trying to equalize the cross current responsibility between the inverter units by the cross flow current suppression control means, and the switching element in the inverter. In the control device that generates the on / off signal of, a voltage command value correction means is provided in front of the cross current suppression control means, and the voltage command value correction means sets a threshold (prohibited band) -Vth with respect to the voltage command value Vref. ~ Vth is provided to prohibit the change of the voltage command value Vref from negative to positive when the first switch means for suppressing the approach of the voltage command value Vref to zero and when the inclination of the carrier triangular wave is positive. It is provided with a second switch means and a third switch means for prohibiting a change of the voltage command value Vref from a positive value to a negative value when the inclination of the carrier triangular wave is negative, and is corrected by the voltage command value correction means. The voltage command value is used as the voltage command value for the cross current suppression control means. The first switching means of the present invention includes a first comparator that detects that the voltage command value Vref is less than the threshold Vth, and a second comparator that detects that the voltage command value Vref exceeds the threshold -Vth. It has a comparator and has a function to output the voltage command value Vref when the voltage command value Vref is out of the range of the threshold-Vth to Vth and to hold the previous output value when it is within the range of the threshold -Vth to Vth. The switching means of is a third comparator that detects that the output of the first switching means is a positive value and a fourth comparator that detects that the previous output value held is a negative value. It has a device and a fifth comparator that detects that the gradient of the differential value of the carrier triangular wave is a positive value, and is held by the output signal "1" from each of the third to fifth comparators. It has a function to output the previous output value and output from the first switching means when the output signal is not "1", and the third switching means has a negative value for the output of the second switching means. It has a 6th comparator that detects, and a 7th comparator that detects that the previous output value held is a positive value, and the output signals from the 6th and 7th comparators " 1 and when the voltage command value Vref ́ corrected for the previous output value held when the gradient of the differential value of the carrier triangular wave is negative and the gradient of the differential value of the carrier triangular wave is positive , It is provided with a function to output the output of the second switching means. Moreover, this invention is multiIIntertaunitIs three-phase, and the voltage command value Vref of the three phases is subtracted from the voltage command value Vref ́ corrected by the voltage command value correction means separately via a subtractor, and the total value of the obtained calculated values is calculated. Each of the three-phase voltage command values Vref is newly corrected by adding each to the three-phase voltage command value Vref.*And the voltage command value Vref*Is the voltage command value for the cross current suppression control means. Further, in the present invention, the voltage command value correction means are connected in series in N-2 stages, and the input of the voltage command value correction means in the second and subsequent stages is used as the output of the voltage command value correction means in the previous stage, and are connected in series. In the voltage command value correction means of the first stage, the input (voltage command value Vref-n of each stage) has a threshold of 2n / (N-1) -1-Vth &lt;Vref-n &lt;2n / (N-1) -1+. The output of the voltage command value correction means of each stage is generated based on whether or not it is within the range of Vth. However, N is the number of multi-level inverters, N 4, n = 1 ... N-2. As described above, according to the present invention, even if the voltage command value is near zero, by always generating one switching between the vertices of the carrier triangle wave, the opportunity to perform the cross current suppression control is increased, and the cross current is reduced. It can be made smaller. The voltage command value correction block diagram which shows the embodiment of this invention. Cross current suppression control block diagram. The voltage command value correction block diagram which shows the other embodiment of this invention. The voltage command value correction block diagram which shows the other embodiment of this invention. Correction waveform diagram of voltage command value. Correction waveform diagram of voltage command value. In the main circuit configuration diagram (1 phase) of the 3-level inverter, (a) is NPC type, (b) is A-NPC type, and (c) FC type. FC type 3-level inverter unit parallel configuration diagram. Explanatory waveform diagram when the switching frequency is lowered. Prior to the description of the embodiment, the cross current suppression control block of the multi-level power converter to which the present invention is applied will be described. Figure 2 shows the cross current suppression control block per phase of the inverter unit, which is installed in each phase of the inverter unit. The control block in FIG. 2 is an example applied to a three-level inverter and is the same as in FIG. 12 of Patent Document 2. However, in this embodiment, the voltage command Vref ́ input to the cross current suppression control block is shown in FIG. It is corrected by the indicated voltage command value correction block. In FIG. 2, the PWM modulator 21 generates gate command values Gref1 and Gref2 based on the input voltage command value Vref ́ and the carrier triangle wave Vcarry. The gate command value Gref1 is, for example, the gate command value corresponding to the switching elements TN1 and TN3 shown in FIG. 8, and the gate command value Gref2 is the gate command value corresponding to the switching elements TN2 and TN4. The gate command values Gref1 and Gref2 are input to the dead time processor 24 through the corresponding delay adders DelayU1, DelayD1, DelayU2, and DelayD2, and after dead time processing is performed, the gate signals G1N, G2N, G3N, and G4N are output. Will be done. These gate signals serve as on / off signals for each switching element. The vertex detection signal of the carrier triangle wave Vcarry detected through the vertex detector 22 and the gate command values Gref1 and Gref2 are input to the gate delay command value calculation block 23. In the gate delay command value calculation block 23, the values of the gate command values Gref1 and Gref2 before the half cycle of the carrier triangle wave Vcarry are held by the buffers 32a and 32b. I1 to I8 are integration amplifiers, SW11, SW21, SW31, SW41, SW51, SW61, SW71, SW81 are input switches, SW12, SW22, SW32, SW42, SW52, SW62, SW72, SW82 are output switches, and AND1 to AND8 are AND. In the circuit, the output signal of the code detector 25 is input to AND circuits AND1 to AND4, and the output current detection value IinvUNdet of the inverter unit is positive as one of the conditions for closing the input switches SW11, SW21, SW31, SW41. I will do it. At this time, the output signal of the code detector 25 becomes 1. In addition, the inverted output signal of the code detector 25 is input to the AND circuits AND5 to AND8, and the output current detection value IinvUNdet of the inverter unit is negative as one of the conditions for closing the input switches SW51, SW61, SW71, SW81. I will do it. At this time, the output signal of the code detector 25 becomes 0. Another condition for closing the input switches SW11 and SW51 is that the gate command value Gref1 is "1", the gate command value Gref1 half cycle before the carrier triangle wave Vcarry is "0", and the gate command value half cycle before the carrier triangle wave Vcarry. This is the case when Gref2 is "1". Another condition for closing the input switches SW21 and SW61 is that the gate command value Gref1 is "0", the gate command value Gref1 half cycle before the carrier triangle wave Vcarry is "1", and the gate half cycle before the carrier triangle wave Vcarry. This is the case when the command value Gref2 is "1". Another condition for closing the input switches SW31 and SW71 is that the gate command value Gref2 is "1", the gate command value Gref2 half a cycle before the carrier triangle wave Vcarry is "0", and the gate command value half a cycle before the carrier triangle wave Vcarry. This is the case when Gref1 is "0". Another condition for closing the input switches SW41 and SW81 is that the gate command value Gref2 is "0", the gate command value Gref2 half a cycle before the carrier triangle wave Vcarry is "1", and the gate half cycle before the carrier triangle wave Vcarry. This is the case when the command value Gref1 is "0". The condition for closing the output switches SW12, SW22, SW32, and SW42 is that the output current detection value IinvUNdet of the inverter unit is positive. The condition for closing the output switches SW52, SW62, SW72, and SW82 is that the output current detection value IinvUNdet of the inverter unit is negative. The adder add1 adds the outputs of the proportional amplifier P and the output switches SW12 and SW52, multiplies the addition result of the adder add1 by -1 in the multiplier mul1 and inverts the sign. The output of this multiplier mul1 becomes Delay U1 at the timing when the gate command value Gref1 rises from "0" to "1". The adder add2 adds the outputs of the proportional amplifier P and the output switches SW22 and SW62, and the addition result of the adder add2 is DelayD1 at the timing when the gate command value Gref1 drops from "1" to "0". The adder add3 adds the outputs of the proportional amplifier P and the output switches SW32 and SW72, multiplies the addition result of the adder add3 by -1 in the multiplier mul2, and inverts the sign. The output of this multiplier mul2 becomes Delay U2 at the timing when the gate command value Gref2 rises from "0" to "1". The adder add4 adds the outputs of the proportional amplifier P and the output switches SW42 and SW82, and the addition result of the adder add4 is Delay D2 at the timing when the gate command value Gref2 falls from "1" to "0". In the present invention, the voltage command value Vref ́ input to the cross current suppression control block shown in FIG. 2 is a voltage command value corrected by the voltage command value correction block shown in FIG. In FIG. 1, the voltage command value Vref is the output of the control amplifier in the case of a current control inverter or a voltage control inverter, and may be given by feedforward without applying control. This voltage command value Vref is input to the comparators cmpA and cmpB and the terminal a of the switch SWA, respectively. The comparator cmpA detects that the voltage command value Vref is less than the set threshold value Vth, and outputs "1". The comparator cmpB detects that the voltage command value Vref exceeds the threshold value -Vth and outputs "1". The outputs of the comparators cmpA and cmpB are separately input to the input terminals of the AND circuit AND11. The threshold value Vth corresponds to the upper limit value of the prohibited band shown in FIG. 5, and the threshold value-Vth corresponds to the lower limit value of the prohibited band shown in FIG. The AND circuit AND11 outputs "1" for both the comparators cmpA and cmpB, and outputs "1" when -Vth &lt;Vref &lt;Vth is satisfied. The switch SWA switches to the terminal b side when the output of the AND circuit AND11 is "1", and switches to the terminal a when the output of the AND circuit AND11 is "0". Buffer Z to input the output of switch SWA-1The output of is connected to the terminal b side of the switch SWA. The switch SWA outputs the Vref as an output signal as it is if the voltage command value Vref is outside the threshold value-Vth to Vth range, and holds the previously output value if the voltage command value Vref is within the threshold value -Vth to Vth range. To do. The output of switch SWA is connected to terminal a of switch SWB. The output of switch SWB is connected to terminal a of switch SWC. Buffer Z to input the output of switch SWB-1The output of is connected to the terminal b side of the switch SWB. The comparator cmpD detects that the switch SWA output is a positive value and outputs "1". The comparator cmpC detects that the value in the buffer is negative and outputs "1". Each detection value is input to the AND circuit AND12. Further, the inclination signal of the carrier triangular wave detected by the comparator cmpG is input to the AND circuit AND12. This slope signal differentiates the carrier triangle wave with the differentiator sT, detects that the differential value (slope) is a positive value with the comparator cmpG, and is input to the AND circuit AND12. Therefore, the AND circuit AND12 outputs "1" when the comparators cmpC, cmpD, and cmpG all output "1", and switches the switch SWB to the terminal b side. The output signal of the switch SWB continues to output the previous negative value even if the voltage command value Vref changes from negative to positive when the slope of the carrier triangle wave is positive, and if the slope of the carrier triangle wave is negative, the voltage command value Vref Is output as it is. The output of the switch SWB is connected to the terminal a of the switch SWC, and the buffer Z that takes the output of the switch SWC as an input.-1Output is connected to terminal b of switch SWC. The comparator cmpF detects that the switch SWB output has a negative value and outputs "1". Comparator cmpE is buffer Z-1Detects that the value of is a positive value and outputs "1". The AND circuit AND13 outputs "1" when the comparators cmpE and cmpF are all "1" and the derivative (slope) of the carrier triangle wave is negative, and switches the switch SWC to the terminal b side. The output signal of the switch SWC continues to output the previous positive value even if the voltage command value Vref changes from positive to negative when the slope of the carrier triangle wave is negative, and if the slope of the carrier triangle wave is positive, the voltage
[ZH CN107039980B]: 一种高压直流潮流控制器 [EN CN107039980B]: A high-voltage direct current power flow controller | [ZH CN107039980B]: 本发明涉及一种高压直流潮流控制器，包括两套模块化多电平变换器；两套模块化多电平变换器采用串联方式，其中一端分别接入直流电网的正极和负极，另一端互联接地，形成中性点；本发明的技术方案无需接入外部电源，结构简单,故障处理能力强，运行效率高。 [EN CN107039980B]: The invention relates to a high voltage DC power flow controller comprising two sets of modular multilevel converters. The two sets of modular multilevel converters are connected in series, and one end is accessed to the positive electrode and the negative electrode of a DC power grid and the other end is interconnected and grounded so as to form a neutral point. According to the technical scheme, an external power supply does not need to be connected so that the structure is simple, the fault processing capacity is high and the operation efficiency is high. | CN107039980B | 2017-08-11 2021-08-06 | CN201610077759A | 2016-02-03 2016-02-03 | CN201610077759A, 2016-02-03 CN201610077759A, 2016-02-03 | CN107039980B: 2021-08-06 | CHINA ELECTRIC POWER RES INST STATE GRID CORP CHINA 中国电力科学研究院 国家电网公司 | YANG BO YAO LIANGZHONG DING JIE CAO YUANZHI ZHUANG JUN CUI HONGFEN LI YAN WANG ZHIBING LU JUNFENG WANG WEISHENG CHI YONGNING TAO YIBIN LI GUANJUN HU JINHANG SANG BINGYU ZHOU CHEN YU HAOJIE FENG XINZHEN LIU HUAN YAN SHENGCHI HOU SHUYI LI YUELONG ZHU HONGBAO MA XINXIN XUE JINHUA TAO QIONG | H02J3/06: I H02M7/49: I | H02J3/06: I H02M7/49: I | CN104009463A CA2916020A1 CN104377720A | CN110048401A CN110048401 110048401 CN109687726A CN109687726 109687726 CN110661433A CN110661433 110661433 WO2021017170A1 WO2021017170 2021/017170 WO2021/017170A1 | [ZH CN107039980B]: 1 .一种高压直流潮流控制器，其特征在于:包括两套模块化多电平变换器；两套模块化 多电平变换器采用串联方式连接，其中一端分别接入直流电网的正极和负极，另一端互联 接地，形成中性点； 所述模块化多电平变换器包括三相全桥MMC单元、级联多电平变换器单元和DC/DC变换 器单元;所述三相全桥MMC单元和级联多电平变换器单元并联，其各自一端接入直流电网的 正极或负极，其另一端接入中性点;所述DC/DC变换器单元的直流输入端分别跨接于所述直 流电网的正极或负极和级联多电平变换器单元中桥臂电感后的第一个子模块直流侧电容 的负端，其输出端串接在所述直流电网正极或负极； 所述DC/DC变换器单元采用了H桥的拓扑结构，包括并联的电容和两个IBGT支路；每个 IGBT支路包括两个串联的IGBT单元;IGBT单元包括反向并联的IBGT和二极管;所述DC/DC变 换器单元的输出设有LC滤波电路； 所述DC/DC变换器单元通过调节输出电压的大小和极性来调节直流线路的潮流； 所述级联多电平变换器单元包括串联的桥臂电感和若干子模块;所述子模块包括并联 的IGBT支路和电容;所述IGBT支路包括两个串联的IGBT单元;所述IGBT单元包括反向并联 的IBGT和二极管;所述子模块的输出端与下一个所述子模块的第一个IGBT单元的输出端连 接；所述级联多电平变换器单元为后级DC/DC变换器单元提供可变的直流输入电压，所述 直流输入电压的调整通过调整级联多电平变换器的输出子模块的数量来实现； 所述级联多电平变换器单元根据当前所需潮流电流的大小和方向，调整后级DC/DC变 换器单元输入侧电压值。 2 .如权利要求1所述的一种高压直流潮流控制器，其特征在于：所述三相全桥MMC单元 包括三个并联的桥臂模块;所述桥臂模块包括由串联的若干子单元组成的半桥臂;所述子 单元包括并联的IGBT支路和电容;所述IGBT支路包括两个串联的IGBT单元;所述IGBT单元 包括反向并联的IBGT和二极管;所述子单元的输出端与下一个所述子单元的第一个IGBT单 元的输出端连接;每个桥臂模块还包括与所述子单元串联的桥臂电感。 3 .如权利要求1所述的一种高压直流潮流控制器，其特征在于:所述模块化多电平变换 器还包括与所述级联多电平变换器单元并联的电容。 [EN CN107039980B]: 1 A high-voltage DC power flow controller, characterized in that it includes two sets of modular multilevel converters; the two sets of modular multilevel converters are connected in series, one end of which is connected to the positive and negative poles of the DC power grid, The other end is interconnected and grounded to form a neutral point; the modular multi-level converter includes a three-phase full-bridge MMC unit, a cascaded multi-level converter unit and a DC/DC converter unit; the three-phase full-bridge MMC The unit and the cascaded multilevel converter unit are connected in parallel, and one end of each is connected to the positive or negative pole of the DC power grid, and the other end is connected to the neutral point; the DC input ends of the DC/DC converter units are respectively connected across all The positive or negative pole of the DC power grid and the negative terminal of the DC side capacitor of the first sub-module after the inductance of the bridge arm in the cascaded multilevel converter unit, the output terminal of which is connected in series with the positive or negative pole of the DC power grid; The DC/DC converter unit uses the H-bridge topology, including parallel capacitors and two IBGT branches; each IGBT branch includes two series IGBT units; the IGBT unit includes anti-parallel IBGT and diodes; The output of the DC/DC converter unit is provided with an LC filter circuit; the DC/DC converter unit adjusts the power flow of the DC line by adjusting the size and polarity of the output voltage; the cascaded multilevel converter unit includes Series-connected bridge arm inductors and several sub-modules; the sub-modules include parallel The IGBT branch and the capacitor; the IGBT branch includes two IGBT units connected in series; the IGBT unit includes an IBGT and a diode connected in anti-parallel; the output terminal of the submodule is connected to the first of the next submodule The output ends of each IGBT unit are connected; the cascaded multilevel converter unit provides a variable DC input voltage for the subsequent DC/DC converter unit, and the adjustment of the DC input voltage is achieved by adjusting the cascaded multilevel conversion The number of output sub-modules of the converter is realized; the cascaded multilevel converter unit adjusts the input side voltage value of the subsequent DC/DC converter unit according to the magnitude and direction of the current required tidal current. 2 The high-voltage DC power flow controller according to claim 1, characterized in that: the three-phase full-bridge MMC unit includes three bridge arm modules connected in parallel; the bridge arm module includes several sub-units connected in series The half bridge arm; the sub-unit includes a parallel IGBT branch and a capacitor; the IGBT branch includes two series-connected IGBT units; the IGBT unit includes an anti-parallel IBGT and a diode; the output of the sub-unit The terminal is connected with the output terminal of the first IGBT unit of the next sub-unit; each bridge arm module further includes a bridge arm inductance connected in series with the sub-unit. 3 The high-voltage DC power flow controller of claim 1, wherein the modular multilevel converter further comprises a capacitor connected in parallel with the cascaded multilevel converter unit. | [ZH CN107039980B]: 一种高压直流潮流控制器 技术领域： [0001]本发明涉及直流输电电力电子技术领域，更具体涉及一种高压直流潮流控制器。 背景技术： [0002]随着传统能源短缺和环境压力等问题逐渐加剧，人们已经认识到从传统能源向清 洁能源过渡的紧迫性和重要性。近年来，以风能、太阳能等为代表的新能源发电技术得到了 快速发展，但是，由于新能源具有间歇性、不稳定性等显著特点，使得接纳超大规模新能源 的传统技术受到越来越多的限制与挑战，因此，必须采用新的技术、装备和优化电网结构来 满足未来能源格局的深刻变化。与传统高压交流输电技术相比，特高压及柔性直流输电具 有无功损耗低、线路损耗低和无同步问题等优点，非常适合超远距离大容量电能输送，但因 其传输路径单一、无冗余方式等缺点，极易容易因系统故障而导致的终端停电等现象。 [0003]随着直流输电技术的发展，在两端直流输电的基础上形成了网络型直流输电系 统，即直流电网。直流电网是由大量直流端通过直流线路互联组成的能量传输系统，能够实 现新能源的平滑接入，具有灵活、安全的潮流控制特性，是一种适应性更强的供电模式。在 含有n个换流站的直流电网系统中，功率调节换流站的个数为n-1，则系统控制自由度为n1；若系统的支路数b大于n-1，则系统潮流无法通过换流站的控制实现有效调节，即会出现 系统自由度不够的情况。此时，系统中某些支路会因为得不到有效控制而出现过载跳闸，从 而导致同一结点的其它线路因为电流突然增大而相继被切除，进而危及整个电网的安全。 因此，需要引入额外的直流电网潮流控制设备，即直流潮流控制器，增加系统控制自由度， 提高系统对潮流的有效控制能力。 [0004] 鉴于直流潮流控制器，国内外众多研究机构已开展包括直流潮流控制器的拓扑结 构、调制方式以及控制策略等方面的研究。目前常用于直流电网的潮流控制器为电压型直 流潮流控制器，该类型潮流控制器具有电压低、容量小、损耗小等优点。专利申请公开号为 CN104009463A中提及一种适用于直流输电的串联型潮流控制器；该潮流控制器采用双向 DC/DC变换器和H桥变换器级联的拓扑结构；该潮流控制器分别串接于正负线路中，主要通 过调节A1和B1端的电压差AV1，A2和B2端之间的电压差AV2的值和方向来调节线路中的潮 流;此潮流控制器虽然能满足直流输电网的潮流控制功能，但存在以下不足。 [0005] 1）潮流控制器输入侧电压过高，使得整机的绝缘等级较高，使得设备的工程造价 过高； [0006] 2）潮流控制器DC/DC变换单元使用多级变换器级联的拓扑结构，每级变换器的效 率均会影响整机的整体效率，最终使得整机损耗过大； [0007] 3）潮流控制器DC/DC变换单元采用双向DC/DC变换器级联H桥单元的结构，使得DC/ DC变换单元的结构复杂，同时也增加了调试和安装的复杂度。 发明内容： [0008]本发明的目的是提供一种高压直流潮流控制器，无需接入外部电源，结构简单，故 障处理能力强，运行效率高。 [0009] 为实现上述目的，本发明采用以下技术方案:一种高压直流潮流控制器，包括两组 模块化多电平变换器;两套模块化多电平变换器采用串联方式连接，其中一端分别接入直 流电网的正极和负极，另一端互联接地，形成中性点。 [0010] 所述模块化多电平变换器包括三相全桥MMC（Modular Multilevel Converter）单 元、级联多电平变换器单元和DC/DC变换器单元;所述三相全桥MMC单元和级联多电平变换 器单元并联，其各自一端接入直流电网的正极（负极），其各自另一端互联共同接入地线;所 述DC/DC变换器单元的直流输入端接入所述直流电网的正极（负极）和级联多电平变换器中 第一个子模块的直流侧电容的负端，输出端串接在所述直流电网正极（负极）。 [0011]所述级联多电平变换器包括串联的电感和若干子模块;所述子模块包括并联的 IGBT支路和电容;所述IGBT支路包括两个串联的IGBT单元;所述IGBT单元包括反向并联的 IBGT和二极管;所述子模块的输出端与下一个所述子模块的第一个IGBT单元的输出端连 接。 [0012] 所述级联多电平变换器单元为后级DC/DC变换器单元提供可变的直流输入电压， 所述直流输入电压的调整通过调整第一个所述级联多电平变换器单元子模块接入数量来 实现。 [0013]所述DC/DC变换器单元采用了H桥的拓扑结构，包括并联的电容和两个IBGT支路； 每个IGBT支路包括两个串联的IGBT单元;IGBT单元包括反向并联的IBGT和二极管;所述DC/ DC变换器单元的输出设有LC滤波电路。 [0014] 所述DC/DC变换器单元通过调节输出电压的大小和极性来调节直流线路的潮流。 [0015]所述三相全桥MMC单元包括三个并联的桥臂模块;所述桥臂模块分为上下桥臂，分 别由串联的若干子单元组成；所述子单元包括并联的IGBT支路和电容;所述IGBT支路包括 两个串联的IGBT单元;所述IGBT单元包括反向并联的IBGT和二极管;所述子单元的输出端 与下一个所述子单元的第一个IGBT单元的输出端连接;每个桥臂模块还包括与所述子单元 串联的电感。 [0016]所述模块化多电平变换器还包括与所述级联多电平变换器并联的电容。 [0017]所述级联多电平变换器根据当前所需潮流电流的大小和方向，调整潮流控制器直 流输出侧电压值。 [0018]和最接近的现有技术比，本发明提供技术方案具有以下优异效果 [0019] 1、本发明技术方案中的级联多电平变换器单元故障处理能力强，运行效率高； [0020] 2、本发明技术方案的DC/DC单元使用H桥变换器加LC滤波器结构，在保持性能不变 的前提下，使变换器结构最简单。； [0021] 3、本发明技术方案不仅降低了变换器的复杂度，还节约了设备成本； [0022] 4、本发明技术方案将故障模块直接切除而不影响变换器的输出，提高了整机的可 靠性； [0023] 5、本发明技术方案的级联多电平变换器可根据当前所需潮流电流的大小和方向， 调整后级DC/DC变换器单元直流输入侧电压值，以使得后级DC/DC变换器单元一直以高效率 的方式运行。 附图说明 [0024]图1为本发明实施例的直流输电系统拓扑结构示意图； [0025]图2为本发明实施例的DC/DC变换器拓扑结构示意图。 具体实施方式 [0026]下面结合实施例对发明作进一步的详细说明。 [0027] 实施例1： [0028]本例的发明提供一种高压直流潮流控制器，其级联多电平变换器单元可为后级 DC/DC变换器提供较低的直流输入电压，此外，该高压直流潮流控制器具有故障处理能力 强，运行效率高等优点。 [0029]本发明控制器的拓扑结构如附图1所示。从图中可以看出本发明控制器具有双极 特性可以应用于真双极高压直流输电系统。双极特性，即整个系统包括两套模块化多电平 变换器(MMC)，且两套变换器的一端输出串联接地，形成中性点，其余两输出端接入直流电 网正极和负极。由于变换器的正极与负极结构对称，下文以单极变换器为例说明本发明装 置的接入方式和基本结构。附图1中框1为级联多电平变换器单元，该变换器单元一端接入 直流电网的正极，另一端与地线互联，该变换器主要为后级DC/DC变换器单元提供可变的直 流输入电压，电压的调整主要通过调整附图1中框1中级联多电平变换器单元子模块接入子 模块的数量;附图1中框2为DC/DC变换器单元(该变换器单元输出电压极性可正可负，但某 一工况下电压的极性是固定的)。该变换器单元的直流输入端分别接直流电网的正极端和 附图1中框1中级联多电平变换器单元直流侧电容的负端，输出端串接在直流母线中。该DC/ DC变换器主要通过调节输出电压的大小和极性来调节直流线路的潮流。该DC/DC变换器的 拓扑结构图如图2所示。如附图2所示，该DC/DC变换器采用了H桥的拓扑结构。 [0030] 本发明控制器中的级联多电平变换器可根据当前所需潮流电流的大小和方向，调 整潮流控制器直流输入侧电压值，以使得后级DC/DC变换器单元一直以高效率的方式运行。 多电平变换器输出电压值的调整，主要通过调整工作子模块的数量来实现的。工作的子模 块数量越多，输出电压值越大;工作的子模块数量越少，输出电压值越小。 [0031]最后应当说明的是：以上实施例仅用以说明本发明的技术方案而非对其限制，所 属领域的普通技术人员尽管参照上述实施例应当理解:依然可以对本发明的具体实施方式 进行修改或者等同替换，这些未脱离本发明精神和范围的任何修改或者等同替换，均在申 请待批的本发明的权利要求保护范围之内。 [EN CN107039980B]: The technical field of a high-voltage DC power flow controller: [0001] The present invention relates to the field of DC transmission power electronics technology, and more specifically to a high voltage DC power flow controller. Background technique: [0002] With the gradual intensification of traditional energy shortages and environmental pressures, people have realized the urgency and importance of the transition from traditional energy to clean energy. In recent years, new energy power generation technologies represented by wind energy and solar energy have been rapidly developed. However, due to the intermittent and unstable characteristics of new energy sources, more and more traditional technologies that accept super-large-scale new energy sources have received more and more attention. Therefore, new technologies, equipment and optimized grid structure must be adopted to meet the profound changes in the future energy pattern. Compared with traditional high-voltage AC transmission technology, UHV and flexible DC transmission have the advantages of low reactive power loss, low line loss and no synchronization problems. They are very suitable for ultra-long-distance and large-capacity power transmission, but because of their single transmission path, there is no redundancy. Other shortcomings such as other methods are extremely easy to cause terminal power outages due to system failures. [0003] With the development of DC power transmission technology, a network-type DC power transmission system, that is, a DC power grid, has been formed on the basis of DC power transmission at both ends. The DC power grid is an energy transmission system composed of a large number of DC terminals interconnected through DC lines. It can realize the smooth access of new energy, has flexible and safe power flow control characteristics, and is a more adaptable power supply mode. In a DC grid system with n converter stations, if the number of power regulation converter stations is n-1, the system control degree of freedom is n1; if the number of branches b of the system is greater than n-1, the system power flow cannot be To achieve effective adjustment through the control of the converter station, there will be insufficient system freedom. At this time, some branches in the system will be overloaded and tripped because they cannot be effectively controlled, which will cause other lines of the same node to be cut off due to the sudden increase in current, which will endanger the safety of the entire power grid. Therefore, it is necessary to introduce additional DC grid power flow control equipment, namely DC power flow controller, to increase the degree of freedom of system control and improve the effective control ability of the system to the power flow. [0004] In view of the DC power flow controller, many domestic and foreign research institutions have carried out research including the topology, modulation method, and control strategy of the DC power flow controller. The current power flow controllers commonly used in DC power grids are voltage-type DC power flow controllers. This type of power flow controller has the advantages of low voltage, small capacity, and low loss. Patent application publication number CN104009463A mentions a series power flow controller suitable for direct current transmission; the power flow controller adopts a cascaded topology of bidirectional DC/DC converters and H-bridge converters; the power flow controllers are connected in series respectively. Connected to the positive and negative lines, the power flow in the line is adjusted mainly by adjusting the voltage difference AV1 between A1 and B1, and the value and direction of the voltage difference AV2 between A2 and B2; although this power flow controller can meet the requirements of the DC transmission grid The power flow control function has the following shortcomings. [0005] 1) The voltage on the input side of the power flow controller is too high, which makes the insulation level of the whole machine higher, and makes the engineering cost of the equipment too high; [0006] 2) The DC/DC conversion unit of the power flow controller uses a multi-level converter cascade topology, and the efficiency of each level of converter will affect the overall efficiency of the whole machine, and ultimately make the whole machine too much loss; [0007] 3) The DC/DC conversion unit of the power flow controller adopts the structure of the bidirectional DC/DC converter cascaded with the H-bridge unit, so that the DC/DC converter The structure of the DC conversion unit is complex, which also increases the complexity of debugging and installation. Summary of the invention: [0008] The purpose of the present invention is to provide a high-voltage DC power flow controller, without access to external power supply, simple structure, so It has strong fault handling capability and high operating efficiency. [0009] In order to achieve the above purpose, the present invention adopts the following technical solutions: a high-voltage direct current power flow controller, including two sets of modular multilevel converters; two sets of modular multilevel converters are connected in series, one of which is connected in series Connected to the positive and negative poles of the DC grid respectively, and the other end is interconnected and grounded to form a neutral point. [0010] The modular multilevel converter includes a three-phase full-bridge MMC (Modular Multilevel Converter) unit, a cascaded multilevel converter unit and a DC/DC converter unit; the three-phase full-bridge MMC unit and The cascaded multilevel converter units are connected in parallel, each end of which is connected to the positive electrode (negative electrode) of the DC power grid, and the other end of each is interconnected and connected to the ground wire; the DC input end of the DC/DC converter unit is connected to the The positive pole (negative pole) of the DC power grid and the negative terminal of the DC side capacitor of the first sub-module in the cascaded multilevel converter, and the output end is connected in series with the positive pole (negative pole) of the DC power grid. [0011] The cascaded multilevel converter includes a series-connected inductor and several sub-modules; the sub-module includes a parallel IGBT branch and a capacitor; the IGBT branch includes two series-connected IGBT units; the IGBT The unit includes an IBGT and a diode connected in reverse parallel; the output end of the sub-module is connected to the output end of the first IGBT unit of the next sub-module. [0012] The cascaded multilevel converter unit provides a variable DC input voltage for the subsequent DC/DC converter unit, and the DC input voltage is adjusted by adjusting the first cascaded multilevel converter. The number of sub-modules of the converter unit can be realized. [0013] The DC/DC converter unit uses an H-bridge topology, including parallel capacitors and two IBGT branches; each IGBT branch includes two series-connected IGBT units; IGBT units include anti-parallel IBGT and diode; the output of the DC/DC converter unit is provided with an LC filter circuit. [0014] The DC/DC converter unit adjusts the power flow of the DC line by adjusting the size and polarity of the output voltage. [0015] The three-phase full-bridge MMC unit includes three parallel bridge arm modules; the bridge arm module is divided into upper and lower bridge arms, respectively composed of several sub-units connected in series; the sub-units include parallel IGBT branches And capacitor; the IGBT branch includes two IGBT units connected in series; the IGBT unit includes an IBGT and a diode connected in anti-parallel; the output of the subunit is connected to the first IGBT unit of the next subunit The output terminal is connected; each bridge arm module also includes an inductor connected in series with the subunit. [0016] The modular multilevel converter also includes a capacitor connected in parallel with the cascaded multilevel converter. [0017] The cascaded multilevel converter adjusts the voltage value of the DC output side of the power flow controller according to the size and direction of the current required power flow current. [0018] Compared with the closest prior art, the technical solution provided by the present invention has the following excellent effects [0019] 1. The cascaded multilevel converter unit in the technical scheme of the present invention has strong fault handling capability and high operating efficiency; [0020] 2. The DC/DC unit of the technical scheme of the present invention uses an H-bridge converter plus an LC filter structure, which makes the converter structure the simplest while maintaining the same performance. ; [0021] 3. The technical solution of the present invention not only reduces the complexity of the converter, but also saves equipment costs; [0022] 4. The technical scheme of the present invention directly removes the faulty module without affecting the output of the converter, which improves the reliability of the whole machine; [0023] 5. The cascaded multilevel converter of the technical scheme of the present invention can adjust the DC input side voltage value of the subsequent DC/DC converter unit according to the current required power flow current size and direction, so that the subsequent DC/ The DC converter unit has been operating in a highly efficient manner. Description of the drawings [0024] FIG. 1 is a schematic diagram of a topological structure of a DC transmission system according to an embodiment of the present invention; [0025] FIG. 2 is a schematic diagram of a topological structure of a DC/DC converter according to an embodiment of the present invention. Detailed ways [0026] The invention will be further described in detail below in conjunction with the embodiments. [0027] Embodiment 1: [0028] The invention of this example provides a high-voltage DC power flow controller whose cascaded multi-level converter unit can provide a lower DC input voltage for the subsequent DC/DC converter. In addition, the high-voltage DC power flow controller It has the advantages of strong fault handling capability and high operating efficiency. [0029] The topology of the controller of the present invention is shown in FIG. 1. It can be seen from the figure that the controller of the present invention has bipolar characteristics and can be applied to a true bipolar high voltage direct current transmission system. Bipolar characteristics, that is, the entire system includes two sets of modular multilevel converters (MMC), and one end of the two sets of converters are connected in series to ground to form a neutral point, and the other two output ends are connected to the positive and negative poles of the DC grid. Since the positive and negative poles of the converter are symmetrical, the following uses a unipolar converter as an example to illustrate the access mode and basic structure of the device of the present invention. Box 1 in Figure 1 is a cascaded multilevel converter unit. One end of the converter unit is connected to the positive pole of the DC power grid, and the other end is connected to the ground wire. The converter mainly provides power for the subsequent DC/DC converter unit. Change the DC input voltage, the voltage adjustment is mainly by adjusting the number of sub-modules connected to the cascaded multi-level converter unit sub-module in box 1 in Figure 1; box 2 in Figure 1 is the DC/DC converter unit ( The output voltage polarity of the converter unit can be positive or negative, but the polarity of the voltage under a certain working condition is fixed). The DC input terminal of the converter unit is respectively connected to the positive terminal of the DC power grid and the negative terminal of the DC side capacitor of the cascaded multilevel converter unit in box 1 in Figure 1, and the output terminal is connected in series to the DC bus. The DC/DC converter mainly adjusts the power flow of the DC line by adjusting the size and polarity of the output voltage. The topological structure diagram of this DC/DC converter is shown as in Fig. 2. As shown in Figure 2, the DC/DC converter uses an H-bridge topology. [0030] The cascaded multilevel converter in the controller of the present invention can adjust the DC input side voltage value of the power flow controller according to the current required power flow current size and direction, so that the downstream DC/DC converter unit is always Run in an efficient manner. The adjustment of the output voltage value of the multilevel converter is mainly realized by adjusting the number of working sub-modules. The more the number of working sub-modules, the greater the output voltage value; the less the number of working sub-modules, the smaller the output voltage value. [0031] Finally, it should be noted that the above embodiments are only used to illustrate the technical solutions of the present invention and not to limit it. Those of ordinary skill in the art should understand that although referring to the above embodiments, specific implementations of the present invention can still be carried out. Modifications or equivalent substitutions, any modifications or equivalent substitutions that do not depart from the spirit and scope of the present invention are within the protection scope of the claims of the present invention for which the application is pending.
[EN CN113412566A]: Integrated charging and motor control system including transformer and multi-level power converter [FR WO2020242444A1]: CHARGEUR INTÉGRÉ ET SYSTÈME DE COMMANDE DE MOTEUR COMPRENANT UN TRANSFORMATEUR ET DES CONVERTISSEURS DE COURANT MULTI-NIVEAUX [ZH CN113412566A]: 包括变压器和多电平功率变换器的集成充电和电机控制系统 | [EN CN113412566A]: According to an aspect of the present disclosure, there is provided an apparatus including a first power converter stage, a second power converter stage, and a third power converter stage connected to a transformer module. At least one of the first power converter stage, the second power converter stage, and the third power converter stage is a multi-level power converter stage having multiple configurations to generate different output voltages from the input voltage. [FR WO2020242444A1]: Selon un aspect, l'invention concerne un appareil qui comprend des premier, deuxième et troisième étages de convertisseur de courant connectés à un module de transformateur. Au moins l'un des premier, deuxième et troisième étages de convertisseur de courant est un étage de convertisseur de courant multi-niveaux qui a de multiples configurations permettant de générer différentes tensions de sortie à partir d'une tension d'entrée. [ZH CN113412566A]: 根据本公开的一个方面，提供了一种包括与变压器模块连接的第一功率变换器级、第二功率变换器级、以及第三功率变换器级的装置。该第一功率变换器级、第二功率变换器级、以及第三功率变换器级中的至少一个是具有多种配置以从输入电压产生不同的输出电压的多电平功率变换器级。 | WO2020242444A1 | 2020-12-03 | US2019034014W | 2019-05-24 | US2019034014W, 2019-05-24 | WO2020242444A1: 2020-12-03 US2021016672A1: 2021-01-21 AU2019447744A1: 2021-09-09 CN113412566A: 2021-09-17 | HUAWEI TECH CO LTD HUAWEI TECHNOLOGIES CO LTD 华为技术有限公司 | ZHU HUIBIN DAI HEPING LIANG YONGTAO LIU WEIPING | H02J7/02: I B60L50/50: N H02M3/335: N B60L53/22: I B60L50/61: I H02J7/00: I B60L15/20: I B60L50/51: I B60L50/60: I B60L53/24: I H02P25/16: I | B60L2210/30: A B60L2210/40: A B60L53/24: I H02J7/02: I H02M1/10: I H02M1/4216: A H02M3/33561: A H02M7/4807: A H02M7/487: A H02J7/0071: I H02J7/00714: I H02J2207/20: A H02J2310/48: A H02M1/0058: A H02M1/0064: A H02M1/007: A H02M1/008: A H02M1/0085: A H02M1/0093: A Y02T10/62: A Y02T10/70: A Y02T10/7072: A Y02T10/72: A Y02T10/92: A Y02T90/14: A B60L2210/14: A B60L50/61: I B60L53/22: I | US2014225432A1 |  | [EN CN113412566A]: 1 A device comprising: a transformer module; a first power converter stage connected between the transformer module and an external power port; a second power converter stage connected between the transformer module and a battery port; A three-power converter stage connected between the transformer module and the motor port; and at least one of the first power converter stage, the second power converter stage, and the third power converter stage It is a multi-level power converter stage that has multiple configurations to generate different output voltages from the input voltage. 2 The apparatus of claim 1, wherein the first power converter stage is a multi-level power converter stage, the second power converter stage is a multi-level power converter stage, and the third The power converter stage is a two-level converter. 3 The device of claim 1, further comprising a rectifier boost circuit coupled between the external power port and the first power converter stage to input alternating current (AC) from the external power port Rectification and boosting are performed to provide a direct current (DC) input to the first power converter stage. 4 The device of claim 1, wherein the external power port is coupled to the battery port through the first power converter stage, the second power converter stage, and the transformer module for use The external power received at the external power port charges the battery coupled to the battery port. 5 The device of claim 1, wherein the battery port is coupled to the motor port through the second power converter stage, the third power converter stage, and the transformer module to use The power of the battery coupled to the battery port provides power to the motor coupled to the motor port. 6 The device of claim 5, wherein the third power converter stage includes an output terminal connected in series with the battery port to generate an output voltage to the motor port, the output voltage being equal to that from the battery The sum of the battery terminal voltage and the output voltage of the third power converter stage. 7 The apparatus of claim 1, further comprising a processor coupled to the first power converter stage, the second power converter stage, and the third power converter stage to provide the The level power converter stage selects the configuration to generate the appropriate input voltage level and output voltage level, so as to maximize the power conversion efficiency. 8 The device of claim 7, wherein the first power converter stage, the second power converter stage, and the transformer module form a resonant converter with a resonant frequency, and the processor is used to select The configuration is to maintain an operating frequency close to the resonance frequency. 9 The device of claim 1, wherein the transformer module comprises a transformer, a first winding of the transformer is coupled to the first power converter stage, and a second winding of the transformer is coupled to the second A power converter stage, a third winding of the transformer is coupled to the third power converter stage, and the first winding, the second winding, and the third winding are wound on a common core. 10 The apparatus of claim 1, wherein the transformer module includes a first transformer and a second transformer, a first winding of the first transformer is coupled to the first power converter stage, and the first transformer The second winding of the second transformer is coupled to the second power converter stage, the third winding of the second transformer is coupled to the third power converter stage, and the fourth winding of the second transformer is coupled to the second In the power converter stage, the first winding and the second winding are wound on the first core in the first transformer, and the third winding and the fourth winding are wound on the second transformer. On the second core. 11 The device according to claim 1, wherein the device is in an electric vehicle, the electric vehicle including a motor And one or more batteries, the motor is used to drive the electric vehicle and is coupled to the motor port, and the one or more batteries are coupled to the battery port to power the motor. 12 A method comprising: receiving power from an external source; transmitting power from the external source to a transformer module through a first power converter stage; transmitting power from the transformer module to a battery through a second power converter stage ; Then transfer the stored power from the battery to the transformer module through the second power converter stage; transfer power from the transformer module to the motor through the third power converter stage; At least one of the power converter stage, the second power converter stage, and the third power converter stage is configured to provide transmitted power at a selected voltage. 13 The method of claim 12, wherein configuring comprises configuring the first power converter stage in one of a plurality of available configurations according to the voltage of the power from the external source One of the available configurations configures the second power converter stage to provide power to the battery at a predetermined voltage. 14 The method according to claim 13, wherein receiving power from the external source comprises: receiving power as alternating current (AC) under a supply voltage, the method further comprising: converting the power provided to the first power The direct current (DC) voltage of the device stage is rectified and boosted to obtain the DC voltage higher than the supply voltage. 15 The method of claim 14, wherein transmitting power from the external source to the transformer module through the first power converter stage comprises: inverting the DC voltage to obtain a corresponding AC voltage , And provide the corresponding AC voltage to the transformer module. 16 The method of claim 15, wherein the first power converter stage, the transformer module, and the second power converter stage form a resonant converter having a resonant frequency, the method further comprising: Detecting the supply voltage of the power from the external source; and configuring the first power converter stage to generate the corresponding AC voltage at or near the resonance frequency. 17 The method of claim 12, further comprising: transferring the stored power from the battery at the battery voltage when transmitting power through the third power converter stage to generate a configurable voltage; and a series combination The battery voltage and the configurable voltage are used to obtain a combined voltage; and the combined voltage is provided to the motor. 18 An electric vehicle, comprising: an external power port for receiving electric power from an external power source; a motor for providing the driving force of the electric vehicle; a battery for storing power from the external power source, and Provide stored power to the motor; and an on-board charging and motor control unit, including: a transformer; a first power converter stage connected between the transformer and the external power port; a second power converter stage connected Between the transformer and the battery; a third power converter stage connected between the transformer and the motor; and at least the first power converter stage and the second power converter stage are Three-level power converter stage, the three The level power converter stage has a variety of configurations to generate different output voltages from the input voltage. 19 The electric vehicle according to claim 18, further comprising a processor coupled to transform the first power converter stage and the second power according to the voltage received at the external power port Device-level selection configuration. 20 The electric vehicle according to claim 19, wherein the first power converter stage, the transformer, and the second power converter stage form a resonant converter having a resonant frequency, and the processor is coupled to A configuration is selected to convert the voltage received at the external power port into a battery charging voltage when the frequency of the resonant converter is close to the resonant frequency. [ZH CN113412566A]: 1 .一种装置，包括： 变压器模块； 第一功率变换器级，连接在所述变压器模块与外部功率端口之间； 第二功率变换器级，连接在所述变压器模块与电池端口之间； 第三功率变换器级，连接在所述变压器模块与电机端口之间；以及 所述第一功率变换器级、所述第二功率变换器级、以及所述第三功率变换器级中的至 少一个是多电平功率变换器级，所述多电平功率变换器级具有多种配置以从输入电压产生 不同的输出电压。 2 .根据权利要求1所述的装置，其中，所述第一功率变换器级是多电平功率变换器级， 所述第二功率变换器级是多电平功率变换器级，所述第三功率变换器级是两电平变换器。 3 .根据权利要求1所述的装置，还包括耦合在所述外部功率端口与所述第一功率变换 器级之间的整流升压电路，以对来自所述外部功率端口的交流电(AC)输入进行整流和升 压，以向所述第一功率变换器级提供直流电(DC)输入。 4 .根据权利要求1所述的装置，其中，所述外部功率端口通过所述第一功率变换器级、 所述第二功率变换器级、以及所述变压器模块耦合至所述电池端口，以使用在所述外部功 率端口处接收的外部功率对耦合至所述电池端口的电池进行充电。 5 .根据权利要求1所述的装置，其中，所述电池端口通过所述第二功率变换器级、所述 第三功率变换器级、以及所述变压器模块耦合至所述电机端口，以使用来自耦合至所述电 池端口的电池的功率向耦合至所述电机端口的电机提供功率。 6 .根据权利要求5所述的装置，其中，所述第三功率变换器级包括与所述电池端口串联 的输出端子，以向所述电机端口产生输出电压，所述输出电压等于来自所述电池的电池端 口电压与所述第三功率变换器级的输出电压之和。 7 .根据权利要求1所述的装置，还包括耦合至所述第一功率变换器级、所述第二功率变 换器级、以及所述第三功率变换器级的处理器，以为所述多电平功率变换器级选择配置，以 产生适当的输入电压电平和输出电压电平，从而使功率变换效率最大化。 8 .根据权利要求7所述的装置，其中，所述第一功率变换器级、所述第二功率变换器级、 以及所述变压器模块形成具有谐振频率的谐振变换器，所述处理器用于选择所述配置以保 持接近所述谐振频率的工作频率。 9 .根据权利要求1所述的装置，其中，所述变压器模块包括变压器，所述变压器的第一 绕组耦合至所述第一功率变换器级，所述变压器的第二绕组耦合至所述第二功率变换器 级，所述变压器的第三绕组耦合至所述第三功率变换器级，所述第一绕组、所述第二绕组、 以及所述第三绕组绕在公共铁心上。 10 .根据权利要求1所述的装置，其中，所述变压器模块包括第一变压器和第二变压器， 所述第一变压器的第一绕组耦合至所述第一功率变换器级，所述第一变压器的第二绕组耦 合至所述第二功率变换器级，所述第二变压器的第三绕组耦合至所述第三功率变换器级， 所述第二变压器的第四绕组耦合至所述第二功率变换器级，所述第一绕组和所述第二绕组 绕在所述第一变压器中的第一铁心上，所述第三绕组和所述第四绕组绕在所述第二变压器 中的第二铁心上。 11 .根据权利要求1所述的装置，其中，所述装置在电动车辆中，所述电动车辆包括电机 和一个或多个电池，所述电机用于驱动所述电动车辆并且耦合至所述电机端口，所述一个 或多个电池耦合至所述电池端口以为所述电机供电。 12 .一种方法，包括： 接收来自外部源的功率； 通过第一功率变换器级将功率从所述外部源传输到变压器模块； 通过第二功率变换器级将功率从所述变压器模块传输到电池； 随后通过所述第二功率变换器级将存储的功率从所述电池传输到所述变压器模块； 通过第三功率变换器级将功率从所述变压器模块传输到电机；以及 对所述第一功率变换器级、所述第二功率变换器级、以及所述第三功率变换器级中的 至少一个进行配置，以在选定电压下提供传输的功率。 13 .根据权利要求12所述的方法，其中，进行配置包括根据来自所述外部源的所述功率 的电压，以多种可用配置中的一个配置所述第一功率变换器级，以所述多种可用配置中的 一个配置所述第二功率变换器级，从而以预定电压向所述电池提供功率。 14 .根据权利要求13所述的方法，其中，接收来自所述外部源的功率包括:在供电电压 下接收作为交流电(AC)的功率，所述方法还包括:对提供给所述第一功率变换器级的直流 电(DC)电压进行整流和升压，以获得高于所述供电电压的所述DC电压。 15 .根据权利要求14所述的方法，其中，通过所述第一功率变换器级将功率从所述外部 源传输到所述变压器模块包括:对所述DC电压进行逆变以获得对应的AC电压，并将所述对 应的AC电压提供给所述变压器模块。 16 .根据权利要求15所述的方法，其中，所述第一功率变换器级、所述变压器模块、以及 所述第二功率变换器级形成具有谐振频率的谐振变换器，所述方法还包括： 检测来自所述外部源的所述功率的供电电压；以及 配置所述第一功率变换器级，以产生频率处于或接近所述谐振频率的所述对应的AC电 压。 17 .根据权利要求12所述的方法，还包括： 在通过所述第三功率变换器级传输功率以产生可配置的电压时，在电池电压下传输来 自所述电池的存储的功率;以及 串联组合所述电池电压与所述可配置的电压，以获得组合电压；以及 向所述电机提供所述组合电压。 18 . 一种电动车辆，包括： 外部功率端口，用于接收来自外部功率源的电功率； 电机，用于提供所述电动车辆的驱动力； 电池，用于存储来自所述外部功率源的功率，并向所述电机提供存储的功率；以及 车载充电和电机控制单元，包括： 变压器； 第一功率变换器级，连接在所述变压器与所述外部功率端口之间； 第二功率变换器级，连接在所述变压器与所述电池之间； 第三功率变换器级，连接在所述变压器与所述电机之间；以及 至少所述第一功率变换器级和所述第二功率变换器级是三电平功率变换器级，所述三 电平功率变换器级具有多种配置以从输入电压产生不同的输出电压。 19 .根据权利要求18所述的电动车辆，还包括处理器，所述处理器耦合以根据在所述外 部功率端口处接收到的电压为所述第一功率变换器级和所述第二功率变换器级选择配置。 20 .根据权利要求19所述的电动车辆，其中，所述第一功率变换器级、所述变压器、以及 所述第二功率变换器级形成具有谐振频率的谐振变换器，所述处理器耦合以选择配置，以 在所述谐振变换器的频率接近所述谐振频率的情况下，将在所述外部功率端口处接收到的 所述电压变换为电池充电电压。 | [EN CN113412566A]: The technical field of integrated charging and motor control systems including transformers and multi-level power converters [0001] The present disclosure generally relates to the field of electric power circuits, such as electric power circuits used in electric vehicles. Background technique [0002] The electric power circuit includes an alternating current (AC) to direct current (direct current, DC) power converter, and a direct current to direct current power converter. Electric power converters have a wide range of uses, including but not limited to use in on board chargers (OBC) to charge electric vehicles (EV) batteries. Due to high voltage and high current, electric power converters are potentially dangerous. Isolation can reduce the risk, and there may be some safety standards that require isolation. [0003] A motor control unit (MCU) can control a motor, such as a motor of an EV. For example, the MCU can control the current from the battery of the EV to the motor. Summary of the invention [0004] According to an aspect of the present disclosure, there is provided an apparatus including a first power converter stage, a second power converter stage, and a third power converter stage connected to a transformer module. At least one of the first power converter stage, the second power converter stage, and the third power converter stage is a multi-level power converter stage, and the multi-level power converter stage has a variety of configurations to input The voltage produces different output voltages. [0005] Optionally, in the foregoing aspect, the first power converter stage is a multi-level power converter stage, and the second power converter stage is a multi-level power converter stage (for example, a three-level converter) And the third power converter stage is a two-level converter (for example, a full-bridge converter). [0006] Optionally, in any of the foregoing aspects, the device includes a rectifying and boosting circuit coupled between the external power port and the first power converter stage to compensate for alternating current (AC) from the external power port. The input is rectified and boosted to provide a direct current (DC) input to the first power converter stage. Optionally, the external power source may be direct current directly connected to the first power converter stage. [0007] Optionally, in any of the foregoing aspects, the external power port is coupled to the battery port through the first power converter stage, the second power converter stage, and the transformer module to use the external power received at the external power port Charge the battery coupled to the battery port. [0008] Optionally, in any of the foregoing aspects, the battery port is coupled to the motor port through the second power converter stage, the third power converter stage, and the transformer module to use power from the battery coupled to the battery port. The motor coupled to the motor port provides power. For example, the motor port can be coupled to an inverter (ie, a voltage source inverter), which generates a pulse width modulation (PWM) voltage output at both ends of the motor winding and is running During this period, the motor winding current is continuously controlled. [0009] Optionally, in any of the foregoing aspects, the third power converter stage includes an output terminal connected in series with the battery port to generate an output voltage to the motor port, the output voltage being equal to the battery port voltage from the battery and the third power The sum of the output voltages of the converter stages. [0010] Optionally, in any of the foregoing aspects, the device includes a first power converter stage coupled to a second power converter The processor stage and the processor of the third power converter stage select the configuration for the multi-level power converter stage to generate the appropriate input voltage level and output voltage level, thereby maximizing the power conversion efficiency. [0011] Optionally, in any of the foregoing aspects, the first power converter stage, the second power converter stage, and the transformer module form a resonant converter having a resonant frequency, and the processor is used to select a configuration to maintain close to the resonant frequency Working frequency. [0012] Optionally, in any of the foregoing aspects, the transformer module includes a transformer, the first winding of which is coupled to the first power converter stage, the second winding of the transformer is coupled to the second power converter stage, and the transformer The third winding of is coupled to the third power converter stage, and the first winding, the second winding, and the third winding are wound on the common core. [0013] Optionally, in any of the foregoing aspects, the transformer module includes a first transformer and a second transformer, the first winding of the first transformer is coupled to the first power converter stage, and the second winding of the first transformer is coupled To the second power converter stage, the third winding of the second transformer is coupled to the third power converter stage, the fourth winding of the second transformer is coupled to the second power converter stage, and the first winding and the second winding are wound around On the first core in the first transformer, the third winding and the fourth winding are wound on the second core in the second transformer. [0014] Optionally, in any of the foregoing aspects, the device is in an electric vehicle, the electric vehicle includes a motor and one or more batteries, the motor is used to drive the electric vehicle and is coupled to the motor port, one or more batteries Coupled to the battery port to power the motor. [0015] According to another aspect of the present disclosure, a method is provided. The method includes receiving power from an external source, transmitting the power to a transformer module through a first power converter stage, and transferring the power to a transformer module through a second power converter stage. Transfer from the transformer module to the battery. The method also includes subsequently transferring the stored power from the battery to the transformer module through the second power converter stage, and transferring power from the transformer module to the electric machine through the third power converter stage. At least one of the first power converter stage, the second power converter stage, and the third power converter stage is configured to provide transmitted power at a selected voltage. [0016] Optionally, in any of the foregoing aspects, configuring includes configuring the first power converter stage in one of multiple available configurations according to the voltage of the power from the external source, and in one of the multiple available configurations. The second power converter stage is configured to provide power to the battery at a predetermined voltage. [0017] Optionally, in any of the foregoing aspects, receiving power from an external source includes: receiving power as AC under a supply voltage, and the method further includes: rectifying the DC voltage provided to the first power converter stage And boost to obtain a DC voltage higher than the supply voltage. [0018] Optionally, in any of the foregoing aspects, transmitting power from an external source to the transformer module through the first power converter stage includes: inverting the DC voltage to obtain a corresponding AC voltage, and converting the corresponding AC voltage Supplied to the transformer module. [0019] Optionally, in any of the foregoing aspects, the first power converter stage, the transformer module, and the second power converter stage form a resonant converter having a resonant frequency, and the method includes: detecting power from an external source The first power converter stage is configured to generate a corresponding AC voltage with a frequency at or close to the resonance frequency. [0020] Optionally, in any of the foregoing aspects, the method includes: when transmitting power through the third power converter stage to generate a configurable voltage, transmitting the stored power from the battery at the battery voltage, and combining the power in series The battery voltage and the configurable voltage are used to obtain the combined voltage and provide the combined voltage to the motor. [0021] According to still another aspect of the present disclosure, there is provided an electric vehicle including: an external power port for receiving electric power from an external power source, a motor for providing driving force of the electric vehicle, and storing Power source A battery that provides power and provides stored power to the motor, and an on-board charger/motor control unit (OBC/MCU). The on-board charging and motor control unit includes a transformer, a first power converter stage connected between the transformer and an external power port, a second power converter stage connected between the transformer and the battery, and connected between the transformer and the motor The third power converter stage. At least the first power converter stage and the second power converter stage are three-level power converter stages having multiple configurations to generate different output voltages from the input voltage. [0022] Optionally, in any of the foregoing aspects, the processor is coupled to select a configuration for the first power converter stage and the second power converter stage according to the voltage received at the external power port. [0023] Optionally, in any of the foregoing aspects, the first power converter stage, the transformer, and the second power converter stage form a resonant converter having a resonant frequency, and the processor is coupled to select a configuration to operate the resonant converter When the frequency of is close to the resonance frequency, the voltage received at the external power port is converted into the battery charging voltage. [0024] The purpose of providing the content of the present invention is to introduce a series of concepts further described in the detailed description below in a simplified form. The content of the present invention is not intended to identify key features or essential features of the claimed subject matter, nor is it intended to be used as an auxiliary means to determine the scope of the claimed subject matter. The claimed subject matter is not limited to implementations that solve any or all of the disadvantages suggested in the background art. Description of the drawings [0025] Aspects of the present disclosure will be explained by way of example, and are not limited by the accompanying drawings. In the accompanying drawings, similar signs indicate similar elements. [0026] FIG. 1A shows the output voltage and output current of the charging station. [0027] FIG. 1B shows an example of a two-stage fast charger. [0028] FIG. 2A is a schematic diagram of an embodiment of an electric vehicle (EV). [0029] FIG. 2B is a schematic diagram of an embodiment of an EV with an OBC/MCU circuit. [0030] FIG. 2c shows the operating range of the electric motor in the EV. [0031] FIG. 2D shows an example of an MCU. [0032] FIG. 2E shows another example of an MCU. [0033] FIG. 3A shows an example of a combined OBC/MCU circuit in an EV. [0034] FIGS. 3B to 3E show examples of power converter stages that can be used in a combined OBC/MCU circuit in an EV. [0035] FIGS. 4A to 4D show different transformer module configurations that can be used in a combined OBC/MCU circuit in an EV. [0036] FIG. 5 shows EV components including two batteries, AC charging, and DC charging. [0037] FIG. 6 shows an example of a combined OBC/MCU circuit coupled with a dual winding motor. [0038] FIGS. 7A to 7B show an example of a combined OBC/MCU circuit including four power converter stages. [0039] FIG. 8 shows an example of a rectifier boost circuit coupled with a power converter stage. [0040] FIGS. 9A to 9B show another example of a rectifier boost circuit coupled with a power converter stage. [0041] FIG. 10 shows a method according to an example of the present technology. Detailed ways [0042] The present disclosure will be described with reference to the accompanying drawings, which generally relate to electric power circuits (for example, electric power circuits that can be used in electric vehicles). For example, the circuit described herein can be used to charge a battery from an external power source and control the power from the battery to the motor. Using shared circuits to perform these different functions is efficient and cost-effective. Examples include using three ports A power converter including a three-port power converter coupled with a transformer module to transfer power between three ports (for example, a port for external power, a port for a battery, and a port for a motor of an electric vehicle) Of three power converter stages. The three power converter stages can be used to transfer and convert power between any two ports in an efficient and adaptive manner. [0043] In an electric vehicle, a three-port power converter can be used to convert the power received from an external power source (for example, a charging station) into a suitable form, so as to charge the battery of the electric vehicle (for example, with the supply voltage The supplied alternating current (AC) is converted to direct current (DC) to be used to charge the battery at a voltage different from the supply voltage). The same three-port power converter can be used to convert the power from the battery to power the motor of the vehicle (for example, from the battery voltage to a voltage suitable for the motor, the voltage suitable for the motor may vary according to conditions). The power transfer between ports can be in either direction (for example, power transfer from the motor to the battery during braking, and power transfer from the battery to the external power consumer (for example, when the home power source is unavailable such as camping or emergency use) spare)). [0044] One or more of the power converter stages used may be a multi-level power converter stage that can be configured to provide two or more from a given input voltage Different output voltages. The use of such a multi-level power converter stage provides flexibility in power conversion, for example, allowing compatibility with external power sources that transmit power in different voltage ranges (for example, electric vehicles can adapt to different charging outputs with different voltages). Stations and/or household power outlets in different countries). [0045] Generally, the power conversion between any two ports in the three-port power converter may pass through two power converter stages and one transformer. In some examples, the two power converter stages and one transformer may be Form a resonant converter. Such a resonant converter may have a resonant frequency. When the resonant converter is operated near the resonant frequency, the efficiency is higher, and when it is operated far away from the resonant frequency, the efficiency is lower. Using one or more multi-level power converter stages, when the frequency used is at or close to the resonant frequency of this converter, voltage conversion within a certain voltage range is allowed, for example, when the frequency is constant or the frequency is relatively changed In small cases, one or more power converter stages are reconfigured to adapt to different supply voltages. [0046] It should be understood that the embodiments of the present disclosure can be implemented in many different forms, and should not be construed as being limited to the embodiments set forth herein. On the contrary, these embodiments are provided to make this disclosure detailed and complete, and to fully convey the concept of creative embodiments to those skilled in the art. In fact, the present disclosure is intended to cover alternatives, modifications, and equivalents of these embodiments included in the spirit and scope of the present disclosure as defined by the appended claims. In addition, in the following specific implementations of the embodiments of the present disclosure, many specific details are explained in order to provide a thorough understanding. However, it is clear to those of ordinary skill in the art that the embodiments of the present disclosure can be practiced without such specific details. [0047] The electric vehicle (EV) and hybrid electric vehicle (electric vehicle/hybrid electric vehicle, EV/HEV) market is a fast-growing segment, which requires the widespread deployment of fast chargers and faces many challenges. Among them, the most advanced The charger design may usually involve the following common practices and examples of related shortcomings: .Universal EV voltage compatibility with isolation: As shown in Figure 1A, EV fast chargers need to be able to use a very wide DC voltage range to charge EV batteries , As shown 200V-1000V DC voltage (output voltage (V) along the x-axis, output current (A) on the y-axis). For reasons of capital investment, the owner of the charging station may require that the same charger can be used for various EV/HEVs of the customer. However, designing the range of power supply output voltage (for example, a ratio of 1:4 or 1:5) is very challenging. .Full power capability under low output voltage level: when charging under low battery voltage, the charger needs to transmit phase The same power capability to reduce vehicle charging time. The rated power of fast chargers can reach 100kW, in some cases even higher. However, due to the rated current of the component, the power capability of a typical charger converter may be reduced at a lower output voltage. Otherwise, a large amount of spare parts may be required, resulting in higher costs and larger package sizes. .High efficiency under low load power conditions: When in the latter part of the battery charging cycle and the charging current is correspondingly reduced, the EV charger may operate at a low load power level. However, the efficiency of a typical AC-DC power converter is significantly reduced at low load power. Therefore, in order to operate the power station economically, it is usually necessary to improve the operating efficiency of the charger (for example, above 96%). .Modular design and economies of scale: From a cost perspective, it is best to build high-power fast chargers as building blocks in a modular design, so that multiple modules can be easily configured in parallel and the rated power can be increased. This also requires the charger module to be able to handle different levels of AC input voltage to cope with the global market. However, this is very challenging, and major suppliers need to provide different module designs for different regions of the world. And this means a loss in cost. .High reliability and low maintenance: Commercial charger units may require less maintenance or replacement of key components such as cooling fans, mechanical contactors or relays. Solid-state switching components are generally more reliable and have a longer service life. Some chargers on the market require the use of a DC contactor to switch modules between series and parallel operation. Although this solution effectively achieves a universal charging voltage range, the DC contactor is bulky, costly, and has a limited operating life. Technical improvements can provide a better choice than DC contactors. [0048] FIG. 1B shows an example of a two-stage fast charger 100 in which a boost power factor correction (PFC) converter 102 receives power (in this example, a three-phase AC input) and regulates the DC bus 104 The DC bus 104 feeds power to the high frequency (HF) isolation inductor-inductor-capacitor (LLC) converter 106 (or PSFB converter) that provides DC output . Generally, the modulation of the LLC converter can only efficiently transmit a small range of output voltage and load power level; otherwise, the modulation efficiency of the LLC converter will be significantly worse (for example, the efficiency may be significantly reduced when the limit is exceeded) . Therefore, under this deployment, it may be important to control the voltage rise and fall of the DC bus to the required operating set point in order to help the LLC converter 106 provide higher output voltage and load power levels within a wide range. s efficiency. [0049] The active PFC converter may have a peak efficiency (for example, about 98% or lower), which may cause a major loss in the overall efficiency of the appliance. In addition, even if the PFC actively controls the set point of the bus voltage, the LLC converter 106 may still not be able to provide a wide enough adjustment range for EV load applications due to the problem of reduced efficiency. In addition, due to factors such as fast switching metal oxide semiconductor field effect transistor (MOSFET)/insulate gate bipolar transistor (IGBT) and magnetic components, the full power rated pulse width modulation ( Pulse width modulation (PWM) switching boost PFC incurs major costs. [0050] In view of the limitations of the deployment of FIG. 1B, technical improvements are needed to provide benefits including specification range, efficiency performance, and cost savings. [0051] Generally, an EV should be able to charge a battery with at least two different power sources (for example, direct current from a charging station and alternating current from a public alternating current grid). Therefore, in addition to the MCU circuit that runs the EV motor during the traction mode, the EV on-board power system may include a DC charging circuit and an AC charging circuit. [0052] The EV power system is sensitive to the size and weight of the components, and the efficiency of the converter. Power switching devices such as gallium nitride (GaN) devices and silicon carbide (SiC) devices can be used to improve efficiency, size, and weight. Integration can also provide further benefits in terms of cost and size. [0053] The charging of the EV battery may include the use of an on-board charging (OBC) circuit. The power from the battery can be used to power one or more motors to drive an electric vehicle under the control of a motor control unit (MCU) circuit. In some cases, these circuits can share certain components, which can reduce costs and improve efficiency. The integration of the OBC circuit and the MCU circuit uses an advanced high-frequency circuit topology, and the use of a shared power converter stage (for example, a power bridge) between the OBC and the MCU can reduce the overall cost, size, and weight of the EV power system. These solutions can solve the technical challenges brought about by the integration of OBC and MCU, that is, having different power ratings, isolation requirements, and wide voltage ranges. [0054] FIG. 2A shows an example of an EV 210 that is connected to a charging station 212 to charge the battery 214 of the EV 210. The cable 216 extends from the charging station 212 and ends with a connector 218 that is coupled to the corresponding connector 220 of the EV 210. The OBC circuit 222 is coupled to the connector 220 to receive power from an external source (in this example, the charging station 212), and use the power to charge the battery 214 (eg, convert alternating current to direct current and control the voltage provided to the battery 214 And current). The battery 214 is coupled to provide electrical power to the MCU 224, and the MCU 224 controls the electrical power provided to the motor 226 (eg, converts direct current from the battery 214 to alternating current and controls the voltage and current provided to the motor 226). [0055] FIG. 2B shows an example of another EV 230, the EV 230 is connected to the charging station 212 through a cable 216 and a connector 218, the connector 218 is connected to the connector 220 (corresponding parts of the electric vehicles 210, 230 use similar The OBC/MCU circuit 232 is coupled to the connector 220 to receive power from an external source (charging station 212 in this example) and use that power to charge the battery 214 (for example, similar to OBC 222, The alternating current is converted to direct current and the voltage and current supplied to the battery 214 are controlled). The battery 214 is coupled to provide electrical power to the OBC/MCU circuit 232, which controls the electrical power provided to the motor 226 (e.g., similar to the MCU224, converts the direct current from the battery 214 to alternating current and controls the voltage provided to the motor 226 And current). Therefore, the OBC/MCU circuit 232 of the EV 230 combines the functions of the OBC 222 and the MCU 224 of the EV 210. This combined circuit can save cost, weight, and space, and can improve efficiency. Aspects of the technology are applicable to such combined circuits (but not limited to such circuits). Although the examples of FIGS. 2A and 2B show charging from the charging station 212, it is understood that household AC power sources, solar panels, or generators can be used. (Including HEV generator) other power sources for charging. [0056] It is challenging to make the motor in an EV operate efficiently outside of its operating range. Figure 2c shows an example of the force curve of the motor over its entire operating range (from speed=0 to maximum speed), with the speed (angular speed) on the x-axis and the force along the y-axis. The operating range can be divided into several areas as shown in the figure, including the constant force area (where the speed ω is at 0&lt;3&lt;sb Within the range) and constant power area. The constant power region includes the field weakening zone I or "partial field weakening zone" (where the speed ω is at sb&lt;3&lt;3 cWithin the range of ω), and the field weakening zone II or "complete field weakening zone" (where the speed ω is in the range of ωΟ&lt;ω). The motor characteristics may be different in each area, making it difficult to efficiently control the motor across this range. [0057] FIG. 2D shows a first example of an MCU 236 coupled between a battery 238 and a motor 240 (for example, in an EV). A pair of switches 242 and 243 couple the battery 238 with the MCU 236. In the MCU 236, the switch 244 and the switch 245 are connected in series between the terminals of the battery 238, and there is a terminal 246 between the switches 244 and 245. The terminal 246 is coupled with the first winding 248 of the motor 240. The switch 250 and the switch 251 are connected in series between the terminals of the battery 238, and there is a terminal 252 between the switches 250 and 251. The terminal 252 is coupled with the second winding 254 of the motor 240. The switch 258 and the switch 259 are connected in series between the terminals of the battery 238, and there is a terminal 260 between the switches 258 and 259. The terminal 260 is coupled with the third winding 262 of the motor 240. The switches 244, 245, 250, 251, 258, 259 may be formed in any suitable manner, for example, using a transistor having a diode coupled between the collector terminal and the emitter terminal. Such a switch can be controlled to provide an appropriate voltage to the windings of the motor 240 (for example, by switching the switch to convert the DC voltage from the battery 238 to the AC voltage provided to the motor 240). So in this example In this case, the MCU 236 is used as a converter, which can also be called an inverter 236. [0058] FIG. 2E shows another example of the MCU connected between the battery 238 and the motor 240. Similar components have similar reference numerals as in FIG. 2D. In addition to the inverter 236 shown in FIG. 2D, the MCU 270 in FIG. 2E also includes a boost converter 272 that receives the voltage from the battery 238 and provides a boost to the inverter 236 After the voltage. The boost converter 272 includes an inductor 274 connected to the battery 238 through a switch 276 at one end, and connected to a node 278 at the other end. The node 278 is located between the switch 280 and the switch 281, and the switch 280 and the switch 281 are connected in series across the input terminal of the inverter 236 to provide the inverter 236 with a boosted output voltage. The switches 280, 281 and/or the switches 244, 245, 250, 251, 258, 259 of the inverter 236 may be formed in any suitable manner, for example, using a diode with a diode coupled between the source terminal and the drain terminal Transistor (for example, MOSFET transistor). [0059] FIG. 3A shows an example embodiment of an OBC/MCU circuit 232 as a three-port converter circuit, which includes three power converter stages coupled with a transformer module 347, that is, the first power The converter stage 341, the second power converter stage 343, and the third power converter stage 345. The first power converter stage 341, the second power converter stage 343, and the third power converter stage 345 are coupled to a processor 349, which controls the components of the power converter stage, for example, controls the configurable power converter stage The configuration and control of the switching frequency of the switchable components to manage the power transmitted by the power converter stage. Each power converter stage is connected to a corresponding port of the OBC/MCU circuit 232. The first power converter stage 341 is connected to the first port 351, the second power converter stage 343 is connected to the second port 353, and the third power converter stage 345 is connected to the third port 355. [0060] Although the ports of such a multi-port circuit can be coupled to various components according to applications, FIG. 3A shows an example suitable for use in an EV, where the first port 351 is configured as an external power port and is connected to, for example, charging An external power source 357 such as a station 212, a household AC power supply, or a generator (such as a generator in an HEV) is connected. In many cases, external power is provided as AC current. The rectifying and boosting circuit 359 is coupled between the first port 351 and the first power converter stage 341 to rectify this alternating current and boost the voltage provided to the first power converter stage 341. In other examples, when the DC current is provided, the rectifying and boosting circuit 359 may be bypassed, or the rectifying and boosting circuit 359 is not needed. The second port 353 is configured as a battery port and is coupled to the battery 214 (more than one battery may be provided in some examples). The third port 355 is configured as a motor port, and is coupled to the motor 226 through a voltage source inverter (VSI) 356 (in some examples, more than one motor may be provided). In some examples, the processor 349 may be coupled with additional components to receive input (for example, to receive a voltage measurement at the first port 351 or the second port 353) or to provide an output (for example, to control the rectifier boost circuit 359) . [0061] Various circuits may be used to implement the first, second, and third power converter stages 341, 343, and 345. This article provides examples for the purpose of illustration, but it can be understood that the above power converter stage is for illustrative purposes, and the power converter stage can be implemented in any suitable manner. [0062] FIG. 3B shows an example of a power converter stage 364 implemented as a multi-level power converter stage (in this example, a three-level half-bridge phase shift converter). This circuit can be used to implement one or more of the first, second, and third power converter stages 341, 343, and 345 of the OBC/MCU circuit 232 shown in FIG. 3A. The power converter stage 364 in FIG. 3B has capacitors 328a and 328b, which are connected in series between the first terminal 363a and the first terminal 363b of the power converter stage 364. In some examples, the intermediate terminal 363c is coupled between the capacitors 328a and 328b for connection. When configured as the first power converter stage 341, the terminals 363a (positive), 363b (negative), and 363c (middle) may be coupled with a rectifier boost circuit (for example, a rectif
[DE DE102015224476A1]: Mehrfachpegel-Abwärts-Aufwärts-Wandler mit hoher Effizienz [EN US10868469B2]: High efficiency multi-level buck-boost converter | [DE DE102015224476A1]: Ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers wird beschrieben. Der Leistungswandler weist einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss auf, wobei der zweite Induktoranschluss mit dem Ausgangsanschluss gekoppelt ist. Weiter weist der Leistungswandler einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss und eine Schaltzelle (S1, S2, S3A, S3B, S4) auf. Zusätzlich weist der Leistungswandler eine Steuereinheit auf, die konfiguriert ist zum Betreiben der Schaltzelle (S1, S2, S3A, S3B, S4) in einer ersten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen; und in einer zweiten Sequenz von Betriebsphasen, um eine Abwärtswandlung durchzuführen. [EN US10868469B2]: A power converter for converting an input voltage at an input port into an output voltage at an output port of the power converter is described. The power converter comprises an inductor having a first inductor port and a second inductor port, wherein the second inductor port is coupled to the output port. Furthermore, the power converter comprises a flying capacitor having a first capacitor port and a second capacitor port, and a switching cell. In addition, the power converter comprises a control unit to operate the switching cell in a first sequence of operation phases to perform step-up conversion; and in a second sequence of operation phases to perform step-down conversion. | US2017163157A1 | 2019-11-12 2017-06-08 | US201615370681A | 2016-12-06 2016-12-06 | DE102015224476A, 2015-12-07 DE102015224476A, 2015-12-07 | DE102015224476A1: 2017-06-08 US10476390B2: 2019-11-12 US10868469B2: 2020-12-15 | DIALOG SEMICONDUCTOR (UK) LTD DIALOG SEMICONDUCTOR UK LTD | PETERSEN HOLGER | H02M3/07: I H02M3/158: I H02M3/28: I H02M1/14: I | H02M3/1582: I H02M1/14: I | US2014070787A1 US7265606B1 US2009072800A1 US2013176076A1 US2017055322A1 US8554019B2 US2011140536A1 US2018006552A1 US8854019B1 | CN108847769A CN108847769 108847769 CN109361316A CN109361316 109361316 US10488881B1 US10488881 US10312810B1 US10312810 10312810 US11088611B2 US11088611 11088611 US10985654B2 US10985654 10985654 | [DE DE102015224476A1]: Ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers, wobei der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der zweite Induktoranschluss mit dem Ausgangsanschluss gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; – eine Schaltzelle (S1, S2, S3A, S3B, S4); wobei die Schaltzelle (S1, S2, S3A, S3B, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Eingangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen dritten Schalter (S3A), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit Masse; und – einen Hilfsschalter (S3B), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Eingangsanschluss; und – eine Steuereinheit, die konfiguriert ist zum Betreiben der Schaltzelle (S1, S2, S3A, S3B, S4) in – einer ersten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen; und – einer zweiten Sequenz von Betriebsphasen, um eine Abwärtswandlung vorzusehen. Der Leistungswandler gemäß Anspruch 1, wobei – die erste Sequenz von Betriebsphasen und die zweite Sequenz von Betriebsphasen jeweils zwei oder mehr Betriebsphasen aufweisen; – während einer Betriebsphase einer oder mehrere der Schalter der Schaltzelle (S1, S2, S3A, S3B, S4) geschlossen ist/sind und einer oder mehrere der Schalter der Schaltzelle (S1, S2, S3A, S3B, S4) geöffnet ist/sind; und – die zwei oder mehr Betriebsphasen der ersten Sequenz von Betriebsphasen und der zweiten Sequenz von Betriebsphasen derart sind, dass sie nur serielle Anordnungen von zwei oder weniger geschlossenen Schaltern aufweisen. Der Leistungswandler gemäß Anspruch 2, wobei die Steuereinheit konfiguriert ist zum Anpassen einer Dauer der zwei oder mehr Betriebsphasen der ersten Sequenz von Betriebsphasen und/oder der zweiten Sequenz von Betriebsphasen in Übereinstimmung mit einem Sollumwandlungsverhältnis zwischen der Eingangsspannung und der Ausgangsspannung. Der Leistungswandler gemäß einem vorhergehenden Anspruch, wobei die Steuereinheit konfiguriert ist zum Anpassen der ersten Sequenz von Betriebsphasen und/oder der zweiten Sequenz von Betriebsphasen derart, dass die Ausgangsspannung auf eine vorgegebene Sollspannung geregelt wird. Der Leistungswandler gemäß einem vorhergehenden Anspruch, wobei – die erste Sequenz von Betriebsphasen eine Magnetisierungsphase aufweist, während der der Hilfsschalter (S3B) geschlossen ist; – die erste Sequenz von Betriebsphasen eine Entmagnetisierungsphase aufweist, während der der Hilfsschalter (S3B) geöffnet ist; und – die Magnetisierungsphase und die Entmagnetisierungsphase auf eine periodische Weise wiederholt werden. Der Leistungswandler gemäß Anspruch 5, wobei während der Magnetisierungsphase der zweite Schalter (S2) geschlossen ist; und der erste Schalter (S1), der dritte Schalter (S3A) und der vierte Schalter (S4) geöffnet sind. Der Leistungswandler gemäß einem der Ansprüche 5 bis 6, wobei während der Entmagnetisierungsphase – der erste Schalter (S1), der zweite Schalter (S2) und der vierte Schalter (S4) geschlossen sind; und der dritte Schalter (S3A) geöffnet ist; oder – der zweite Schalter (S2) und der vierte Schalter (S4) geschlossen sind; und der erste Schalter (S1) und der dritte Schalter (S3A) geöffnet sind; oder – der erste Schalter (S1), der dritte Schalter (S3A) und der vierte Schalter (S4) geschlossen sind; und der zweite Schalter (S2) geöffnet ist. Der Leistungswandler gemäß einem vorhergehenden Anspruch, wobei der Hilfsschalter (S3B) während aller Betriebsphasen der zweiten Sequenz von Betriebsphasen geöffnet gehalten wird. Der Leistungswandler gemäß Anspruch 8, wobei die zweite Sequenz von Betriebsphasen aufweist – eine erste Betriebsphase, während der der erste Schalter (S1) und der dritte Schalter (S3A) geschlossen sind und während der der zweite Schalter (S2) und der vierte Schalter (S4) geöffnet sind; und – eine zweite Betriebsphase, während der der erste Schalter (S1) und der dritte Schalter (S3A) geöffnet sind und während der der zweite Schalter (S2) und der vierte Schalter (S4) geschlossen sind; und – eine dritte Betriebsphase, während der der erste Schalter (S1) und der zweite Schalter (S2) geschlossen sind und während der der dritte Schalter (S3A) und der vierte Schalter (S4) geöffnet sind; und/oder – eine vierte Betriebsphase, während der der erste Schalter (S1) und der zweite Schalter (S2) geöffnet sind und während der der dritte Schalter (S3A) und der vierte Schalter (S4) geschlossen sind. Der Leistungswandler gemäß einem vorhergehenden Anspruch, der weiter aufweist – einen verschachtelnden fliegenden Kondensator (C2) mit einem ersten verschachtelnden Kondensatoranschluss und einem zweiten verschachtelnden Kondensatoranschluss; und – eine verschachtelnde Schaltzelle (S5, S6A, S6B, S7, S8); wobei die verschachtelnden Schaltzelle (S5, S6A, S6B, S7, S8) aufweist – einen ersten verschachtelnden Schalter (S8), der konfiguriert ist zum Koppeln des ersten verschachtelnden Kondensatoranschlusses mit dem Eingangsanschluss; – einen zweiten verschachtelnden Schalter (S7), der konfiguriert ist zum Koppeln des ersten verschachtelnden Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen dritten verschachtelnden Schalter (S6A), der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses mit dem ersten Induktoranschluss; und – einen vierten verschachtelnden Schalter (S5), der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses mit Masse; wobei die Steuereinheit konfiguriert ist zum Betreiben der Schaltzelle (S1, S2, S3A, S3B, S4) und der verschachtelnden Schaltzelle (S5, S6A, S6B, S7, S8) auf eine verschachtelte Weise für eine Abwärtswandlung. Der Leistungswandler gemäß Anspruch 10, wobei – die verschachtelnde Schaltzelle (S5, S6A, S6B, S7, S8) weiter einen verschachtelnden Hilfsschalter (S6B) aufweist, der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses mit dem Eingangsanschluss; und – die Steuereinheit konfiguriert ist zum Betreiben der verschachtelnden Schaltzelle (S5, S6A, S6B, S7, S8) in einer ersten Sequenz von synchronen Betriebsphasen, um eine Aufwärtswandlung durchzuführen; und/oder einer zweiten Sequenz von verschachtelten Betriebsphasen, um eine Abwärtswandlung durchzuführen. Der Leistungswandler gemäß einem vorhergehenden Anspruch, wobei der Leistungswandler weiter einen Ausgangskondensator aufweist, der parallel zwischen dem Ausgangsanschluss und Masse angeordnet ist. Ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers, wobei der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der erste Induktoranschluss mit dem Eingangsanschluss gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; – eine Schaltzelle (S1, S2, S3A, S3B, S4); wobei die Schaltzelle (S1, S2, S3A, S3B, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Ausgangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem zweiten Induktoranschluss; – einen dritten Schalter (S3A), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem zweiten Induktoranschluss; – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit Masse; und – einen Hilfsschalter (S3B), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Ausgangsanschluss; und – eine Steuereinheit, die konfiguriert ist zum Betreiben der Schaltzelle (S1, S2, S3A, S3B, S4) in – einer ersten Sequenz von Betriebsphasen, um eine Abwärtswandlung durchzuführen; und – einer zweiten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen. Ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers, wobei der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der zweite Induktoranschluss mit Masse gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; – eine Schaltzelle (S1, S2, S3, S4); wobei die Schaltzelle (S1, S2, S3, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Eingangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Ausgangsanschluss; – einen dritten Schalter (S3), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem ersten Induktoranschluss; und – eine Steuereinheit, die konfiguriert ist zum Betreiben der Schaltzelle (S1, S2, S3, S4) in einer Sequenz von Betriebsphasen, um eine Inversion mit einem absoluten Umwandlungsverhältnis größer als eins, mit einem absoluten Umwandlungsverhältnis gleich eins oder mit einem absoluten Umwandlungsverhältnis kleiner als eins durchzuführen. Ein Verfahren (600) zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss eines Leistungswandlers, wobei – der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der zweite Induktoranschluss mit dem Ausgangsanschluss gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; und – eine Schaltzelle (S1, S2, S3A, S3B, S4); – wobei die Schaltzelle (S1, S2, S3A, S3B, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Eingangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen dritten Schalter (S3A), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem ersten Induktoranschluss; – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit Masse; und – einen Hilfsschalter (S3B), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Eingangsanschluss; und – das Verfahren (600) aufweist – Betreiben (601) der Schaltzelle (S1, S2, S3A, S3B, S4) in einer ersten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen; und – Betreiben (602) der Schaltzelle (S1, S2, S3A, S3B, S4) in einer zweiten Sequenz von Betriebsphasen, um eine Abwärtswandlung vorzusehen. Ein Verfahren (600) zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss eines Leistungswandlers, wobei – der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der erste Induktoranschluss mit dem Eingangsanschluss gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; – eine Schaltzelle (S1, S2, S3A, S3B, S4); – die Schaltzelle (S1, S2, S3A, S3B, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Ausgangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem zweiten Induktoranschluss; – einen dritten Schalter (S3A), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem zweiten Induktoranschluss; – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit Masse; und – einen Hilfsschalter (S3B), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Ausgangsanschluss; und – das Verfahren (600) aufweist – Betreiben (601) der Schaltzelle (S1, S2, S3A, S3B, S4) in einer ersten Sequenz von Betriebsphasen, um eine Abwärtswandlung durchzuführen; und – Betreiben (602) der Schaltzelle (S1, S2, S3A, S3B, S4) in einer zweiten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen. Ein Verfahren (600) zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss eines Leistungswandlers, wobei – der Leistungswandler aufweist – einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss; wobei der zweite Induktoranschluss mit Masse gekoppelt ist; – einen fliegenden Kondensator (C) mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss; und – eine Schaltzelle (S1, S2, S3, S4); – die Schaltzelle (S1, S2, S3, S4) aufweist – einen ersten Schalter (S1), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Eingangsanschluss; – einen zweiten Schalter (S2), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Ausgangsanschluss; – einen dritten Schalter (S3), der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem ersten Induktoranschluss; und – einen vierten Schalter (S4), der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem ersten Induktoranschluss; und – das Verfahren (600) ein Betreiben (601) der Schaltzelle (S1, S2, S3, S4) aufweist, um eine Inversion mit einem absoluten Umwandlungsverhältnis größer als eins, mit einem absoluten Umwandlungsverhältnis gleich eins oder mit einem absoluten Umwandlungsverhältnis kleiner als eins durchzuführen. [EN US10868469B2]: 1. A power converter for converting an input voltage at an input port into an output voltage at an output port of the power converter, the power converter comprising, an inductor having a first inductor port and a second inductor port; wherein the first inductor port is coupled to the input port;a flying capacitor having a first capacitor port and a second capacitor port;a switching cell; wherein the switching cell comprises a first switch configured to connect the first capacitor port to the output port;a second switch configured to connect the first capacitor port to the second inductor port;a third switch configured to connect the second capacitor port to the second inductor port;a fourth switch configured to connect the second capacitor port to ground; andan auxiliary switch configured to connect the second capacitor port to the output port; anda control unit configured to operate the switching cell in a first sequence of operation phases to perform step-down conversion; anda second sequence of operation phases to perform step-up conversion. 2. The power converter of claim 1, wherein the first sequence of operation phases and the second sequence of operation phases each comprise two or more operation phases;during an operation phase one of more of the switches of the switching cell are closed and one of more of the switches of the switching cell are open; andthe two or more operation phases of the first sequence of operation phases and of the second sequence of operation phases are such that they only comprise serial arrangements of two or less closed switches. 3. The power converter of claim 2, wherein the control unit is configured to adapt a duration of the two or more operation phases of the first sequence of operation phases and/or of the second sequence of operation phases in accordance to a target conversion ratio between the input voltage and the output voltage. 4. The power converter of claim 1, wherein the control unit is configured to adapt the first sequence of operation phases and/or the second sequence of operation phases, such that the output voltage is regulated to a pre-determined target voltage. 5. The power converter of claim 1, wherein the first sequence of operation phases comprises a de-magnetization phase, during which the auxiliary switch is closed;the first sequence of operation phases comprises a magnetization phase, during which the auxiliary switch is open; andthe magnetization phase and the demagnetization phase are repeated in a periodic manner. 6. The power converter of claim 5, wherein during the de-magnetization phase, the second switch is closed; and the first switch, the third switch and the fourth switch are open. 7. The power converter of claim 5, wherein during the magnetization phase, the first switch, the second switch and the fourth switch are closed; and the third switch is open; and/orthe second switch and the fourth switch are closed; and the first switch and the third switch are open; orthe first switch, the third switch and the fourth switch are closed; and the second switch is open. 8. The power converter of claim 1, wherein the auxiliary switch is maintained open during all the operation phases of the second sequence of operation phases. 9. The power converter of claim 8, wherein the second sequence of operation phases comprises, a first operation phase during which the first switch and the third switch are closed and during which the second switch and the fourth switch are open; anda second operation phase during which the first switch and the third switch are open and during which the second switch and the fourth switch are closed; anda third operation phase during which the first switch and the second switch are closed and during which the third switch and the fourth switch are open; and/ora fourth operation phase during which the first switch and the second switch are open and during which the third switch and the fourth switch are closed. 10. The power converter of claim 1, further comprising an interleaving flying capacitor having a first interleaving capacitor port and a second interleaving capacitor port; andan interleaving switching cell; wherein the interleaving switching cell comprises, a first interleaving switch configured to couple the first interleaving capacitor port to the input port;a second interleaving switch configured to couple the first interleaving capacitor port to the first inductor port;a third interleaving switch configured to couple the second interleaving capacitor port to the first inductor port; anda fourth interleaving switch configured to couple the second interleaving capacitor port to ground;wherein the control unit is configured to operate the switching cell and the interleaving switching cell in an interleaved manner for step-down conversion. 11. The power converter of claim 10, wherein the interleaving switching cell further comprises an auxiliary interleaving switch configured to couple the second interleaving capacitor port to the input port; andthe control unit is configured to operate the interleaving switching cell in a first sequence of synchronous operation phases to perform a step-down conversion; and/or a second sequence of interleaved operation phases to perform a step-up conversion. 12. The power converter of claim 1, wherein the power converter further comprises an output capacitor arranged in parallel between the output port and ground. 13. A method for converting an input voltage at an input port into an output voltage at an output port of a power converter, wherein the power converter comprises, an inductor having a first inductor port and a second inductor port; wherein the first inductor port is coupled to the input port;a flying capacitor having a first capacitor port and a second capacitor port;a switching cell;the switching cell comprises a first switch to connect the first capacitor port to the output port;a second switch to connect the first capacitor port to the second inductor port;a third switch to connect the second capacitor port to the second inductor port;a fourth switch to connect the second capacitor port to ground; andan auxiliary switch to connect the second capacitor port to the output port; andthe method comprises operating the switching cell in a first sequence of operation phases to perform step-down conversion; andoperating the switching cell in a second sequence of operation phases to perform step-up conversion. 14. A power converter for converting an input voltage at an input port into an output voltage at an output port of the power converter, the power converter comprising, an inductor having a first inductor port and a second inductor port; wherein the second inductor port is coupled to ground;a flying capacitor having a first capacitor port and a second capacitor port;a switching cell; wherein the switching cell comprises a first switch configured to connect the first capacitor port to the input port;a second switch configured to connect the second capacitor port to the output port;a third switch configured to connect the second capacitor port to the first inductor port; anda fourth switch configured to connect the first capacitor port to the first inductor port; and a control unit configured to operate the switching cell in a sequence of operation phases to perform inversion with an absolute conversion ratio greater than one, with an absolute conversion ratio equal to one or with an absolute conversion ratio smaller than one. 15. The power converter of claim 14, wherein the sequence of operation phases comprises two or more operation phases;during an operation phase one of more of the switches of the switching cell are closed and one of more of the switches of the switching cell are open; andthe two or more operation phases of the sequence of operation phases are such that they only comprise serial arrangements of two or less closed switches. 16. The power converter of claim 15, wherein the control unit is configured to adapt a duration of the two or more operation phases of the sequence of operation phases in accordance to a target conversion ratio between the input voltage and the output voltage. 17. The power converter of claim 14, wherein the control unit is configured to adapt the sequence of operation phases such that the output voltage is regulated to a pre-determined target voltage. 18. The power converter of claim 14, wherein the sequence of operation phases comprises a magnetization phase, during which the first switch and the third switch are closed; and the second switch and the fourth switch are open;the sequence of operation phases comprises a demagnetization phase, during which the second switch and the fourth switch are closed; and the first switch and the third switch are open; andthe magnetization phase and the demagnetization phase are repeated in a periodic manner. 19. The power converter of claim 18, wherein one or more magnetization phases are inserted to the sequence of operation phases, wherein during this magnetization phase the first switch and the fourth switch are closed; and the second switch and the third switch are open. 20. The power converter of claim 18, wherein one or more demagnetization phases are inserted to the sequence of operation phases, wherein during this demagnetization phase the second switch and the third switch are closed; and the first switch and the fourth switch are open. 21. The power converter of claim 14, wherein the power converter further comprises an output capacitor arranged in parallel between the output port and ground. 22. A method for converting an input voltage at an input port into an output voltage at an output port of a power converter, wherein the power converter comprises, an inductor having a first inductor port and a second inductor port; wherein the second inductor port is coupled to ground;a flying capacitor having a first capacitor port and a second capacitor port; anda switching cell;the switching cell comprises a first switch to connect the first capacitor port to the input port;a second switch to connect the second capacitor port to the output port;a third switch to connect the second capacitor port to the first inductor port; anda fourth switch to connect the first capacitor port to the first inductor port; andthe method comprises operating the switching cell to perform inversion with an absolute conversion ratio greater than one, with an absolute conversion ratio equal to one or with an absolute conversion ratio smaller than one. | [DE DE102015224476A1]: Technischer Bereich Das vorliegende Dokument betrifft Leistungswandler mit geregelter Ausgangsspannung oder geregeltem Ausgangsstrom. Insbesondere betrifft das vorliegende Dokument geschaltete Leistungswandler für batteriebetriebene Anwendungen. Hintergrund In den letzten Jahren wurde die Rechenleistung, Bildschirmauflösung und Anzeigerahmenrate von batteriebetriebenen Anwendungen (wie Smartphones und Tablet-PCs) erhöht und verbundene Standby-Modi hinzugefügt. Dies verursachte eine erhöhte Entleerung der Batterie, so dass viele moderne Smartphones täglich wieder aufgeladen werden müssen. Eine begrenzte Mobilitätszeit kann durch eine Verwendung von Batteriepacks mit einer höheren Kapazität adressiert werden, aber ein Wiederaufladen von derartigen Batteriepacks erfordert typischerweise eine längere Zeitdauer. Dies ist aufgrund der Tatsache, dass Smartphones typischerweise über einen Standard(Micro)-USB-Anschluss geladen werden, der eine begrenzte Stromhandhabungsfähigkeit vorsieht (~1,5 A). Daher benötigt ein 5 Ah Batteriepack mehrere Stunden zum Wiederaufladen, auch wenn die Batterietechnologie (typischerweise Lilon/LiPolymer) höhere Ladeleistungspegel ermöglichen würde (zum Beispiel 1–2C Aufladung). Jüngste Änderungen in der USB-Ladespezifikation erlauben höhere Spannungen als die standardmäßigen 5 V, ermöglichen bis zu 4× der Leistung von der USB-Versorgung (9 V, 12 V und 20 V). Da jedoch Smartphones in Raum und Höhe begrenzt sind (insbesondere hinsichtlich Induktoren, die für Schaltwandler verwendet werden), kann eine zunehmende Induktorstromwelligkeit (von höheren Eingangsspannungen) nicht mit Spulen kompensiert werden, die eine höhere Induktivität haben. Als Ergebnis kann entweder der DCR (Gleichstromwiderstand) der Spule erhöht werden oder die Schaltfrequenz kann erhöht werden. Beide Maßnahmen führen zu einer höheren Verlustleistung und können zu heißen Stellen an dem Gehäuse einer batteriebetriebenen Anwendung führen. Das vorliegende Dokument adressiert das technische Problem eines Vorsehens eines effizienten und kompakten Leistungswandlers, der eine Aufwärts(step-up)- und Abwärts(step-down)-Leistungswandlung ermöglicht (zum Beispiel für batteriebetriebene Anwendungen). Zusammenfassung Gemäß einem Aspekt wird ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss des Leistungswandlers in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers beschrieben. Die Eingangsspannung kann der Spannungspegeldifferenz zwischen dem Eingangsanschluss und Masse entsprechen. Die Ausgangsspannung kann der Spannungspegeldifferenz zwischen dem Ausgangsanschluss und Masse entsprechen. Der Leistungswandler weist einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss auf. Der zweite Induktoranschluss kann (zum Beispiel direkt) mit dem Ausgangsanschluss gekoppelt werden. Weiter weist der Leistungswandler (zumindest einen) fliegenden (flying) Kondensator mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss sowie zumindest eine Schaltzelle auf. Eine Schaltzelle kann konfiguriert sein zum Modifizieren der Anordnung des entsprechenden fliegenden Kondensators und/oder des Induktors in dem Leistungswandler, zum Beispiel unter Verwendung einer Vielzahl von Schaltern. Somit kann der Leistungswandler in verschiedenen Betriebsphasen betrieben werden, wobei eine bestimmte Betriebsphase typischerweise eine bestimmte Konfiguration der Schaltzelle aufweist oder dieser entspricht. Die Schaltzelle weist einen ersten Schalter auf, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses (zum Beispiel direkt) mit dem Eingangsanschluss. Weiter weist die Schaltzelle einen zweiten Schalter auf, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses (zum Beispiel direkt) mit dem ersten Induktoranschluss. Zusätzlich weist die Schaltzelle einen dritten Schalter auf, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses (zum Beispiel direkt) mit dem ersten Induktoranschluss. Weiter weist die Schaltzelle einen vierten Schalter auf, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses (zum Beispiel direkt) mit Masse. Der erste, zweite, dritte und vierte Schalter können verwendet werden zum Konfigurieren des Leistungswandlers für eine Abwärts(d. h. Buck)-Wandlung. Die Schaltzelle weist weiter einen Hilfsschalter auf, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Eingangsanschluss. Der Hilfsschalter kann zum Konfigurieren des Leistungswandlers für eine Aufwärts(d. h. Boost)-Wandlung verwendet werden. Zusätzlich weist der Leistungswandler eine Steuereinheit auf, die konfiguriert ist zum Betreiben der Schaltzelle in einer ersten Sequenz von Betriebsphasen, um eine Aufwärtswandlung vorzusehen (wobei die Ausgangsspannung höher ist als die Eingangsspannung). Die erste Sequenz von Betriebsphasen umfasst typischerweise ein Schalten des Hilfsschalters. Weiter ist die Steuereinheit konfiguriert zum Betreiben der Schaltzelle in einer zweiten Sequenz von Betriebsphasen, um eine Abwärtswandlung vorzusehen (wobei die Ausgangsspannung niedriger ist als die Eingangsspannung). Die zweite Sequenz von Betriebsphasen umfasst typischerweise kein Schalten des Hilfsschalters. Insbesondere kann der Hilfsschalter durch die Steuereinheit während aller Betriebsphasen der zweiten Sequenz von Betriebsphasen offen gehalten werden. Somit muss die Abwärtswandlung durch den Hilfsschalter nicht wesentlich beeinträchtigt werden. Es kann eine geringe Begleiterscheinung von einer Drain-Source-Kapazität des Hilfsschalters geben, was einen Übergangsverlust erhöhen kann, wenn der erste Schalter geschlossen wird, aber diese Begleiterscheinung reduziert jedoch typischerweise die Wandlungseffizienz nicht merkbar. Somit wird ein Leistungswandler beschrieben, der eine leistungseffiziente Aufwärts- und Abwärts-Wandlung mit einer begrenzten Anzahl von Schaltern ermöglicht (zum Beispiel Metalloxid-Halbleiter-Transistoren). Insbesondere wird ein Abwärts-basierter Leistungswandler vorgesehen, der eine Aufwärtswandlung unter Verwendung nur eines einzelnen zusätzlichen (Hilfs-)Schalters ermöglicht. Die erste Sequenz von Betriebsphasen und die zweite Sequenz von Betriebsphasen weisen typischerweise jeweils zwei oder mehr Betriebsphasen auf (mit einer anderen Kombination von Konfigurationen der Schalter der Schaltzelle). Während einer (zum Beispiel während jeder) Betriebsphase ist/sind einer oder mehrere der Schalter der Schaltzelle geschlossen und einer oder mehrere der Schalter der Schaltzelle ist/sind geöffnet. Die zwei oder mehr Betriebsphasen der ersten Sequenz von Betriebsphasen und die zwei oder mehr Betriebsphasen der zweiten Sequenz von Betriebsphasen sind typischerweise derart, dass sie nur serielle Anordnungen von zwei oder weniger geschlossenen Schaltern der Schalter von der Schaltzelle aufweisen. Somit kann der Leistungswandler auf eine leistungseffiziente Weise betrieben werden (mit relativ geringen Verlusten, die durch die Ein-Widerstände der Schalter verursacht werden). Die Steuereinheit kann konfiguriert sein zum Anpassen der Dauer der zwei oder mehr Betriebsphasen der ersten Sequenz von Betriebsphasen und/oder der zweiten Sequenz von Betriebsphasen in Übereinstimmung mit einem Sollumwandlungsverhältnis zwischen der Eingangsspannung und der Ausgangsspannung. Insbesondere kann ein Arbeitszyklus der ersten und/oder zweiten Sequenzen von Betriebsphasen angepasst werden. Weiter kann die Steuereinheit konfiguriert sein zum Anpassen der ersten Sequenz von Betriebsphasen und/oder der zweiten Sequenz von Betriebsphasen derart, dass die Ausgangsspannung auf eine vorgegebene Sollspannung geregelt wird. Somit kann der Leistungswandler konfiguriert sein zum Vorsehen von stabilen Ausgangsspannungen bei unterschiedlichen Sollspannungspegeln. Die erste Sequenz von Betriebsphasen (für eine Aufwärtswandlung) kann eine Magnetisierungsphase aufweisen, während der der Hilfsschalter geschlossen ist. Während der Magnetisierungsphase kann der zweite Schalter geschlossen sein und der erste Schalter, der dritte Schalter und der vierte Schalter können geöffnet sein (wie zum Beispiel in 4A gezeigt). Weiter kann die erste Sequenz von Betriebsphasen eine Entmagnetisierungsphase aufweisen, während der der Hilfsschalter geöffnet ist. Verschiedene Varianten der Entmagnetisierungsphase können vorgesehen werden, um verschiedene Umwandlungsverhältnisse vorzusehen. Eine oder mehrere dieser Varianten können in der ersten Sequenz von Betriebsphasen verwendet werden. Während einer ersten Variante der Entmagnetisierungsphase sind der erste Schalter, der zweite Schalter und der vierte Schalter geschlossen und der dritte Schalter ist geöffnet (wie zum Beispiel in 4B gezeigt). Während einer zweiten Variante der Entmagnetisierungsphase sind der zweite Schalter und der vierte Schalter geschlossen und der erste Schalter und der dritte Schalter sind geöffnet (wie zum Beispiel in 4D gezeigt). Während einer dritten Variante der Entmagnetisierungsphase sind der erste Schalter, der dritte Schalter und der vierte Schalter geschlossen und der zweite Schalter ist geöffnet (wie zum Beispiel in 4C gezeigt). Die Magnetisierungsphase und die Entmagnetisierungsphase können auf eine periodische Weise wiederholt werden (mit einer bestimmten Kommutierungszyklusrate), wodurch die Leistungswandlung von dem Eingangsanschluss zu dem Ausgangsanschluss des Schaltmodus-Leistungswandlers vorgesehen wird. Insbesondere können die Magnetisierungsphase und die erste Variante der Entmagnetisierungsphase auf periodische Weise wiederholt werden. Optional kann die dritte Variante der Entmagnetisierungsphase anstelle von oder in Serie mit der ersten Variante der Entmagnetisierungsphase verwendet werden. Gemäß einer weiteren Sequenz von Betriebsphasen kann die zweite Variante von der Magnetisierungsphase gefolgt werden vor einem Fortsetzen mit der ersten Variante oder der dritten Variante (insbesondere in dem Fall von Verstärkungsverhältnissen, die wesentlich kleiner als 2 sind), und so weiter. Die zweite Sequenz von Betriebsphasen (für eine Abwärtswandlung) kann eine erste Betriebsphase aufweisen, während der der erste Schalter und der dritte Schalter geschlossen sind und während der der zweite Schalter und der vierte Schalter geöffnet sind (wie zum Beispiel in 3A gezeigt). Weiter kann die zweite Sequenz von Betriebsphasen eine zweite Betriebsphase aufweisen, während der der erste Schalter und der dritte Schalter geöffnet sind und während der der zweite Schalter und der vierte Schalter geschlossen sind (wie zum Beispiel in 3B gezeigt). Die erste Betriebsphase und die zweite Betriebsphase können auf eine periodische Weise wiederholt werden, wodurch die Leistungswandlung von dem Eingangsanschluss zu dem Ausgangsanschluss des Schaltmodus-Leistungswandlers vorgesehen wird. Die zweite Sequenz von Betriebsphasen kann weitere Betriebsphasen aufweisen, zum Beispiel eine dritte Betriebsphase, während der der erste Schalter und der zweite Schalter geschlossen sind und während der der dritte Schalter und der vierte Schalter geöffnet sind (wie zum Beispiel in 3C gezeigt), und/oder eine vierte Betriebsphase, während der der erste Schalter und der zweite Schalter geöffnet sind und während der der dritte Schalter und der vierte Schalter geschlossen sind (wie zum Beispiel in 3D gezeigt). Zumindest eine der dritten Betriebsphase und der vierten Betriebsphase kann einmal oder zweimal pro Zyklus verwendet werden (mit einem Arbeitszyklus abhängig von dem Vout/Vin-Verhältnis). Weiter kann die zweite Sequenz von Betriebsphasen eine fünfte Betriebsphase aufweisen, während der der erste Schalter, der zweite Schalter und der dritte Schalter geöffnet sind (wie zum Beispiel in 3E gezeigt). Die fünfte Betriebsphase kann eine inaktive Betriebsphase sein. Während einer inaktiven Betriebsphase, wie zum Beispiel in 3E gezeigt, ist es ausreichend, dass maximal ein Kontakt des fliegenden Kondensators und des Induktors entweder mit GND, mit dem Eingangsanschluss Vin oder mit dem Ausgangsanschluss Vout verbunden ist (um jeden Stromfluss neben dem Strom zu verhindern, der von dem Ausgangskondensator Cout an den Ausgang Vout fließt). Die fünfte Betriebsphase kann eingefügt werden, um Schaltverluste zu reduzieren. Der Leistungswandler kann weiter einen verschachtelnden fliegenden Kondensator mit einem ersten verschachtelnden Kondensatoranschluss und einem zweiten verschachtelnden Kondensatoranschluss sowie eine verschachtelnde Schaltzelle zum Modifizieren der Anordnung des verschachtelnden fliegenden Kondensators in dem Leistungswandler aufweisen. Die Steuereinheit kann konfiguriert sein zum Betreiben der Schaltzelle und der verschachtelnden Schaltzelle auf eine verschachtelte Weise (zum Beispiel bei einer Phasendifferenz von 180 Grad), wodurch die Stromwelligkeit des Leistungswandlers reduziert wird (wie zum Beispiel in 2A gezeigt). Auf ähnliche Weise zu der Schaltzelle kann die verschachtelnde Schaltzelle aufweisen: einen ersten verschachtelnden Schalter, der konfiguriert ist zum Koppeln des ersten verschachtelnden Kondensatoranschlusses (zum Beispiel direkt) mit dem Eingangsanschluss; einen zweiten verschachtelnden Schalter, der konfiguriert ist zum Koppeln des ersten verschachtelnden Kondensatoranschlusses (zum Beispiel direkt) mit dem ersten Induktoranschluss; einen dritten verschachtelnden Schalter, der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses (zum Beispiel direkt) mit dem ersten Induktoranschluss; und einen vierten verschachtelnden Schalter, der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses (zum Beispiel direkt) mit Masse. Durch eine Verwendung dieser Schalter kann eine Stromwelligkeitsreduzierung während einer Abwärtswandlung vorgesehen werden. Weiter kann die verschachtelnde Schaltzelle einen verschachtelnden Hilfsschalter aufweisen, der konfiguriert ist zum Koppeln des zweiten verschachtelnden Kondensatoranschlusses (zum Beispiel direkt) mit dem Eingangsanschluss. Durch eine Verwendung des verschachtelnden Hilfsschalters kann eine Stromwelligkeitsreduzierung während einer Aufwärtswandlung vorgesehen werden. Insbesondere kann die Steuereinheit konfiguriert sein zum Betreiben der verschachtelnden Schaltzelle in einer ersten Sequenz von synchronen Betriebsphasen, um eine Aufwärtswandlung durchzuführen. Insbesondere kann die verschachtelte Schaltzelle synchron mit der Schaltzelle betrieben werden, wodurch höhere Ausgangsströme ermöglicht werden. Auch während solch eines synchronen Betriebs wird eine Welligkeit im Vergleich zu einem induktiven Aufwärtswandler reduziert durch Vorsehen von Strom an den Ausgang während sowohl Induktor-Magnetisierungsphasen als auch -Entmagnetisierungsphasen. Weiter kann die Steuereinheit konfiguriert sein zum Betreiben der verschachtelnden Schaltzelle in einer zweiten Sequenz von verschachtelten Betriebsphasen, um eine Abwärtswandlung vorzusehen. Als Ergebnis dessen kann eine Stromwelligkeitsreduzierung während einer Abwärtswandlung durchgeführt werden. Der Leistungswandler kann weiter einen Ausgangskondensator aufweisen, der parallel zwischen dem Ausgangsanschluss und Masse angeordnet ist, wodurch eine Stromwelligkeit weiter reduziert wird. Gemäß einem weiteren Aspekt wird ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers beschrieben. Der Leistungswandler weist eine Anordnung auf, die im Vergleich zu dem oben beschriebenen Leistungswandler invertiert oder gespiegelt ist. Der Leistungswandler kann als ein Mehrfachpegel-Aufwärts(d. h. Boost)-Leistungswandler mit zusätzlicher Abwärtswandlungsfähigkeit (durch einen Hilfsschalter vorgesehen) angesehen werden. Die Merkmale, die für den oben angeführten Leistungswandler beschrieben werden, sind auf eine analoge (d. h. gespiegelte) Weise auf den Leistungswandler anwendbar, der im Folgenden beschrieben wird. Insbesondere sind die Merkmale durch den Austausch des Eingangsanschlusses und des Ausgangsanschlusses anwendbar. Ein Beispiel für die Verwendung eines Aufwärtswandlers mit einer Abwärtswandlerfähigkeit, d. h. für den unten beschriebenen Betrieb eines Leistungswandlers, ist die umgekehrte Bereitstellung von Energie von einem 2S-Batteriepack zurück in den Ladegerätanschluss, wie zum Beispiel für USB OTG (On The Go) spezifiziert wird. Ein Hinzufügen einer Abwärtswandlerfähigkeit zu einem umgekehrten Aufwärtswandlermodus eines DCDC-USB-Ladegeräts ermöglicht zum Beispiel ein Vorsehen von 5 V von dem 2S-Batteriepack. Der Leistungswandler weist einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss auf. Der erste Induktoranschluss kann (zum Beispiel direkt) mit dem Eingangsanschluss gekoppelt sein. Weiter weist der Leistungswandler einen fliegenden Kondensator mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss sowie eine Schaltzelle auf. Die Schaltzelle weist einen ersten Schalter auf, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses (zum Beispiel direkt) mit dem Ausgangsanschluss; einen zweiten Schalter, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses (zum Beispiel direkt) mit dem zweiten Induktoranschluss; einen dritten Schalter, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses (zum Beispiel direkt) mit dem zweiten Induktoranschluss; einen vierten Schalter, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses (zum Beispiel direkt) mit Masse; und einen Hilfsschalter, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses (zum Beispiel direkt) mit dem Ausgangsanschluss. Zusätzlich weist der Leistungswandler eine Steuereinheit auf, die konfiguriert ist zum Betreiben der Schaltzelle in einer ersten Sequenz von Betriebsphasen, um eine Abwärtswandlung (unter Verwendung des Hilfsschalters) durchzuführen. Die Steuereinheit ist weiter konfiguriert zum Betreiben der Schaltzelle in einer zweiten Sequenz von Betriebsphasen, um eine Aufwärtswandlung durchzuführen (ohne Verwendung des Hilfsschalters, insbesondere während der Hilfsschalter offen gehalten wird). Gemäß einem weiteren Aspekt wird ein Leistungswandler zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss des Leistungswandlers beschrieben. Insbesondere ist der Leistungswandler zum Invertieren der Ausgangsspannung in Bezug auf die Eingangsspannung vorgesehen. Der Leistungswandler weist einen Induktor mit einem ersten Induktoranschluss und einem zweiten Induktoranschluss auf, wobei der zweite Induktoranschluss mit Masse gekoppelt ist. Weiter weist der Leistungswandler einen fliegenden Kondensator mit einem ersten Kondensatoranschluss und einem zweiten Kondensatoranschluss auf. Zusätzlich weist der Leistungswandler eine Schaltzelle auf, wobei die Schaltzelle einen ersten Schalter aufweist, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem Eingangsanschluss; einen zweiten Schalter, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem Ausgangsanschluss; einen dritten Schalter, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses mit dem ersten Induktoranschluss; und einen vierten Schalter, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses mit dem ersten Induktoranschluss. Weiter weist der Leistungswandler eine Steuereinheit auf, die konfiguriert ist zum Betreiben der Schaltzelle in einer Sequenz von Betriebsphasen, um eine Inversion mit einem absoluten Umwandlungsverhältnis größer als ein oder mit einem absoluten Umwandlungsverhältnis kleiner als eins durchzuführen. Die Sequenz von Betriebsphasen kann die Betriebsphasen aufweisen, die in den 5A und 5B gezeigt werden. Durch Ändern des Arbeitszyklus der Betriebsphasen der 5A und der 5B kann das absolute Umwandlungsverhältnis geändert werden. Weiter können eine oder mehrere zusätzliche Betriebsphasen (insbesondere die Betriebsphasen der 5C und 5D) verwendet werden, um eine Regelung in Bezug auf einen Sollausgangsstrom oder eine Sollausgangsspannung zu ermöglichen (insbesondere, wenn die/der absolute Ausgangsspannung/Strom zunimmt (5D) oder abnimmt (5C). Weiter kann eine Betriebsphase, wie in 5E dargestellt, eingefügt werden, um Schaltverluste zu reduzieren (bei relativ niedrigen Ausgangsströmen). Gemäß einem weiteren Aspekt wird ein Verfahren für einen Betrieb eines der oben angeführten Leistungswandler beschrieben, der eine Schaltzelle aufweist. Das Verfahren weist auf einen Betrieb der Schaltzelle in einer ersten Sequenz von Betriebsphasen, um jeweils eine Aufwärtswandlung oder Abwärtswandlung oder Inversion mit einem absoluten Umwandlungsverhältnis kleiner als eins durchzuführen. Das Verfahren weist weiter einen Betrieb der Schaltzelle in einer zweiten Sequenz von Betriebsphasen auf, um jeweils eine Abwärtswandlung oder Aufwärtswandlung oder Inversion mit einem absoluten Umwandlungsverhältnis kleiner als eins durchzuführen. In dem vorliegenden Dokument bezeichnet der Begriff „koppeln” oder „gekoppelt” Elemente, die in elektrischer Kommunikation miteinander sind, entweder direkt zum Beispiel über Drähte oder auf eine andere Weise verbunden. Kurze Beschreibung der Figuren Die Erfindung wird nachfolgend auf beispielhafte Weise unter Bezugnahme auf die beigefügten Zeichnungen beschrieben, wobei 1 ein Schaltungsdiagramm eines beispielhaften Mehrfachpegel-Abwärts-Aufwärts-Leistungswandlers zeigt; 2A ein Schaltungsdiagramm eines beispielhaften verschachtelten Mehrfachpegel-Abwärts-Aufwärts-Leistungswandlers zeigt; 2B ein Schaltungsdiagramm eines beispielhaften Leistungswandlers mit einer invertierten Topologie im Vergleich zu dem Leistungswandler von 1 zeigt; 2C ein Schaltungsdiagramm eines beispielhaften Inverters zeigt, d. h. eines invertierenden Abwärts-Aufwärts-Wandlers; 3A, 3B, 3C, 3D und 3E beispielhafte Betriebsphasen des Leistungswandlers von 1 zeigen (für eine Abwärtswandlung); 4A, 4B, 4C und 4D beispielhafte Betriebsphasen des Leistungswandlers von 1 zeigen (für eine Aufwärtswandlung); 5A, 5B, 5C, 5D und 5E beispielhafte Betriebsphasen des Leistungswandlers, d. h. Inverters, von 2C zeigen; und 6 ein Ablaufdiagramm eines beispielhaften Verfahrens zum Umwandeln einer Eingangsspannung in eine Ausgangsspannung zeigt. Detaillierte Beschreibung Wie oben dargelegt, betrifft das vorliegende Dokument ein Vorsehen eines Größe- und Leistungs-effizienten Leistungswandlers für einen Aufwärts- und Abwärts-Leistungswandler, zum Beispiel für batteriebetriebene Anwendungen. Kapazitive Mehrfachpegel-Leistungswandler nutzen einen oder mehrere fliegende Kondensatoren zum Vorsehen einer Aufwärtswandlung oder Abwärtswandlung. Jedoch unterstützt ein Mehrfachpegel-Abwärtswandler keine Umwandlung, bei der die Eingangsspannung niedriger ist als die Ausgangsspannung (zum Koppeln zum Beispiel mit einem Batteriepack). Eine derartige Situation kann auftreten, wenn zum Beispiel ein Batteriepack aus zumindest 2 Lilon/LiPolymer-Zellen hergestellt wird, die in Serie verbunden sind (2S, 3S, ...), wobei der Batteriepack von einem Legacy-USB-Anschluss aufgeladen werden muss, der nur eine Spannung von 5 V vorsieht. DC/DC-Leistungswandler, die sowohl eine Abwärts- als auch eine Aufwärts-Wandlung vorsehen, können als Abwärts-Aufwärts-Leistungswandler bezeichnet werden. Derartige Leistungswandler können erlangt werden durch Kombinieren der Schaltzelle eines Abwärtswandlers mit der Schaltzelle eines Aufwärtswandlers, wobei beide Schaltzellen einen gemeinsamen Induktor L nutzen. Während eine derartige Anordnung eine flexible Aufwärts- und/oder Abwärts-Wandlung ermöglicht, ist eine derartige Anordnung ineffizient in Bezug auf die Anzahl von erforderlichen Schaltern (d. h. in Bezug auf den erforderlichen Raum) und in Bezug auf die Anzahl von Schaltern, die in Serie angeordnet sind (d. h. in Bezug auf den Energieverbrauch), insbesondere wenn Vout/Vin &gt; 2 ist oder &lt; 1/2 ist. In dem vorliegenden Dokument wird ein effizienter Mehrfachpegel-Abwärts-Leistungswandler beschrieben, der auch eine Aufwärtswandlung unterstützt (zum Beispiel Ausgangsspannungen Vout &lt; (n – 1) × Vin bei einer Verwendung eines n-stufigen Leistungswandlers), und/oder ein effizienter Mehrfachpegel-Aufwärts-Leistungswandler wird beschrieben, der auch eine Abwärtswandlung unterstützt. Die beschriebenen Leistungswandler haben eine reduzierte Größe im Vergleich zu einem Leistungswandler, der einen Mehrfachpegel-Abwärtswandler mit einem Mehrfachpegel-Aufwärtswandler über einen gemeinsamen Induktor kaskadiert. Weiter sehen die beschriebenen Leistungswandler eine hohe Leistungseffizienz vor, da die Leistungswandler ein Maximum von nur zwei Schaltern in Serie anordnen. 1 zeigt einen beispielhaften Abwärts-Aufwärts-Leistungswandler mit drei Pegeln. Der Leistungswandler weist auf einen ersten Schalter S1, der konfiguriert ist zum Koppeln eines ersten Kondensatoranschlusses des fliegenden Kondensators C mit dem Eingangsanschluss des Leistungswandlers, einen zweiten Schalter S2, der konfiguriert ist zum Koppeln des ersten Kondensatoranschlusses des fliegenden Kondensators C mit dem Induktor L, einen dritten Schalter S3A, der konfiguriert ist zum Koppeln eines zweiten Kondensatoranschlusses des fliegenden Kondensators C mit dem Induktor L, einen vierten Schalter S4, der konfiguriert ist zum Koppeln des zweiten Kondensatoranschlusses des fliegenden Kondensators C mit Masse, und einen Hilfsschalter S35, der konfiguriert ist zum Koppeln des zweiten Hilfsanschlusses des fliegenden Kondensators C mit dem Eingangsanschluss. Die Schalter S1, S3, S3A, S3B und S4 können eine Schaltzelle bilden. Der Induktor L kann die Schaltzelle mit dem Ausgangsanschluss des Leistungswandlers koppeln. Wenn der Hilfsschalter S3B offen gehalten wird, arbeitet der Leistungswandler von 1 als ein 3-Pegel-Abwärts-Leistungswandler, der durch eine Sequenz von Betriebsphasen geht, die in den 3A, 3B und 3C gezeigt werden. Insbesondere kann auf die Betriebsphase von 3A die Betriebsphase von 3C folgen, auf die die Betriebsphase von 3B folgen kann, auf die die Betriebsphase von 3C folgen kann, bevor alles noch einmal startet. Als Ergebnis einer solchen Sequenz von Betriebsphasen kann eine Ausgangsspannung Vout erzeugt werden, die größer als das 0,5-fache der Eingangsspannung Vin ist (und kleiner als die Eingangsspannung Vin). In der oben angeführten Sequenz von Betriebsphasen kann eine der zwei Betriebsphasen gemäß 3C ausgelassen werden. Zum Erzeugen einer Spannung Vout, die kleiner ist als das 0,5-fache der Eingangsspannung Vin, kann die folgende Sequenz von Betriebsphasen verwendet werden: auf die Betriebsphase von 3A folgt die Betriebsphase von 3D, auf die die Betriebsphase von 3B folgt, auf die die Betriebsphase von 3D folgt, bevor alles noch einmal startet. Eine der zwei Betriebsphasen gemäß 3D kann ausgelassen werden. In dem Fall eines niedrigen Ausgangsstroms kann ein inaktiver bzw. Ruhezustand oder eine inaktive Betriebsphase, wie in 3E gezeigt, in die Sequenzen von Betriebsphasen eingefügt werden, um einen Schaltverlust zu reduzieren. Es ist aus den 3A, 3B, 3C, 3D und 3E zu erkennen, dass der Hilfsschalter S3B für eine Abwärtswandlung offen gehalten wird, wodurch die Leistungseffizienz des Leistungswandlers nicht beeinträchtigt wird, wenn als ein Abwärts-Leistungswandler betrieben. Andererseits kann der Hilfsschalter S3B verwendet werden zum Vorsehen eines Aufwärtsleistungswandlers (d. h. eines Aufwärts(Boost)leistungswandlers) mit einem maximalen Umwandlungsverhältnis Vout/Vin &lt; 2. Die 4A und 4B zeigen beispielhafte Betriebsphasen zum Vorsehen einer Aufwärtswandlung. Insbesondere kann der Leistungswandler zwischen der Betriebsphase von 4A und der Betriebsphase von 4B wechseln, um eine Aufwärtswandlung von bis zu Vout/Vin, &lt; 2 zu erreichen. Während der Betriebsphase von 4B ist der fliegenden Kondensator C parallel zu dem Eingang des Leistungswandlers angeordnet, wodurch der fliegende Kondensator C auf ein mögliches Maximum von VC = Vin geladen wird. Als Folge davon wird eine höhere virtuelle Eingangsspannung (die die Summe von Vin und VC ist) während der Betriebsphase der 4B vorgesehen, wodurch eine Aufwärtswandlung möglich wird. In dem Fall eines Aufwärtsverhältnisses Vout/Vin &lt; 1,5 kann ein Zustand oder eine Betriebsphase, wie die in 4D gezeigte, verwendet werden, um den Induktor L auch während der Kondensatorentladephase zu entmagnetisieren. Eine schnellere Entmagnetisierung des Induktors L kann auch erreicht werden durch Verwendung des dritten Schalters S3A in einem Zustand oder einer Betriebsphase, wie die in 4C gezeigte. Eine Drücken-Ziehen(Push-Pull)-Topologie mit Stromwelligkeitsunterdrückung kann auf den 3-Pegel-Abwärts-Aufwärts-Leistungswandler von 1 angewendet werden durch Addieren einer verschachtelnden Schaltzelle (die die Schalter S5, S6A, S6B, S7, S8 aufweist) und eines verschachtelnden fliegenden Kondensators C2 (siehe 2A). Die verschachtelnde Schaltzelle kann auf dieselbe Weise betrieben werden wie die erste oder Hauptschaltzelle (die die Schalter S1, S2, S3A, S3B, S4 aufweist). Allerdings kann (für eine Abwärtswandlung) die Hauptschaltzelle auf eine verschachtelte Weise betrieben werden (zum Beispiel mit einer 180-Grad-Phasenverschiebung) im Vergleich zu der verschachtelnden Schaltzelle, wodurch eine Stromwelligkeit unterdrückt oder reduziert wird. Es sollte angemerkt werden, dass für einen reduzierten Ausgangsstrom in dem Aufwärtsmodus die verschachtelnde Schaltzelle ohne den verschachtelnden Hilfsschalter S6B vorgesehen sein kann. Ansonsten müssten beide Schaltzellen synchron in dem Aufwärtsmodus betrieben werden. Der Hilfsschalter S3B (und S6B) kann individuell gemäß den Effizienzanforderungen (maximale Umwandlungsverlustleistung) während des Aufwärtsmodus skaliert werden. 2B zeigt eine invertierte Topologie des Leistungswandlers von 1. Der Leistungswandler von 2B kann als ein 3-Pegel-Aufwärtsleistungswandler mit einem Hilfsschalter S3B betrachtet werden, der eine Abwärtswandlung ermöglicht (wobei VC an dem fliegenden Kondensator ungefähr gleich ist zu der Ausgangsspannung Vout). Die Effizienz des Aufwärtswandlers wird durch den Hilfsschalter S3B nicht beeinflusst. Eine Ausgangswelligkeitsreduktion kann vorgesehen werden durch Verwendung eines verschachtelnden zweiten fliegenden Kondensators in einer analogen Konfiguration, wie in 2A gezeigt. 2C zeigt einen beispielhaften Inverter, d. h. einen invertierenden DC/DC-Wandler mit (absoluter) Aufwärts- und Abwärts-Fähigkeit. Die 5A, 5B, 5C, 5D und 5E zeigen beispielhafte Betriebsphasen für den Inverter von 2C. Durch komplementäres Schalten des ersten Schalters S1 zusammen mit dem Schalter S3, und S2 zusammen mit dem Schalter S4, arbeitet der Inverter von 2C als ein invertierender Abwärts-Aufwärtswandler mit verbesserter Effizienz bei Umwandlungsverhältnissen Vout/Vin = –1/2 oder –2 (zusätzlich zu Vout/Vin = –1). Insbesondere können die Betriebsphasen der 5A und 5B auf eine periodische Weise wiederholt werden, wodurch eine Standardsequenz von Betriebsphasen vorgesehen wird. Durch Ändern der Arbeitszyklen der verschiedenen Betriebsphasen kann das Umwandlungsverhältnis angepasst werden. Somit ermöglicht der Inverter von 2C eine Inversion mit flexiblen (absoluten) Umwandlungsverhältnissen. Zum Erhöhen der (absoluten) Ausgangsspannung und/oder des Stroms kann eine zusätzliche Magnetisierungsphase einmal (oder zweimal) in einen kompletten Schaltzyklus eingefügt werden (wie in 5C gezeigt). Ein Entmagnetisieren für ein Abwärtsregeln einer (absoluten) Ausgangsspannung und/oder eines Stroms kann erreicht werden durch Einfügen einer Betriebsphase, wie in 5D gezeigt (anstelle der Betriebsphase von 5C). Die Phasen von 5C und 5D können zum Regeln der Spannung und/oder des Stroms an dem Ausgang des Leistungswandlers verwendet werden. Bei einem niedrigen Ausgangsstrom kann ein inaktiver Zustand, wie in 5E gezeigt, in die erste oder zweite Sequenz von Betriebsphasen eingefügt werden, um einen Schaltverlust zu reduzieren. Es sollte angemerkt werden, dass die Abwärts-Aufwärts-Schalttopologie, die in dem vorliegenden Dokument gezeigt wird (insbesondere in den 1, 2B und 2C), nicht auf eine 3-Pegel-Umwandlung begrenzt ist, sondern auf ähnliche Weise auf andere (Kondensator-basierte) Mehrfachpegel-Leistungswandler erweitert werden kann. 6 zeigt ein Ablaufdiagramm eines beispielhaften Verfahrens 600 zum Umwandeln einer Eingangsspannung an einem Eingangsanschluss in eine Ausgangsspannung an einem Ausgangsanschluss eines Leistungswandlers. Die Eingan
[JA JPWO2019030859A1]: 電力変換装置 [EN EP3667893B1]: POWER CONVERSION DEVICE [FR EP3667893B1]: DISPOSITIF DE CONVERSION DE PUISSANCE [DE EP3667893B1]: STROMWANDLUNGSVORRICHTUNG | [JA JPWO2019030859A1]: 一実施形態の電力変換装置は、互いに直列に接続された複数のサブモジュールを（４０）備える。各サブモジュール（４０）において、第１の端子（４３）、第２の端子（４２）、および第３の端子（４４）は、パッケージ（４１）の表面上または表面から突出するように設けられる。第１の半導体スイッチング素子（４５）は、パッケージ（４１）に内蔵され、第１の端子（４３）と第２の端子（４２）との間に接続される。第２の半導体スイッチング素子（４６）は、パッケージ（４１）に内蔵され、第２の端子（４２）と第３の端子（４４）との間に接続される。直流コンデンサ（４９）は、パッケージ（４１）に内蔵され、第１の端子（４３）と第３の端子（４４）との間に接続される。 [EN EP3667893B1]: A power conversion device according to one embodiment includes a plurality of submodules (40) connected in series to each other. In each submodule (40), a first terminal (43), a second terminal (42) and a third terminal (44) are provided on or provided to protrude from a surface of a package (41). A first semiconductor switching element (45) is built into the package (41) and connected between the first terminal (43) and the second terminal (42). A second semiconductor switching element (46) is built into the package (41) and connected between the second terminal (42) and the third terminal (44). A DC capacitor (49) is built into the package (41) and connected between the first terminal (43) and the third terminal (44). [FR WO2019030859A1]: Un dispositif de conversion de puissance selon un mode de réalisation comprend une pluralité de sous-modules (40) connectés en série entre eux. Dans chacun des sous-modules (40), une première borne (43), une deuxième borne (44) et une troisième borne (44) sont disposées sur une surface d'un boîtier (41), ou de façon à faire saillie à partir de la surface. Un premier élément de commutation à semi-conducteur (45) est intégré dans le boîtier (41) et connecte la première borne (43) et la deuxième borne (42). Un second élément de commutation à semi-conducteur (46) est intégré dans le boîtier (41) et connecte la deuxième borne (42) et la troisième borne (44). Un condensateur à courant continu (49) est intégré dans le boîtier (41) et connecte la première borne (43) et la troisième borne (44). | EP3667893B1 | 2020-06-17 2020-08-05 2021-09-22 | EP17920796A | 2017-08-09 2017-08-09 2017-08-09 | JP2017028941W, 2017-08-09 JP2017028941W, 2017-08-09 JP2017028941W, 2017-08-09 | JPWO2019030859A1: 2019-11-07 WO2019030859A1: 2019-02-14 US2020177097A1: 2020-06-04 EP3667893B1: 2021-09-22 | 三菱電機株式会社 MITSUBISHI ELECTRIC CORP | TAKAHASHI TATSUYA HAYASHI SHIGEO | H02M7/483: I H02M7/49: I H02M7/48: I H02M7/00: I H02M7/5387: I H01L25/04: I H01L25/10: I | H02M7/003: I H02M7/483: I H02M7/4835: I H02M7/5387: I | WO2015037537A1 WO2016162915A1 US2013148392A1 WO2015131931A1 DE102009031574A1 | WO2021052730A1 WO2021052730 2021/052730 WO2021/052730A1 EP3796539A1 EP3796539 3796539 WO2020017033A1 WO2020017033 2020/017033 WO2020/017033A1 US10992219B2 US10992219 10992219 US10886858B1 US10886858 10886858 US11075587B2 US11075587 11075587 | [JA JPWO2019030859A1]: 互いに直列に接続された複数のサブモジュールを備え、 前記複数のサブモジュールの各々は、 パッケージの表面上または表面から突出するように設けられた、第1の端子、第2の端子、および第3の端子と、 前記パッケージに内蔵され、前記第1の端子と前記第2の端子との間に接続された第1の半導体スイッチング素子と、 前記パッケージに内蔵され、前記第2の端子と前記第3の端子との間に接続された第2の半導体スイッチング素子と、 前記パッケージに内蔵され、前記第1の端子と前記第3の端子との間に接続された直流コンデンサとを備え、 前記複数のサブモジュールは、第1のサブモジュールおよび第2のサブモジュールを含み、 前記第1のサブモジュールの前記第1の端子と前記第2のサブモジュールの前記第1の端子とは、配線を介して相互に接続され、 前記第1のサブモジュールの前記第3の端子と前記第2のサブモジュールの前記第3の端子とは、配線を介して相互に接続される、電力変換装置。 前記第1のサブモジュールは、前記第2のサブモジュールに隣接し、 前記複数のサブモジュールは、前記第2のサブモジュールに隣接する第3のサブモジュールを含み、 前記第2のサブモジュールの前記第2の端子と前記第3のサブモジュールの前記第2の端子とは、配線を介して相互に接続される、請求項1に記載の電力変換装置。 前記第1のサブモジュールは、前記第2のサブモジュールに隣接し、 前記複数のサブモジュールは、前記第1のサブモジュールに隣接する第4のサブモジュールを含み、 前記第4のサブモジュールの前記第3の端子と前記第1のサブモジュールの前記第2の端子とは、配線を介して相互に接続される、請求項1または2に記載の電力変換装置。 前記複数のサブモジュールは、互いに隣接する第5のサブモジュールおよび第6のサブモジュールを含み、 前記第5のサブモジュールの前記第3の端子と前記第6のサブモジュールの前記第2の端子とは、配線を介して相互に接続される、請求項1~3のいずれか1項に記載の電力変換装置。 前記複数のサブモジュールは、複数のブロックに分割され、 前記電力変換装置は、複数の絶縁性容器をさらに備え、 各前記絶縁性容器には、対応する前記ブロックを構成する複数のサブモジュールが収納され、 前記複数の絶縁性容器は上下方向に積み上げられることによってタワーを構成する、請求項4に記載の電力変換装置。 前記複数の絶縁性容器のうちの1つに、前記第1のサブモジュール、前記第2のサブモジュール、前記第5のサブモジュール、および前記第6のサブモジュールが収納される、請求項5に記載の電力変換装置。 [EN EP3667893B1]: A power conversion device of modular multilevel conversion type, comprising a plurality of converter cells (5, 6) cascade-connected to each other, the plurality of converter cells including: one or more full bridge-type converter cells (FB, 5); anda plurality of half bridge-type converter cells (HB, 6),each of the plurality of half bridge-type converter cells (HB, 6) including one submodule (40),each of the one or more full bridge-type converter cells (FB, 5) including two submodules (40),each of the submodules (40) including: a first terminal (43), a second terminal (42) and a third terminal (44), the first to third terminals being provided on or provided to protrude from a surface of a package (41);a first semiconductor switching element (45) built into the package (41) and connected between the first terminal (43) and the second terminal (42);a second semiconductor switching element (46) built into the package (41) and connected between the second terminal (42) and the third terminal (44); anda DC capacitor (49) built into the package (41) and connected between the first terminal (43) and the third terminal (42),a first full bridge-type converter cell (FB in Fig. 6(C)) included in the plurality of converter cells including a first submodule (40_2) and a second submodule (40_3) as the two submodules,the first terminal (41) of the first submodule (40_2) and the first terminal (41) of the second submodule (40_3) being connected to each other through a wiring (60),the third terminal (43) of the first submodule (40_2) and the third terminal (43) of the second submodule (43) being connected to each other through a wiring (61),the second terminal (42_2) of the first submodule (40_2) being used for connection to a second converter cell (HB (40_1) in Fig. 6(C)),the second terminal (42_3) of the second submodule (40_3) being used for connection to a third converter cell (HB (40_4) in Fig. 6(C)) different from the second converter cell. The power conversion device according to claim 1, wherein the third converter cell (HB (40_4) in Fig. 6(C)) is a half bridge-type converter cell including a third submodule (40_4), andthe second terminal (42_3) of the second submodule (40_3) and the second terminal (42_4) of the third submodule (40_4) are connected to each other through a wiring. The power conversion device according to claim 2, wherein the second converter cell (HB (40_1) in Fig. 6(C)) is a half bridge-type converter cell including a fourth submodule (40_1), andthe third terminal (44_1) of the fourth submodule (40_1) and the second terminal (42_2) of the first submodule (40_2) are connected to each other through a wiring. The power conversion device according to any one of claims 1 to 3, wherein the plurality of converter cells further includes: a fourth half bridge-type converter cell including a fifth submodule (40_1 in Fig. 6(B)); anda fifth half bridge-type converter cell including a sixth submodule (40_2 in Fig. 6(B)) adjacent to the fifth submodule (40_1 in Fig. 6(B)), andthe third terminal (44_1) of the fifth submodule (40_1) and the second terminal (42_2) of the sixth submodule (40_2) are connected to each other through a wiring. The power conversion device according to any one of claims 1 to 4, wherein the plurality of converter cells are divided into a plurality of blocks,the power conversion device further includes a plurality of insulating containers (31),a plurality of submodules (40) forming a corresponding one of the blocks are housed in each of the insulating containers (31), andthe plurality of insulating containers (31) are stacked vertically to form a tower (30). The power conversion device according to claim 5, wherein at least one half bridge-type converter cell (HB) and at least one full bridge-type converter cell (FB) are housed in at least one of the plurality of insulating containers (31) in a mixed manner. [DE EP3667893B1]: Leistungswandlereinrichtung von einer modularen Mehrstufen-Wandlerart, mit einer Mehrzahl von Wandlerzellen (5, 6), die miteinander kaskadenverbunden sind, wobei die Mehrzahl von Wandlerzellen aufweist: eine oder mehrere Wandlerzellen vom Vollbrückentyp (FB, 5), undeine Mehrzahl von Wandlerzellen vom Halbbrückentyp (HB, 6),wobei jede der Mehrzahl von Wandlerzellen vom Halbbrückentyp (HB, 6) ein Submodul (40) aufweist,wobei jede der ein oder mehreren Wandlerzellen vom Vollbrückentyp (FB, 5) zwei Submodule (40) aufweist,wobei jedes der Submodule (40) aufweist: einen ersten Anschluss (43), einen zweiten Anschluss (42) und einen dritten Anschluss (44), wobei der erste bis dritte Anschluss bereitgestellt sind auf einer Oberfläche eines Gehäuses (41) oder von einer Oberfläche eines Gehäuses (41) vorstehend,ein erstes Halbleiterschaltelement (45), das in das Gehäuse (41) gebaut ist und zwischen dem ersten Anschluss (43) und dem zweiten Anschluss (42) verbunden ist,ein zweites Halbleiterschaltelement (46), das in das Gehäuse (41) gebaut ist und zwischen dem zweiten Anschluss (42) und den dritten Anschluss (44) verbunden ist, undeinen DC-Kondensator (49), der in das Gehäuse (41) gebaut ist und zwischen dem ersten Anschluss (43) und dem dritten Anschluss (42) verbunden ist,wobei eine erste Wandlerzelle vom Vollbrückentyp (FB in Fig. 6(C)), die in der Mehrzahl von Wandlerzellen vorhanden ist, ein erstes Submodul (40_2) und ein zweites Submodul (40_3) als die zwei Submodule aufweist,der erste Anschluss (41) des ersten Submoduls (40_2) und der erste Anschluss (41) des zweiten Submoduls (40_3) miteinander mittels einer Leitung (60) verbunden sind,der dritte Anschluss (43) des ersten Submoduls (40_2) und der dritte Anschluss (43) des zweiten Submoduls (43) miteinander durch eine Leitung (61) verbunden sind,der zweite Anschluss (42_2) des ersten Submoduls (40_2) genutzt wird zur Verbindung zu einer zweiten Wandlerzelle (HB(40_1) in Fig. 6(C)),wobei der zweite Anschluss (42_3) des zweiten Submoduls (40_3) genutzt wird zur Verbindung zu einer dritten Wandlerzelle (HB(40_4) in Fig. 6(C)) verschieden von der zweiten Wandlerzelle. Leistungswandlereinrichtung nach Anspruch 1, wobei: die dritte Wandlerzelle (HB(40_4) in Fig. 6(C)) eine Wandlerzelle vom Halbbrückentyp ist, die ein drittes Submodul (40_4) aufweist, undder zweite Anschluss (42_3) des zweiten Submoduls (40_3) und der zweite Anschluss (42_4) des dritten Submoduls (40_4) miteinander durch eine Leitung verbunden sind. Leistungswandlereinrichtung nach Anspruch 2, wobei: die zweite Wandlerzelle (HB(40_1) in Fig. 6(C)) eine Wandlerzelle vom Halbbrückentyp ist, die ein viertes Submodul (40_1) aufweist, undder dritte Anschluss (44_1) des vierten Submoduls (40_1) und der zweite Anschluss (42_2) des ersten Submoduls (40_2) miteinander durch eine Leitung verbunden sind. Leistungswandlereinrichtung nach einem der Ansprüche 1 bis 3, wobei: die Mehrzahl von Wandlerzellen des Weiteren aufweist: eine vierte Wandlerzelle vom Halbbrückentyp mit einem fünften Submodul (40_1 in Fig. 6(B)), undeine fünfte Wandlerzelle vom Halbbrückentyp mit einem sechsten Submodul (40_2 in Fig. 6(B)) benachbart zu dem fünften Submodul (40_1 in Fig. 6(B)), undwobei der dritte Anschluss (44_1) des fünften Submoduls (40_1) und der zweite Anschluss (42_2) des sechsten Submoduls (40_2) miteinander durch eine Leitung verbunden sind. Leistungswandlereinrichtung nach einem der Ansprüche 1 bis 4, wobei: die Mehrzahl von Wandlerzellen in eine Mehrzahl von Blöcken geteilt ist,die Leistungswandlereinrichtung des Weiteren eine Mehrzahl von isolierenden Containern (31) aufweist,die Mehrzahl von Submodulen (40), die einen entsprechenden der Blöcke ausbilden, in einem jeweiligen der isolierenden Container (31) beherbergt sind, unddie Mehrzahl von isolierenden Containern (31) vertikal gestapelt ist, um einen Turm (30) auszubilden. Leistungswandlereinrichtung nach Anspruch 5, wobei: mindestens eine Wandlerzelle vom Halbbrückentyp (HB) und mindestens eine Wandlerzelle vom Vollbrückentyp (FB) in mindestens einer der Mehrzahl von isolierenden Containern (31) auf gemischte Weise beherbergt sind. [FR EP3667893B1]: Dispositif de conversion de puissance faisant partie d'un type de conversion multiniveaux modulaire, comprenant une pluralité de cellules de convertisseurs (5, 6) reliées en série l'une à l'autre, la pluralité de cellules de convertisseurs incluant : une ou plusieurs cellules de convertisseurs de type pont complet (FB, 5), etune pluralité de cellules de convertisseurs de type demi pont (HB, 6),chacune de la pluralité de cellules de convertisseurs de type demi pont (HB, 6) incluant un sous module (40),chacune de la ou des cellules de convertisseurs de type pont complet (FB, 5) incluant deux sous modules (40),chacun des sous modules (40) incluant : une première borne (43), une deuxième borne (42) et une troisième borne (44), les première à troisième bornes étant disposées sur la surface d'un boîtier (41) ou prévues pour dépasser de celle-ci,un premier élément de commutation à semi-conducteur (45) intégré dans le boîtier (41) et relié entre la première borne (43) et la deuxième borne (42),un second élément de commutation à semi-conducteur (46) intégré dans le boîtier (41) et relié entre la deuxième borne (42) et la troisième borne (44), etun condensateur à courant continu (49) intégré dans le boîtier (41) et relié entre la première borne (43) et la troisième borne (42),une première cellule de convertisseur de type pont complet (FB sur la figure 6(C)), incluse dans la pluralité de cellules de convertisseurs incluant un premier sous module (40_2) et un deuxième sous module (40_3) utilisés comme deux sous modules,la première borne (41) du premier sous module (40_2) et la première borne (41) du deuxième sous module (40_3) étant reliées l'une à l'autre par l'intermédiaire d'un câblage (60),la troisième borne (43) du premier sous module (40_2) et la troisième borne (43) du deuxième sous module (43) étant reliées l'une à l'autre par l'intermédiaire d'un câblage (61),la deuxième borne (42_2) du premier sous module (40_2) étant utilisée pour une connexion à une deuxième cellule de convertisseur (HB(40_1) sur la figure 6(C)),la deuxième borne (42_3) du deuxième sous module (40_3) étant utilisée pour une connexion à une troisième cellule de convertisseur (HB(40_4) sur la figure 6(C)) différente de la deuxième cellule de convertisseur. Dispositif de conversion de puissance selon la revendication 1, dans lequel : la troisième cellule de convertisseur (HB(40_4) sur la figure 6(C)) est une cellule de convertisseur de type demi pont incluant un troisième sous module (40_4), etla deuxième borne (42_3) du deuxième sous module (40_3) et la deuxième borne (42_4) du troisième sous module (40_4) sont reliées l'une à l'autre par l'intermédiaire d'un câblage. Dispositif de conversion de puissance selon la revendication 2, dans lequel : la deuxième cellule de convertisseur (HB(40_1) sur la figure 6(C)) est une cellule de convertisseur de type demi pont incluant un quatrième sous module (40_1), etla troisième borne (44_1) du quatrième sous module (40_1) et la deuxième borne (42_2) du premier sous module (40_2) sont reliées l'une à l'autre par l'intermédiaire d'un câblage. Dispositif de conversion de puissance selon l'une quelconque des revendications 1 à 3, dans lequel : la pluralité de cellules de convertisseurs inclut en outre : une quatrième cellule de convertisseur de type demi pont incluant un cinquième sous module (40_1 sur la figure 6(B)), etune cinquième cellule de convertisseur de type demi pont incluant un sixième sous module (40_2 sur la figure 6(B)) adjacent au cinquième sous module (40_1 sur la figure 6(B)), etla troisième borne (44_1) du cinquième sous module (40_1) et la deuxième borne (42_2) du sixième sous module (40_2) sont reliées l'une à l'autre par l'intermédiaire d'un câblage. Dispositif de conversion de puissance selon l'une quelconque des revendications 1 à 4, dans lequel : les différentes cellules de convertisseurs sont divisées en une pluralité de blocs,le dispositif de conversion de puissance inclut en outre une pluralité d'enveloppes isolantes (31), une pluralité de sous modules (40), formant l'un correspondant des blocs, est accueillie dans chacune des enveloppes isolantes (31), etles différentes enveloppes isolantes (31) sont empilées verticalement pour former une tour (30). Dispositif de conversion de puissance selon la revendication 5, dans lequel : au moins une cellule de convertisseur de type demi pont (HB) et au moins une cellule de convertisseur de type pont complet (FB) sont accueillis dans au moins l'une de la pluralité d'enveloppes isolantes (31) en étant mélangées. | [JA JPWO2019030859A1]: 本開示は、複数の変換器セルがカスケードに接続されることによって構成された自励式の電力変換装置に関し、たとえば、高圧直流送電、周波数変換器などに好適に用いられるものである。 電力系統に接続される大容量の電力変換装置としてモジュラーマルチレベル変換器(MMC:Modular Multilevel Converter)が知られている。モジュラーマルチレベル変換器は、交流の各相に対して、高電位側直流ノードに接続された上アーム(arm)回路と低電位側直流ノードに接続された下アーム回路とを有する。各アーム回路は、多数の変換器セルがカスケードに接続されることによって構成されている。 各変換器セルは、エネルギー蓄積器としてのコンデンサと、第1および第2の入出力ノードと、これらの入出力ノードとコンデンサとの間を接続または非接続に切替えるためのブリッジ回路とを備える。ブリッジ回路として、ハーフブリッジ型またはフルブリッジ型などが用いられる。 実際の高電圧変換器では、複数個の変換器セルでブロックを構成し、このブロックを上下方向に積み上げることによってタワーを構成する方法がよく用いられる(たとえば、特許文献1(国際公開第2016/162915号)の図5を参照)。この文献の場合、各ブロックは、絶縁体のトレイ(tray)内に配置されている。 国際公開第2016/162915号 ハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルを混在させることによって各アーム回路を構成する場合がある。一例として、各アーム回路を構成する複数の変換器セルのうち半数をフルブリッジ型で構成し、半数をハーフブリッジ型で構成する場合が考えられる。この場合には、フルブリッジ型の変換器セルのみで構成されたタワーと、ハーフブリッジ型の変換器セルのみで構成されたタワーとを設けることができる。 ところが、他の例として、各アーム回路に少数(たとえば、2~3個)のフルブリッジ型の変換器セルしか含まれていない場合には、1つのタワー内にハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとを混在させなければならない。そうすると、ハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとでは大きさが異なるので、スペース効率の点で問題が生じる。 この開示は、上記の問題点を考慮したものであり、その目的は、スペースを効率良く使用してハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとを配置することが可能なMMC方式の電力変換装置を提供することである。 なお、上記では極端な例を示したが、本開示の電力変換装置は、個数に関係なく、ハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとが混在している場合に広く適用することができる。 一実施形態の電力変換装置は、互いに直列に接続された複数のサブモジュールを備える。複数のサブモジュールの各々は、第1の端子、第2の端子、第3の端子、第1の半導体スイッチング素子、第2の半導体スイッチング素子、および直流コンデンサを備える。第1の端子、第2の端子、および第3の端子は、パッケージの表面上または表面から突出するように設けられる。第1の半導体スイッチング素子は、パッケージに内蔵され、第1の端子と第2の端子との間に接続される。第2の半導体スイッチング素子は、パッケージに内蔵され、第2の端子と第3の端子との間に接続される。直流コンデンサは、パッケージに内蔵され、第1の端子と第3の端子との間に接続される。複数のサブモジュールは、互いに隣接する第1のサブモジュールおよび第2のサブモジュールを含む。第1のサブモジュールの第1の端子と第2のサブモジュールの第1の端子とは、配線を介して相互に接続される。第1のサブモジュールの第3の端子と第2のサブモジュールの第3の端子とは、配線を介して相互に接続される。 上記の実施形態によれば、単一サブモジュールはハーフブリッジ型の変換器セルとして用いることができ、隣接する2つのサブモジュールは、端子間を相互に接続することよってフルブリッジ型の変換器セルとして使用することができる。したがって、スペースを効率良く使用してハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとを配置することが可能になる。 電力変換装置の一例を示す概略構成図である。 交流回路と各レグ回路との接続部の変形例を示す図である。 交流回路と各レグ回路との接続部の他の変形例を示す図である。 サブモジュールの回路構成の一例を示す図である。 サブモジュールの物理的な外観を模式的に示す斜視図である。 高電位側アーム回路の構成の一例を示す回路図である。 アーム回路の物理的な外観を模式的に示す斜視図である。 アーム回路を構成するサブモジュール間の接続を説明するための図である。 図8に示すサブモジュールの配列を、ハーフブリッジ型の変換器セルおよびフルブリッジ型の変換器セルの配列に置き替えて示した図である。 図8のサブモジュール40_3~40_6の相互の接続を模式的に示す外観図である。 図8のサブモジュール40_11~40_14の相互の接続を模式的に示す外観図である。 以下、各実施の形態について図面を参照して詳しく説明する。なお、同一または相当する部分には同一の参照符号を付して、その説明を繰返さない。 実施の形態1. [電力変換装置の概略構成] 図1は、電力変換装置の一例を示す概略構成図である。図1を参照して、電力変換装置は、主回路であるレグ回路4u,4v,4w(総称する場合または不特定のものを示す場合、レグ回路4と記載する)と、これらのレグ回路4を制御する中央制御装置3とを備える。 レグ回路4は、交流を構成する複数相の各相ごとに設けられる。レグ回路4は、交流回路20と直流回路21との間に接続され、両回路間で電力変換を行う。図1には交流回路20が三相交流の場合が示され、u相、v相、w相にそれぞれ対応して3個のレグ回路4u,4v,4wが設けられる。 レグ回路4u,4v,4wにそれぞれ設けられた交流ノード(node)Nu,Nv,Nwは、連系変圧器22を介して交流回路20に接続される。交流回路20は、たとえば、交流電源などを含む交流電力系統である。図1では、図解を容易にするために、交流ノードNv,Nwと連系変圧器22との間の接続は図示していない。 各レグ回路4に共通に設けられた直流ノードNp,Nn(すなわち、高電位側直流ノードNp,低電位側直流ノードNn)は、直流回路21に接続される。直流回路21は、高圧直流送電(HVDC:High Voltage Direct Current)システムにおける直流電力系統、またはBTB(Back To Back)システムにおける他の電力変換装置との接続配線に相当する。 なお、HVDCシステムは、高電圧の交流電力を直流電力に変換してから直流長距離送電を行うものである。この場合の交流/直流変換に、図1の電力変換装置1が利用される。また、BTBシステムは、交流を直流に変換する順変換と、直流を交流に変換する逆変換とを行うことによって、2つの交流回路間で電力融通を行うものである。順変換および逆変換に図1の電力変換装置1が利用される。 図1の連系変圧器22を用いる代わりに、連系リアクトルを介して交流回路20に接続した構成としてもよい。また、図2および図3に示すように、交流回路20と各レグ回路4は、交流的に接続されていてもよい。この場合の交流回路20と各レグ回路4との接続部の詳細な構成については後述する。 レグ回路4uは、高電位側直流ノードNpから交流ノードNuまでの高電位側アーム回路(上アーム回路または1次アーム回路とも称する)10と、低電位側直流ノードNnから交流ノードNuまでの低電位側アーム回路(下アーム回路または2次アーム回路とも称する)11とに区分される。高電位側アーム回路10と低電位側アーム回路11との接続点Nuが変圧器22と接続される。高電位側直流ノードNpおよび低電位側直流ノードNnが直流回路21に接続される。レグ回路4v,4wについても同様の構成を有しているので、以下、レグ回路4uを代表として説明する。 高電位側アーム回路10は、複数のハーフブリッジ(HB:Half Bridge)型の変換器セル5と、一つまたは複数のフルブリッジ(FB:Full Bridge)型の変換器セル6と、リアクトル7aとを含む。複数の変換器セル5と、少なくとも1つの変換器セル6と、リアクトル7aとは互いに直列接続されている。以下、簡単のために変換器セルを単にセルと称する場合がある。ハーフブリッジ型の変換器セル5とフルブリッジ型の変換器セル6とはどのような並び順で接続されていても構わない。 同様に、低電位側アーム回路11は、複数のハーフブリッジ型の変換器セル5と、一つまたは複数のフルブリッジ型の変換器セル6と、リアクトル7bとを含む。複数の変換器セル5と、少なくとも1つの変換器セル6と、リアクトル7bとは互いに直列接続されている。ハーフブリッジ型の変換器セル5とフルブリッジ型の変換器セル6とはどのような並び順で接続されていても構わない。 リアクトル7a,7bは、レグ回路中のセルがオンもしくはオフとなって出力電圧が急激に変化する瞬間に、または交流回路20または直流回路21などの故障時に、アーム電流Ipu,Ipnが急激に変化しないように設けられている。 リアクトル7aが挿入される位置は、レグ回路4uの高電位側アーム回路10のいずれの位置であってもよく、リアクトル7bが挿入される位置は、レグ回路4uの低電位側アーム回路11のいずれの位置であってもよい。リアクトル7a,7bはそれぞれ複数個あってもよい。各リアクトルのインダクタンス値は互いに異なっていてもよい。さらに、高電位側アーム回路10のリアクトル7aのみ、もしくは、低電位側アーム回路11のリアクトル7bのみを設けてもよい。 図1の電力変換装置1は、さらに、制御に使用される電気量(すなわち、電流および電圧)を計測する検出器として、交流電圧検出器23と、交流電流検出器24と、直流電圧検出器25p,25nと、各レグ回路4に設けられたアーム電流検出器9a,9bとを含む。これらの検出器によって検出された信号は、中央制御装置3に入力される。 具体的に、交流電圧検出器23は、交流回路20のU相の電圧値Vacu、V相の電圧値Vacv、およびW相の電圧値Vacwを検出する。交流電流検出器24は、交流回路20のU相、V相、W相の各相の電流値Iacu,Iacv,Iacwを検出する。直流電圧検出器25pは、直流回路21に接続された高電位側直流ノードNpの電圧を検出する。直流電圧検出器25nは、直流回路21に接続された低電位側直流ノードNnの電圧を検出する。 また、U相用のレグ回路4uに設けられたアーム電流検出器9a,9bは、高電位側アーム回路10に流れるアーム電流Ipuおよび低電位側アーム回路11に流れるアーム電流Inuをそれぞれ検出する。同様に、V相用のレグ回路4vに設けられたアーム電流検出器9a,9bは、高電位側アーム電流Ipvおよび低電位側アーム電流Invをそれぞれ検出する。W相用のレグ回路4wに設けられたアーム電流検出器9a,9bは、高電位側アーム電流Ipwおよび低電位側アーム電流Inwをそれぞれ検出する。これらのアーム電流に基づいて、直流回路21を流れる直流電流Idcおよび各レグ回路間を循環する循環電流を計算することができる。 上記の検出器によって検出された信号は、中央制御装置3に入力される。中央制御装置3は、さらに、各セル5,6からセルキャパシタ電圧の検出値を表す信号を受信する。中央制御装置3は、上記の各検出器の検出信号とセルキャパシタ電圧の情報とに基づいて、各セル5,6の運転状態を制御するための制御指令ならびに各セル5,6を保護するための運転/停止指令(運転指令または停止指令)を各セル5,6に出力する。 なお、図1では図解を容易にするために、各検出器から中央制御装置3に入力される信号の信号線ならびに中央制御装置3と各セル5との間で伝送される信号の信号線は一部まとめて記載されているが、実際には検出器ごとおよびセル5,6ごとに個別に設けられている。各セル5,6と中央制御装置3との間の信号線は、送信用と受信用とが別個に設けられていてもよい。また、本実施の形態の場合、これらの信号線は耐ノイズ性の観点から光ファイバによって構成される。 中央制御装置3は、回路によって構成され、たとえば、少なくとも1つのマイクロコンピュータ、または少なくとも1つのASIC(Application Specific Integrated Circuit)、または少なくとも1つのFPGA(Field Programmable Gate Array)によって構成することができる。もしくは、中央制御装置3は、上記のいずれかを組み合わせることによって構成されていてもよい。マイクロコンピュータは、少なくとも1つのプロセッサ(たとえば、CPU(Central Processing Unit))を含む。プロセッサは、少なくとも1つのコンピュータ読み取り可能な非一時的な記憶媒体(たとえば、ハードディスクなどの磁気媒体、CD(Compact Disk)およびDVD(Digital Video Disk)などの光学媒体、半導体メモリなど)から1つ以上の命令を読み取ることによって、中央制御装置3の機能の全部または一部を実行することができる。 [交流回路と各レグ回路との接続部の変形例] 図1では、レグ回路4u,4v,4wにそれぞれ設けられた交流ノードNu,Nv,Nwを介して、交流回路20と電力変換回路部2とが直流的に接続される例を示した。これに代えて、交流回路20と各レグ回路4は、変圧器を介して交流的に接続されていてもよい。以下、図2および図3を参照していくつかの具体例を説明する。 図2は、交流回路と各レグ回路との接続部の変形例を示す図である。図2を参照して、交流回路20とレグ回路4u,4v,4wとは、三相変圧器80Bを介して接続される。 図2に示すように、三相変圧器80Bでは、一次巻線81u,81v,81wがΔ結線されている。具体的に、三相変圧器80Bの一次巻線81uは、交流回路20のU相とV相の間に接続される。三相変圧器80Bの一次巻線81vは、交流回路20のV相とW相との間に接続される。三相変圧器80Bの一次巻線81wは、交流回路20のW相とU相との間に接続される。 三相変圧器80Bの二次巻線82u,82v,82wは、それぞれ共通の鉄心を介して一次巻線81u,81v,81wと磁気結合する。さらに、二次巻線82uはU相のアーム回路10u,11uと直列に接続され、二次巻線82vはV相のアーム回路10v,11vと直列に接続され、二次巻線82wはW相のアーム回路10w,11wと直列に接続される。 図2の場合、二次巻線82u,82v,82wの各々は、各相のリアクトル7a,7bを兼ねている。図2の場合と異なり、リアクトル7a,7bとは別に三相変圧器80Bの二次巻線82u,82v,82wを設けてもよい。 なお、鉄心内に生じる直流磁束は、Δ結線された一次巻線81u,81v,81wに直流成分を流すことによって打ち消すことができる。 図3は、交流回路と各レグ回路との接続部の他の変形例を示す図である。図3を参照して、交流回路20とレグ回路4u,4v,4wとは、3巻線の三相変圧器80Cを介して接続される。 具体的に、図3の三相変圧器80Cの一次巻線81u,81v,81wの各一端は、交流回路20のU相、V相、W相の各送電線と連系変圧器22を介してそれぞれ接続される。三相変圧器80Cの一次巻線81u,81v,81wの各他端は共通の中性点84と接続される。すなわち、図3の場合、一次巻線81u,81v,81wはY結線されている。 三相変圧器80Cの二次巻線82u,82v,82wは、それぞれ共通の鉄心を介して一次巻線81u,81v,81wと磁気結合する。図3の三相変圧器80Cでは、さらに、二次巻線82u,82v,82wとそれぞれ直列に接続された三次巻線83u,83v,83wが設けられている。各相の二次巻線と対応する三次巻線とは逆極性になるように接続され、共通の鉄心に巻回される。また、各相の二次巻線と対応する三次巻線との接続点は共通の中性点810に接続される。 さらに、二次巻線82uおよび三次巻線83uはU相のアーム回路10u,11uと直列に接続される。二次巻線82vおよび三次巻線83vはV相のアーム回路10v,11vと直列に接続される。二次巻線82wおよび三次巻線83wはW相のアーム回路10w,11wと直列に接続される。図3の場合、二次巻線82u,82v,82wの各々および三次巻線83u,83v,83wの各々は、各相のリアクトル7a,7bを兼ねている。リアクトル7a,7bとは別に三相変圧器80Cの二次巻線82u,82v,82wおよび三次巻線83u,83v,83wを設けてもよい。 図3の三相変圧器80Cによれば、各相のアーム電流(U相:Ipu,Inu、V相:Ipv,Inv、W相:Ipw,Inw)によって二次巻線に生じる直流起電力と三次巻線に生じる起電力とは互いに打ち消し合うため、鉄心内に直流磁束が生じないというメリットがある。 [変換器セルの具体的構成例] 本実施の形態において、ハーフブリッジ型の変換器セル5は、パッケージングされた単一のサブモジュール40として構成される。フルブリッジ型の変換器セル6は、サブモジュール40を2個組み合わせることによって構成される。これによって、同一形状および大きさのサブモジュール40のみによって、ハーフブリッジ型とフルブリッジ型とが混在したアーム回路10,11を構成することができるというメリットがある。以下、図面を参照して説明する。 図4は、サブモジュールの回路構成の一例を示す図である。図4(A)は、2個のサブモジュール40_1,40_2を組み合わせて1個のフルブリッジ型の変換器セルを構成した例を示す。なお、図4(A)に示すように、複数のサブモジュール40およびそれらの構成要素を相互に区別する場合には、参照符号の後にアンダーバーおよび識別番号を付す。 図4(A)を参照して、各サブモジュール40は、パッケージ41、交流端子42、正側端子43、負側端子44、半導体スイッチング素子45,46、ダイオード47,48、およびエネルギー蓄積器としての直流コンデンサ49を備える。 パッケージ41は、サブモジュール40を構成する各種部品(半導体スイッチング素子45,46、ダイオード47,48、および直流コンデンサ49など)を内蔵する。パッケージ41は、たとえば、樹脂製のケースを含む。交流端子42、正側端子43、および負側端子44は、パッケージ41の表面上または表面から突出するように設けられる。 半導体スイッチング素子45は、正側端子43と交流端子42と間に接続される。半導体スイッチング素子46は、交流端子42と負側端子44との間に接続される。半導体スイッチング素子45,46として、たとえば、IGBT(Insulated Gate Bipolar Transistor)またはGCT(Gate Commutated Turn-off thyristor)などの自励式の半導体スイッチング素子が用いられる。 ダイオード47,48は、半導体スイッチング素子45,46とそれぞれ逆並列(すなわち、並列かつ逆バイアス方向)に接続される。ダイオード47,48は対応する半導体スイッチング素子45,46に逆方向電圧が印加されたときの電流経路確保のために設けられている。 直流コンデンサ49は、正側端子43と負側端子44との間に接続される。したがって、直流コンデンサ49は、互いに直列接続された半導体スイッチング素子45,46と並列に接続される。 図示のように、2個のサブモジュール40_1,40_2によってフルブリッジ型の変換器セル6が構成される場合、一方のサブモジュール40_1の正側端子43_1と他方のサブモジュール40_2の正側端子43_2とが配線60を介して接続される。さらに、一方のサブモジュール40_1の負側端子44_1と他方のサブモジュール40_2の負側端子44_2とが配線61を介して接続される。サブモジュール40_1の交流端子42_1およびサブモジュール40_2の交流端子42_2は低電位側で隣接する他の素子等との接続に用いられる。 上記の配線60,61として、たとえば、ブスバーと称される導体棒または導体板を用いることができるが、これに限定されるものではない。たとえば、裸電線、金属パイプなどを用いてもよい。 図4(B)は図4(A)に対応する等価回路図である。図4(B)の等価回路図では、図4(A)に示す互いに連結された正側端子43_1,43_2は、1つの正側ノード43Aに置換されている。図4(A)に示す互いに連結された負側端子44_1,44_2は、1つの負側ノード44Aに置換されている。図4(A)に示す並列接続された直流コンデンサ49_1,49_2は、1個の直流コンデンサ50に置換されている。図4(B)から明らかなように、図4(A)に示す端子間の接続によってフルブリッジ型の変換器セル6が構成できていることがわかる。 図5は、サブモジュールの物理的な外観を模式的に示す斜視図である。以下の説明において、前後方向をX方向と、左右方向(または横方向)をY方向とし、上下方向(または縦方向)をZ方向とする。 図5(A)は、単一のサブモジュール40の外観の一例を示す。図5(A)の例では、サブモジュール40は、X方向が長手方向である略直方体形状のパッケージ41を有する。パッケージ41の正面(+X方向側の面)に交流端子42、正側端子43、負側端子44が設けられている。図5(A)の場合には、上から正側端子43、交流端子42、負側端子44の順に並んでいる。ただし、この並び順は一例であって、これに限定されるものではない。 図5(B)は、2個のサブモジュール40_1,40_2を組み合わせて1個のフルブリッジ型の変換器セルを構成した場合の外観図を示す。 図5(B)を参照して、サブモジュール40_1,40_2は左右方向に並んで配置される。これによって、各サブモジュール40に設けられた端子は共通の正面側に向けて配置される。図示のように、一方のサブモジュール40_1の正側端子43_1と他方のサブモジュール40_2の正側端子43_2とが配線60を介して接続される。さらに、一方のサブモジュール40_1の負側端子44_1と他方のサブモジュール40_2の負側端子44_2とが配線61を介して接続される。図5(B)の場合、配線60,61としてブスバーと称される導体棒が用いられている。 上述した図5の構成は一例であって、サブモジュール40のパッケージ41の形状、およびパッケージ41の表面上での交流端子42、正側端子43、および負側端子44の配置は図5の例に限定されるものでない。たとえば、後述するように正側端子43はフルブリッジ型の変換器セルを構成する2個のサブモジュール40間の接続だけにしか用いられない。したがって、図5(A)において、交流端子42および負側端子44をパッケージ41の正面(+X側の面)に配置し、正側端子43をパッケージ41の背面(-X側の面)に配置してもよい。 [アーム回路の具体的構成例] 次に、複数のサブモジュールを連結することによって構成されるアーム回路の構成例について説明する。 図6は、高電位側アーム回路の構成の一例を示す回路図である。図6(A)の回路図は、フルブリッジ型の変換器セルが直流回路21に接続される高電位側の直流線路26pに近接して配置された例を示す。図6(B)の回路図は、フルブリッジ型の変換器セルが交流回路20に接続される交流線路27に近接して配置された例を示す。図6(C)の回路図は、ハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとが混在して配置された例を示す。また、いずれの例においても、高電位側からサブモジュール40_1,40_2,40_3,...の順番で、複数のサブモジュール40が配列されている。 図6(A)を参照して、サブモジュール40_1,40_2によってフルブリッジ型の変換器セルが構成される。さらに、サブモジュール40_3,40_4によってフルブリッジ型の変換器セルが構成される。サブモジュール40_5は、ハーフブリッジ型の変換器セルとして用いられる。 この場合、サブモジュール40_1の交流端子42_1は直流線路26pと接続される。サブモジュール40_2の交流端子42_2とサブモジュール40_3の交流端子42_3とが配線を介して接続される。サブモジュール40_4の交流端子42_4とサブモジュール40_5の交流端子42_5とが配線を介して接続される。 図6(B)を参照して、サブモジュール40_1~40_3は、ハーフブリッジ型の変換器セルとして用いられる。 この場合、サブモジュール40_1の交流端子42_1は直流線路26pと接続される。サブモジュール40_1の負側端子44_1とサブモジュール40_2の交流端子42_2とが配線を介して接続される。サブモジュール40_2の負側端子44_2とサブモジュール40_3の交流端子42_3とが配線を介して接続される。 このように、サブモジュール40がハーフブリッジ型の変換器セルとして用いられる場合には、交流端子42および負側端子44が隣接する素子との接続に用いられる。正側端子43は接続に用いられない。 図6(C)を参照して、サブモジュール40_1は、ハーフブリッジ型の変換器セルとして用いられる。サブモジュール40_2,40_3によってフルブリッジ型の変換器セルが構成される。サブモジュール40_4は、ハーフブリッジ型の変換器セルとして用いられる。 この場合、サブモジュール40_1の交流端子42_1は直流線路26pと接続される。サブモジュール40_1の負側端子44_1とサブモジュール40_2の交流端子42_2とが配線を介して接続される。サブモジュール40_3の交流端子42_3とサブモジュール40_4の交流端子42_4とが配線を介して接続される。 以上をまとめると、互いに隣接する2個のサブモジュール40によってフルブリッジ型の変換器セルを構成した場合には、一方のサブモジュール40の交流端子42と他方のサブモジュール40の交流端子42とがそれぞれ隣接する外部の素子との接続に用いられる。また、図4および図5で説明したように、フルブリッジ型の変換器セルを構成する2個のサブモジュール40では、正側端子43同士が接続され、負側端子44同士が接続される。 一方、単一のサブモジュール40によってハーフブリッジ型の変換器セルを構成した場合には、交流端子42および負側端子44が隣接する外部の素子との接続に用いられる。正側端子43は用いられない。 図7は、アーム回路の物理的な外観を模式的に示す斜視図である。図7の例では、複数のサブモジュール40が横方向(Y方向)に並べられることよってブロックが構成され、各ブロックはトレイ(tray)状の絶縁性容器31内に配置されている。そして、複数の容器31が上下方向に積み上げられることによってタワー30が構成されている。 各絶縁性容器31は、図7の例では、略長方形状の底板35と、底板35の周縁部から起立する側板34によって構成される。最下段の絶縁性容器31は、床面上に起立する複数の支柱32によって支持されている。最下段よりも上段の絶縁性容器31の各々は、一段下の絶縁性容器31から起立する複数の支柱33によって支持されている。 具体的に図7の例では、2個のタワー30_1,30_2によってアーム回路が構成される。タワー30_1は5個の絶縁性容器31_1~31_5を備え、タワー30_2は5個の絶縁性容器31_11~31_15を備える。各絶縁性容器31には8個のサブモジュール40が横方向(Y方向)に並ぶように配置されている。無論、これらの個数は一例であってこれに限られるものではない。 図示のように、各サブモジュール40の形状が同一であるので、スペースを有効に利用してサブモジュール40を配置することができる。次に、具体例を挙げて、サブモジュール40間の接続について詳しく説明する。 [アーム回路を構成するサブモジュール間の接続の具体例] 図8は、アーム回路を構成するサブモジュール間の接続を説明するための図である。 図8では、高電位側アーム回路10が3段の絶縁性容器31_1~31_3を備えるタワー30によって構成される例が示されている。各絶縁性容器31には6個のサブモジュール40が配列されている。具体的に、絶縁性容器31_1には6個のサブモジュール40_1~40_6が配列され、絶縁性容器31_2には6個のサブモジュール40_7~40_12が配列され、絶縁性容器31_3には6個のサブモジュール40_13~40_18が配列される。サブモジュール40_1が最も高電位側であり、サブモジュール40_18が最も低電位側である。 なお、各サブモジュール40が横方向に配列されることによって、各サブモジュール40の正面に端子(すなわち、正側端子43、交流端子42、負側端子44)が設けられている。これによって、隣接するサブモジュール40間の接続が容易になっている。 図9は、図8に示すサブモジュールの配列を、ハーフブリッジ型の変換器セルおよびフルブリッジ型の変換器セルの配列に置き替えて示した図である。図8および図9に示す例では、サブモジュール40_1,40_2によってフルブリッジ型の変換器セルが構成され、サブモジュール40_3,40_4によってフルブリッジ型の変換器セルが構成される。その他の各サブモジュール40は、ハーフブリッジ型の変換器セルとして使用される。 次に、図8を参照して、各サブモジュール間に接続について具体的に説明する。まず、フルブリッジ型の変換器セルを構成するサブモジュール40_1とサブモジュール40_2とは、正側端子43同士が接続され、負側端子44同士が接続される。サブモジュール40_1の交流端子42は直流回路の高電位側の直流線路26pと接続される。サブモジュール40_2の交流端子42は、低電位側に隣接するサブモジュール40_3の交流端子42と接続される。 同様に、フルブリッジ型の変換器セルを構成するサブモジュール40_3とサブモジュール40_4とは、正側端子43同士が接続され、負側端子44同士が接続される。サブモジュール40_3の交流端子42は、高電位側に隣接するサブモジュール40_2の交流端子42と接続される。サブモジュール40_4の交流端子42は低電位側に隣接するサブモジュール40_5の交流端子42と接続される。 サブモジュール40_5~40_18の各々はハーフブリッジ型の変換器セルを構成する。この場合、各サブモジュール40の交流端子42は、高電位側に隣接するサブモジュール40がハーフブリッジ型の変換器セルを構成する場合にはそのサブモジュール40の負側端子44に接続される。また、サブモジュール40の交流端子42は、高電位側に隣接するサブモジュール40がフルブリッジ型の変換器セルを構成する場合にはそのサブモジュール40の交流端子42に接続される。 一方、ハーフブリッジ型の変換器セルを構成する各サブモジュール40の負側端子44は、低電位側に隣接するサブモジュール40の交流端子42に接続される。低電位側に隣接するサブモジュール40がハーフブリッジ型の変換器セルを構成するか、フルブリッジ型の変換器セルを構成するかによる違いはない。場合も、なお、最も低電位側のサブモジュール40_18の負側端子44は、交流回路20の交流線路27と接続される。 図10は、図8のサブモジュール40_3~40_6の相互の接続を模式的に示す外観図である。 図8および図10を参照して、フルブリッジ型の変換器セルを構成する互いに隣接するサブモジュール40_3および40_4に関して、正側端子43_3および43_4がブスバー62を介して相互に接続されるともに、負側端子44_3および44_4がブスバー63を介して相互に接続される。 サブモジュール40_4よりも低電位側のサブモジュール40_5,40_6の各々は、ハーフブリッジ型の変換器セルとして用いられる。この場合、サブモジュール40_5の交流端子42_5は、高電位側に隣接するフルブリッジ型変換器セルを構成するサブモジュール40_4の交流端子42_4とブスバー64を介して接続される。サブモジュール40_5の負側端子44_5は、低電位側に隣接するハーフブリッジ型変換器セルを構成するサブモジュール40_6の交流端子42_6とブスバー65を介して接続される。 図11は、図8のサブモジュール40_11~40_14の相互の接続を模式的に示す外観図である。 図8および図11を参照して、サブモジュール40_11~40_14の各々は、ハーフブリッジ型の変換器セルとして用いられる。この場合、サブモジュール40_11の負側端子44_11は、低電位側に隣接するサブモジュール40_12の交流端子42_12とブスバー66を介して接続される。サブモジュール40_12の負側端子44_12は、低電位側に隣接するサブモジュール40_13の交流端子42_13とブスバー67を介して接続される。サブモジュール40_13の負側端子44_13は、低電位側に隣接するサブモジュール40_14の交流端子42_14とブスバー68を介して接続される。 ここで、サブモジュール40_13は、サブモジュール40_12が配置されている絶縁性容器31_2よりも下段の絶縁性容器31_3に配置されている。したがって、両者を接続するブスバー67は絶縁性容器31_2の側板を迂回するように比較的長い経路で接続されている。 [効果] 以上のとおり、本実施の形態の電力変換装置によれば、ハーフブリッジ型の変換器セルは、パッケージングされた単一のサブモジュール40として構成され、フルブリッジ型の変換器セルは、上記のサブモジュール40を2個組み合わせることによって構成される。これによって、同一形状および大きさのサブモジュール40のみによって、ハーフブリッジ型とフルブリッジ型とが混在したアーム回路を構成することができる。このため、スペースを効率良く使用してハーフブリッジ型の変換器セルとフルブリッジ型の変換器セルとを配置することが可能なMMC方式の電力変換装置を提供することができる。 今回開示された実施の形態はすべての点で例示であって制限的なものでないと考えられるべきである。この発明の範囲は上記した説明ではなくて請求の範囲によって示され、請求の範囲と均等の意味および範囲内でのすべての変更が含まれることが意図される。 1 電力変換装置、2 電力変換回路部、3 中央制御装置、4u,4v,4w レグ回路、5 ハーフブリッジ型の変換器セル、6 フルブリッジ型の変換器セル、7a,7b リアクトル、9a,9b アーム電流検出器、10 高電位側アーム回路、11 低電位側アーム回路、20 交流回路、21 直流回路、22 連系変圧器、23 交流電圧検出器、24 交流電流検出器、25n,25p 直流電圧検出器、30 タワー、31 絶縁性容器、40 サブモジュール、41 パッケージ、42 交流端子、43 正側端子、44 負側端子、45,46 半導体スイッチング素子、47,48 ダイオード、49,50 直流コンデンサ、Nn 低電位側直流ノード、Np 高電位側直流ノード、Nu,Nv,Nw 交流ノード。 [EN EP3667893B1]: TECHNICAL FIELD The present disclosure relates to a self-exciting power conversion device formed by cascade-connecting a plurality of converter cells and suitably used in, for example, high-voltage direct-current power transmission, a frequency converter and the like. BACKGROUND ART A modular multilevel converter (MMC) is known as a large-capacity power conversion device connected to a power system. The modular multilevel converter has, for each phase of an alternating current, an upper arm circuit connected to a high potential-side DC node and a lower arm circuit connected to a low potential-side DC node. Each arm circuit is formed by cascade-connecting multiple converter cells. Each converter cell includes a capacitor serving as an energy accumulator, first and second input/output nodes, and a bridge circuit configured to perform switching between connection and non-connection of a portion between these input/output nodes and the capacitor. A half bridge-type circuit, a full bridge-type circuit or the like is used as the bridge circuit. A method commonly used in an actual high-voltage converter is a method for forming a block from a plurality of converter cells, and vertically stacking the blocks to form a tower (see, for example, Fig. 5 in International Publication No. 2016/162915). In the case of this literature, each block is arranged in a tray of an insulator. Document US 2013/0148392 A1, according to its abstract, states that a power conversion device includes at least two legs connected in parallel each of which includes at least two unit converters connected in series, wherein at least one of the legs is formed using at least two kinds of unit converters including a first type unit converter capable of outputting a unipolar voltage and a second type unit converter capable of outputting a bipolar voltage. Document WO 2015/131931 A1, according to its abstract, states a multilevel converter cell or power electronics building block for a multilevel converter comprising a half bridge module having a capacitor unit and at least two semiconductor switches, a gate unit configured to control the semiconductor switches, an electric conductor, at least a first and second terminal portions and a sub cell. The sub cell may comprise at least two half bridge modules connected in parallel and the electric conductor and the two terminal portions are configured to be connected to the sub cell in at least two different ways in order to provide a half bridge configured sub cell or a full bridge configured sub cell for the multilevel converter cell. SUMMARY OF INVENTION TECHNICAL PROBLEM Half bridge-type converter cells and full bridge-type converter cells may be arranged in a mixed manner to form each arm circuit in some cases. As one example, it is conceivable that a half of a plurality of converter cells forming each arm circuit are full bridge-type converter cells and the other half are half bridge-type converter cells. In this case, a tower formed only of the full bridge-type converter cells and a tower formed only of the half bridge-type converter cells can be provided. However, as another example, when each arm circuit includes only a few (e.g., two to three) full bridge-type converter cells, half bridge-type converter cells and the full bridge-type converter cells must be arranged in a mixed manner in one tower. This causes a problem in terms of space efficiency because the half bridge-type converter cells and the full bridge-type converter cells differ in size. The present disclosure has been made in view of the above-described problem and an object of the present disclosure is to provide an MMC-type power conversion device in which half bridge-type converter cells and full bridge-type converter cells can be arranged with high space efficiency. Although the extreme example has been described above, the power conversion device according to the present disclosure is widely applicable to the case in which half bridge-type converter cells and full bridge-type converter cells are arranged in a mixed manner, regardless of the number of the converter cells. SOLUTION TO PROBLEM There is provided a power conversion device of modular multilevel conversion type, comprising a plurality of converter cells cascade-connected to each other, the plurality of converter cells including: one or more full bridge-type converter cells; and a plurality of half bridge-type converter cells, each of the plurality of half bridge-type converter cells including one submodule, each of the one or more full bridge-type converter cells including two submodules, each of the submodules including: a first terminal, a second terminal and a third terminal, the first to third terminals being provided on or provided to protrude from a surface of a package; a first semiconductor switching element built into the package and connected between the first terminal and the second terminal; a second semiconductor switching element built into the package and connected between the second terminal and the third terminal; and a DC capacitor built into the package and connected between the first terminal and the third terminal, a first full bridge-type converter cell included in the plurality of converter cells including a first submodule and a second submodule as the two submodules, the first terminal of the first submodule and the first terminal of the second submodule being connected to each other through a wiring, the third terminal of the first submodule and the third terminal of the second submodule being connected to each other through a wiring, the second terminal of the first submodule being used for connection to a second converter cell, the second terminal of the second submodule being used for connection to a third converter cell different from the second converter cell. ADVANTAGEOUS EFFECTS OF INVENTION According to the above-described embodiment, a single submodule can be used as a half bridge-type converter cell, and two adjacent submodules can be used as a full bridge-type converter cell by connecting terminals thereof to each other. Therefore, half bridge-type converter cells and full bridge-type converter cells can be arranged with high space efficiency. BRIEF DESCRIPTION OF DRAWINGS Fig. 1 is a schematic configuration diagram showing an example power conversion device. Fig. 2 shows a modification of a connection portion connecting an AC circuit and each leg circuit. Fig. 3 shows another modification of the connection portion connecting the AC circuit and each leg circuit. Fig. 4 shows an example circuit configuration of a submodule. Fig. 5 is a perspective view schematically showing a physical appearance of the submodule. Fig. 6 is a circuit diagram showing an example configuration of a high potential-side arm circuit. Fig. 7 is a perspective view schematically showing a physical appearance of the arm circuit. Fig. 8 is a diagram for illustrating connection between the submodules forming the arm circuit. Fig. 9 is a diagram in which arrangement of the submodules shown in Fig. 8 is replaced with arrangement of half bridge-type converter cells and full bridge-type converter cells. Fig. 10 is an appearance diagram schematically showing mutual connection among submodules 40_3 to 40_6 in Fig. 8. Fig. 11 is an appearance diagram schematically showing mutual connection among submodules 40_11 to 40_14 in Fig. 8. DESCRIPTION OF EMBODIMENTS Each embodiment will be described in detail hereinafter with reference to the drawings. The same or corresponding portions are denoted by the same reference characters and description thereof will not be repeated. First Embodiment [Schematic Configuration of Power Conversion Device] Fig. 1 is a schematic configuration diagram showing an example power conversion device. Referring to Fig. 1, the power conversion device includes leg circuits 4u, 4v and 4w (which are denoted as a leg circuit 4 when they are collectively referred to or an unspecified one is referred to) serving as main circuits, and a central controller 3 configured to control leg circuit 4. Leg circuit 4 is provided for each of a plurality of phases forming an alternating current. Leg circuit 4 is connected between an AC circuit 20 and a DC circuit 21, and performs power conversion between these circuits. Fig. 1 shows the case in which AC circuit 20 is a three-phase AC circuit, and three leg circuits 4u, 4v and 4w are provided to correspond to a U phase, a V phase and a W phase, respectively. AC nodes Nu, Nv and Nw provided in leg circuits 4u, 4v and 4w, respectively, are connected to AC circuit 20 with an interconnection transformer 22 being interposed. AC circuit 20 is, for example, an AC power system including an AC power supply and the like. For ease of illustration, Fig. 1 does not show connection of AC nodes Nv and Nw to interconnection transformer 22. DC nodes Np and Nn (i.e., high potential-side DC node Np and low potential-side DC node Nn) provided in common for each leg circuit 4 are connected to DC circuit 21. DC circuit 21 corresponds to a connection wiring to a DC power system in a high-voltage direct-current (HVDC) system or another power conversion device in a BTB (Back To Back) system. The HVDC system is configured to convert high-voltage AC power to DC power and perform DC long-distance power transmission. Power conversion device 1 in Fig. 1 is used for this AC/DC conversion. The BTB system is configured to perform forward conversion for converting AC to DC and reverse conversion for converting DC to AC, thereby implementing power interchange between two AC circuits. Power conversion device 1 in Fig. 1 is used for the forward conversion and the reverse conversion. Instead of using interconnection transformer 22 in Fig. 1, AC nodes Nu, Nv and Nw may be connected to AC circuit 20 with an interconnection reactor being interposed. In addition, as shown in Figs. 2 and 3, AC circuit 20 and each leg circuit 4 may be connected in an AC manner. A detailed configuration of a connection portion connecting AC circuit 20 and each leg circuit 4 in this case will be described below. Leg circuit 4u is separated into a high potential-side arm circuit (also referred to as "upper arm circuit" or "primary arm circuit") 10 extending from high potential-side DC node Np to AC node Nu, and a low potential-side arm circuit (also referred to as "lower arm circuit" or "secondary arm circuit") 11 extending from low potential-side DC node Nn to AC node Nu. A connection point Nu connecting high potential-side arm circuit 10 and low potential-side arm circuit 11 is connected to transformer 22. High potential-side DC node Np and low potential-side DC node Nn are connected to DC circuit 21. Leg circuits 4v and 4w have a similar configuration, and thus, leg circuit 4u will be described below as a typical example. High potential-side arm circuit 10 includes a plurality of half bridge (HB)-type converter cells 5, one or more full bridge (FB)-type converter cells 6, and a reactor 7a. The plurality of converter cells 5, at least one converter cell 6 and reactor 7a are connected in series to each other. Hereinafter, for ease of description, the converter cell may be simply referred to as "cell". Half bridge-type converter cells 5 and one or more full bridge-type converter cells 6 may be connected in any order. Similarly, low potential-side arm circuit 11 includes a plurality of half bridge-type converter cells 5, one or more full bridge-type converter cells 6, and a reactor 7b. The plurality of converter cells 5, at least one converter cell 6 and reactor 7b are connected in series to each other. Half bridge-type converter cells 5 and one or more full bridge-type converter cells 6 may be connected in any order. Reactors 7a and 7b are provided such that arm currents Ipu and Ipn do not rapidly change at the moment when the cells in each leg circuit are turned on or off and an output voltage rapidly changes or when AC circuit 20, DC circuit 21 or the like fails. A position where reactor 7a is inserted may be any position in high potential-side arm circuit 10 of leg circuit 4u, and a position where reactor 7b is inserted may be any position in low potential-side arm circuit 11 of leg circuit 4u. A plurality of reactors 7a may be provided and a plurality of reactors 7b may be provided. The reactors may be different from each other in inductance value. Furthermore, only reactor 7a of high potential-side arm circuit 10 or only reactor 7b of low potential-side arm circuit 11 may be provided. As detectors configured to measure an amount of electricity (i.e., a current and a voltage) used for control, power conversion device 1 in Fig. 1 further includes an AC voltage detector 23, an AC current detector 24, DC voltage detectors 25p and 25n, and arm current detectors 9a and 9b provided in each leg circuit 4. Signals detected by these detectors are input to central controller 3. Specifically, AC voltage detector 23 detects a voltage value Vacu of the U phase of AC circuit 20, a voltage value Vacv of the V phase of AC circuit 20, and a voltage value Vacw of the W phase of AC circuit 20. AC current detector 24 detects a current value Iacu of the U phase of AC circuit 20, a current value Iacv of the V phase of AC circuit 20, and a current value Iacw of the W phase of AC circuit 20. DC voltage detector 25p detects a voltage of high potential-side DC node Np connected to DC circuit 21. DC voltage detector 25n detects a voltage of low potential-side DC node Nn connected to DC circuit 21. In addition, arm current detectors 9a and 9b provided in leg circuit 4u for the U phase detect arm current Ipu flowing through high potential-side arm circuit 10 and arm current Inu flowing through low potential-side arm circuit 11, respectively. Similarly, arm current detectors 9a and 9b provided in leg circuit 4v for the V phase detect a high potential-side arm current Ipv and a low potential-side arm current Inv, respectively. Arm current detectors 9a and 9b provided in leg circuit 4w for the W phase detect a high potential-side arm current Ipw and a low potential-side arm current Inw, respectively. Based on these arm currents, a DC current Idc flowing through DC circuit 21 and a circulating current circulating among the leg circuits can be calculated. The signals detected by the above-described detectors are input to central controller 3. Central controller 3 further receives, from each cell 5, 6, a signal indicating a detection value of a cell capacitor voltage. Based on the signals detected by the above-described detectors and the information about the cell capacitor voltages, central controller 3 outputs, to each cell 5, 6, a control instruction for controlling an operation state of each cell 5, 6 and an operation/stop instruction (an operation instruction or a stop instruction) for protecting each cell 5, 6. For ease of illustration, Fig. 1 collectively shows a part of signal lines for the signals input from the detectors to central controller 3 and a part of signal lines for the signals transmitted between central controller 3 and cells 5. Actually, however, the signal line is individually provided for each detector and for each cell 5, 6. A signal line for transmission and a signal line for reception may be separately provided between each cell 5, 6 and central controller 3. In the case of the present embodiment, these signal lines are formed of optical fibers from the viewpoint of noise resistance. Central controller 3 is formed by a circuit and can be formed by, for example, at least one microcomputer, or at least one ASIC (Application Specific Integrated Circuit), or at least one FPGA (Field Programmable Gate Array). Alternatively, central controller 3 may be formed by combining any of the foregoing. The microcomputer includes at least one processor (e.g., a CPU (Central Processing Unit)). The processor can execute all or a part of functions of central controller 3 by reading one or more commands from at least one computer-readable non-transitory storage medium (such as, for example, a magnetic medium such as a hard disk, an optical medium such as a CD (Compact Disk) and a DVD (Digital Video Disk), and a semiconductor memory). [Modification of Connection Portion Connecting AC Circuit and Each Leg Circuit] Fig. 1 shows an example in which AC circuit 20 and a power conversion circuit portion 2 are connected in a DC manner through AC nodes Nu, Nv and Nw provided in leg circuits 4u, 4v and 4w, respectively. Instead of this, AC circuit 20 and each leg circuit 4 may be connected in an AC manner with a transformer being interposed. Some specific examples will be described below with reference to Figs. 2 and 3.
[ZH CN111224574B]: 一种多电平变换系统 [EN CN111224574B]: A multi-level conversion system | [ZH CN111224574B]: 本发明提出一种多电平变换系统，包括：直流电源VH、第一电容器C1和第二电容器C2、i个T型三电平电路、DC/DC变换器、i个第三电容器C3及i个开关电容多电平电路；第一电容器C1的负极与直流电源VH的负极相连，第二电容器C2的正极与直流电源VH的正极相连，第一电容器C1的正极与第二电容器C2的负极相连于中性点N；DC/DC变换器的输入端连接直流电源VH,i个第三电容器C3中的任意一个均并联在DC/DC变换器的输出端，第k个开关电容多电平电路与第k个第三电容器C3并联连接，本发明提出的多电平变换系统，结构简单且输入电源的需求数量少。 [EN CN111224574B]: The invention provides a multi-level conversion system, which comprises a direct-current power supply VH, a first capacitor C1, a second capacitor C2, i T-shaped three-level circuits, a DC/DC converter, i third capacitors C3 and i switched capacitor multi-level circuits, wherein the negative electrode of the first capacitor C1 is connected with the negative electrode of the direct-current power supply VH, the positive electrode of the second capacitor C2 is connected with the positive electrode of the direct-current power supply VH, and the positive electrode of the first capacitor C1 and thenegative electrode of the second capacitor C2 are connected to a neutral point N; and the input end of the DC/DC converter is connected with the direct-current power supply VH, any one of the i thirdcapacitors C3 is connected to the output end of the DC/DC converter in parallel, and the kth switched capacitor multi-level circuit is connected with the kth third capacitor C3 in parallel. The multi-level conversion system provided by the invention is simple in structure and requires a small number of input power supplies. | CN111224574B | 2020-06-02 2021-08-03 | CN202010091038A | 2020-02-13 2020-02-13 | CN202010091038A, 2020-02-13 CN202010091038A, 2020-02-13 | CN111224574B: 2021-08-03 | UNIV GUANGDONG TECHNOLOGY 广东工业大学 | YE YUANMAO WANG XIAOLIN YI YONG | H02M7/483: I | H02M7/483: I H02M7/4835: I | CN101667775A CN102882411A CN102882412A US2013301314A1 JP2015035902A CN107769600A CN108521232A CN109787291A JP2015035869A |  | [ZH CN111224574B]: 1 .一种多电平变换系统，其特征在于，包括:直流电源VH、用于将直流电源VH的输出电压 均分的第一电容器”和第二电容器C2、i个用于电平变换的T型三电平电路1、DC/DC变换器、i 个用于滤波的第三电容器C3及i个开关电容多电平电路;第一电容器”的负极与直流电源VH 的负极相连，第二电容器C2的正极与直流电源VH的正极相连，第一电容器”的正极与第二电 容器C2的负极相连于中性点N；DC/DC变换器的输入端连接直流电源VH,i个第三电容器C3中 的任意一个均并联在DC/DC变换器的输出端，第k个开关电容多电平电路与第k个第三电容 器C3并联连接;任意一个T型三电平电路1的第一输入端a连接直流电源VH的负极，第二输入 端b连接中性点N,第三输入端c连接直流电源VH的正极，第k个T型三电平电路1的输出端d连 接第k个开关电容多电平电路的第一输出端e,i表示正整数，k取1〜i之间的正整数； 所述DC/DC变换器将所述直流电源VH的输出电压Vh转换成直流电压VL,开关电容多电平 电路将DC/DC变换器的输出直流电压VL转换成0、土 VL、±2VL五种或0、土 VL、士2VL、±3VL七种 交流电压,T型三电平电路1将直流电源VH的输出电压Vh转换成±0.5Vh、0三种交流电压；当 直流电源VH的输出电压Vh与所述DC/DC变换器的输出电压VL之比不同时，所述多电平变换系 统输出的交流电压的种类不同;控制直流电源VH的输出电压Vh与所述DC/DC变换器的输出电 压VL之比，能实现多电平变换系统输出的交流电压： 当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 6:1时，所述多电平变 换系统输出0、土Vl、士2Vl、±3Vl、±4V/D±5Vl4^一种交流电压； 当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 8:1时，所述多电平变 换系统输出输出0、土VL、± 2VL、±3VL、±4Vl、±5VL、±6VL和±7VL十五种交流电压； 当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL=10:1时，所述多电平变 换系统输出0、土丫「士2丫「±3丫「±4丫「±5丫「±6丫「±7丫1和士8丫1十七种交流电压； 当直流电源电压VH与所述DC/DC变换器的输出电压VL之比VH：VL=12:1时，所述多电平变 换系统输出0、土丫「士2丫「±3丫「±4丫「±5丫「±6丫「±7丫「±8丫1和士9丫1十九种交流电压； 当直流电源电压VH与所述DC/DC变换器的输出电压VL之比Vh:Vl=14:1时，所述多电平变 换系统输出0、土 VL、± 2VL、± 3VL、± 4Vl、± 5VL、± 6VL、± 7VL、± 8VL、± 9VL和 ± 10VL二十-一种 交流电压。 2 .根据权利要求1所述的多电平变换系统，其特征在于，所述多电平变换系统还包括为 所述T型三电平电路1和开关电容多电平电路提供控制信号的控制器、驱动器;T型三电平电 路1和开关电容多电平电路中均包括若干个全控开关管，驱动器连接控制器，将控制器产生 的控制信号转换成驱动T型三电平电路1和开关电容多电平电路中全控开关管导通或关断 的驱动信号。 3 .根据权利要求2所述的多电平变换系统，其特征在于，所述T型三电平电路1包括第一 全控开关管S1、第二全控开关管S2、第三全控开关管S3和第四全控开关管S4；所述第一全控 开关管S1的第一端为T型三电平电路1的第一输入端a,第二全控开关管S2的第二端为T型三 电平电路1的第二输入端b,所述第一全控开关管S1的第二端分别与所述第二全控开关管S2 的第一端、所述第三全控开关管S3的第二端连接，连接点为所述T型三电平电路1的输出端 d,所述第三全控开关管S3的第一端与所述第四全控开关管S4的第一端相连，所述第四全控 开关S4的第二端为所述T型三电平电路1的第三输入端c。 4 .根据权利要求2所述的多电平变换系统，其特征在于，所述开关电容多电平电路包括 第五全控开关管S5、第六全控开关管S6、第七全控开关管S7、第八全控开关管S8、第九全控 开关管S9、第十全控开关管S10、第一二极管D3和第四电容器C4；所述第五全控开关管S5的 第一端分别与所述第七全控开关管S7的第一端、第九全控开关管S9的第一端相连，连接点 为开关电容多电平电路的第一输入端f，所述第五全控开关管S5的第二端分别连接所述第 四电容器C4的负极及所述第六全控开关管S6的第一端，所述第六全控开关管S6的第二端与 所述第一二极管D3的阳极相连并作为所述开关电容多电平电路的第二输入端g，所述第一 二极管D3的阴极分别连接第四电容器C4的正极、第八全控开关管S8的第二端及第十全控开 关管S10的第二端，所述第八全控开关管S8的第一端和所述第七全控开关管S7的第二端相 连，并作为所述开关电容多电平电路的第一输出端e，所述第十全控开关管S10的第一端和 所述第九全控开关管S9的第二端相连，并作为所述开关电容多电平电路的第二输出端h。 5 .根据权利要求4所述的多电平变换系统，其特征在于，所述开关电容多电平电路还包 括第十一全控开关管S11、第十二全控开关管S12、第二二极管D4和第五电容器C5,所述第十 一全控开关管S11的第一端分别连接所述第五全控开关S5的第一端及所述第二二极管D4的 阴极，所述第二二极管D4的阳极分别与第七全控开关管S7的第一端、所述第九全控开关管 S9的第一端、所述第五电容器C5的负极相连，所述第五电容器C5的正极分别与所述第十一 全控开关管S11的第二端和所述第十二全控开关管S12的第一端连接，所述第十二全控开关 管S12的第二端分别与所述第六全控开关管S6的第二端、第一二极管D3的阳极相连。 6 .根据权利要求5所述的多电平变换系统，其特征在于，所述第一二极管D3及第二二极 管D4中的任意一个均能用全控开关管替代。 7 .根据权利要求2所述的多电平变换系统，其特征在于，所述全控开关管为N沟道电力 场效应晶体管、P沟道电力场效应晶体管或绝缘栅双极型晶体管中的一种或任意组合。 [EN CN111224574B]: 1 A multi-level conversion system, characterized in that it comprises: DC power supply VH, Used to connect the DC power supply VHThe output voltage is divided equally between the first capacitor" and the second capacitor C2, I T-type three-level circuits for level conversion 1, DC/DC converter, i third capacitors C for filtering3And i switched capacitor multilevel circuits; the negative pole of the first capacitor is connected to the DC power supply VH Is connected to the negative pole, the second capacitor C2Positive pole and DC power supply VHThe positive pole of the first capacitor is connected to the positive pole of the second capacitor C2The negative pole of is connected to the neutral point N; the input end of the DC/DC converter is connected to the DC power supply VH,i third capacitor C3Any one of them is connected in parallel with the output end of the DC/DC converter, the k-th switched capacitor multilevel circuit and the k-th third capacitor C3Parallel connection; the first input terminal a of any T-type three-level circuit 1 is connected to the DC power supply VHThe second input terminal b is connected to the neutral point N, and the third input terminal c is connected to the DC power supply VHThe output terminal d of the k-th T-type three-level circuit 1 is connected to the first output terminal e of the k-th switched capacitor multilevel circuit, where i represents a positive integer, and k takes a positive integer between 1~i; The DC/DC converter converts the DC power supply VHThe output voltage VhConverted into DC voltage VL, The switched capacitor multilevel circuit converts the output DC voltage V of the DC/DC converterLConvert to 0, soil VL, ±2VLFive kinds or 0, soil VL, ± 2VL, ±3VLSeven kinds of AC voltage, T-type three-level circuit 1 will DC power supply VHThe output voltage VhConvert to ±0.5Vh, 0 three kinds of AC voltage; when the DC power supply VHThe output voltage VhAnd the output voltage V of the DC/DC converterLWhen the ratio is different, the types of AC voltage output by the multi-level conversion system are different; control the DC power supply VHThe output voltage VhAnd the output voltage V of the DC/DC converterLRatio, the AC voltage output by the multi-level conversion system can be realized: When the DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL = 6:1, the multi-level conversion system outputs 0, ±Vl, ± 2Vl, ±3Vl, ±4V/D±5Vl4^An AC voltage; when the DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL = 8:1, the output of the multi-level conversion system is 0, ±VL, ± 2VL, ±3VL, ±4Vl, ±5VL, ±6VLAnd ±7VLFifteen kinds of AC voltage; when DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL=10:1, the multi-level conversion system outputs 0, Tuya, ±2, ±3, ±4, ±5, ±6, ±7, 1 and ±8, 17. Kind of AC voltage; when the DC power supply voltage VHAnd the output voltage V of the DC/DC converterLRatio VH: VL=12:1, the multi-level conversion system outputs 0, Tuya, ±2, ±3, ±4, ±5, ±6, ±7, ±8, 1 and ±9 Y1 Nineteen AC voltages; when the DC power supply voltage VHAnd the output voltage V of the DC/DC converterLRatio Vh:Vl=14:1, the multi-level conversion system outputs 0, ± VL, ± 2VL, ± 3VL, ± 4Vl, ± 5VL, ± 6VL, ± 7VL, ± 8VL, ± 9VLAnd ± 10VLTwenty-one AC voltage. 2 The multi-level conversion system according to claim 1, wherein the multi-level conversion system further comprises a controller that provides control signals for the T-type three-level circuit 1 and the switched capacitor multi-level circuit , Driver; T-type three-level circuit 1 and switched capacitor multi-level circuit include several fully-controlled switch tubes, the driver is connected to the controller, the control signal generated by the controller is converted to drive the T-type three-level circuit 1 and The driving signal for the turn-on or turn-off of the fully-controlled switch in the switched-capacitor multi-level circuit. 3 The multi-level conversion system according to claim 2, wherein the T-type three-level circuit 1 includes a first fully-controlled switching tube S1, a second fully-controlled switching tube S2, and a third fully-controlled switching tube S3 and the fourth full control switch S4; the first end of the first full control switch S1 is the first input terminal a of the T-type three-level circuit 1, and the second end of the second full control switch S2 is The second input terminal b of the T-type three-level circuit 1, the second terminal of the first full control switch S1 and the first terminal of the second full control switch S2 and the third full control switch respectively The second terminal of the tube S3 is connected, the connection point is the output terminal d of the T-type three-level circuit 1, the first terminal of the third fully-controlled switch tube S3 and the first terminal of the fourth fully-controlled switch tube S4 One end is connected, and the second end of the fourth full control switch S4 is the third input terminal c of the T-type three-level circuit 1. 4 The multilevel conversion system according to claim 2, wherein the switched capacitor multilevel circuit comprises Fifth full control switch S5, sixth full control switch S6, seventh full control switch S7, eighth full control switch S8, ninth full control switch S9, tenth full control switch S10, first The diode D3 and the fourth capacitor C4; the first end of the fifth full control switch S5 is connected to the first end of the seventh full control switch S7 and the first end of the ninth full control switch S9, respectively The connection point is the first input terminal f of the switched capacitor multilevel circuit, and the second terminal of the fifth full-control switch S5 is respectively connected to the negative electrode of the fourth capacitor C4 and the sixth full-control switch The first terminal of S6, the second terminal of the sixth full-control switch S6 is connected to the anode of the first diode D3 and serves as the second input terminal g of the switched capacitor multilevel circuit. The cathode of the first diode D3 is respectively connected to the anode of the fourth capacitor C4, the second end of the eighth full control switch S8, and the second end of the tenth full control switch S10. The eighth full control switch S8 The first terminal of is connected to the second terminal of the seventh full-control switch S7, and serves as the first output terminal e of the switched capacitor multilevel circuit, and the first terminal of the tenth full-control switch S10 It is connected to the second terminal of the ninth fully-controlled switch S9 and serves as the second output terminal h of the switched capacitor multilevel circuit. 5 The multi-level conversion system according to claim 4, wherein the switched capacitor multi-level circuit further comprises an eleventh fully-controlled switching tube S11, a twelfth fully-controlled switching tube S12, and a second diode Tube D4 and the fifth capacitor C5, the first terminal of the eleventh fully-controlled switch tube S11 is respectively connected to the first terminal of the fifth fully-controlled switch S5 and the cathode of the second diode D4, the The anode of the second diode D4 is respectively connected to the first end of the seventh full control switch S7, the first end of the ninth full control switch S9, and the cathode of the fifth capacitor C5, and the fifth The positive electrode of the capacitor C5 is respectively connected to the second end of the eleventh full control switch S11 and the first end of the twelfth full control switch S12, and the second end of the twelfth full control switch S12 The terminals are respectively connected to the second terminal of the sixth full control switch S6 and the anode of the first diode D3. 6 The multi-level conversion system according to claim 5, wherein any one of the first diode D3 and the second diode D4 can be replaced by a fully controlled switch. 7 The multi-level conversion system according to claim 2, wherein the fully-controlled switch is one of an N-channel power field effect transistor, a P-channel power field effect transistor, or an insulated gate bipolar transistor. Kind or any combination. | [ZH CN111224574B]: 一种多电平变换系统 技术领域 [0001]本发明涉及电力电子功率变换的技术领域，更具体地，涉及一种多电平变换系统。 背景技术 [0002] 随着石油、煤炭等化石能源的日益枯竭，能源危机和能源污染步步逼近，获取新型 能源已经变得十分迫切，以风能和太阳能为代表的分布式发电技术以及以电池和超级电容 为代表的分布式储能技术越来越受到世界各国的高度重视，这些新兴能源和新技术的发展 和应用高度依赖于电力电子逆变装置的性能。 [0003]然而，传统的两电平逆变电路具有谐波含量高和效率低等缺陷。近年来，随着电力 电子技术的高速发展，多电平逆变电路系统备受关注，其优点包括输出电压谐波含量少、器 件电压应力低、电磁干扰少和效率较高等。典型的多电平逆变电路包括二极管钳位型、电容 钳位型和H桥级联型。其中电容钳位型和电容钳位型多电平逆变电路在输出电平数较多时 所需钳位器件非常多、电路非常复杂，而H桥级联型多电平逆变电路需要多个独立的直流电 源。 [0004]综上所述，如何设计出电路结构简单、输出电平数多和输入电源数量少的多电平 逆变电路是有待解决的问题。 发明内容 [0005]为克服现有多电平逆变电路系统的结构复杂，且具有输入电源数量多的弊端，本 发明提出一种多电平变换系统，基于开关电容和T型电路，结构简单且输入电源的需求数量 少。 [0006]本发明旨在至少在一定程度上解决上述技术问题。 [0007]为了达到上述技术效果，本发明的技术方案如下： [0008] 一种多电平变换系统，包括:直流电源VH、用于将直流电源VH输出电压均分的第一 电容器”和第二电容器C2、i个用于电平变换的T型三电平电路1、DC/DC变换器、i个用于滤波 的第三电容器c3及i个开关电容多电平电路;第一电容器q的负极与直流电源vh的负极相 连，第二电容器C2的正极与直流电源vh的正极相连，第一电容器”的正极与第二电容器分的 负极相连于中性点N；DC/DC变换器的输入端连接直流电源VH,i个第三电容器C3中的任意一 个均并联在DC/DC变换器的输出端，第k个开关电容多电平电路与第k个第三电容器C3并联 连接;任意一个T型三电平电路1的第一输入端a连接直流电源VH的负极，第二输入端b连接 中性点N,第三输入端c连接直流电源VH的正极，第k个T型三电平电路1的输出端d连接第k个 开关电容多电平电路的第一输出端e,i表示正整数，k取1〜i之间的正整数。 [0009] 在此,T型三电平电路1将第一电容器C1和第二电容器C2的电压转换成三电平交流 电压，DC/DC变换器将直流电源VH输出的直流电压转换成另一种幅值的直流电压，开关电容 多电平电路将DC/DC变换器输出的直流电压转换成多电平交流电压。 [0010] 优选地，所述多电平变换系统还包括为所述T型三电平电路1和开关电容多电平电 路提供控制信号的控制器、驱动器;T型三电平电路1和开关电容多电平电路中均包括若干 个全控开关管，驱动器连接控制器，将控制器产生的控制信号转换成驱动T型三电平电路1 和开关电容多电平电路中全控开关管导通或关断的驱动信号。 [0011] 在此，利用驱动器与控制器的配合，将控制器发出的控制信号转换成驱动T型三电 平电路1和开关电容多电平电路中全控开关管导通或关断的驱动信号，属于现有比较成熟 的技术，现有多种型号的驱动器均可实现。 [0012] 优选地，所述T型三电平电路1包括第一全控开关管S1、第二全控开关管S2、第三全 控开关管S3和第四全控开关管S4；所述第一全控开关管S1的第一端为T型三电平电路1的第 一输入端a，第二全控开关管S2的第二端为T型三电平电路1的第二输入端b，所述第一全控 开关管S1的第二端分别与所述第二全控开关管S2的第一端、所述第三全控开关管S3的第二 端连接，连接点为所述T型三电平电路1的输出端d，所述第三全控开关管S3的第一端与所述 第四全控开关管S4的第一端相连，所述第四全控开关S4的第二端为所述T型三电平电路1的 第三输入端c。 [0013]优选地，所述开关电容多电平电路包括第五全控开关管S5、第六全控开关管S6、第 七全控开关管S7、第八全控开关管S8、第九全控开关管S9、第十全控开关管S10、第一二极管 D3和第四电容器C4；所述第五全控开关管S5的第一端分别与所述第七全控开关管S7的第一 端、第九全控开关管S9的第一端相连，连接点为开关电容多电平电路的第一输入端f，所述 第五全控开关管S5的第二端分别连接所述第四电容器C4的负极及所述第六全控开关管S6 的第一端,所述第六全控开关管S6的第二端与所述第一二极管D3的阳极相连并作为所述开 关电容多电平电路的第二输入端g，所述第一二极管D3的阴极分别连接第四电容器C4的正 极、第八全控开关管S8的第二端及第十全控开关管S10的第二端,所述第八全控开关管S8的 第一端和所述第七全控开关管S7的第二端相连，并作为所述开关电容多电平电路的第一输 出端e，所述第十全控开关管S10的第一端和所述第九全控开关管S9的第二端相连，并作为 所述开关电容多电平电路的第二输出端h。 [0014]优选地，所述开关电容多电平电路还包括第十一全控开关管S11、第十二全控开关 管S12、第二二极管D4和第五电容器C5,所述第十一全控开关管S11的第一端分别连接所述 第五全控开关S5的第一端及所述第二二极管D4的阴极，所述第二二极管D4的阳极分别与第 七全控开关管S7的第一端、所述第九全控开关管S9的第一端、所述第五电容器C5的负极相 连，所述第五电容器C5的正极分别与所述第十一全控开关管S11的第二端和所述第十二全 控开关管S12的第一端连接，所述第十二全控开关管S12的第一端分别与所述第六全控开关 管S6的第二端、第二二极管D4的阳极相连。 [0015]优选地，所述第一二极管D3及第二二极管D4中的任意一个均能用全控开关管替 代。 [0016]优选地，所述全控开关管为N沟道电力场效应晶体管、P沟道电力场效应晶体管或 绝缘栅双极型晶体管中的一种或任意组合。 [0017]在此，当全控开关管为N沟道电力场效应晶体管时，N沟道电力场效应晶体管的栅 极作为全控开关管的控制端，N沟道电力场效应晶体管的源极作为全控开关管的第一端，N 沟道电力场效应晶体管的漏极作为全控开关管的第二端；当全控开关管为P沟道电力场效 应晶体管时，P沟道电力场效应晶体管的栅极作为全控开关管的控制端，P沟道电力场效应 晶体管的漏极作为全控开关管的第一端，P沟道电力场效应晶体管的源极作为全控开关的 第二端；当全控开关管为绝缘栅双极型晶体管时，绝缘栅双极型晶体管的门极作为全控开 关管的控制端，绝缘栅双极型晶体管的发射极作为全控开关管的第一端，绝缘栅双极型晶 体管的集电极作为全控开关管的第二端。 [0018] 优选地，所述DC/DC变换器将所述直流电源VH的输出电压Vh转换成直流电压VL，开 关电容多电平电路将DC/DC变换器的输出直流电压VL转换成0、土VL、±2VL五种或0、土VL、± 2VL、±3VL七种交流电压，T型三电平电路1将直流电源VH的输出电压Vh转换成±0.5Vh、0三种 交流电压；当直流电源VH的输出电压Vh与所述DC/DC变换器的输出电压VL之比不同时，所述 多电平变换系统输出的交流电压的种类不同。 [0019] 在此，控制直流电源VH的输出电压Vh与所述DC/DC变换器的输出电压VL之比，可以 实现多电平变换系统输出的交流电压： [0020]当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 6:1时，所述多电 平变换系统输出0、土VL、± 2VL、±3VL、±4VL和±5VJ^一种交流电压； [0021]当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 8:1时，所述多电 平变换系统输出输出0、土 VL、± 2VL、±3VL、±4VL、±5VL、±6VL和±7VL十五种交流电压； [0022]当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL=10:1时，所述多电 平变换系统输出0、土 VL、士 2VL、± 3VL、± 4VL、± 5VL、± 6VL、± 7VL和± 8VL十七种交流电压； [0023]当直流电源电压VH与所述DC/DC变换器的输出电压VL之比VH：VL = 12:1时，所述多 电平功率变换系统输出0、土丫「士2丫「±3丫「±4丫「±5丫「±6丫「±7丫「±8丫1和士9丫1十九 种交流电压； [0024] 当直流电源电压VH与所述DC/DC变换器的输出电压VL之比VH:VL = 14:1时，所述多 电平功率变换系统输出0、土Vl、士2Vl、±3Vl、±4Vl、±5Vl、±6Vl、±7Vl、±8Vl、±9V/D± 10VL二十^一种交流电压。 [0025]与现有技术相比，本发明技术方案的有益效果是： [0026]本发明提出一种多电平变换系统，利用T型三电平电路、开关电容多电平电路进行 多电平变换，与现有采用电容钳位型和电容钳位型多电平逆变电路的多电平变换系统相 比，结构简单，可实现多电平的输出，且仅需一个输入直流电源，避免了现有多电平变换系 统所需电源数量多的弊端。 附图说明 [0027]图1为本发明提出的多电平变换系统三相输出的电路结构示意图。 [0028]图2为本发明提出的多电平变换系统单相输出的电路结构示意图。 [0029]图3为本发明提出的开关电容多电平电路的一种具体电路示意图。 [0030]图4为本发明提出的开关电容多电平电路的第二种具体电路示意图。 [0031]图5为本发明提出利用全控开关管S13替代第一二极管D3的开关电容多电平电路 示意图。 [0032]图6为本发明提出利用全控开关管S14替代第二二极管D4的开关电容多电平电路 示意图。 具体实施方式 [0033]附图仅用于示例性说明，不能理解为对本专利的限制； [0034]为了更好说明本实施例，附图某些部件会有省略、放大或缩小，并不代表实际产品 的尺寸； [0035]对于本领域技术人员来说，附图中某些公知结构及其说明可能省略是可以理解 的。 [0036]下面结合附图和实施例对本发明的技术方案做进一步的说明。 [0037] 实施例1 [0038]如图1所示的多电平变换系统的三相输出的电路结构示意图，包括:直流电源VH、 用于将直流电源vh输出电压均分的第一电容器q和第二电容器c2、3个用于电平变换的t型 三电平电路1、DC/DC变换器、3个用于滤波的第三电容器C3及3个开关电容多电平电路，T型 三电平电路1将第一电容器C1和第二电容器C2的电压转换成三电平交流电压，DC/DC变换器 将直流电源VH输出的直流电压转换成另一种幅值的直流电压，开关电容多电平电路将DC/ DC变换器输出的直流电压转换成多电平交流电压，多电平变换系统还包括为T型三电平电 路1和开关电容多电平电路提供控制信号的控制器、驱动器;T型三电平电路1和开关电容多 电平电路中均包括若干个全控开关管，驱动器连接控制器，将控制器产生的控制信号转换 成驱动T型三电平电路1和开关电容多电平电路中全控开关管导通或关断的驱动信号，利用 驱动器与控制器的配合，将控制器发出的控制信号转换成驱动T型三电平电路1和开关电容 多电平电路中全控开关管导通或关断的驱动信号，属于现有比较成熟的技术，现有多种型 号的驱动器均可实现，在本实施例中，驱动器选用的型号为SI8233。 [0039] 参见图1，第一电容器q的负极与直流电源vh的负极相连，第二电容器4的正极与 直流电源VH的正极相连，第一电容器”的正极与第二电容器C2的负极相连于中性点N；DC/DC 变换器的输入端连接直流电源Vh,3个第三电容器C3中的任意一个均并联在DC/DC变换器的 输出端，第一个开关电容多电平电路与第一个第三电容器C3并联连接，第二个开关电容多 电平电路与第二个第三电容器C3并联连接，第三个开关电容多电平电路与第三个第三电容 器C3并联连接;任意一个T型三电平电路1的第一输入端a连接直流电源VH的负极，第二输入 端b连接中性点N，第三输入端c连接直流电源VH的正极，第一个T型三电平电路1的输出端d 连接第一个开关电容多电平电路的第一输出端e，第二个T型三电平电路1的输出端d连接第 二个开关电容多电平电路的第一输出端e，第三个T型三电平电路1的输出端d连接第三个开 关电容多电平电路的第一输出端e,再进一步具体的如图2所示的多电平变换系统的单相输 出的电路结构示意图，在实际实施时，可根据需要进行单相至三相之间的调整。 [0040] 参见图2，T型三电平电路1包括第一全控开关管S1、第二全控开关管S2、第三全控 开关管S3和第四全控开关管S4；所述第一全控开关管S1的第一端为T型三电平电路1的第一 输入端a，第二全控开关管S2的第二端为T型三电平电路1的第二输入端b，所述第一全控开 关管S1的第二端分别与所述第二全控开关管S2的第一端、所述第三全控开关管S3的第二端 连接,连接点为所述T型三电平电路1的输出端d，所述第三全控开关管S3的第一端与所述第 四全控开关管S4的第一端相连，所述第四全控开关S4的第二端为所述T型三电平电路1的第 三输入端c。 [0041]图3表示开关电容多电平电路的一种具体电路，包括第五全控开关管S5、第六全控 开关管S6、第七全控开关管S7、第八全控开关管S8、第九全控开关管S9、第十全控开关管 S10、第一二极管D3和第四电容器C4；所述第五全控开关管S5的第一端分别与所述第七全控 开关管S7的第一端、第九全控开关管S9的第一端相连，连接点为开关电容多电平电路的第 一输入端f，所述第五全控开关管S5的第二端分别连接所述第四电容器C4的负极及所述第 六全控开关管S6的第一端，所述第六全控开关管S6的第二端与所述第一二极管D3的阳极相 连并作为所述开关电容多电平电路的第二输入端g，所述第一二极管D3的阴极分别连接第 四电容器C4的正极、第八全控开关管S8的第二端及第十全控开关管S10的第二端，所述第八 全控开关管S8的第一端和所述第七全控开关管S7的第二端相连，并作为所述开关电容多电 平电路的第一输出端e，所述第十全控开关管S10的第一端和所述第九全控开关管S9的第二 端相连，并作为所述开关电容多电平电路的第二输出端h。 [0042]图4为本发明提出的开关电容多电平电路的第二种具体电路示意图，开关电容多 电平电路还包括第十一全控开关管S11、第十二全控开关管S12、第二二极管D4和第五电容 器C5,所述第十一全控开关管S11的第一端分别连接所述第五全控开关S5的第一端及所述 第二二极管D4的阴极，所述第二二极管D4的阳极分别与第七全控开关管S7的第一端、所述 第九全控开关管S9的第一端、所述第五电容器C5的负极相连，所述第五电容器C5的正极分 别与所述第十一全控开关管S11的第二端和所述第十二全控开关管S12的第一端连接，所述 第十二全控开关管S12的第一端分别与所述第六全控开关管S6的第二端、第二二极管D4的 阳极相连。 [0043]实际实施时，第一二极管D3及第二二极管D4中的任意一个均能用全控开关管替 代。图5表示利用全控开关管S13替代第一二极管D3的开关电容多电平电路示意图，图6表示 利用全控开关管S14替代第二二极管D4的开关电容多电平电路示意图，其中，第一二极管D3 及第二二极管D4分别用第十三全控开关管S13和第十四全控开关管S14代替；其中，第十三 全控开关管S13的第一端与第六全控开关管S6的第二端连接，第十三全控管开关S13的第二 端第四电容器C4的正极连接，第十四全控开关管S14的第一端与第五电容器C5的负极连接， 第十四全控开关管S15的第二端与第十一全控开关S11的第一端连接。 [0044] 在本实施例中，全控开关管为N沟道电力场效应晶体管，N沟道电力场效应晶体管 的栅极作为全控开关管的控制端，N沟道电力场效应晶体管的源极作为全控开关管的第一 端，N沟道电力场效应晶体管的漏极作为全控开关管的第二端。 [0045] DC/DC变换器将直流电源VH的输出电压Vh转换成直流电压VL，开关电容多电平电路 将DC/DC变换器的输出直流电压VL转换成0、土 VL、±2VL五种或0、土 VL、士2VL、±3VL七种交流 电压,T型三电平电路1将直流电源VH的输出电压Vh转换成±0.5Vh、0三种交流电压；当直流 电源VH的输出电压Vh与所述DC/DC变换器的输出电压VL之比不同时，所述多电平变换系统输 出的交流电压的种类不同，当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 6:1时，所述多电平变换系统输出0、土Vl、士2Vl、±3Vl、±4V/D±5Vl4^一种交流电压； [0046]当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL = 8:1时，所述多电 平变换系统输出输出0、土 VL、± 2VL、±3VL、±4VL、±5VL、±6VL和±7VL十五种交流电压； [0047]当直流电源VH的电压Vh与DC/DC变换器的输出电压VL之比Vh：VL=10:1时，所述多电 平变换系统输出0、土 VL、士 2VL、± 3VL、± 4VL、± 5VL、± 6VL、± 7VL和± 8VL十七种交流电压； [0048] 当直流电源电压VH与所述DC/DC变换器的输出电压VL之比VH：VL = 12:1时，所述多 电平功率变换系统输出0、土丫「士2丫「±3丫「士3「±5丫「±6丫「±7丫「±8丫1和士9丫1十九 种交流电压； [0049] 当直流电源电压VH与所述DC/DC变换器的输出电压VL之比VH：VL = 14:1时，所述多 电平功率变换系统输出0、土Vl、士2Vl、±3Vl、±4Vl、±5Vl、±6Vl、±7Vl、±8Vl、±9V/D± 10VL二十^一种交流电压。 [0050]附图中描述位置关系的用于仅用于示例性说明，不能理解为对本专利的限制； [0051]显然，本发明的上述实施例仅仅是为清楚地说明本发明所作的举例，而并非是对 本发明的实施方式的限定。对于所属领域的普通技术人员来说，在上述说明的基础上还可 以做出其它不同形式的变化或变动。这里无需也无法对所有的实施方式予以穷举。凡在本 发明的精神和原则之内所作的任何修改、等同替换和改进等，均应包含在本发明权利要求 的保护范围之内。 [EN CN111224574B]: A multi-level conversion system technical field [0001] The present invention relates to the technical field of power electronic power conversion, and more specifically, to a multi-level conversion system. Background technique [0002] With the increasing depletion of fossil energy such as oil and coal, the energy crisis and energy pollution are approaching, it has become very urgent to obtain new energy sources, such as distributed power generation technologies represented by wind and solar energy, as well as batteries and super capacitors. Distributed energy storage technology represented by more and more countries in the world pays more and more attention. The development and application of these emerging energy and new technologies highly depend on the performance of power electronic inverter devices. [0003] However, the traditional two-level inverter circuit has defects such as high harmonic content and low efficiency. In recent years, with the rapid development of power electronics technology, multi-level inverter circuit systems have attracted much attention. Its advantages include less output voltage harmonic content, low device voltage stress, less electromagnetic interference, and higher efficiency. Typical multi-level inverter circuits include diode clamp type, capacitor clamp type and H-bridge cascade type. Among them, the capacitor clamp type and capacitor clamp type multi-level inverter circuit require a lot of clamp devices and the circuit is very complicated when the number of output levels is large, while the H-bridge cascaded multi-level inverter circuit requires multiple Independent DC power supply. [0004] In summary, how to design a multi-level inverter circuit with a simple circuit structure, a large number of output levels, and a small number of input power sources is a problem to be solved. Summary of the invention [0005] In order to overcome the complex structure of the existing multi-level inverter circuit system and the disadvantages of a large number of input power sources, the present invention proposes a multi-level conversion system, based on switched capacitors and T-type circuits, with simple structure and input The number of power requirements is small. [0006] The present invention aims to solve the above technical problems at least to a certain extent. [0007] In order to achieve the above technical effects, the technical solutions of the present invention are as follows: [0008] A multi-level conversion system includes: a DC power supply VH, Used to connect the DC power supply VHThe first capacitor" and the second capacitor C that divide the output voltage equally2, I T-type three-level circuits for level conversion 1, DC/DC converter, i third capacitors for filtering c3And i switched capacitor multilevel circuits; the negative pole of the first capacitor q and the DC power supply vhIs connected to the negative pole, the second capacitor C2Positive pole and DC power supply vhThe positive pole of the first capacitor is connected to the negative pole of the second capacitor to the neutral point N; the input terminal of the DC/DC converter is connected to the DC power supply VH,i third capacitor C3Any one of them is connected in parallel with the output end of the DC/DC converter, the k-th switched capacitor multilevel circuit and the k-th third capacitor C3Parallel connection; the first input terminal a of any T-type three-level circuit 1 is connected to the DC power supply VHThe second input terminal b is connected to the neutral point N, and the third input terminal c is connected to the DC power supply VHThe output terminal d of the k-th T-type three-level circuit 1 is connected to the first output terminal e of the k-th switched capacitor multilevel circuit, where i represents a positive integer, and k takes a positive integer between 1 and i. [0009] Here, the T-type three-level circuit 1 converts the voltages of the first capacitor C1 and the second capacitor C2 into a three-level AC voltage, and the DC/DC converter converts the DC power supply VHThe output DC voltage is converted into another amplitude DC voltage, and the switched capacitor multi-level circuit converts the DC voltage output by the DC/DC converter into a multi-level AC voltage. [0010] Preferably, the multi-level conversion system further includes the T-type three-level circuit 1 and the switched capacitor multi-level circuit. A controller and driver that provide control signals; both the T-type three-level circuit 1 and the switched capacitor multi-level circuit include several fully-controlled switch tubes, the driver is connected to the controller, and the control signal generated by the controller is converted into a drive T Type three-level circuit 1 and switched-capacitor multi-level circuit with a driving signal for the turn-on or turn-off of the fully controlled switch tube. [0011] Here, the cooperation of the driver and the controller is used to convert the control signal sent by the controller into a driving T-type three-level circuit 1 and a full-control switch in the switched capacitor multi-level circuit to turn on or turn off. The signal belongs to the existing relatively mature technology, which can be realized by various types of drivers. [0012] Preferably, the T-type three-level circuit 1 includes a first full control switch S1, a second full control switch S2, a third full control switch S3, and a fourth full control switch S4; The first terminal of the first full control switch S1 is the first input terminal a of the T-type three-level circuit 1, and the second terminal of the second full control switch S2 is the second input terminal of the T-type three-level circuit 1. b. The second end of the first full control switch S1 is respectively connected to the first end of the second full control switch S2 and the second end of the third full control switch S3, and the connection points are all For the output terminal d of the T-type three-level circuit 1, the first terminal of the third full control switch S3 is connected to the first terminal of the fourth full control switch S4, and the fourth full control switch S4 The second terminal of is the third input terminal c of the T-type three-level circuit 1. [0013] Preferably, the switched capacitor multilevel circuit includes a fifth fully-controlled switch tube S5, a sixth fully-controlled switch tube S6, a seventh fully-controlled switch tube S7, an eighth fully-controlled switch tube S8, and a ninth fully-controlled switch tube. The control switch S9, the tenth full control switch S10, the first diode D3 and the fourth capacitor C4; the first end of the fifth full control switch S5 and the seventh full control switch S7 The first end is connected to the first end of the ninth full control switch S9, the connection point is the first input terminal f of the switched capacitor multilevel circuit, and the second end of the fifth full control switch S5 is respectively connected to the The cathode of the fourth capacitor C4 and the first end of the sixth full control switch S6, the second end of the sixth full control switch S6 is connected to the anode of the first diode D3 and serves as the The second input terminal g of the switched capacitor multilevel circuit, the cathode of the first diode D3 is respectively connected to the anode of the fourth capacitor C4, the second end of the eighth fully-controlled switch tube S8, and the tenth fully-controlled switch tube The second terminal of S10, the first terminal of the eighth fully-controlled switch tube S8 and the second terminal of the seventh fully-controlled switch tube S7 are connected, and serve as the first output terminal of the switched capacitor multilevel circuit e. The first terminal of the tenth full-control switch tube S10 is connected to the second terminal of the ninth full-control switch tube S9, and serves as the second output terminal h of the switched capacitor multilevel circuit. [0014] Preferably, the switched capacitor multilevel circuit further includes an eleventh fully-controlled switching tube S11, a twelfth fully-controlled switching tube S12, a second diode D4, and a fifth capacitor C5, and the tenth The first end of a full control switch S11 is connected to the first end of the fifth full control switch S5 and the cathode of the second diode D4, and the anode of the second diode D4 is connected to the seventh The first terminal of the full control switch S7, the first terminal of the ninth full control switch S9, and the negative electrode of the fifth capacitor C5 are connected, and the positive electrode of the fifth capacitor C5 is connected to the eleventh full The second end of the control switch S11 is connected to the first end of the twelfth full control switch S12, and the first end of the twelfth full control switch S12 is connected to the sixth full control switch S6. The second end of the second diode is connected to the anode of the second diode D4. [0015] Preferably, any one of the first diode D3 and the second diode D4 can be replaced by a fully controlled switch. [0016] Preferably, the full control switch is one or any combination of N-channel power field effect transistors, P-channel power field effect transistors, or insulated gate bipolar transistors. [0017] Here, when the full control switch is an N-channel power field effect transistor, the gate of the N-channel power field effect transistor serves as the control end of the full control switch, and the source of the N-channel power field effect transistor As the first end of the fully-controlled switch, the drain of the N-channel power field effect transistor is used as the second end of the fully-controlled switch; when the fully-controlled switch is a P-channel power field effect transistor, the P-channel power field The gate of the effect transistor is used as the control terminal of the full control switch, and the P-channel power field effect The drain of the transistor is used as the first terminal of the fully controlled switch, and the source of the P-channel power field effect transistor is used as the second terminal of the fully controlled switch; when the fully controlled switch is an insulated gate bipolar transistor, the insulated gate double The gate of the polar transistor is used as the control terminal of the fully controlled switch, the emitter of the insulated gate bipolar transistor is used as the first terminal of the fully controlled switch, and the collector of the insulated gate bipolar transistor is used as the first terminal of the fully controlled switch. Two ends. [0018] Preferably, the DC/DC converter converts the DC power supply VHThe output voltage VhConverted into DC voltage VL, The switched capacitor multilevel circuit converts the output DC voltage V of the DC/DC converterLConvert to 0, soil VL, ±2VLFive kinds or 0, soil VL, ± 2VL, ±3VLSeven kinds of AC voltage, T-type three-level circuit 1 will DC power supply VHThe output voltage VhConvert to ±0.5Vh, 0 three kinds of AC voltage; when the DC power supply VHThe output voltage VhAnd the output voltage V of the DC/DC converterLWhen the ratios are different, the types of AC voltages output by the multi-level conversion system are different. [0019] Here, the DC power supply V is controlledHThe output voltage VhAnd the output voltage V of the DC/DC converterLThe ratio can realize the AC voltage output by the multi-level conversion system: [0020] When the DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL = 6:1, the multi-level conversion system outputs 0, ±VL, ± 2VL, ±3VL, ±4VLAnd ±5VJ^ an AC voltage; [0021] When the DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL = 8:1, the output of the multi-level conversion system is 0, ± VL, ± 2VL, ±3VL, ±4VL, ±5VL, ±6VLAnd ±7VLFifteen AC voltages; [0022] When the DC power supply VHThe voltage VhAnd DC/DC converter output voltage VLRatio Vh: VL=10:1, the multi-level conversion system outputs 0, ± VL, ± 2VL, ± 3VL, ± 4VL, ± 5VL, ± 6VL, ± 7VLAnd ± 8VLSeventeen kinds of AC voltage; [0023] When the DC power supply voltage VHAnd the output voltage V of the DC/DC converterLRatio VH: VL = 12:1, the multi-level power conversion system outputs 0, ±2, ±3, ±4, ±5, ±6, ±7, ±8, 1 and ± 9 Ah 1 Nineteen AC voltages; [0024] When the DC power supply voltage VHAnd the output voltage V of the DC/DC converterLRatio VH:VL = 14:1, the multi-level power conversion system outputs 0, ±Vl, ± 2Vl, ±3Vl, ±4Vl, ±5Vl, ±6Vl, ±7Vl, ±8Vl, ±9V/D± 10VLTwenty-one AC voltages. [0025] Compared with the prior art, the beneficial effects of the technical solution of the present invention are: [0026] The present invention proposes a multi-level conversion system that uses a T-type three-level circuit and a switched capacitor multi-level circuit for multi-level conversion, which is different from the existing capacitor clamp type and capacitor clamp type multilevel Compared with the multi-level conversion system of the inverter circuit, the structure is simple, multi-level output can be realized, and only one input DC power supply is needed, which avoids the disadvantage of the existing multi-level conversion system that requires a large number of power supplies. Description of the drawings [0027] FIG. 1 is a schematic diagram of the circuit structure of the three-phase output of the multi-level conversion system proposed by the present invention. [0028] FIG. 2 is a schematic diagram of the circuit structure of the single-phase output of the multi-level conversion system proposed by the present invention. [0029] FIG. 3 is a schematic diagram of a specific circuit of the switched capacitor multilevel circuit proposed by the present invention. [0030] FIG. 4 is a schematic diagram of a second specific circuit of the switched capacitor multilevel circuit proposed by the present invention. [0031] FIG. 5 is a schematic diagram of a switched capacitor multilevel circuit proposed by the present invention using a fully controlled switch S13 instead of the first diode D3. [0032] FIG. 6 is a schematic diagram of a switched capacitor multilevel circuit proposed by the present invention using a fully controlled switch S14 instead of the second diode D4. Detailed ways [0033] The drawings are only used for exemplary description and cannot be understood as a limitation of the patent; [0034] In order to better illustrate this embodiment, some parts of the drawings may be omitted, enlarged or reduced, and do not represent the size of the actual product; [0035] For those skilled in the art, it is understandable that some well-known structures in the drawings and their descriptions may be omitted. [0036] The technical solution of the present invention will be further described below with reference to the accompanying drawings and embodiments. Example 1 [0038] The circuit structure diagram of the three-phase output of the multi-level conversion system as shown in FIG. 1 includes: a DC power supply VH, Used to connect the DC power supply vhThe first capacitor q and the second capacitor c that divide the output voltage equally2, 3 t-type three-level circuits for level conversion 1, DC/DC converter, 3 third capacitors C for filtering3And three switched capacitor multi-level circuits, the T-type three-level circuit 1 converts the voltages of the first capacitor C1 and the second capacitor C2 into a three-level AC voltage, and the DC/DC converter converts the DC power supply VHThe output DC voltage is converted into another amplitude DC voltage. The switched capacitor multi-level circuit converts the DC voltage output by the DC/DC converter into a multi-level AC voltage. The multi-level conversion system also includes a T-type three The level circuit 1 and the switched capacitor multilevel circuit provide the controller and driver of the control signal; the T-type three-level circuit 1 and the switched capacitor multilevel circuit both include several fully-controlled switch tubes, and the driver is connected to the controller. The control signal generated by the controller is converted into a driving signal for driving the T-type three-level circuit 1 and the fully-controlled switch in the switched capacitor multi-level circuit to turn on or off, and use the cooperation of the driver and the controller to send the signal from the controller. The control signal is converted into a drive signal for driving the T-type three-level circuit 1 and the switch-capacitor multi-level circuit to turn on or off the fully controlled switch. It belongs to the existing relatively mature technology. The existing drivers of various types can be used. To achieve, in this embodiment, the model selected for the driver is SI8233. [0039] Referring to FIG. 1, the negative electrode of the first capacitor q and the DC power source vhThe negative pole of the second capacitor 4 is connected to the DC power supply VHThe positive pole of the first capacitor is connected to the positive pole of the second capacitor C2The negative pole of is connected to the neutral point N; the input end of the DC/DC converter is connected to the DC power supply Vh, 3 third capacitors C3Any one of them is connected in parallel with the output terminal of the DC/DC converter, the first switched capacitor multilevel circuit and the first third capacitor C3Connected in parallel, the second switched capacitor multilevel circuit and the second third capacitor C3Connected in parallel, the third switched capacitor multilevel circuit and the third third capacitor C3Parallel connection; the first input terminal a of any T-type three-level circuit 1 is connected to the DC power supply VHThe second input terminal b is connected to the neutral point N, and the third input terminal c is connected to the DC power supply VHThe output terminal d of the first T-type three-level circuit 1 is connected to the first output terminal e of the first switched capacitor multilevel circuit, and the output terminal d of the second T-type three-level circuit 1 is connected to the first output terminal e of the first switched capacitor multilevel circuit. The first output terminal e of the two switched capacitor multilevel circuits, the output terminal d of the third T-type three-level circuit 1 is connected to the first output terminal e of the third switched capacitor multilevel circuit, and further details The circuit structure diagram of the single-phase output of the multi-level conversion system shown in FIG. 2 can be adjusted from single-phase to three-phase according to actual implementation. [0040] Referring to FIG. 2, the T-type three-level circuit 1 includes a first fully-controlled switching tube S1, a second fully-controlled switching tube S2, a third fully-controlled switching tube S3, and a fourth fully-controlled switching tube S4; The first terminal of a fully-controlled switch tube S1 is the first input terminal a of the T-type three-level circuit 1, and the second terminal of the second fully-controlled switch tube S2 is the second input terminal b of the T-type three-level circuit 1 , The second end of the first full control switch S1 is respectively connected to the first end of the second full control switch S2 and the second end of the third full control switch S3, and the connection point is the At the output terminal d of the T-type three-level circuit 1, the first terminal of the third fully controlled switch S3 is connected to the first terminal of the fourth fully controlled switch S4, and the fourth fully controlled switch S4 The second terminal is the third input terminal c of the T-type three-level circuit 1. [0041] FIG. 3 shows a specific circuit of a switched capacitor multilevel circuit, including a fifth full control switch S5 and a sixth full control Switch S6, seventh full control switch S7, eighth full control switch S8, ninth full control switch S9, tenth full control switch S10, first diode D3 and fourth capacitor C4; The first end of the fifth full control switch S5 is connected to the first end of the seventh full control switch S7 and the first end of the ninth full control switch S9 respectively, and the connection point is the switch capacitor multilevel circuit. The first input terminal f, the second end of the fifth full control switch S5 is connected to the negative electrode of the fourth capacitor C4 and the first end of the sixth full control switch S6, and the sixth full control switch S6 The second terminal of the switch tube S6 is connected to the anode of the first diode D3 and serves as the second input terminal g of the switched capacitor multilevel circuit. The cathodes of the first diode D3 are respectively connected to the fourth The positive electrode of the capacitor C4, the second end of the eighth full control switch S8 and the second end of the tenth full control switch S10, the first end of the eighth full control switch S8 and the seventh full control switch The second terminal of the tube S7 is connected and serves as the first output terminal e of the switched capacitor multilevel circuit. The first terminal of the tenth fully controlled switch S10 and the second terminal of the ninth fully controlled switch S9 The two ends are connected and serve as the second output end h of the switched capacitor multilevel circuit. 4 is a schematic diagram of a second specific circuit of the switched capacitor multilevel circuit proposed by the present invention. The switched capacitor multilevel circuit also includes an eleventh fully controlled switch S11, a twelfth fully controlled switch S12, The second diode D4 and the fifth capacitor C5, the first end of the eleventh full control switch S11 is connected to the first end of the fifth full control switch S5 and the second diode D4 The cathode, the anode of the second diode D4 is respectively connected to the first end of the seventh full control switch S7, the first end of the ninth full control switch S9, and the cathode of the fifth capacitor C5, The positive electrode of the fifth capacitor C5 is respectively connected to the second end of the eleventh fully-controlled switching tube S11 and the first end of the twelfth fully-controlled switching tube S12, and the twelfth fully-controlled switching tube The first end of S12 is respectively connected to the second end of the sixth full control switch S6 and the anode of the second diode D4. [0043] In actual implementation, any one of the first diode D3 and the second diode D4 can be replaced by a fully controlled switch. Figure 5 shows a schematic diagram of a switched capacitor multi-level circuit using a fully-controlled switching tube S13 to replace the first diode D3, and Figure 6 shows a schematic diagram of a switched capacitor multi-level circuit using a fully-controlled switching tube S14 to replace the second diode D4, Among them, the first diode D3 and the second diode D4 are replaced by the thirteenth fully-controlled switching tube S13 and the fourteenth fully-controlled switching tube S14 respectively; among them, the first end of the thirteenth fully-controlled switching tube S13 Connected to the second end of the sixth full control switch S6, and the fourth capacitor C at the second end of the thirteenth full control switch S134Is connected to the positive pole of the fourteenth full control switch S14 and the fifth capacitor C5The negative electrode of the fourteenth full control switch S15 is connected to the first end of the eleventh full control switch S11. [0044] In this embodiment, the full control switch is an N-channel power field effect transistor, the gate of the N-channel power field effect transistor serves as the control end of the full control switch, and the source of the N-channel power field effect transistor The pole is used as the first end of the fully controlled switch, and the drain of the N-channel power field effect transistor is used as the second end of the fully controlled switch. [0045] The DC/DC converter converts the DC power supply VHThe output voltage VhConverted into DC voltage VL, The switched capacitor multilevel circuit converts the output DC voltage V of the DC/DC converterLConvert to 0, soil VL, ±2VLFive kinds or 0, soil VL, ± 2VL, ±3VLSeven kinds of AC voltage, T-type three-level circuit 1 will DC power supply VHThe output voltage VhConvert to ±0.5Vh, 0 three kinds of AC voltage; when the DC power supply VHThe output voltage VhAnd the output voltage V of the DC/DC converterLWhen the ratio is different, the type of AC voltage output by the multi-level conversion system is different. When the DC power supply
[ZH CN109787291B]: 模块化级联多电平变换器及其模块切换方法和控制器 [EN CN109787291B]: Modular cascade multilevel converter and its module switching method and controller | [ZH CN109787291B]: 本发明提供的模块化级联多电平变换器及其模块切换方法和控制器，在功率信息对应于功率效率关系曲线的效率上升区间时，控制模块化级联多电平变换器以满足输出电压要求的最少模块投入模式进行工作，使每个模块以较高的功率工作，将模块化级联多电平变换器的工作点向效率上升的方向移动，进而实现对于该模块化级联多电平变换器转换效率的提高；并在功率信息对应于功率效率关系曲线的效率下降区间时，控制模块化级联多电平变换器以全部模块投入模式进行工作，使每个模块以较低的功率工作，将模块化级联多电平变换器的工作点向与效率下降相反的方向移动，进而实现对于该模块化级联多电平变换器转换效率的提高。 [EN CN109787291B]: The present invention provides a modular cascaded multilevel converter, and a module switching method and a controller thereof. When power information corresponds to an efficiency rise interval of a power efficiency relationship curve, the modular cascaded multilevel converter is controlled to operate in a minimum-module input mode that satisfies output voltage requirements, so that each module isoperated at higher power. An operating point of the modular cascaded multilevel converter is moved to a direction of efficiency increase, thereby realizing the improvement of the conversion efficiency of the modular cascaded multilevel converter. When the power information corresponds to an efficiency decline interval of the power efficiency relationship curve, the modular cascaded multilevel converter is controlled to operate in an all-module input mode, so that each module is operated at lower power. The operating point of the modular cascaded multilevel converter is moved to a direction opposite to efficiency decline, thereby realizing the improvement of the conversion efficiency of the modular cascaded multilevel converter. | CN109787291B | 2019-05-21 2021-06-11 | CN201910232864A | 2019-03-26 2019-03-26 | CN201910232864A, 2019-03-26 CN201910232864A, 2019-03-26 | CN109787291B: 2021-06-11 | SUNGROW POWER SUPPLY CO LTD 阳光电源股份有限公司 | WANG XINYU ZHUANG YUAN ZHUANG FUSHUAI ZHUANG JIACAI XU JUN | H02J3/38: I |  | US2016020628A1 CN106787893A CN107204627A CN107276439A CN107508311A | CN111224574A CN111224574 111224574 WO2021056911A1 WO2021056911 2021/056911 WO2021/056911A1 | [ZH CN109787291B]: 1 .一种模块化级联多电平变换器的模块切换方法，其特征在于，包括： 获取模块化级联多电平变换器的功率信息；其中，所述功率信息为预测功率或者实时 功率，且所述功率信息是所述模块化级联多电平变换器的总功率或者所述模块化级联多电 平变换器各个级联模块或模块组的功率； 根据所述功率信息和所述模块化级联多电平变换器的功率效率关系曲线，进行比较判 断;所述功率效率关系曲线至少包括，工作点位于所述功率效率曲线最高效率点左侧部分 的效率上升区间，以及，工作点位于所述功率效率曲线最高效率点右侧部分的效率下降区 间； 若所述功率信息对应于所述效率上升区间，则控制所述模块化级联多电平变换器以满 足输出电压要求的最少模块投入模式进行工作； 若所述功率信息对应于所述效率下降区间，则控制所述模块化级联多电平变换器以全 部模块投入模式进行工作。 2 .根据权利要求1所述的模块化级联多电平变换器的模块切换方法，其特征在于，获取 模块化级联多电平变换器的功率信息，包括： 在预测周期内，获取未来一个设置周期内所述模块化级联多电平变换器在主要发电时 间的预测功率和所述预测功率中各功率的时长占比;所述预测周期和所述设置周期构成工 作模式的一个调整周期。 3 .根据权利要求2所述的模块化级联多电平变换器的模块切换方法，其特征在于，根据 所述功率信息和所述模块化级联多电平变换器的功率效率关系曲线，进行比较判断，包括： 分别对所述预测功率中各功率和预设功率点，以及，所述预测功率中各功率的时长占 比和预设时长占比，进行比较判断； 若所述预测功率中各功率均小于等于所述预设功率点，或者，所述预测功率中小于等 于所述预设功率点的各功率总时长占比大于等于所述预设时长占比，则判定所述功率信息 对应于所述功率效率关系曲线的效率上升区间； 若所述预测功率中各功率均大于所述预设功率点，或者，所述预测功率中大于所述预 设功率点的各功率总时长占比大于等于所述预设时长占比，则判定所述功率信息对应于所 述功率效率关系曲线的效率下降区间。 4 .根据权利要求2或3所述的模块化级联多电平变换器的模块切换方法，其特征在于， 控制所述模块化级联多电平变换器以满足输出电压要求的最少模块投入模式进行工作，包 括： 依次设定所述模块化级联多电平变换器各相内，满足输出电压要求的最少数量的模块 处于正常工作状态，而其他模块处于关闭状态； 在所述设置周期内，所述模块化级联多电平变换器上电后，控制所述最少数量的模块 进行工作。 5 .根据权利要求2或3所述的模块化级联多电平变换器的模块切换方法，其特征在于， 控制所述模块化级联多电平变换器以全部模块投入模式进行工作，包括： 依次设定所述模块化级联多电平变换器各相内的全部正常模块均处于正常工作状态； 在所述设置周期内，所述模块化级联多电平变换器上电后，控制所述全部正常模块进 行工作。 6 .根据权利要求2或3所述的模块化级联多电平变换器的模块切换方法，其特征在于， 所述预测周期为:上一个所述设置周期结束后，所述模块化级联多电平变换器处于停机状 态的时间段或者进入停机状态之前； 所述调整周期为至少一天。 7 .根据权利要求1所述的模块化级联多电平变换器的模块切换方法，其特征在于，所述 功率信息为实时功率； 根据所述功率信息和所述模块化级联多电平变换器的功率效率关系曲线，进行比较判 断之后，还包括： 若所述功率信息对应于所述功率效率关系曲线的效率平缓区间，则维持所述模块化级 联多电平变换器的工作模式不变;所述效率平缓区间位于所述效率上升区间与所述效率下 降区间之间。 8 .一种模块化级联多电平变换器的控制器，其特征在于，包括:辅助电源、通信模块、检 测模块以及至少一个中央处理器;其中： 所述中央处理器用于执行权利要求1-7任一所述的模块化级联多电平变换器的模块切 换方法； 所述通信模块用于实现所述中央处理器与所述模块化级联多电平变换器的其他控制 器以及外部之间的通信； 所述检测模块用于实现对于所述模块化级联多电平变换器的电压、电流、温度以及电 弧检测功能； 所述辅助电源用于为所述模块化级联多电平变换器的控制器供电。 9 .一种模块化级联多电平变换器，其特征在于，包括:三个相电路，以及，如权利要求8 所述的模块化级联多电平变换器的控制器;其中： 所述相电路包括:N+M个级联模块和N+M个中高压隔离型DC/DC变换器;N和M均为正整 数，且N为能够满足所述模块化级联多电平变换器的输出电压要求的最少模块数量； 每个相电路内，N+M个所述级联模块的输出端依次串联，串联的两端构成相应相电路的 输出端;N+M个所述级联模块的输入端分别与N+M个中高压隔离型DC/DC变换器的输出端一 一对应相连;N+M个中高压隔离型DC/DC变换器的输入端均与直流母线并联连接。 10 .根据权利要求9所述的模块化级联多电平变换器，其特征在于，所述中高压隔离型 DC/DC变换器包括:变换电路和独立控制器； 所述独立控制器包括:辅助电源、通信模块、检测模块以及至少一个处理器;其中： 所述处理器用于实现对于所述变换电路的控制； 所述通信模块用于实现所述处理器与所述模块化级联多电平变换器的控制器之间的 通信； 所述检测模块用于实现对于所述中高压隔离型DC/DC变换器的电压、电流、温度以及电 弧检测功能； 所述辅助电源用于为所述独立控制器供电。 [EN CN109787291B]: 1 A module switching method of a modular cascaded multilevel converter, characterized by comprising: obtaining power information of the modular cascaded multilevel converter; wherein the power information is predicted power or real-time power, And the power information is the total power of the modular cascaded multilevel converter or the power of each cascaded module or module group of the modular cascaded multilevel converter; according to the power information and the The power efficiency relationship curve of the modular cascaded multilevel converter is compared and judged; the power efficiency relationship curve includes at least the efficiency rise interval where the operating point is located on the left side of the highest efficiency point of the power efficiency curve, and, The point is located in the efficiency drop interval on the right side of the highest efficiency point of the power efficiency curve; if the power information corresponds to the efficiency increase interval, the modular cascaded multilevel converter is controlled to meet the output voltage requirement Work in a minimum module input mode; if the power information corresponds to the efficiency drop interval, control the modular cascaded multilevel converter to work in an all-module input mode. 2 The module switching method of the modular cascaded multilevel converter according to claim 1, wherein obtaining the power information of the modular cascaded multilevel converter comprises: obtaining the next one within the prediction period The predicted power of the modular cascaded multilevel converter in the main power generation time and the proportion of the duration of each power in the predicted power within the set period; the predicted period and the set period constitute an adjustment period of the working mode . 3 The module switching method of the modular cascaded multilevel converter according to claim 2, wherein the method is performed according to the power information and the power efficiency relationship curve of the modular cascaded multilevel converter The comparison judgment includes: comparing and judging each power in the predicted power and the preset power point, and the time-to-time ratio and the preset time-to-time ratio of each power in the predicted power; Each power is less than or equal to the preset power point, or if the total duration of each power in the predicted power is less than or equal to the preset power point is greater than or equal to the preset duration, then the power information is determined Corresponding to the efficiency increase interval of the power efficiency relationship curve; if each power in the predicted power is greater than the preset power point, or the total time length of each power in the predicted power greater than the preset power point accounts for If the ratio is greater than or equal to the preset time duration ratio, it is determined that the power information corresponds to the efficiency drop interval of the power efficiency relationship curve. 4 The module switching method of the modular cascaded multilevel converter according to claim 2 or 3, characterized in that the modular cascaded multilevel converter is controlled to meet the minimum module input mode required by the output voltage Performing work includes: sequentially setting in each phase of the modular cascaded multilevel converter, the minimum number of modules that meet the output voltage requirements are in the normal working state, and the other modules are in the off state; in the setting period After the modular cascaded multilevel converter is powered on, the minimum number of modules are controlled to work. 5 The module switching method of the modular cascaded multilevel converter according to claim 2 or 3, characterized in that controlling the modular cascaded multilevel converter to work in an all-module input mode includes: Set in sequence all normal modules in each phase of the modular cascaded multilevel converter to be in a normal working state; in the setting period, after the modular cascaded multilevel converter is powered on, control All the normal modules work. 6 The module switching method of the modular cascaded multilevel converter according to claim 2 or 3, wherein the prediction period is: after the previous setting period ends, the modular cascaded multilevel converter The time period during which the level converter is in the shutdown state or before entering the shutdown state; the adjustment period is at least one day. 7 The module switching method of the modular cascaded multilevel converter according to claim 1, wherein the power information is real-time power; according to the power information and the modular cascaded multilevel converter After comparing and determining the power efficiency relationship curve of the power efficiency relationship curve, the method further includes: if the power information corresponds to the gentle efficiency interval of the power efficiency relationship curve, maintaining the working mode of the modular cascaded multilevel converter is not Change; The efficiency flat interval is located between the efficiency increase interval and the efficiency decrease interval. 8 A modular cascaded multilevel converter controller, characterized by comprising: an auxiliary power supply, a communication module, a detection module and at least one central processing unit; wherein: the central processing unit is used to execute claim 1- 7. Any of the module switching methods of the modular cascaded multilevel converter; the communication module is used to implement the central processing unit and other controllers of the modular cascaded multilevel converter and external The detection module is used to realize the voltage, current, temperature and arc detection functions of the modular cascaded multilevel converter; the auxiliary power supply is used to provide the modular cascaded multi-level converter The controller of the level converter supplies power. 9 A modular cascaded multilevel converter, characterized by comprising: three phase circuits, and a controller for the modular cascaded multilevel converter according to claim 8; wherein: said The phase circuit includes: N+M cascaded modules and N+M medium and high voltage isolated DC/DC converters; N and M are both positive integers, and N is the modular cascaded multilevel converter The minimum number of modules required for the output voltage of each phase circuit; In each phase circuit, the output terminals of the N+M cascade modules are connected in series, and the two ends of the series form the output terminals of the corresponding phase circuit; N+M cascades The input terminals of the module are respectively connected with the output terminals of the N+M medium and high voltage isolation DC/DC converters in a one-to-one correspondence; the input terminals of the N+M medium and high voltage isolation DC/DC converters are all connected in parallel with the DC bus. 10 The modular cascaded multilevel converter according to claim 9, characterized in that the medium and high voltage isolated DC/DC converter comprises: a conversion circuit and an independent controller; the independent controller comprises: auxiliary A power supply, a communication module, a detection module, and at least one processor; wherein: the processor is used to implement control of the conversion circuit; the communication module is used to implement the processor and the modular cascaded multilevel The communication between the controllers of the converter; the detection module is used to realize the voltage, current, temperature, and arc detection functions of the medium and high voltage isolated DC/DC converter; the auxiliary power supply is used to provide the independent Controller power supply. | [ZH CN109787291B]: 模块化级联多电平变换器及其模块切换方法和控制器 技术领域 [0001]本发明涉及自动控制技术领域，特别涉及一种模块化级联多电平变换器及其模块 切换方法和控制器。 背景技术 [0002]模块化级联多电平变换器已广泛应用于新能源发电、无功补偿、电机调速、柔性直 流输电等领域。为了提高模块化级联多电平变换器的可靠性，现有技术中通常采用模块N+1 冗余设计，即根据系统最大交流电压等级计算需要至少由N个模块才能提供，设计时再增加 1个模块，构成N+1个模块；即使有某个模块无法正常工作，此时只需将此模块旁路，其他模 块仍正常工作，可保证系统正常工作，进而提高可靠性。 [0003]关于冗余模块的处理方法，当前存在两种具体形式，一种是：正常工况时，冗余模 块始终处于备用待工作状态；故障发生时，冗余模块替代故障模块进行工作；两种工况系统 始终保持N个模块工作。另一种是:正常工况时，冗余模块同其他模块一样正常工作，系统N+ 1个模块工作；故障发生时，旁路故障模块，系统N个模块工作；两种工况下系统工作模块数 目不相同。 [0004] 然而上述两种冗余模块的处理方法，都只是人为的固定性择一设置，而无法通过 自动切换来实现转换效率的提升。 发明内容 [0005]本发明提供一种模块化级联多电平变换器及其模块切换方法和控制器，以提升模 块化级联多电平变换器的转换效率。 [0006]为实现上述目的，本申请提供的技术方案如下： [0007]本发明一方面提供一种模块化级联多电平变换器的模块切换方法，包括： [0008]获取模块化级联多电平变换器的功率信息； [0009]根据所述功率信息和所述模块化级联多电平变换器的功率效率关系曲线，进行比 较判断； [0010]若所述功率信息对应于所述功率效率关系曲线的效率上升区间，则控制所述模块 化级联多电平变换器以满足输出电压要求的最少模块投入模式进行工作； [0011]若所述功率信息对应于所述功率效率关系曲线的效率下降区间，则控制所述模块 化级联多电平变换器以全部模块投入模式进行工作。 [0012]优选的，获取模块化级联多电平变换器的功率信息，包括： [0013]在预测周期内，获取未来一个设置周期内所述模块化级联多电平变换器在主要发 电时间的预测功率和所述预测功率中各功率的时长占比;所述预测周期和所述设置周期构 成工作模式的一个调整周期。 [0014]优选的，根据所述功率信息和所述模块化级联多电平变换器的功率效率关系曲 线，进行比较判断，包括： [0015] 分别对所述预测功率中各功率和预设功率点，以及，所述预测功率中各功率的时 长占比和预设时长占比，进行比较判断； [0016] 若所述预测功率中各功率均小于等于所述预设功率点，或者，所述预测功率中小 于等于所述预设功率点的各功率总时长占比大于等于所述预设时长占比，则判定所述功率 信息对应于所述功率效率关系曲线的效率上升区间； [0017] 若所述预测功率中各功率均大于所述预设功率点，或者，所述预测功率中大于所 述预设功率点的各功率总时长占比大于等于所述预设时长占比，则判定所述功率信息对应 于所述功率效率关系曲线的效率下降区间。 [0018]优选的，控制所述模块化级联多电平变换器以满足输出电压要求的最少模块投入 模式进行工作，包括： [0019]依次设定所述模块化级联多电平变换器各相内，满足输出电压要求的最少数量的 模块处于正常工作状态，而其他模块处于关闭状态； [0020]在所述设置周期内，所述模块化级联多电平变换器上电后，控制所述最少数量的 模块进行工作。 [0021]优选的，控制所述模块化级联多电平变换器以全部模块投入模式进行工作，包括： [0022]依次设定所述模块化级联多电平变换器各相内的全部正常模块均处于正常工作 状态； [0023]在所述设置周期内，所述模块化级联多电平变换器上电后，控制所述全部正常模 块进行工作。 [0024]优选的，所述预测周期为:上一个所述设置周期结束后，所述模块化级联多电平变 换器处于停机状态的时间段或者进入停机状态之前； [0025] 所述调整周期为至少一天。 [0026]优选的，所述功率信息为实时功率； [0027]根据所述功率信息和所述模块化级联多电平变换器的功率效率关系曲线，进行比 较判断之后，还包括： [0028]若所述功率信息对应于所述功率效率关系曲线的效率平缓区间，则维持所述模块 化级联多电平变换器的工作模式不变;所述效率平缓区间位于所述效率上升区间与所述效 率下降区间之间。 [0029]本发明另一发明提供一种模块化级联多电平变换器的控制器，包括:辅助电源、通 信模块、检测模块以及至少一个中央处理器;其中： [0030]所述中央处理器用于执行上述任一所述的模块化级联多电平变换器的模块切换 方法； [0031]所述通信模块用于实现所述中央处理器与所述模块化级联多电平变换器的其他 控制器以及外部之间的通信； [0032]所述检测模块用于实现对于所述模块化级联多电平变换器的电压、电流、温度以 及电弧检测功能； [0033]所述辅助电源用于为所述模块化级联多电平变换器的控制器供电。 [0034]本发明第三方面提供一种模块化级联多电平变换器，包括:三个相电路，以及，如 上述所述的模块化级联多电平变换器的控制器;其中： [0035] 所述相电路包括:N+M个级联模块和N+M个中高压隔离型DC/DC变换器;N和M均为正 整数，且N为能够满足所述模块化级联多电平变换器的输出电压要求的最少模块数量； [0036]每个相电路内，N+M个所述级联模块的输出端依次串联，串联的两端构成相应相电 路的输出端;N+M个所述级联模块的输入端分别与N+M个中高压隔离型DC/DC变换器的输出 端一一对应相连;N+M个中高压隔离型DC/DC变换器的输入端均与直流母线并联连接。 [0037] 优选的，所述中高压隔离型DC/DC变换器包括:变换电路和独立控制器； [0038] 所述独立控制器包括:辅助电源、通信模块、检测模块以及至少一个处理器;其中： [0039] 所述处理器用于实现对于所述变换电路的控制； [0040]所述通信模块用于实现所述处理器与所述模块化级联多电平变换器的控制器之 间的通信； [0041]所述检测模块用于实现对于所述中高压隔离型DC/DC变换器的电压、电流、温度以 及电弧检测功能； [0042]所述辅助电源用于为所述独立控制器供电。 [0043]本发明提供的模块化级联多电平变换器的模块切换方法，通过获取模块化级联多 电平变换器的功率信息;然后根据所述功率信息和所述模块化级联多电平变换器的功率效 率关系曲线，进行比较判断；若所述功率信息对应于所述功率效率关系曲线的效率上升区 间，则控制所述模块化级联多电平变换器以满足输出电压要求的最少模块投入模式进行工 作，使每个模块以较高的功率工作，将模块化级联多电平变换器在功率效率关系曲线上的 工作点向效率上升的方向移动，进而实现对于该模块化级联多电平变换器转换效率的提 高；而若所述功率信息对应于所述功率效率关系曲线的效率下降区间，则控制所述模块化 级联多电平变换器以全部模块投入模式进行工作，使每个模块以较低的功率工作，将模块 化级联多电平变换器在功率效率关系曲线上的工作点向与效率下降相反的方向移动，进而 实现对于该模块化级联多电平变换器转换效率的提高。 附图说明 [0044]为了更清楚地说明本发明实施例或现有技术内的技术方案，下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述内的附图仅仅是本 发明的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动的前提下，还可以 根据这些附图获得其他的附图。 [0045]图1是本发明申请实施例提供的功率变换器典型的功率效率关系曲线示意图； [0046]图2是本发明申请实施例提供的模块化级联多电平变换器的部分结构以及与外部 的连接关系示意图； [0047]图3是本发明申请实施例提供的模块化级联多电平变换器的模块切换方法的流程 图； [0048]图4是本发明申请实施例提供的采用不同模块数目运行时系统的工作点变化示意 图； [0049]图5是本发明申请另一实施例提供的模块化级联多电平变换器的控制器的结构示 意图； [0050]图6是本发明申请另一实施例提供的中高压隔离型DC/DC变换器连接级联模块的 电路框图。 具体实施方式 [0051]下面将结合本申请实施例中的附图，对本申请实施例中的技术方案进行清楚、完 整地描述，显然，所描述的实施例仅仅是本申请一部分实施例，而不是全部的实施例。基于 本申请中的实施例，本领域普通技术人员在没有作出创造性劳动前提下所获得的所有其他 实施例，都属于本申请保护的范围。 [0052]图1所示为功率变换器典型的功率效率关系曲线示意图，由图1可见，随着功率的 上升，其效率逐渐上升到最高点，然后又逐渐降低;常规功率变换器的最高效率点通常处于 20 %〜40 %额定功率之间。在从零功率到较低功率时，功率变换器整体功率较小，而功率变 换器的辅助电源供电、控制系统供电等损耗相对固定，因而此时损耗的功率占比比较大，导 致系统效率较低；随着功率变换器整体功率的逐步抬升，其辅助电源供电、控制系统供电等 损耗的功率占比逐步减小，使其效率逐渐提升。 [0053]基于此，本发明提供一种模块化级联多电平变换器的模块切换方法，以提升模块 化级联多电平变换器的转换效率。 [0054]该模块化级联多电平变换器的模块切换方法，应用于模块化级联多电平变换器的 控制器，图2所示为模块化级联多电平变换器除控制器以外的一种具体结构示意图，其具体 包括:三个相电路，每个相电路均包括:N+M个级联模块和N+M个中高压隔离型DC/DC变换器; N和M均为正整数，且N为能够满足模块化级联多电平变换器的输出电压要求的最少模块数 量;并且，每个相电路内，N+M个级联模块的输出端依次串联，串联的两端构成相应相电路的 输出端;N+M个级联模块的输入端分别与N+M个中高压隔离型DC/DC变换器的输出端一一对 应相连;N+M个中高压隔离型DC/DC变换器的输入端均与直流母线并联连接。 [0055]值得说明的是，本申请关于端口的描述中，其输入端和输出端的命名仅用于区分 每个器件的两端，并不用于限定器件内部电流的流动方向。比如，当级联模块为逆变电路 时，其输出端指代其交流侧，而其输入端指代其直流侧;其内部的电流可以从称为输入端的 直流侧流向称为输出端的交流侧，也可以从称为输出端的交流侧流向称为输入端的直流 侧。其他情况类似,此处不再一一赘述。 [0056]具体的，该模块化级联多电平变换器的模块切换方法如图3所示，包括： [0057] S101、获取模块化级联多电平变换器的功率信息； [0058]该功率信息可以是指实际测量得到的实时功率，也可以是指通过气象预测或者历 史数据分析等多种手段进行预判和校验得到的预测功率;此处不做具体限定，视其应用环 境而定，均在本申请的保护范围内。 [0059] S102、根据功率信息和模块化级联多电平变换器的功率效率关系曲线，进行比较 判断； [0060]模块化级联多电平变换器属于功率变换器中的一种，所以图1所示的功率效率关 系曲线同样适用于模块化级联多电平变换器中的任意一相、任意一个级联模块。对于其功 率效率关系曲线，可以通过理论计算、仿真、实际测试等多种手段获取，此处不做限定，视其 具体应用环境而定，均在本申请的保护范围内。 [0061]对于如图2所示的模块化光伏发电系统，其模块化级联多电平变换器的输入端有 一个低压公共直流母线，系统中每一个模块组(级联模块及其对应连接的中高压隔离型DC/ DC变换器)的输入输出功率相同，也即各个模块组平分总输入功率。例如，光伏发电系统中 总共有3 X (N+M)个模块组，即每相有N+M个模块组，光伏发电系统总输入功率为3P，则每一 个模块组的输入功率为P/(N+M)。 [0062]图4给出了采用不同模块数目运行时系统的工作点变化示意图；假设光伏发电系 统一开始工作于A点，此时每相N个级联模块参与工作；然后增加工作模块数目，比如增加到 N+M时，由于光伏发电系统输入总功率不变，而每个模块组的输入功率从P/N减小到P/(N+ M)，因此，对每个模块组而言，可以使其工作点从A点迁移到B点。 [0063] 计算系统整体转换效率时，首先A点模块组效率为97.7%,B点模块组效率为 98.0% ；然后分别计算两种情况下的系统损耗和效率:对于A点而言，其单模块组功率损耗 P10ss= (100%-97.7%) *P/N = 2.3%*P/N,系统总损耗P10ss total= (100%-97.7%) *P/N*3N = 2.3% X3P；而对于B点而言，其单模块组功率损耗P10ss= (100%-98.0%)*P/(N+M)= 2.0%*P/(N+M),此时，其系统总损耗P10ss tota1= (100%-98.0%) *P/ (N+M) *3 (N+M) =2.0% X3P；因此可以得到,A点光伏发电系统效率为97.7%,而B点光伏发电系统效率为98.0%。 [0064]也就是说，当模块化级联多电平变换器的工作点位于功率效率曲线最高效率点的 右侧部分时，其工作模块数目越多，系统效率越高。同理，在功率效率曲线最高效率点的左 侧部分，工作模块数目越少，系统效率越高。因此，通过对光伏发电系统中工作模块数目的 不同选择，可以实现系统效率或发电量优化。 [0065]实际应用中，步骤S101中获取的功率信息，不仅可以是实时功率或者预测功率，而 且还可以是指模块化级联多电平变换器的总功率，或者模块化级联多电平变换器各个级联 模块或模块组的功率;若获取的是总功率，则除以工作模块的个数即可得到各个级联模块 或模块组的功率;再与功率效率关系曲线进行比较判断即可。 [0066]为了方便比较，可以将该功率效率关系曲线划分为至少两个区间，比如，将工作点 位于功率效率曲线最高效率点的左侧部分定义为功率效率关系曲线的效率上升区间，而将 工作点位于功率效率曲线最高效率点的右侧部分定义为功率效率关系曲线的效率下降区 间；或者，也可以将效率快速上升的较低功率区间定义为功率效率关系曲线的效率上升区 间，将效率逐渐下降的较高功率区间定义为功率效率关系曲线的效率下降区间，而将效率 变化较小的部分功率区间定义为功率效率关系曲线的效率平缓区间；一种具体方式为:将 0%〜20%额定功率之间定义为功率效率关系曲线的效率上升区间，将40%〜100%额定功 率之间定义为功率效率关系曲线的效率下降区间，而将20%〜40%额定功率之间定义为功 率效率关系曲线的效率平缓区间。对于功率效率关系曲线的划分，可以视其具体应用环境 而定，此处不做限定，均在本申请的保护范围内。 [0067]经过比较判断之后，若功率信息对应于功率效率关系曲线的效率上升区间，则执 行步骤S103；而若功率信息对应于功率效率关系曲线的效率下降区间，则执行步骤S104； [0068] S103、控制模块化级联多电平变换器以满足输出电压要求的最少模块投入模式进 行工作； [0069]最少模块投入模式是指每一相中投入运行的级联模块数量能够满足模块化级联 多电平变换器的输出电压要求即可，比如上述内容中在N个级联模块均正常、无故障的情况 下，以N个级联模块投入运行的工作模式。当级联模块为逆变电路时，该输出电压要求指的 是交流侧电压要求。 [0070] 在功率信息对应于功率效率关系曲线的效率上升区间时，通过控制模块化级联多 电平变换器以满足输出电压要求的最少模块投入模式进行工作，能够使每个级联模块以较 高的功率工作，将模块化级联多电平变换器在功率效率关系曲线上的工作点向效率上升的 方向移动，进而实现对于该模块化级联多电平变换器转换效率的提高。 [0071] S104、控制模块化级联多电平变换器以全部模块投入模式进行工作。 [0072]全部模块投入模式是指每一相中的全部正常级联模块均投入运行的工作模式，比 如上述内容中在N+M个级联模块均正常、无故障的情况下，以N+M个级联模块投入运行的工 作模式;若存在故障模块，则仅以剩余的正常级联模块投入运行即可。 [0073] 在功率信息对应于功率效率关系曲线的效率下降区间时，通过控制模块化级联多 电平变换器以全部模块投入模式进行工作，能够使每个级联模块以较低的功率工作，将模 块化级联多电平变换器在功率效率关系曲线上的工作点向与效率下降相反的方向移动，进 而实现对于该模块化级联多电平变换器转换效率的提高。 [0074]本实施例提供的该模块化级联多电平变换器的模块切换方法，以效率为优化目 标，进而实现对于工作模块数目的选择；同现有的模块化多电平运行模块选择方案及同类 型拓扑的电力电子变压器运行模块选择方案相比，本实施例在所有模块正常或部分模块故 障这两种条件下都可以实现效率优化;并且，只需要算法软件执行，不仅算法简单容易执 行，而且不增加系统成本。另外，本实施例通过该模块化级联多电平变换器的控制器执行上 述模块切换方案，实现了对于中高压隔离型DC/DC变换器部分的完全模块化设计，降低了系 统设计、施工安装、后期运维的难度。 [0075]可选的，当步骤S101中获取的功率信息为实时功率时，步骤S102之后还包括： [0076]若功率信息对应于功率效率关系曲线的效率平缓区间，则维持模块化级联多电平 变换器的工作模式不变； [0077]该效率平缓区间位于效率上升区间与效率下降区间之间，通过上述维持控制，能 够避免系统运行期间反复调整工作模块数目，确保系统运行的稳定性。 [0078]此外，在上一实施例的基础之上，本实施例提供了一种更为优选的具体方案，即在 系统待机或不工作时对模块化级联多电平变换器的工作模式进行设定，避免在系统正常工 作时进行切换，确保运行稳定，并且不会影响系统发电量。 [0079]具体的，在上一实施例及图3的基础之上，其步骤S101、获取模块化级联多电平变 换器的功率信息，具体包括： [0080]在预测周期内，获取未来一个设置周期内模块化级联多电平变换器在主要发电时 间的预测功率和预测功率中各功率的时长占比。 [0081]需要说明的是，该预测周期和该设置周期构成工作模式的一个调整周期。 [0082]该预测周期是指上一个设置周期结束后，模块化级联多电平变换器处于停机状态 的时间段，比如夜间；或者该预测周期也可以是指处于停机状态之前的时间段，比如进入夜 间之前先通过执行该方法得到下一设置周期内该化级联多电平变换器的工作模块设置。该 方法在该预测周期内完成即可，优选为该预测周期开始时即执行步骤S101。 [0083]该调整周期为至少一天，比如一天、一周、一月、一季度，或者任意天数均可，视其 具体应用环境而定，此处不做限定，均在本申请的保护范围内。 [0084]该设置周期是指调整周期减去一个预测周期的时长;具体可以为一天内模块化级 联多电平变换器处于正常运行的时间段，比如一个白天，此时该预测周期为夜间；或者，该 设置周期也可以为一天内模块化级联多电平变换器处于正常运行的时间段减去进入停机 状态之前的一个预设时长^t，即模块化级联多电平变换器正常运行至即将停机的预设时 长At之前，然后进入预测周期、完成下一个设置周期的工作模块设置，然后进入夜间停机 状态;再到白天时即可以设置好的模式进行运行。或者，该设置周期也可以是指一周、一月、 一季度以及任意天数中的任意一种减去开始或者结束时一个预测周期的时长；以该设置周 期指代一周减去一个预测周期的时长为例进行说明，此时一个完整的调整周期是指一周。 [0085]该主要发电时间是指模块化级联多电平变换器的功率高于发电要求的时间段；比 如，夏季的07:00-18:00，或者其他季节的08:00-17:00；视其具体应用环境而定，此处不做 限定，均在本申请的保护范围内。 [0086]例如，实际应用中，该步骤S101可以是:根据气象预测，未来一天的主要发电时间 内，各级联模块的预测功率都将处于＜ = 20%额定功率的状态;或者，未来一天的主要发电 时间内，各级联模块的预测功率将有10%的时间处于＜ = 20%额定功率的状态，有20%的时 间处于20%〜40%额定功率的状态，有70%的时间处于40%〜100%额定功率的状态。 [0087]与上述内容相对应的，图3中的步骤S102、根据功率信息和模块化级联多电平变换 器的功率效率关系曲线，进行比较判断,具体包括： [0088] 分别对预测功率中各功率和预设功率点，以及，预测功率中各功率的时长占比和 预设时长占比，进行比较判断； [0089] 若预测功率中各功率均小于等于预设功率点，或者，预测功率中小于等于预设功 率点的各功率总时长占比大于等于预设时长占比，则判定功率信息对应于功率效率关系曲 线的效率上升区间； [0090] 若预测功率中各功率均大于预设功率点，或者，预测功率中大于预设功率点的各 功率总时长占比大于等于预设时长占比，则判定功率信息对应于功率效率关系曲线的效率 下降区间。 [0091]实际应用中，该预设功率点Pset,以及，该预设时长占比Ratio均为提前设置的，并 且均可视其应用环境而定。例如，该模块化级联多电平变换器的功率效率关系曲线的最大 功率点为30%额定功率，可以设置预设功率点Pset为30%额定功率点、40%额定功率点、 50%额定功率点、60%额定功率点等等，此处不做限定；并且，可以设置该预设时长占比 Ratio = 50%,当然也可以为其他数值，此处仅为一种示例。 [0092]如果未来一段时间内模块化级联多电平变换器在主要发电时间内，其各级联模块 的预测功率都要小于预设功率点Pset,则判定功率信息对应于功率效率关系曲线的效率上 升区间，此时执行步骤S103,即选择最少模块投入模式。例如:Pset = 50%,未来一天/一周 内，模块化级联多电平变换器在主要发电时间段内，其各级联模块的预测功率都要小于 Pset,则选择最少模块投入模式。 [0093]如果未来一段时间内模块化级联多电平变换器在主要发电时间内，其各级联模块 的预测功率部分超过预设功率点Pset,但没有超过预设时长占比Ratio,即：其各级联模块 的预测功率中一部分小于预设功率点Pset,另外的要大于预设功率点Pset,但大于预设功 率点Pset的部分的时长占比要小于预设时长占比Ratio,则选择最少模块投入模式。例如： Pset = 50%,Ratio = 50%,未来一天/一周内，模块化级联多电平变换器在主要发电时间段 内，其各级联模块的预测功率中有40%的时间处于50%〜100%额定功率段(&gt;Pset)，有 60%时间处于0%〜50%额定功率段(&lt;Pset),由于60%大于预设时长占比Ratio,所以选择 最少模块投入模式。 [0094]如果未来一段时间内模块化级联多电平变换器在主要发电时间内，其各级联模块 的预测功率部分超过预设功率点Pset,且超过时长占比Ratio,即：其各级联模块的预测功 率中一部分小于预设功率点Pset,另外的要大于预设功率点Pset,且大于预设功率点Pset 的部分的时长占比要大于预设时长占比Ratio,所以选择全部模块投入模式。例如:Pset = 50% ,Ratio = 50% ,未来一天/一周内，模块化级联多电平变换器在主要发电时间段内，其 各级联模块的预测功率中有30%时间处于0%〜50%额定功率段(&lt;Pset),有70%的时间处 于50%〜100%额定功率段(&gt;Pset),由于70%大于预设时长占比Ratio = 50%,所以选择全 部模块投入模式。 [0095]此外，优选的，其步骤S103、控制模块化级联多电平变换器以满足输出电压要求的 最少模块投入模式进行工作，具体包括： [0096]依次设定模块化级联多电平变换器各相内，满足输出电压要求的最少数量的模块 处于正常工作状态,而其他模块处于关闭状态； [0097]在设置周期内，模块化级联多电平变换器上电后，控制最少数量的模块进行工作。 [0098]实际应用中，首先选择该模块化级联多电平变换器三相中的任意一相，设定能够 正常工作且满足其输出电压要求的N个级联模块及其对应的中高压隔离型DC/DC变换器都 处于正常工作状态，并设定其余级联模块及其对应的中高压隔离型DC/DC变换器处于关闭 状态;然后依次设定其他未设定的相。 [0099]而其步骤S104、控制模块化级联多电平变换器以全部模块投入模式进行工作，具 体包括： [0100]依次设定模块化级联多电平变换器各相内的全部正常模块均处于正常工作状态； [0101]在设置周期内，模块化级联多电平变换器上电后，控制全部正常模块进行工作。 [0102]实际应用中，首先选择该模块化级联多电平变换器三相中的任意一相，设定能够 正常工作的所有级联模块及其对应的中高压隔离型DC/DC变换器都处于正常工作状态;然 后依次设定其他未设定的相。 [0103]以上为一个调整周期内的具体过程，当下一个预测周期开始后，重新执行步骤 S101,进行新一轮工作模块的切换调整。 [0104]本实施例提提供的模块化级联多电平变换器的模块切换方法，同现有控制策略相 比，不仅可以优化系统效率，还能够提升系统发电量。 [0105] 其余原理与上一实施例相同，此处不再一一赘述。 [0106]本发明另一实施例还提供了一种模块化级联多电平变换器的控制器，如图5所示， 包括:辅助电源104、通信模块102、检测模块103以及至少一个中央处理器101；其中： [0107]其中央处理器101用于执行上述任一实施例所述的模块化级联多电平变换器的模 块切换方法； [0108]其通信模块102用于实现中央处理器101与该模块化级联多电平变换器的其他控 制器以及外部之间的通信； [0109]其检测模块103用于实现对于该模块化级联多电平变换器的电压、电流、温度以及 电弧检测功能； [0110]其辅助电源104用于为该模块化级联多电平变换器的控制器供电。 [0111] 中央处理器101的物理实现方式包括但不限于CPU（Central Processing Unit，中 央处理器）、MCU （Microcontrol ler Unit，微控制单元）、DSP （Digital Signal Processing，数字信号处理）、ARM （AdvancedRISCMachines）、FPGA （Field-Programmable Gate Array,现场可编程门阵列）、CPLD（Complex Programmable Logic Device,复杂可编 程逻辑器件）、ASIC（Application Specific Integrated Circuit）芯片等。该控制器的其 他功能和原理均与现有技术相同，能够实现对三相级联模块部分的并网控制以及同外界的 数据交互，可以接收系统功率信息，可实现对中高压隔离型DC/DC变换器下达指令。 [0112]该模块化级联多电平变换器的模块切换方法的过程及原理，参见上述实施例即 可，此处不再一一赘述。 [0113]本发明另一实施例还提供了一种模块化级联多电平变换器，如图2所示，包括:三 个相电路（图2中的A、B、C三相），以及，如上一实施例所述的模块化级联多电平变换器的控 制器（未进行图示）；其中： [0114]该相电路包括:N+M个级联模块（图2中的级联模块#1、级联模块#2…级联模块#N+ M）和N+M个中高压隔离型DC/DC变换器;N和M均为正整数，且N为能够满足模块化级联多电平 变换器的输出电压要求的最少模块数量； [0115]每个相电路内，N+M个级联模块的输出端依次串联，串联的两端构成相应相电路的 输出端;N+M个级联模块的输入端分别与N+M个中高压隔离型DC/DC变换器的输出端一一对 应相连;N+M个中高压隔离型DC/DC变换器的输入端均与直流母线并联连接。 [0116]值得说明的是，当级联模块为逆变电路时，该模块化级联多电平变换器的输出电 压要求指代的是其交流侧电压要求，且三个相电路的输出端通过滤波器以星型或角型方式 并网；各个级联模块可以采用H桥、NPC全桥、飞跨电容全桥等拓扑;各个中高压隔离型DC/DC 变换器可以采用功率单向谐振式变换器、功率双向谐振式变换器、功率单向非谐振式变换 器、功率双向非谐振式变换器等。 [0117]另外，图6给出了中高压隔离型DC/DC变换器连接级联模块的电路框图。其中高压 隔离型DC/DC变换器可以是单个输出端口，也可以是多个输出端口。级联模块内部的子级联 模块数目同中高压隔离型DC/DC变换器的输出端口数目相同，且一一对应相连。比如,第N个 中高压隔离型DC/DC变换器包括一个DC/AC模块#N和j个AC/DC模块（AC/DC模块#N1、AC/DC模 块#N2…AC/DC模块#Nj）；j个AC/DC模块的直流侧分别作为该第N个中高压隔离型DC/DC变换 器的j个输出端口，分别与级联模块#N内的j个子级联模块（级联模块#N1、级联模块#N2…级 联模块#Nj）输入端一一对应相连。单输入单输出的中高压隔离型DC/DC变换器是这种单输 入多输出中高压隔离型DC/DC变换器的一种形式。并且，此处输入和输出也只是用于区分两 个端口名称，并不表明功率一定是从输入流向输出，实际应用中功率也可以是从输出流向 输入。 [0118]实际应用中，该模块化级联多电平变换器的直流侧可以与光伏发电系统的多个非 隔离式DC/DC变换器的一侧相连，各个非隔离式DC/DC变换器的另一侧用于连接光伏板或者 蓄电池，多个非隔离式DC/DC变换器可以直接并联到公共的直流母线，也可以多个非隔离式 DC/DC变换器经过串联后再并联到直流母线上。 [0119] 另外，该中高压隔离型DC/DC变换器包括:变换电路和独立控制器；其独立控制器 具体包括:辅助电源、通信模块、检测模块以及至少一个处理器;其中：其处理器用于实现对 于变换电路的控制;其通信模块用于实现处理器与模块化级联多电平变换器的控制器之间 的通信;其检测模块用于实现对于中高压隔离型DC/DC变换器的电压、电流、温度以及电弧 检测功能；其辅助电源用于为独立控制器供电。 [0120] 该中高压隔离型DC/DC变换器部分的控制策略，可以完全按照DC/DC变换器独立执 行，实现模块化设计。 [0121] 其余结构及原理参见上述实施例即可，此处不再一一赘述。 [0122]本发明中各个实施例采用递进的方式描述，每个实施例重点说明的都是与其他实 施例的不同之处，各个实施例之间相同相似部分互相参见即可。对于实施例公开的装置而 言，由于其与实施例公开的方法相对应，所以描述的比较简单，相关之处参见方法部分说明 即可。 [0123]以上所述，仅是本发明的较佳实施例而已，并非对本发明作任何形式上的限制。虽 然本发明已以较佳实施例揭露如上，然而并非用以限定本发明。任何熟悉本领域的技术人 员，在不脱离本发明技术方案范围情况下，都可利用上述揭示的方法和技术内容对本发明 技术方案做出许多可能的变动和修饰，或修改为等同变化的等效实施例。因此，凡是未脱离 本发明技术方案的内容，依据本发明的技术实质对以上实施例所做的任何简单修改、等同 变化及修饰，均仍属于本发明技术方案保护的范围内。 [EN CN109787291B]: Modular cascade multilevel converter and its module switching method and controller technical field [0001] The present invention relates to the field of automatic control technology, and in particular to a modular cascaded multilevel converter and its module switching method and controller. Background technique [0002] Modular cascaded multilevel converters have been widely used in fields such as new energy power generation, reactive power compensation, motor speed regulation, and flexible direct current transmission. In order to improve the reliability of modular cascaded multilevel converters, module N+1 redundancy design is usually adopted in the prior art, that is, according to the maximum AC voltage level of the system, at least N modules can be used to provide it. One module constitutes N+1 modules; even if a certain module fails to work normally, you only need to bypass this module at this time, and other modules still work normally, which can ensure the normal operation of the system and improve reliability. [0003] Regarding the processing method of the redundant module, there are currently two specific forms. One is: in normal operating conditions, the redundant module is always in a standby standby state; when a failure occurs, the redundant module replaces the failed module to work; In the two working conditions, the system always keeps N modules working. The other is: in normal working conditions, the redundant module works normally like other modules, and the system N+1 modules work; when a fault occurs, the faulty module is bypassed, and the system N modules work; the system working modules under two working conditions The numbers are not the same. [0004] However, the above-mentioned two processing methods for redundant modules are only artificially fixed alternative settings, and the conversion efficiency cannot be improved by automatic switching. Summary of the invention [0005] The present invention provides a modular cascaded multilevel converter and its module switching method and controller to improve the conversion efficiency of the modular cascaded multilevel converter. [0006] In order to achieve the above purpose, the technical solutions provided by this application are as follows: [0007] One aspect of the present invention provides a module switching method of a modular cascaded multilevel converter, including: [0008] Obtain the power information of the modular cascaded multilevel converter; [0009] Perform comparison and judgment based on the power information and the power efficiency relationship curve of the modular cascaded multilevel converter; [0010] If the power information corresponds to the efficiency increase interval of the power efficiency relationship curve, control the modular cascaded multilevel converter to work in the minimum module input mode that meets the output voltage requirement; [0011] If the power information corresponds to the efficiency drop interval of the power efficiency relationship curve, the modular cascaded multilevel converter is controlled to work in an all-module input mode. [0012] Preferably, obtaining the power information of the modular cascaded multilevel converter includes: [0013] In the prediction period, obtain the predicted power of the modular cascaded multilevel converter in the main power generation time and the proportion of the duration of each power in the predicted power in a set period in the future; the predicted period and The setting period constitutes an adjustment period of the working mode. [0014] Preferably, the comparison and judgment based on the power information and the power efficiency relationship curve of the modular cascaded multilevel converter includes: [0015] compare and judge each power in the predicted power and the preset power point, and the time-to-time ratio and the preset time-to-time ratio of each power in the predicted power, respectively; [0016] If each power in the predicted power is less than or equal to the preset power point, or the proportion of the total duration of each power in the predicted power that is less than or equal to the preset power point is greater than or equal to the preset time length Percentage, it is determined that the power information corresponds to the efficiency increase interval of the power efficiency relationship curve; [0017] If each power in the predicted power is greater than the preset power point, or the proportion of the total duration of each power greater than the preset power point in the predicted power is greater than or equal to the preset duration , It is determined that the power information corresponds to the efficiency drop interval of the power efficiency relationship curve. [0018] Preferably, controlling the modular cascaded multilevel converter to work in a minimum module input mode that meets output voltage requirements includes: [0019] In each phase of the modular cascaded multilevel converter, set in sequence, the minimum number of modules that meet the output voltage requirements are in a normal working state, and other modules are in a closed state; [0020] In the setting period, after the modular cascaded multilevel converter is powered on, the minimum number of modules are controlled to work. [0021] Preferably, controlling the modular cascaded multilevel converter to work in an all-module input mode includes: [0022] In turn, set all normal modules in each phase of the modular cascaded multilevel converter to be in a normal working state; [0023] In the setting period, after the modular cascaded multilevel converter is powered on, all normal modules are controlled to work. [0024] Preferably, the prediction period is: after the last setting period ends, the time period during which the modular cascaded multilevel converter is in the shutdown state or before it enters the shutdown state; [0025] The adjustment period is at least one day. [0026] Preferably, the power information is real-time power; [0027] After comparing and determining according to the power information and the power efficiency relationship curve of the modular cascaded multilevel converter, the method further includes: [0028] If the power information corresponds to the gentle efficiency interval of the power efficiency relationship curve, the working mode of the modular cascaded multilevel converter is maintained unchanged; the gentle efficiency interval is located in the efficiency increase Between the interval and the efficiency drop interval. [0029] Another invention of the present invention provides a modular cascaded multilevel converter controller, including: an auxiliary power supply, a communication module, a detection module and at least one central processing unit; wherein: [0030] The central processing unit is used to execute any one of the above-mentioned modular cascaded multilevel converter module switching methods; [0031] The communication module is used to implement communication between the central processing unit and other controllers of the modular cascaded multilevel converter and the outside; [0032] The detection module is used to realize the voltage, current, temperature, and arc detection functions of the modular cascaded multilevel converter; [0033] The auxiliary power supply is used to supply power to the controller of the modular cascaded multilevel converter. [0034] The third aspect of the present invention provides a modular cascaded multilevel converter, including: three phase circuits, and, as described above, the controller of the modular cascaded multilevel converter; wherein: [0035] The phase circuit includes: N+M cascade modules and N+M medium and high voltage isolated DC/DC converters; N and M are both positive integers, and N is capable of satisfying the modular cascade The minimum number of modules required by the output voltage of the multilevel converter; [0036] In each phase circuit, the output terminals of the N+M cascade modules are connected in series, and the two ends of the series form the output terminals of the corresponding phase circuit; The input ends of the N+M cascade modules are respectively connected to the output ends of the N+M medium and high voltage isolated DC/DC converters in a one-to-one correspondence; the inputs of the N+M medium and high voltage isolated DC/DC converters Both ends are connected in parallel with the DC bus. [0037] Preferably, the medium and high voltage isolated DC/DC converter includes: a conversion circuit and an independent controller; [0038] The independent controller includes: an auxiliary power supply, a communication module, a detection module, and at least one processor; wherein: [0039] The processor is used to implement control of the conversion circuit; [0040] The communication module is used to implement communication between the processor and the controller of the modular cascaded multilevel converter; [0041] The detection module is used to realize the voltage, current, temperature, and arc detection functions of the medium and high voltage isolated DC/DC converter; [0042] The auxiliary power supply is used to supply power to the independent controller. [0043] The module switching method of the modular cascaded multilevel converter provided by the present invention obtains the power information of the modular cascaded multilevel converter; and then according to the power information and the modular cascaded multiple The power efficiency relationship curve of the level converter is compared and judged; if the power information corresponds to the efficiency rise interval of the power efficiency relationship curve, the modular cascaded multilevel converter is controlled to meet the output voltage requirement In the minimum module input mode, each module can work at a higher power, and the operating point of the modular cascaded multilevel converter on the power efficiency curve is moved to the direction of increasing efficiency, so as to realize the To improve the conversion efficiency of the cascaded multilevel converter; and if the power information corresponds to the efficiency drop interval of the power efficiency relationship curve, the modular cascaded multilevel converter is controlled to operate in all modules Work to make each module work at a lower power, move the operating point of the modular cascaded multilevel converter on the power efficiency relationship curve to the opposite direction of the efficiency drop, and then realize the modular cascade The conversion efficiency of multi-level converters is improved. Description of the drawings [0044] In order to more clearly illustrate the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the drawings that need to be used in the description of the embodiments or the prior art. Obviously, the following description The drawings are only some embodiments of the present invention. For those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative work. [0045] FIG. 1 is a schematic diagram of a typical power efficiency relationship curve of a power converter provided by an embodiment of the present application; [0046] FIG. 2 is a partial structure of a modular cascaded multilevel converter provided by an embodiment of the present application and Schematic diagram of the connection relationship with the outside; [0047] FIG. 3 is a flowchart of a module switching method of a modular cascaded multilevel converter provided by an embodiment of the present invention; [0048] FIG. 4 is a schematic diagram of operating point changes of the system when running with different numbers of modules provided by an embodiment of the present invention; [0049] FIG. 5 is a schematic structural diagram of a controller of a modular cascaded multilevel converter provided by another embodiment of the present application; [0050] FIG. 6 is a connection cascade module of a medium and high voltage isolated DC/DC converter provided by another embodiment of the present application Circuit block diagram. Detailed ways [0051] The following will clearly and completely describe the technical solutions in the embodiments of the present application in conjunction with the drawings in the embodiments of the present application. Obviously, the described embodiments are only a part of the embodiments of the present application, rather than all implementations. example. Based on the embodiments in this application, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of this application. [0052] Figure 1 shows a schematic diagram of a typical power efficiency relationship curve of a power converter. It can be seen from Figure 1 that as the power increases, its efficiency gradually rises to the highest point, and then gradually decreases; the highest efficiency of a conventional power converter The point is usually between 20% and 40% of the rated power. From zero power to lower power, the overall power of the power converter is small, while the auxiliary power supply and control system power supply losses of the power converter are relatively fixed. Therefore, the power loss at this time accounts for a relatively large proportion, resulting in a relatively high system efficiency. Low; With the gradual increase of the overall power of the power converter, the proportion of the power loss of its auxiliary power supply and control system power supply is gradually reduced, and its efficiency is gradually improved. [0053] Based on this, the present invention provides a module switching method of a modular cascaded multilevel converter to improve the conversion efficiency of the modular cascaded multilevel converter. [0054] The modular switching method of the modular cascaded multilevel converter is applied to the controller of the modular cascaded multilevel converter. Figure 2 shows the modular cascaded multilevel converter except the controller A specific structure diagram other than that, which specifically includes: three phase circuits, each phase circuit includes: N+M cascade modules and N+M medium and high voltage isolated DC/DC converters; N and M are both Is a positive integer, and N is the minimum number of modules that can meet the output voltage requirements of the modular cascaded multilevel converter; and, in each phase circuit, the output terminals of N+M cascaded modules are serially connected in series. The two ends constitute the output terminal of the corresponding phase circuit; the input terminals of the N+M cascade modules are respectively connected to the output terminals of the N+M medium and high voltage isolated DC/DC converters in a one-to-one correspondence; N+M medium and high voltage isolation The input ends of the DC/DC converters are all connected in parallel with the DC bus. [0055] It is worth noting that in the description of the port in this application, the naming of the input terminal and the output terminal is only used to distinguish the two ends of each device, and is not used to limit the flow direction of the internal current of the device. For example, when the cascade module is an inverter circuit, its output terminal refers to its AC side, and its input terminal refers to its DC side; its internal current can flow from the DC side called the input terminal to the AC side called the output terminal , It can also flow from the AC side called the output end to the DC side called the input end. Other situations are similar, so I won't repeat them here. [0056] Specifically, the module switching method of the modular cascaded multilevel converter is shown in FIG. 3 and includes: [0057] S101. Obtain power information of the modular cascaded multilevel converter; [0058] The power information may refer to the real-time power obtained by actual measurement, or it may refer to the predicted power obtained by predicting and verifying through various means such as meteorological prediction or historical data analysis; there is no specific limitation here, depending on Depending on the application environment, they are all within the protection scope of this application. [0059] S102. Perform comparison and judgment based on the power information and the power efficiency relationship curve of the modular cascaded multilevel converter; [0060] The modular cascaded multilevel converter is one of the power converters, so the power efficiency relationship curve shown in FIG. 1 is also applicable to any phase and any of the modular cascaded multilevel converters. A cascade module. The power efficiency relationship curve can be obtained by various means such as theoretical calculation, simulation, actual test, etc., and it is not limited here, depending on the specific application environment, and all are within the protection scope of this application. [0061] For the modular photovoltaic power generation system as shown in Figure 2, the input of the modular cascaded multilevel converter has For a low-voltage public DC bus, the input and output power of each module group in the system (cascade module and its corresponding medium and high voltage isolated DC/DC converter) is the same, that is, each module group equally divides the total input power. For example, there are a total of 3 X (N+M) module groups in a photovoltaic power generation system, that is, there are N+M module groups per phase, and the total input power of the photovoltaic power generation system is 3P, so the input power of each module group is P/ (N+M). [0062] FIG. 4 shows a schematic diagram of the operating point changes of the system when operating with different numbers of modules; assuming that the photovoltaic power generation system initially works at point A, at this time N cascade modules per phase participate in the work; then increase the number of working modules, For example, when increasing to N+M, since the total input power of the photovoltaic power generation system remains unchanged, and the input power of each module group decreases from P/N to P/(N+M), therefore, for each module group, It can make its working point migrate from point A to point B. [0063] When calculating the overall conversion efficiency of the system, first, the efficiency of the module group at point A is 97.7%, and the efficiency of the module group at point B is 98.0%; Module group power loss P10ss= (100%-97.7%) *P/N = 2.3%*P/N, total system loss P10ss total= (100%-97.7%) *P/N*3N = 2.3% X3P; for point B, the power loss of a single module group is P10ss= (100%-98.0%)*P/(N+M)= 2.0%*P/(N+M), at this time, the total system loss P10ss tota1= (100%-98.0%) *P/ (N+M) *3 (N+M) =2.0% X3P; therefore, it can be obtained that the efficiency of the photovoltaic power generation system at point A is 97.7%, and the efficiency of the photovoltaic power generation system at point B is 98.0%. [0064] That
[ZH CN107104600B]: 模块化多电平变换器及电力电子变压器 [EN US11038434B2]: Modular multilevel converter and power electronic transformer [FR EP3400644A1]: CONVERTISSEUR MODULAIRE MULTINIVEAU ET TRANSFORMATEUR ÉLECTRONIQUE DE PUISSANCE [DE EP3400644A1]: MODULARER MEHRSTUFIGER WANDLER UND ELEKTRONISCHER LEISTUNGSTRANSFORMATOR | [ZH CN107104600B]: 本发明提供了一种模块化多电平变换器和一种电力电子变压器，所述模块化多电平变换器包括：一低频交流转直流模块，包括三个并联在输出端V、V之间的分支电路，每一分支电路由复数IGBT半桥电路串联而成，且所述分支电路中间位置的两个相邻的IGBT半桥电路的电联接点N与一电压输入端Vin相连；一直流转高频交流模块，连接在所述输出端V、V之间，所述直流转高频交流模块由复数IGBT半桥电路串联而成，所述直流转高频交流模块具有复数组输出端。本发明的模块化多电平变换器和电力电子变压器具有较小的体积、较低的成本和较佳的使用稳定性。 [EN US11038434B2]: A modular multilevel converter and a power electronic transformer is provided. The modular multilevel converter includes: a low-frequency AC to DC conversion module, comprising three branch circuits connected in parallel between output ends, each branch circuit being formed of multiple IGBT half-bridge circuits connected in series, and an electric coupling point of two adjacent IGBT half-bridge circuits in a middle position of the branch circuit being connected to a voltage input end Vin; a DC to high-frequency AC conversion module, connected between the output ends, the DC to high-frequency AC conversion module being formed of multiple IGBT half-bridge circuits connected in series, the DC to high-frequency AC conversion module having multiple sets of output ends. The MMC and power electronic transformer includes a smaller volume, lower cost and better stability in use. [FR EP3400644A1]: La présente invention concerne un convertisseur modulaire multiniveau (MMC) et un transformateur électronique de puissance, le convertisseur modulaire multiniveau comprenant : un module de conversion de courant alternatif basse fréquence en courant continu, comprenant trois circuits de branche connectés en parallèle entre des bornes de sortie V1, V2, chaque circuit de branche étant constitué de multiples circuits en demi-pont à IGBT connectés en série, et un point de couplage électrique N0 de deux circuits en demi-pont à IGBT adjacents dans une position centrale du circuit de branche étant connecté à une borne d'entrée de tension Vin ; et un module de conversion de courant continu en courant alternatif haute fréquence connecté entre les bornes de sortie V1, V2, le module de conversion de courant continu en courant alternatif haute fréquence étant constitué de multiples circuits en demi-pont à IGBT connectés en série, le module de conversion de courant continu en courant alternatif haute fréquence comprenant de multiples ensembles de bornes de sortie. Le MMC et le transformateur électronique de puissance de la présente invention présentent un plus petit volume, un plus bas coût et une meilleure stabilité lors de l'utilisation. | WO2017144430A1 | 2017-08-31 | EP2017053833W | 2017-02-21 | CN201610100169A, 2016-02-23 | CN107104600B: 2019-09-17 WO2017144430A1: 2017-08-31 EP3400644A1: 2018-11-14 US11038434B2: 2021-06-15 | SIEMENS AG 西门子公司 | YAO JILONG ZHAO YANFENG SHI LEI YAO JI LONG ZHAO YAN FENG | H02M5/458: I H02M5/45: I H02M7/483: I H02M7/48: I | H02M5/4585: I H02M1/008: A H02M5/225: A H02M1/0095: I H02M7/4835: A H02M7/483: I | WO2014001079A1 CN104393614A CN104410260A CN104638940A US2015155716A1 FR3017259A1 CN101258670A CN103762861A CN103762879A EP2845303A1 CN104796025A US2015250027A1 US2019296654A1 US2015311724A1 US2016231366A1 US2009161398A1 US6519169B1 US2015365003A1 CN101707443A WO2011141059A1 | CN110308347A CN110308347 110308347 CN112039314A CN112039314 112039314 | [ZH CN107104600B]: 1. 一种模块化多电平变换器（10)，其特征在于，所述模块化多电平变换器(10)包括： 一低频交流转直流模块(12)，包括三个并联在输出端(Vi、V2)之间的分支电路（122)，每 一分支电路（122)由复数IGBT半桥电路（123)串联而成，且所述分支电路（122)中间位置的 两个相邻的IGBT半桥电路(123)的电联接点(No)与一电压输入端(Vin)相连； 一直流转高频交流模块（13)，连接在所述输出端(Vi、V2)之间，所述直流转高频交流模 块(13)由复数IGBT半桥电路（123)串联而成，所述直流转高频交流模块（13)具有可设定的 复数组输出端，每组输出端包括一第一输出端(V3)和一第二输出端(V4)，所述第一输出端 (v3)与所述IGBT半桥电路（123)中的两个相邻的IGBT半桥电路（123)间的电联接点（m)相 连，所述第二输出端(V4)与所述IGBT半桥电路（123)中的另两个相邻的IGBT半桥电路（123) 间的电联接点(N2)相连。 2. 如权利要求1所述的模块化多电平变换器（10)，其特征在于，所述IGBT半桥电路 (123)包括一第一电容(Ci)、一第一IGBT管（IGBTD 及一第二IGBT管（IGBT2)，所述第一IGBT 管（IGBT0和所述第二IGBT管（IGBT2)串联后与所述第一电容（⑸并联;所述第一IGBT管 (IGBTD的集电极和所述第一电容(CD的正极相连，所述第一IGBT管（IGBTD的发射极和所 述第二IGBT管（IGBT2)的集电极相连并作为一第一连接端子(124)，所述第二IGBT管（IGBT2) 的发射极和所述第一电容(CD的负极相连并作为一第二连接端子(125)，所述第二连接端 子(125)与相邻的所述IGBT半桥电路(123)的所述第一连接端子(124)相连。 3. 如权利要求1所述的模块化多电平变换器(10)，其特征在于，所述直流转高频交流模 块(13)中每两个相邻的IGBT半桥电路（123)间的电联接点与所述第一输出端(V3)或所述第 二输出端㈤相连。 4. 如权利要求2所述的模块化多电平变换器（10)，其特征在于，所述低频交流转直流模 块(12)还包括偶数个电感(L)，所述电感(L)串联于所述分支电路（122)的中间位置，且所述 电感(L)串联在所述第一连接端子（124)和与其相邻的所述第二连接端子（125)之间，所述 偶数个电感(L)中间的电联接点(NQ)与所述电压输入端(Vin)相连。 5. —种电力电子变压器(100)，其特征在于，所述电力电子变压器(100)包括： 一模块化多电平变换器(10)，其包括： 一低频交流转直流模块（12)，包括三个并联在输出端(VuV2)之间的分支电路（122)，每 一分支电路（122)由复数IGBT半桥电路（123)串联而成，且所述分支电路（122)中间位置的 两个相邻的IGBT半桥电路(123)的电联接点(N0)与一电压输入端(Vin)相连； 一直流转高频交流模块（13)，连接在所述输出端(V^Vd之间，所述直流转高频交流模 块（13)由复数IGBT半桥电路（123)串联而成，所述直流转高频交流模块（13)具有可设定的 复数组输出端，每组输出端包括一第一输出端(V3)和一第二输出端(V4)，所述第一输出端 (V3)与所述IGBT半桥电路（123)中的两个相邻的IGBT半桥电路（123)间的电联接点(阶）相 连，所述第二输出端(V4)与所述IGBT半桥电路(123)中的另两个相邻的IGBT半桥电路(123) 间的电联接点(N2)相连； 复数高频变压模块(20)，每一高频变压模块(20)与对应的所述第一输出端(V3)及所述 第二输出端(V4)相连； 复数高频交流变低频交流模块(30)，每一高频交流变低频交流模块(30)与对应的所述 高频变压模块(20)相连。 6.如权利要求5所述的电力电子变压器（100)，其特征在于，所述IGBT半桥电路（123)包 括一第一电容（Ci)、一第一IGBT管（IGBTi)及一第二IGBT管（IGBT2)，所述第一IGBT管 (IGBT!)和所述第二IGBT管（IGBT2)串联后与所述第一电容（d)并联；所述第一IGBT管 (IGBT0的集电极和所述第一电容(Q)的正极相连，所述第一IGBT管（IGBT0的发射极和所 述第二IGBT管（IGBT2)的集电极相连并作为一第一连接端子(124)，所述第二IGBT管（IGBT2) 的发射极和所述第一电容(Ci)的负极相连并作为一第二连接端子(125)，所述第二连接端 子(125)与相邻的所述IGBT半桥电路(123)的所述第一连接端子(124)相连。 7. 如权利要求5所述的电力电子变压器（100)，其特征在于，所述直流转高频交流模块 (13)中每两个相邻的IGBT半桥电路（123)间的电联接点与所述第一输出端(V3)或所述第二 输出端(V4)相连。 8. 如权利要求6所述的电力电子变压器（100)，其特征在于，所述低频交流转直流模块 (12)还包括偶数个电感(L)，所述电感(L)串联于所述分支电路(122)的中间位置，且所述电 感(L)串联在所述第一连接端子（124)和与其相邻的所述第二连接端子（125)之间，所述偶 数个电感(L)中间的电联接点(No)与所述电压输入端(Vin)相连。 9. 如权利要求5所述的电力电子变压器（100)，其特征在于，所述高频变压模块(20)包 括一变压器0\)和一第二电容(C2)，所述变压器(TD的原边线圈与对应的所述第一输出端 (V3)及所述第二输出端(V4)相连，所述变压器(TD的副边线圈的输出端V5、V6与所述高频交 流变低频交流模块(30)相连。 10. 如权利要求9所述的电力电子变压器（100)，其特征在于，所述高频交流变低频交流 模块（30)包括复数二极管01、〇2、〇3、〇4、一第三电容（(：3)和复数1681'管1631'3、扣314、1〇81'5、 IGBT6、IGBT7、IGBT8,所述二极管DjP所述二极管D2构成一第一桥臂，所述二极管D3和所述二 极管D4构成一第二桥臂，所述二极管Di和所述二极管D2间的电联接点与所述输出端V5相连， 所述二极管D3和所述二极管D4间的电联接点与所述输出端V6相连;所述IGBT管IGBT3和所述 IGBT管IGBT4构成一第三桥臂，所述IGBT管IGBT5和所述IGBT管IGBT6构成一第四桥臂，所述 IGBT管IGBT^P所述IGBT管IGBTs构成一第五桥臂，所述第三电容(C3)、所述第一桥臂、所述 第二桥臂、所述第三桥臂、所述第四桥臂及所述第五桥臂并联，三个电压输出端(V〇ut)分别 与所述IGBT管IGBT3和所述IGBT管IGBT4间的电联接点、所述IGBT管IGBT5和所述IGBT管 IGBT6间的电联接点、所述IGBT管IGBT7和所述IGBT管IGBT8间的电联接点相连。 [EN US11038434B2]: 1. A modular multilevel converter (MMC), comprising: a low-frequency AC to DC conversion module including at least three branch circuits connected in parallel between first output ends, each branch circuit of the at least three branch circuits being formed of multiple first IGBT half-bridge circuits connected in series, and an electric coupling point of two adjacent first IGBT half-bridge circuits of the multiple first IGBT half-bridge circuits, in a middle position of the respective branch circuit, being connected to a voltage input end; anda DC to high-frequency AC conversion module, connected between the first output ends, the DC to high-frequency AC conversion module being formed of multiple second IGBT half-bridge circuits connected in series, the DC to high-frequency AC conversion module including multiple sets of second output ends, each set of second output ends including a third output end and a fourth output end, the third output end being directly connected to an electric coupling point between a first pair of two adjacent second IGBT half-bridge circuits of the multiple second IGBT half-bridge circuits, and the fourth output end being directly connected to another electric coupling point between a second pair of two adjacent second IGBT half-bridge circuits different from the first pair of two adjacent second IGBT half-bridge circuits. 2. The MMC of claim 1, wherein each of the IGBT half-bridge circuits comprises a first capacitor, a first IGBT and a second IGBT connected in series, the first IGBT and the second IGBT being further connected in parallel with the first capacitor; a collector of the first IGBT being connected to a positive terminal of the first capacitor, an emitter of the first IGBT being connected to a collector of the second IGBT and serving as a first connection terminal, and an emitter of the second IGBT being connected to a negative terminal of the first capacitor and serving as a second connection terminal; and the second connection terminal being connected to the first connection terminal of an adjacent IGBT half-bridge circuit. 3. The MMC of claim 2, wherein the electric coupling point between every two adjacent IGBT half-bridge circuits of the multiple IGBT half-bridge circuits in the DC to high-frequency AC conversion module is connected to the first output end or the second output end. 4. The MMC of claim 1, wherein the electric coupling point between every two adjacent IGBT half-bridge circuits of the multiple second IGBT half-bridge circuits in the DC to high-frequency AC conversion module is connected to the third output end or the fourth output end. 5. The MMC of claim 1, wherein the low-frequency AC to DC conversion module further includes an even number of inductors, the inductors being connected in series in middle positions of the branch circuits and the inductors being connected in series between a first connection terminal and a second connection terminal adjacent thereto, and wherein an electric coupling point, in a middle of the even number of inductors, is connected to the voltage input end. 6. The MMC of claim 1, wherein the at least three branch circuits are connected in parallel between the first output ends, and the DC to high-frequency AC conversion module includes multiple additional second sets of output ends, each additional set of second output ends including a third output end and a fourth output end. 7. A power electronic transformer, comprising: an MMC, including: a low-frequency AC to DC conversion module, including at least three branch circuits connected in parallel between first output ends, each branch circuit of the at least three branch circuits being formed of multiple first IGBT half-bridge circuits connected in series, and an electric coupling point of two adjacent first IGBT half-bridge circuits, in a middle position of the branch circuit, being connected to a voltage input end,a DC to high-frequency AC conversion module, connected between the first output ends, the DC to high-frequency AC conversion module being formed of multiple second IGBT half-bridge circuits connected in series, the DC to high-frequency AC conversion module including multiple sets of second output ends, each set of second output ends including a third output end and a fourth output end, the third output end being connected to an electric coupling point between two adjacent second IGBT half-bridge circuits of the multiple second IGBT half-bridge circuits, and the fourth output end being connected to an electric coupling point between another two adjacent second IGBT half-bridge circuits of the multiple second IGBT half-bridge circuits;multiple high-frequency transforming modules, each high-frequency transforming module, of the multiple high-frequency transforming modules, being connected to a corresponding third output end and a corresponding fourth output end; andmultiple high-frequency AC to low-frequency AC conversion modules, each high-frequency AC to low-frequency AC conversion module, of the multiple high-frequency AC to low-frequency AC conversion modules, being connected to a corresponding high-frequency transforming module of the of the multiple high-frequency transforming modules. 8. The power electronic transformer of claim 7, wherein each IGBT half-bridge circuit includes a first capacitor, a first IGBT and a second IGBT connected in series, the first IGBT and a second IGBT further being connected in parallel with the first capacitor; a collector of the first IGBT being connected to a positive terminal of the first capacitor, an emitter of the first IGBT being connected to a collector of the second IGBT and serving as a first connection terminal, and an emitter of the second IGBT being connected to a negative terminal of the first capacitor and serving as a second connection terminal, the second connection terminal being connected to the first connection terminal of an adjacent IGBT half-bridge circuit. 9. The power electronic transformer of claim 8, wherein each of the electric coupling points being between two adjacent second IGBT half-bridge circuits in the DC to high-frequency AC conversion module, are each connected to either the first output end or the second output end. 10. The power electronic transformer of claim 8, wherein the low-frequency AC to DC conversion module further includes an even number of inductors, the inductors being connected in series in middle positions of the branch circuits and the inductors being connected in series between a first connection terminal and a second connection terminal adjacent thereto, an electric coupling point in a middle of the even number of inductors being connected to the voltage input end. 11. The power electronic transformer of claim 8, wherein at least one of the high-frequency transforming modules includes a first transformer and a second capacitor, a primary coil of the transformer being connected to a corresponding third output end and a corresponding fourth output end, and output ends of a secondary coil of the first transformer being connected to the high-frequency AC to low-frequency AC conversion module. 12. The power electronic transformer of claim 7, wherein electric coupling points, each of the electric coupling points being between two adjacent IGBT half-bridge circuits in the DC to high-frequency AC conversion module, are each connected to either the third output end or the fourth output end. 13. The power electronic transformer of claim 7, wherein the low-frequency AC to DC conversion module further includes an even number of inductors, the inductors being connected in series in middle positions of the branch circuits and the inductors being connected in series between a first connection terminal and a second connection terminal adjacent thereto, an electric coupling point in a middle of the even number of inductors being connected to the voltage input end. 14. The power electronic transformer of claim 7, wherein at least one of the high-frequency transforming modules includes a first transformer and a second capacitor, a primary coil of the transformer being connected to a corresponding third output end and a corresponding fourth output end, and output ends of a secondary coil of the first transformer being connected to the high-frequency AC to low-frequency AC conversion module. 15. The power electronic transformer of claim 7, wherein at least one of the high-frequency AC to low-frequency AC conversion modules includes multiple diodes, a third capacitor and multiple additional IGBTs, a first two of the multiple diodes forming a first bridge arm and a second two of the multiple diodes forming a second bridge arm, an electric coupling point between one of the two first diodes and one of the two second diodes being connected to the output end, and an electric coupling point between another one of the two first diodes and one of the two second diodes being connected to the output end; a first IGBT of the multiple additional IGBTs and a second IGBT of the multiple additional IGBTs form a third bridge arm, a third IGBT of the multiple additional IGBTs and a fourth IGBT of the multiple additional IGBTs form a fourth bridge arm, a fifth IGBT of the multiple additional IGBTs and a sixth IGBT of the multiple additional IGBTs form a fifth bridge arm;the third capacitor, the first bridge arm, the second bridge arm, the third bridge arm, the fourth bridge arm and the fifth bridge arm are connected in parallel; andthree voltage output ends are each connected respectively to an electric coupling point between the first IGBT and the second IGBT of the multiple additional IGBTs, an electric coupling point between the third IGBT and the fourth IGBT of the multiple additional IGBTs, and an electric coupling point between the fifth IGBT and the sixth IGBT of the multiple additional IGBTs. | [ZH CN107104600B]: 模块化多电平变换器及电力电子变压器 技术领域 [0001]本发明涉及变压器技术领域，特别涉及一种模块化多电平变换器和一种电力电子 变压器。 背景技术 [0002]变压器是电力系统所用到的关键装置。在电力系统中，变压器将发电厂发出的电 压升高后进行远距离输电，到达目的地以后再用变压器将电压降低以供用户使用。因此，在 整个电力系统中，变压器是最为常见和重要的装置之一。 [0003]请参见图1，传统的变压器包括三个主要部分，分别为铁芯、原边线圈和副边线圈， 原边线圈和副边线圈分别绕设于铁芯上，原边线圈与电源连接，副边线圈与负载连接。铁芯 一般由铁制成，铁芯为变压器的原边和副边提供磁回路，且将原边和副边隔离。然而，此种 变压器体积大，重量重，一旦原边侧的电压波形确定，副边侧的电压波形也就确定，不可控， 波形大小、频率和质量均无法调节。另外，此种变压器没有冗余，当出现问题时，需要关闭进 行维修。 [0004]随着用户需求的变化，出现越来越多的非线性负载和谐波负载，负载的需求越来 越大，且具有间歇性和多样性，电力电子变压器应运而生。一种现有的电力电子变压器，由 高压级、隔离级和低压级三级组成，所述电力电子变压器采用模块化级联结构。为了使原边 电流谐波较小，在每一级联模块下需加设移相变压器，然而，移相变压器的体积大，成本较 高。 发明内容 [0005] 有鉴于此，本发明的目的是提出一种模块化多电平变换器和一种电力电子变压 器，具有较小的体积、较低的成本和较佳的使用稳定性。 [0006] 本发明提供了一种模块化多电平变换器，其包括： [0007] 一低频交流转直流模块，包括三个并联在输出端Vi、v2之间的分支电路，每一分支 电路由复数IGBT半桥电路串联而成，且所述分支电路中间位置的两个相邻的IGBT半桥电路 的电联接点No与一电压输入端Vin相连； [0008] 一直流转高频交流模块，连接在所述输出端Vi、V2之间，所述直流转高频交流模块 由复数IGBT半桥电路串联而成，所述直流转高频交流模块具有复数组输出端，每组输出端 包括一第一输出端V3和一第二输出端V4,所述第一输出端V3与所述IGBT半桥电路中的两个 相邻的IGBT半桥电路间的电联接点阶相连，所述第二输出端V4与所述IGBT半桥电路中的另 两个相邻的IGBT半桥电路间的电联接点N2相连。 [0009] 在模块化多电平变换器的一种示意性实施例中，所述IGBT半桥电路包括一第一电 容心、一第一 IGBT管IGBTi&amp;amp;—第二IGBT管IGBT2,所述第一 IGBT管IGBTi和所述第二IGBT管 IGBT2串联后与所述第一电容心并联;所述第一 IGBT管IGBT!的集电极和所述第一电容Ci的 正极相连，所述第一 IGBT管IGBT!的发射极和所述第二IGBT管IGBT2的集电极相连并作为一 第一连接端子，所述第二IGBT管IGBT2的发射极和所述第一电容&amp;amp;的负极相连并作为一第二 连接端子，所述第二连接端子与相邻的所述IGBT半桥电路的所述第一连接端子相连。 [0010] 在模块化多电平变换器的一种示意性实施例中，所述直流转高频交流模块中每两 个相邻的IGBT半桥电路间的电联接点与所述第一输出端V3或所述第二输出端V4相连。 [0011] 在模块化多电平变换器的一种示意性实施例中，所述低频交流转直流模块还包括 偶数个电感L，所述电感L串联于所述分支电路的中间位置，且所述电感L串联在所述第一连 接端子和与其相邻的所述第二连接端子之间，所述偶数个电感L中间的电联接点No与所述 电压输入端Vin相连。 [0012] 本发明还提供了一种电力电子变压器，其包括:上述的模块化多电平变换器； [0013] 复数高频变压模块，每一高频变压模块与对应的所述第一输出端V3及所述第二输 出端V4相连； [0014] 复数高频交流变低频交流模块，每一高频交流变低频交流模块与对应的所述高频 变压模块相连。 [0015] 在电力电子变压器的一种示意性实施例中，所述高频变压模块包括一变压器1\和 一第二电容C2,所述变压器1\的原边线圈与对应的所述第一输出端v3及所述第二输出端V4 相连，所述变压器的副边线圈的输出端v5、v6与所述高频交流变低频交流模块相连。 [0016] 在电力电子变压器的一种示意性实施例中，所述高频交流变低频交流模块包括复 数二极管 01、02、03、04、一第三电容〇3和复数1681'管1681'3、10814、1031'5、1681'6、1031'7、168!'8， 所述二极管Di和所述二极管D2构成一第一桥臂，所述二极管D3和所述二极管D4构成一第二 桥臂，所述二极管Di和所述二极管D2间的电联接点与所述输出端V5相连，所述二极管D3和所 述二极管04间的电联接点与所述输出端V6相连;所述IGBT管IGBT3和所述IGBT管IGBT4构成 一第三桥臂，所述IGBT管IGBT5和所述IGBT管IGBTe构成一第四桥臂，所述IGBT管IGBTV和所 述IGBT管IGBTs构成一第五桥臂，所述第三电容C3、所述第一桥臂、所述第二桥臂、所述第三 桥臂、所述第四桥臂及所述第五桥臂并联，三个电压输出端Vout分别与所述IGBT管IGBT3和 所述IGBT管IGBT4间的电联接点、分别与所述IGBT管IGBT5和所述IGBT管IGBTe间的电联接 点、所述IGBT管IGBT7和所述IGBT管IGBT8间的电联接点相连。 [0017] 从上述方案中可以看出，在本发明的模块化多电平变换器及电力电子变压器中， 低频交流转直流模块和直流转高频交流模块均包括复数串联的IGBT半桥电路，采用IGBT半 桥电路而无需设置移相变压器，从而有利于减小体积，降低成本;此外，直流转高频交流模 块具有复数输出端，每一输出端的电压数值可依照实际需求设定，当一组输出端出现故障 时，其他输出端可正常使用，而不需要立即停机维修，有利于降低成本，提升使用的稳定性。 附图说明 [0018] 下面将通过参照附图详细描述本发明的优选实施例，使本领域的普通技术人员更 清楚本发明的上述及其它特征和优点，附图中： [0019] 图1为传统的变压器的结构示意图。 [0020] 图2为本发明一实施例的电力电子变压器的架构示意图。 [0021] 图3为图2所示的电力电子变压器的模块化多电平变换器的一实施例的拓扑结构 图。 [0022]图4为图3所示的模块化多电平变换器的IGBT半桥电路的一实施例的电路图。 [0023]图5为图2所示的电力电子变压器的高频变压模块和高频交流变低频交流模块的 一实施例的电路图。 [0024] 在上述附图中，所采用的附图标记如下： [0025] 1〇〇 电力电子变压器 [0026] 10 模块化多电平变换器 [0027] 12 低频交流转直流模块 [0028] 122 分支电路 [0029] 123 IGBT 半桥电路 [0030] 124 第一连接端子 [0031] 125 第二连接端子 [0032] 13 直流转高频交流模块 [0033] 20 高频变压模块 [0034] 30 高频交流变低频交流模块 [0035] N〇、Ni、N2 电联接点 [0036] Vin 电压输入端 [0037] L 电感 [0038] IGBTi 第一 IGBT 管 [0039] IGBT2 第二 IGBT 管 [0040] IGBT3、IGBT4、IGBT5、 [0041] IGBT 管 [0042] IGBT6、IGBT7、IGBT8 [0043] Ci 第一电容 [0044] C2 第二电容 [0045] C3 第三电容 [0046] Vi,V2&gt;V5&gt;V6 输出端 [0047] V3 第一输出端 [0048] V4 第二输出端 [0049] Di、D2、D3、D4 二极管 [0050] Vout 电压输出端 具体实施方式 [0051] 为使本发明的目的、技术方案和优点更加清楚，以下举实施例对本发明进一步详 细说明。 [0052] 图2为本发明一实施例的电力电子变压器的架构示意图。请参见图2,本实施例的 电力电子变压器1〇〇包括模块化多电平变换器(Modular Multilevel Converter，MMC) 10、 复数高频变压模块2〇和复数高频交流变低频交流模块30,其中，模块化多电平变换器10包 括低频交流转直流模块12和直流转高频交流模块13。 [0053]具体地，图3为图2所示的电力电子变压器的模块化多电平变换器的一实施例的拓 扑结构图，请参见图3,低频交流转直流模块12包括三个并联在输出端之间的分支电路 122,每一分支电路122由复数IGBT半桥电路123串联而成，且分支电路122中间位置的两个 相邻的IGBT半桥电路123的电联接点NQ与一电压输入端Vin相连。其中，电压输入端Vin为三 个，三个电压输入端Vin分别对应于二相电的一个相。IGBT (Insulated Gate Bipolar Transistor)是指绝缘栅双极型晶体管，IGBT是由BJT (双极型三极管)和MOS (绝缘栅型场效 应管)组成的复合全控型电压驱动式功率半导体器件，兼有M0SFET的高输入阻抗和GTR的低 导通压降的优点。 [0054]图4为图3所示的模块化多电平变换器的IGBT半桥电路的一实施例的电路图。请一 并参见图4, IGBT半桥电路123包括第一电容Ci、第一IGBT管IGBTi及第二IGBT管IGBT2。第一 IGBT管IGBT1和第二IGBT管IGBT2串联后与第一电容Ci并联。第一 IGBT管IGBI\的集电极和第 一电容G的正极相连，第一 IGBT管IGBTj^发射极和第二IGBT管IGBT2的集电极相连并作为 一第一连接端子124,第二IGBT管IGBT2的发射极和第一电容Q的负极相连并作为一第二连 接端子125,第二连接端子125与相邻的IGBT半桥电路123的第一连接端子124相连。 [0055]需要说明的是，IGBT半桥电路123所包含的电子元件及电子元件间的连接不以图4 为限，IGBT半桥电路123的结构可依照实际需求任意设定。 [0056]低频交流转直流模块12还包括偶数个电感L，电感L串联于分支电路122的中间位 置的两个相邻的IGBT半桥电路123之间，且电感L串联在第一连接端子124和与其相邻的所 述第二连接端子125之间，所述偶数个电感L中间的电联接点与所述电压输入端Vin相连。换 言之，对于每一分支电路122,图3所示的电联接点No位于分支电路122的正中间，分支电路 122上的电子元器件相对于电联接点No为对称关系。在本实施例中，每一分支电路122包括 两个电感L，两个电感L分别位于电联接点No的上方和下方。 [0057] 直流转高频交流模块13连接在输出端Vi、V2之间。直流转高频交流模块13由复数 IGBT半桥电路123串联而成，直流转高频交流模块13具有复数组输出端，每组输出端包括第 一输出端V3和第二输出端V4。第一输出端V3与IGBT半桥电路123中的两个相邻的IGBT半桥电 路123间的电联接点阶相连，第二输出端V4与IGBT半桥电路123中的另两个相邻的IGBT半桥 电路123间的电联接点N2相连。 [0058] 在本实施例中，直流转高频交流模块13中每两个相邻的IGBT半桥电路123的电联 接点与第一输出端V3或第二输出端V4相连，从图3中可以看出，在直流转高频交流模块13的 从上至下的IGBT半桥电路123中，第一个IGBT半桥电路123和第二个IGBT半桥电路123间的 电联接点阶与第一输出端V3相连，第三个IGBT半桥电路123和第四个IGBT半桥电路123间的 电联接点％与第二输出端V4相连;也就是说，在本实施例中，每两个相邻的IGBT半桥电路123 的电联接点作为一输出端，但本发明不以此为限，在其他实施例中，第一输出端V3和第二输 出端V4的设置位置可依照实际对输出电压的需求而定。例如，第一个IGBT半桥电路123和第 二个IGBT半桥电路123间的电联接点作为第一输出端，第四个IGBT半桥电路123和第五个 IGBT半桥电路m间的电联接点作为第二输出端，相邻的第三个IGBT半桥电路123和第四个 IGBT半桥电路123间不设置输出端。 [0059]图5为图2所示的电力电子变压器的高频变压模块和高频交流变低频交流模块的 一实施例的电路图。请参见图5,高频变压模块20包括变压器Ti和第二电容C2,变压器Ti的原 边线圈与对应的第一输出端v3及第二输出端v4相连，变压器^的副边线圈的输出端v5、v6与 高频交流变低频交流模块30相连。 [0060]高频交流变低频交流模块30包括复数二极管〇1、〇2、〇3、〇4、第三电容€3和复数108丁 管 IGBT3、IGBT4、IGBT5、IGBT6、IGBT7、IGBT8，二极管 DdP二极管 D2 构成一第一桥臂，二极管 D3 和二极管D4构成一第二桥臂，二极管队和二极管D2间的电联接点与输出端V5相连，二极管D3 和二极管D4间的电联接点与输出端V6相连。IGBT管IGBT3和IGBT管IGBT4构成一第三桥臂， IGBT管IGBT5和IGBT管IGBT6构成一第四桥臂，IGBT管IGBT7和IGBT管IGBT8构成一第五桥臂， 第三电容C3、第一桥臂、第二桥臂、第三桥臂、第四桥臂及第五桥臂并联，三个电压输出端 Vout分别与IGBT管IGBT3和IGBT管IGBT4间的电联接点、分别与IGBT管IGBT5和IGBT管IGBTe 间的电联接点、IGBT管IGBT7和IGBT管IGBTs间的电联接点相连。 [0061]工作时，由于低频交流转直流模块12的三个分支电路122分别包括复数IGBT半桥 电路I23,当三相电从电压输入端Vin输入时，通过第一IGBT管IGBTi和第二IGBT管IGBT2的导 通或截止，可将低频交流电转换为直流电，且直流电由输出端Vi、V2输出。直流电由输出端 VuVs输入直流转高频交流模块13,直流转高频交流模块13由复数IGBT半桥电路123串联而 成，对于每一 IGBT半桥电路U3,当第一 IGBT管IGBTi导通时，第二IGBT管IGBT2截止，第一连 接端子124和第二连接端子1¾间的电压即等于第一电容Q的电压，输出电压大于〇;当第一 IGBT管IGBTi截止时，第二IGBT管IGBT2导通，第一连接端子1M和第二连接端子125间短路， 输出电压等于0。由于第二连接端子125与相邻的IGBT半桥电路123的第一连接端子124相 连，而第一输出端V3或第二输出端V4与相邻的IGBT半桥电路I23间的电联接点相连，第一输 出端V3和第二输出端V4间的电压总大于或等于0。与此同时，直流转高频交流模块13将直流 电转换为高频交流电，并设有多组输出端V3、V4。输出端V3、V4的数量及输出的电压值可依照 实际情况任意设定。 [0062]高频变压模块2〇对输出端V3、V4输出的高频交流电进行高压隔离，最后，高频交流 变低频交流模块3〇将由高频变压模块20的输出端V5、V6输出的高频交流电转换为低频交流 电，并使所述低频交流电由电压输出端Vout输出。 [0063]本发明的模块化多电平变换器及电力电子变压器至少具有以下的优点： [0064] 1 •在本发明的模块化多电平变换器及电力电子变压器中，低频交流转直流模块和 直流转高频交流模块均包括复数串联的IGBT半桥电路，采用IGBT半桥电路而无需设置移相 变压器，从而有利于减小体积，降低成本;此外，直流转高频交流模块具有复数输出端，每一 输出端的电压数值可依照实际需求设定，当一组输出端出现故障时，其他输出端可正常使 用，而不需要立即停机维修，有利于降低成本，提升使用的稳定性。 [0065] 2 •在本发明的模块化多电平变换器及电力电子变压器的一个实施例中，电感L串 联于分支电路的中间位置，且电感L串联在第一连接端子和与其相邻的第二连接端子之间， 偶数个电感L中间的电联接点N〇与电压输入端Vin相连，从而使得输入电压更加稳定。 [0066] 3 •在本发明的模块化多电平变换器及电力电子变压器的一个实施例中，低频交流 转直流模块和直流转高频交流模块均设置有IGBT半桥电路，频交流转直流模块可有效将低 频交流电转换为直流电；IGBT半桥电路可使直流转高频交流模块输出的电压值大于或等于 0,且可依照实际情况作调整，以满足用户的不同需求。 [0067] 以上所述仅为本发明的较佳实施例而己，并不用以限制本发明，凡在本发明的精 神和原则之内，所作的任何修改、等同替换、改进等，均应包含在本发明的保护范围之内。 [EN US11038434B2]: PRIORITY STATEMENT This application is the national phase under 35 U.S.C. § 371 of PCT International Application No. PCT/EP2017/053833 which has an International filing date of Feb. 21, 2017, which designated the United States of America and which claims priority to Chinese patent application number CN 201610100169.3 filed Feb. 23, 2016, the entire contents of which are hereby incorporated herein by reference. FIELD An embodiment of present invention relates to the technical field of transformers, in particular to a modular multilevel converter (MMC) and a power electronic transformer. BACKGROUND ART A transformer is a key apparatus used in a power system. In a power system, after a transformer increases a voltage outputted by a power station, the electricity is transmitted over a long distance, and once it has arrived at its destination, a transformer is used again to reduce the voltage for use by a user. Thus, the transformer is one of the most common and important apparatuses in the entire power system. Referring to FIG. 1, a conventional transformer comprises three main parts, namely a core, a primary coil and a secondary coil. The primary coil and secondary coil are wound separately onto the core, the primary coil being connected to a power source, and the secondary coil being connected to a load. The core, which is generally made of iron, provides a magnetic circuit for the primary side and secondary side of the transformer, and isolates the primary side from the secondary side. However, such a transformer is large in volume and heavy, and once the voltage waveform of the primary side is determined, the voltage waveform of the secondary side is also determined, and cannot be controlled; the waveform size, frequency and quality cannot be regulated. Furthermore, such a transformer lacks redundancy; if a problem should occur, it must be shut down to be overhauled. As user demands change, more and more non-linear loads and harmonic loads are arising; the load demands are ever greater, and are intermittent and diverse in nature. In response to these conditions, power electronic transformers have appeared. An existing power electronic transformer consists of three stages, namely a high-voltage stage, an isolation stage and a low-voltage stage, and employs a modular cascaded structure. In order to make current harmonics on the primary side smaller, a phase-shifting transformer must be added under each cascaded module. However, a phase-shifting transformer has a large volume and a high cost. SUMMARY At least one embodiment of the present invention proposes an MMC and a power electronic transformer with a smaller volume, lower cost and better stability in use. At least one embodiment of the present invention provides an MMC including a low-frequency AC to DC conversion module having three branch circuits connected in parallel between output ends V1, V2, each branch circuit being formed of multiple IGBT half-bridge circuits connected in series, and an electric coupling point N0 of two adjacent IGBT half-bridge circuits in a middle position of the branch circuit being connected to a voltage input end Vin and a DC to high-frequency AC conversion module, connected between the output ends V1V2, the DC to high-frequency AC conversion module being formed of multiple IGBT half-bridge circuits connected in series. The DC to high-frequency AC conversion module has multiple sets of output ends, each set of output ends include a first output end V3 and a second output end V4, the first output end V3 being connected to an electric coupling point N1 between two adjacent IGBT half-bridge circuits amongst the IGBT half-bridge circuits, and the second output end V4 being connected to an electric coupling point N2 between another two adjacent IGBT half-bridge circuits amongst the IGBT half-bridge circuits. At least one embodiment of the present invention provides a power electronic transformer, including an MMC, multiple high-frequency transforming modules, each high-frequency transforming module being connected to the corresponding first output end V3 and the corresponding second output end V4, and multiple high-frequency AC to low-frequency AC conversion modules, each high-frequency AC to low-frequency AC conversion module being connected to the corresponding high-frequency transforming module. BRIEF DESCRIPTION OF THE DRAWINGS Preferred embodiments of the present invention are described in detail below with reference to the accompanying drawings, to give those skilled in the art a clearer understanding of the abovementioned and other features and advantages of the present invention. Drawings: FIG. 1 is a structural schematic diagram of a conventional transformer. FIG. 2 is a structural schematic diagram of the power electronic transformer in an embodiment of the present invention. FIG. 3 is a topological structural diagram of an embodiment of the MMC of the power electronic transformer shown in FIG. 2. FIG. 4 is a circuit diagram of an embodiment of an IGBT half-bridge circuit of the MMC shown in FIG. 3. FIG. 5 is a circuit diagram of an embodiment of the high-frequency transforming module and high-frequency AC to low-frequency AC conversion module of the power electronic transformer shown in FIG. 2. The labels used in the abovementioned accompanying drawings are as follows: 100 power electronic transformer10 MMC12 low-frequency AC to DC conversion module122 branch circuit123 IGBT half-bridge circuit124 first connection terminal125 second connection terminal13 DC to high-frequency AC conversion module20 high-frequency transforming module30 high-frequency AC to low-frequency AC conversion moduleN0, N1, N2 electric coupling pointsVin voltage input endL inductorIGBT1 first IGBTIGBT2 second IGBTIGBT3, IGBT4, IGBT5, IGBT6, IGBT7, IGBT8 IGBTsC1 first capacitorC2 second capacitorC3 third capacitorV1, V2, V5, V6 output endsV3 first output endV4 second output endD1, D2, D3, D4 diodesVout voltage output end DETAILED DESCRIPTION OF EXAMPLE EMBODIMENTS At least one embodiment of the present invention provides an MMC, including a low-frequency AC to DC conversion module having three branch circuits connected in parallel between output ends V1, V2, each branch circuit being formed of multiple IGBT half-bridge circuits connected in series, and an electric coupling point No of two adjacent IGBT half-bridge circuits in a middle position of the branch circuit being connected to a voltage input end Vin. The MMC also has a DC to high-frequency AC conversion module, connected between the output ends V1V2, the DC to high-frequency AC conversion module being formed of multiple IGBT half-bridge circuits connected in series, the DC to high-frequency AC conversion module having multiple sets of output ends, each set of output ends comprising a first output end V3 and a second output end V4. The first output end V3 is connected to an electric coupling point N1 between two adjacent IGBT half-bridge circuits amongst the IGBT half-bridge circuits, and the second output end V4 is connected to an electric coupling point N2 between another two adjacent IGBT half-bridge circuits amongst the IGBT half-bridge circuits. In a schematic embodiment of the MMC, the IGBT half-bridge circuit comprises a first capacitor C1, a first IGBT (IGBT1) and a second IGBT (IGBT2). The first IGBT (IGBT1) and the second IGBT (IGBT2) are connected in series and then connected in parallel with the first capacitor C1. A collector of the first IGBT (IGBT1) is connected to a positive terminal of the first capacitor C1, an emitter of the first IGBT (IGBT1) is connected to a collector of the second IGBT (IGBT2) and serves as a first connection terminal, and an emitter of the second IGBT (IGBT2) is connected to a negative terminal of the first capacitor C1 and serves as a second connection terminal. The second connection terminal is connected to the first connection terminal of the adjacent IGBT half-bridge circuit. In a schematic embodiment of the MMC, the electric coupling point between every two adjacent IGBT half-bridge circuits in the DC to high-frequency AC conversion module is connected to the first output end V3 or the second output end V4. In a schematic embodiment of the MMC, the low-frequency AC to DC conversion module also comprises an even number of inductors L, the inductors L being connected in series in middle positions of the branch circuits; moreover, the inductors L are connected in series between the first connection terminal and the second connection terminal adjacent thereto, and an electric coupling point N0 in the middle of the even number of inductors L is connected to the voltage input end Vin. At least one embodiment of the present invention provides a power electronic transformer, including an MMC, multiple high-frequency transforming modules, each high-frequency transforming module being connected to the corresponding first output end V3 and the corresponding second output end V4, and multiple high-frequency AC to low-frequency AC conversion modules, each high-frequency AC to low-frequency AC conversion module being connected to the corresponding high-frequency transforming module. In a schematic embodiment of the power electronic transformer, the high-frequency transforming module comprises a transformer T1 and a second capacitor C2, the primary coil of the transformer T1 is connected to the corresponding first output end V3 and the corresponding second output end V4, and output ends V5, V6 of the secondary coil of the transformer TI are connected to the high-frequency AC to low-frequency AC conversion module. In a schematic embodiment of the power electronic transformer, the high-frequency AC to low-frequency AC conversion module has multiple diodes (D1, D2, D3, D4), a third capacitor C3 and multiple IGBTs (IGBT3, IGBTa, IGBT5, IGBT6, IGBT7, IGBT8). The diode D1 and the diode D2 form a first bridge arm and the diode D3 and the diode D4 form a second bridge arm. An electric coupling point between the diode D1 and the diode D2 is connected to the output end V5, and an electric coupling point between the diode D3 and the diode D4 is connected to the output end V6. The IGBT (IGBT3) and the IGBT (IGBT4) form a third bridge arm, the IGBT (IGBT5) and the IGBT (IGBT6) form a fourth bridge arm, and the IGBT (IGBT7) and the IGBT (IGBT8) form a fifth bridge arm. The third capacitor C3, the first bridge arm, the second bridge arm, the third bridge arm, the fourth bridge arm and the fifth bridge arm are connected in parallel. Three voltage output ends (Vout) are connected respectively to an electric coupling point between the IGBT (IGBT3) and the IGBT (IGBT4), an electric coupling point between the IGBT (IGBT5) and the IGBT (IGBT6), and an electric coupling point between the IGBT (IGBT7) and the IGBT (IGBT8). It can be seen from the solution above that in the MMC and power electronic transformer of the present invention, the low-frequency AC to DC conversion module and the DC to high-frequency AC conversion module both comprise multiple IGBT half-bridge circuits connected in series. IGBT half-bridge circuits are used, with no need for a phase-shifting transformer; this helps to reduce volume and costs. Furthermore, the DC to high-frequency AC conversion module has multiple output ends, and the voltage value of each output end may be set according to actual demands. When one set of output ends develops a fault, the other output ends can be used normally, with no need for immediate shutdown and overhaul; this helps to lower costs, and increases stability of use. In order to clarify the object, technical solution and advantages of the present invention, the present invention is explained in further detail below by way of embodiments. FIG. 2 is a structural schematic diagram of the power electronic transformer in an embodiment of the present invention. Referring to FIG. 2, the power electronic transformer 100 in this embodiment comprises a modular multilevel converter (MMC) 10, multiple high-frequency transforming modules 20 and multiple high-frequency AC to low-frequency AC conversion modules 30, wherein the MMC 10 comprises a low-frequency AC to DC conversion module 12 and a DC to high-frequency AC conversion module 13. Specifically, FIG. 3 is a topological structural diagram of an embodiment of the MMC of the power electronic transformer shown in FIG. 2. Referring to FIG. 3, the low-frequency AC to DC conversion module 12 comprises three branch circuits 122 connected in parallel between output ends V1 and V2. Each branch circuit 122 is formed of multiple IGBT half-bridge circuits 123 connected in series, and an electric coupling point N0 of two adjacent IGBT half-bridge circuits 123 in a middle position of the branch circuit 122 is connected to a voltage input end Vin. There are three voltage input ends Vin, each corresponding to one phase of three-phase power. IGBT means Insulated Gate Bipolar Transistor. An IGBT is a compound fully-controlled voltage-driven power semiconductor device formed from a BJT (bipolar junction transistor) and a MOS (insulated gate field effect transistor), and combines the advantages of high input impedance of a MOSFET and low conduction voltage drop of a GTR. FIG. 4 is a circuit diagram of an embodiment of an IGBT half-bridge circuit of the MMC shown in FIG. 3. Referring to FIG. 4 too, the IGBT half-bridge circuit 123 comprises a first capacitor C1, a first IGBT (IGBT1) and a second IGBT (IGBT2). The first IGBT (IGBT1) and second IGBT (IGBT2) are connected in series, and then connected in parallel with the first capacitor C1. The collector of the first IGBT (IGBT1) is connected to a positive terminal of the first capacitor C1, the emitter of the first IGBT (IGBT1) is connected to the collector of the second IGBT (IGBT2) and serves as a first connection terminal 124, and the emitter of the second IGBT (IGBT2) is connected to a negative terminal of the first capacitor C1 and serves as a second connection terminal 125; the second connection terminal 125 is connected to the first connection terminal 124 of an adjacent IGBT half-bridge circuit 123. It must be explained that the electronic elements contained in the IGBT half-bridge circuit 123, and the connections between the electronic elements, are not restricted to those shown in FIG. 4. The structure of the IGBT half-bridge circuit 123 may be set according to actual demands. The low-frequency AC to DC conversion module 12 also comprises an even number of inductors L. The inductors L are connected in series between the two adjacent IGBT half-bridge circuits 123 in the middle positions of the branch circuits 122. Moreover, the inductors L are connected in series between the first connection terminal 124 and the second connection terminal 125 adjacent thereto. An electric coupling point in the middle of the even number of inductors L is connected to the voltage input end Vin. In other words, for each branch circuit 122, the electric coupling point N0 shown in FIG. 3 is located in the exact middle of the branch circuit 122, with the electronic components on the branch circuit 122 being in a symmetrical relationship relative to the electric coupling point N0. In this embodiment, each branch circuit 122 comprises two inductors L, which are located above and below the electric coupling point N0 respectively. The DC to high-frequency AC conversion module 13 is connected between output ends V1 and V2. The DC to high-frequency AC conversion module 13 is formed of multiple IGBT half-bridge circuits 123 connected in series. The DC to high-frequency AC conversion module 13 has multiple sets of output ends, each set of output ends comprising a first output end V3 and a second output end V4. The first output end V3 is connected to an electric coupling point N1 between two adjacent IGBT half-bridge circuits 123 amongst the IGBT half-bridge circuits 123; the second output end V is connected to an electric coupling point N2 between another two adjacent IGBT half-bridge circuits 123 amongst the IGBT half-bridge circuits 123. In this embodiment, the electric coupling point of every two adjacent IGBT half-bridge circuits 123 in the DC to high-frequency AC conversion module 13 is connected to a first output end V3 or second output end V4. It can be seen from FIG. 3 that, amongst the IGBT half-bridge circuits 123 of the DC to high-frequency AC conversion module 13 counted from top to bottom, the electric coupling point i between the first IGBT half-bridge circuit 123 and second IGBT half-bridge circuit 123 is connected to a first output end V3, while the electric coupling point N2 between the third IGBT half-bridge circuit 123 and fourth IGBT half-bridge circuit 123 is connected to a second output end V4. In other words, in this embodiment, the electric coupling point of every two adjacent IGBT half-bridge circuits 123 serves as an output end. However, the present invention is not restricted to this; in other embodiments, the positions of the first output end V3 and second output end V4 may be determined according to actual demands on output voltages. For example, the electric coupling point between the first IGBT half-bridge circuit 123 and second IGBT half-bridge circuit 123 serves as a first output end, and the electric coupling point between the fourth IGBT half-bridge circuit 123 and fifth IGBT half-bridge circuit 123 serves as a second output end; no output end is disposed between the third IGBT half-bridge circuit 123 and fourth IGBT half-bridge circuit 123 which are adjacent to each other. FIG. 5 is a circuit diagram of an embodiment of the high-frequency transforming module and high-frequency AC to low-frequency AC conversion module of the power electronic transformer shown in FIG. 2. Referring to FIG. 5, the high-frequency transforming module 20 comprises a transformer T1 and a second capacitor C2. The primary coil of the transformer T1 is connected to a corresponding first output end V3 and corresponding second output end V4, while output ends V5 and V6 of the secondary coil of the transformer T1 are connected to the high-frequency AC to low-frequency AC conversion module 30. The high-frequency AC to low-frequency AC conversion module 30 comprises multiple diodes D1, D2, D3 and D4, a third capacitor C3 and multiple IGBTs (IGBT3, IGBT4, IGBT5, IGBT6, IGBT7 and IGBT8). Diode D1 and diode D2 form a first bridge arm, while diode D3 and diode D4 form a second bridge arm. An electric coupling point between diode D1 and diode D2 is connected to output end V5, while an electric coupling point between diode D3 and diode D4 is connected to output end V6. The IGBT (IGBT3) and the IGBT (IGBT4) form a third bridge arm, the IGBT (IGBT5) and the IGBT (IGBT6) form a fourth bridge arm, the IGBT (IGBT7) and the IGBT (IGBT8) form a fifth bridge arm. The third capacitor C3, first bridge arm, second bridge arm, third bridge arm, fourth bridge arm and fifth bridge arm are connected in parallel. Three voltage output ends Vout are connected respectively to an electric coupling point between the IGBT (IGBT3) and the IGBT (IGBT4), an electric coupling point between the IGBT (IGBT5) and the IGBT (IGBT6), and an electric coupling point between the IGBT (IGBT7) and the IGBT (IGBT8). During operation, since the three branch circuits 122 of the low-frequency AC to DC conversion module 12 comprise multiple IGBT half-bridge circuits 123, when three-phase power is inputted via the voltage input ends Vin, low-frequency AC power can be converted to DC power through the on/off switching of the first IGBT (IGBT1) and the second IGBT (IGBT2), and the DC power is outputted via the output ends V1 and V2. The DC power is inputted via the output ends V1 and V2 to the DC to high-frequency AC conversion module 13. The DC to high-frequency AC conversion module 13 is formed of multiple IGBT half-bridge circuits 123 connected in series. In each IGBT half-bridge circuit 123, when the first IGBT (IGBT1) is conducting, the second IGBT (IGBT2) is shut off; the voltage between the first connection terminal 124 and second connection terminal 125 is then equal to the voltage of the first capacitor C1, so the output voltage is greater than 0. When the first IGBT (IGBT1) is shut off, the second IGBT (IGBT2) is conducting; there is a short circuit between the first connection terminal 124 and second connection terminal 125, so the output voltage is equal to 0. Since the second connection terminal 125 is connected to the first connection terminal 124 of an adjacent IGBT half-bridge circuit 123, and the first output end V3 or second output end V4 is connected to the electric coupling point between adjacent IGBT half-bridge circuits 123, the voltage between the first output end V3 and second output end V4 is always greater than or equal to 0. At the same time, the DC to high-frequency AC conversion module 13 converts DC power to high-frequency AC power, and is provided with multiple sets of output ends V3 and V4. The number of output ends V3 and V4 and the outputted voltage values may be set arbitrarily according to actual circumstances. The high-frequency transforming module 20 performs high-voltage isolation on the high-frequency AC power outputted by output ends V3 and V4. Finally, the high-frequency AC to low-frequency AC conversion module 30 converts high-frequency AC power outputted by output ends V5 and V6 of the high-frequency transforming module 20 to low-frequency AC power, and outputs this low-frequency AC power via the voltage output ends Vout. The MMC and power electronic transformer of the present invention at least have the following advantages: 1. In the MMC and power electronic transformer of the present invention, the low-frequency AC to DC conversion module and the DC to high-frequency AC conversion module both comprise multiple IGBT half-bridge circuits connected in series. IGBT half-bridge circuits are used, with no need for a phase-shifting transformer; this helps to reduce volume and costs. Furthermore, the DC to high-frequency AC conversion module has multiple output ends, and the voltage value of each output end may be set according to actual demands. When one set of output ends develops a fault, the other output ends can be used normally, with no need for immediate shutdown and overhaul; this helps to lower costs, and increases stability of use. 2. In one embodiment of the MMC and power electronic transformer of the present invention, inductors L are connected in series in a middle position of each branch circuit. Moreover, the inductors L are connected in series between the first connection terminal and the second connection terminal adjacent thereto. Electric coupling points N0 in the middle of the even number of inductors L are connected to the voltage input ends Vin, thereby making the input voltage more stable. 3. In one embodiment of the MMC and power electronic transformer of the present invention, the low-frequency AC to DC conversion module and the DC to high-frequency AC conversion module are both provided with IGBT half-bridge circuits, and the low-frequency AC to DC conversion module can effectively convert low-frequency AC power to DC power. The IGBT half-bridge circuits can make the voltage values outputted by the DC to high-frequency AC conversion module greater than or equal to 0, and adjustments can be made according to actual circumstances, to meet different demands of users. The embodiments above are merely preferred embodiments of the present invention, which are not intended to limit it. Any amendments, equivalent substitutions or improvements etc. made within the spirit and principles of the present invention shall be included in the scope of protection thereof.
[ZH CN110768556B]: 一种基于升降压的多电平逆变电路以及逆变系统 [EN CN110768556B]: Multi-level inverter circuit and inverter system based on buck-boost | [ZH CN110768556B]: 本发明实施例涉及一种基于升降压的多电平逆变电路以及逆变系统，包括直流电源、降压逆变单元、升压逆变单元、交流输出端和控制器，降压逆变单元和升压逆变单元分别与直流电源并联连接，降压逆变单元和升压逆变单元中均包括多个全控开关元件，各个全控开关元件的控制端均还与控制器连接。该基于升降压的多电平逆变电路将一个直流电源输出的电压通过降压逆变单元和升压逆变单元上各个全控开关元件的导通或截止转换成多电平的交流电从交流输出端输出，使得采用一个电源输入实现了多电平交流电的输出，并且该基于升降压的多电平逆变电路的电路结构简单。 [EN CN110768556B]: The embodiment of the invention relates to a multi-level inverter circuit based on buck-boost and an inverter system. The circuit comprises a DC power supply, a step-down inversion unit, a step-up inversion unit, an AC output end and a controller, wherein the step-down inversion unit and the step-up inversion unit are respectively connected with the DC power supply in parallel, each of the step-down inversion unit and the step-up inversion unit comprises a plurality of full-control switch elements, and a control end of each full-control switch element is further connected with the controller.The multi-level inverter circuit based on buck-boost is advantaged in that the voltage outputted by the DC power supply is converted into multi-level AC through conduction or cut-off of all full-control switch elements on the buck-boost inverter unit and the boost inverter unit, the multi-level AC is outputted from an AC output end, so the output of the multi-level AC is realized by adopting one power supply input, and the circuit structure of the multi-level inverter circuit based on buck-boost is simple. | CN110768556B | 2020-02-07 2021-08-13 | CN201911194927A | 2019-11-28 2019-11-28 | CN201911194927A, 2019-11-28 CN201911194927A, 2019-11-28 | CN110768556B: 2021-08-13 | UNIV GUANGDONG TECHNOLOGY 广东工业大学 | YE YUANMAO CHEN SHIKAI | H02M7/483: I H02M7/537: I | H02M7/483: I H02M7/537: I | CN1625037A JP2010246189A CN103368427A CN105071679A CN110098756A CN110112943A |  | [ZH CN110768556B]: 1 .一种基于升降压的多电平逆变电路，其特征在于，包括直流电源、降压逆变单元、升 压逆变单元、交流输出端和控制器； 所述直流电源用于提供直流电源； 所述降压逆变单元与所述直流电源并联连接，所述降压逆变单元的降压输出端与所述 交流输出端的第一端连接； 所述升压逆变单元与所述直流电源并联连接，所述升压逆变单元的升压输出端与所述 交流输出端的第二端连接； 其中，所述降压逆变单元和所述升压逆变单元中均包括多个全控开关元件，各个所述 全控开关元件的控制端均还与控制器连接，所述控制器控制所述降压逆变单元和所述升压 逆变单元中的各个所述全控开关元件的导通或关断，以实现所述交流输出端输出多电平交 流电； 所述降压逆变单元包括第一全控开关元件、第二全控开关元件、第一开关元件、第一电 容器和第二电容器；所述升压逆变单元包括第七全控开关元件、第八全控开关元件、第九开 关元件、第十开关元件、第十一全控开关元件、第十二全控开关元件、第四电容器和第五电 容器;所述第一全控开关元件的第一端与所述第一电容器的第一端连接并作为所述降压逆 变单元的第一连接端，所述第二全控开关元件的第二端与所述第二电容器的第二端连接并 作为所述降压逆变单元的第二连接端，所述第一全控开关元件的第二端分别与所述第二全 控开关元件的第一端和所述第一开关元件的第一端连接并作为所述降压逆变单元的降压 输出端，所述第一电容器的第二端分别与所述第二电容器的第一端和所述第一开关元件的 第二端连接;所述降压逆变单元的第一连接端与所述直流电源的负极连接，所述降压逆变 单元的第二连接端与所述直流电源的正极连接;所述第一开关元件为双向全控开关，所述 直流电源输出的电压为Vdc； 所述第七全控开关元件的第一端与所述第十开关元件的第二端连接并作为所述升压 逆变单元的第一端，所述第十开关元件的第一端分别与所述第四电容器的第一端和所述第 十一全控开关元件的第一端来接，所述第十一全控开关元件的第二端与所述第十二全控开 关元件的第一端连接并作为所述升压逆变单元的升压输出端，所述第十二全控开关元件的 第二端分别与所述第五电容器的第一端和所述第九开关元件的第二端连接，所述第九开关 元件的第一端与所述第八全控开关元件的第二端连接并作为所述升压逆变单元的第二端， 所述第八全控开关元件的第一端与所述第七全控开关元件的第二端连接后再分别与所述 第四电容器的第二端和所述第五电容器的第一端连接;所述升压逆变单元的第一端与所述 直流电源的负极连接，所述升压逆变单元的第二端与所述直流电源的正极连接； 若开通双向全控开关、第八全控开关元件和第十二全控开关元件，其他的开关元件全 部关断，交流输出端输出的电压为+1.5Vdc；若开通双向全控开关、第七全控开关元件和第十 一全控开关元件，其他的开关元件全部关断，交流输出端输出的电压为T.5Vdc； 若开通第一全控开关元件、第七全控开关元件和第十二全控开关元件，其他的开关元 件全部关断，交流输出端Uo输出的电压为+Vdc；若开通第一全控开关元件、第七全控开关元 件和第十一全控开关元件，其他的开关元件全部关断，交流输出端Uo输出的电压为-Vdc； 若开通第一全控开关元件、第八全控开关元件和第十二全控开关元件，其他的开关元 件全部关断，交流输出端Uo输出的电压为+2Vde ；若开通第二全控开关元件、第七全控开关元 件和第十一全控开关元件，其他的开关元件全部关断，交流输出端Uo输出的电压为-2Vdc； 若开通双向全控开关、第七全控开关元件和第十二全控开关元件，其他的开关元件全 部关断，交流输出端Uo输出的电压为0.5Vdc；若开通双向全控开关、第八全控开关元件和第 十一全控开关元件，其他的开关元件全部关断，交流输出端Uo输出的电压为-0.5Vdc； 若开通第二全控开关元件、第七全控开关元件和第十二全控开关元件，其他的开关元 件全部关断，交流输出端Uo输出的电压为0。 2 .根据权利要求1所述的基于升降压的多电平逆变电路，其特征在于，所述双向全控开 关包括两个反向串联的IGBT器件或两个反向串联的MOSFET。 3 .根据权利要求1所述的基于升降压的多电平逆变电路，其特征在于，所述第九开关元 件和所述第十开关元件为全控开关元件或二极管;其中， 所述二极管的阳极作为开关元件的第一端，所述二极管的阴极作为开关元件的第二 端。 4 .根据权利要求1所述的基于升降压的多电平逆变电路，其特征在于，所述降压逆变单 元和所述升压逆变单元中的各个全控开关元件均选用N沟道MOSFET或P沟道MOSFET或IGBT 器件，其中： 当各个所述全控开关元件均选用N沟道MOSFET时，所述N沟道MOSFET的源极作为全控开 关元件的第一端，所述N沟道MOSFET的漏极作为全控开关元件的第二端，所述N沟道MOSFET 的栅极作为全控开关元件的控制端； 当各个所述全控开关元件均选用P沟道MOSFET时，所述P沟道MOSFET的漏极作为全控开 关元件的第一端，所述P沟道MOSFET的源极作为全控开关元件的第二端，所述P沟道MOSFET 的栅极作为全控开关元件的控制端； 当各个所述全控开关元件均选用IGBT器件时，所述IGBT器件的发射极作为全控开关元 件的第一端，所述IGBT器件的集电极作为全控开关元件的第二端，所述IGBT器件的基极作 为全控开关元件的控制端。 5 .一种逆变系统，其特征在于，包括如权利要求1-4任一项所述的基于升降压的多电平 逆变电路及用于控制所述基于升降压的多电平逆变电路中各个全控开关元件导通或关断 的控制器，所述控制器控制所述基于升降压的多电平逆变电路中的各个全控开关元件导通 或关断实现多电平交流电的输出。 [EN CN110768556B]: 1 A multi-level inverter circuit based on buck-boost, which is characterized by comprising a DC power supply, a step-down inverter unit, a step-up inverter unit, an AC output terminal and a controller; the DC power supply is used to provide DC Power supply; the step-down inverter unit is connected in parallel with the DC power supply, and the step-down output end of the step-down inverter unit is connected to the first end of the AC output end; the step-up inverter unit is connected to the The DC power supplies are connected in parallel, and the boost output end of the boost inverter unit is connected to the second end of the AC output end; wherein each of the step-down inverter unit and the boost inverter unit includes a plurality of Full-control switching element, the control end of each of the full-control switching elements is also connected with a controller, and the controller controls each of the full-control switches of the step-down inverter unit and the step-up inverter unit The components are turned on or off to realize the output of multi-level AC power at the AC output terminal; the step-down inverter unit includes a first fully-controlled switching element, a second fully-controlled switching element, a first switching element, a first A capacitor and a second capacitor; the boost inverter unit includes a seventh full-control switching element, an eighth full-control switching element, a ninth switching element, a tenth switching element, an eleventh full-control switching element, and a twelfth full-control switching element The first terminal of the first fully-controlled switching element is connected to the first terminal of the first capacitor and serves as the first connection terminal of the step-down inverter unit, The second end of the second fully-controlled switching element is connected to the second end of the second capacitor and As the second connection terminal of the step-down inverter unit, the second terminal of the first fully-controlled switching element is respectively connected to the first terminal of the second fully-controlled switching element and the first terminal of the first switching element. Terminal is connected and used as the step-down output terminal of the step-down inverter unit, and the second end of the first capacitor is connected to the first end of the second capacitor and the second end of the first switching element, respectively; The first connection end of the step-down inverter unit is connected to the negative electrode of the direct current power supply, and the second connection end of the step-down inverter unit is connected to the positive electrode of the direct current power supply; the first switching element is bidirectional Fully controlled switch, the output voltage of the DC power supply is VdcThe first end of the seventh full-control switching element is connected to the second end of the tenth switching element and serves as the first end of the step-up inverter unit, and the first ends of the tenth switching element are respectively Is connected to the first end of the fourth capacitor and the first end of the eleventh fully-controlled switching element, and the second end of the eleventh fully-controlled switching element is connected to the twelfth fully-controlled switching element The first terminal is connected to and used as the boost output terminal of the boost inverter unit, and the second terminal of the twelfth fully-controlled switching element is respectively connected to the first terminal of the fifth capacitor and the ninth switch The second end of the element is connected, and the first end of the ninth switching element is connected to the second end of the eighth fully-controlled switching element and serves as the second end of the boost inverter unit. The first end of the control switching element is connected to the second end of the seventh full control switching element and then to the second end of the fourth capacitor and the first end of the fifth capacitor respectively; the boost The first terminal of the inverter unit is connected to the negative pole of the DC power supply, and the second terminal of the boost inverter unit is connected to the positive pole of the DC power supply; if the bidirectional full control switch, the eighth full control switch element and The twelfth fully controlled switching element, all other switching elements are turned off, and the output voltage of the AC output terminal is +1.5Vdc; If the two-way full-control switch, the seventh full-control switch element and the eleventh full-control switch element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal is T.5Vdc; If the first full-control switching element, the seventh full-control switching element, and the twelfth full-control switching element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is +Vdc; If the first fully-controlled switching element, the seventh fully-controlled switching element, and the eleventh fully-controlled switching element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is -Vdc; If the first full-control switching element, the eighth full-control switching element, and the twelfth full-control switching element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is +2Vde ; If the second full control switch element and the seventh full control switch element are turned on And the eleventh fully-controlled switching element, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is -2Vdc; If the two-way full-control switch, the seventh full-control switch element and the twelfth full-control switch element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is 0.5Vdc; If the two-way full control switch, the eighth full control switch element and the eleventh full control switch element are turned on, all other switching elements are turned off, and the output voltage of the AC output terminal Uo is -0.5Vdc; If the second full-control switching element, the seventh full-control switching element, and the twelfth full-control switching element are turned on, all other switching elements are turned off, and the voltage output by the AC output terminal Uo is 0. 2 The multi-level inverter circuit based on buck-boost according to claim 1, wherein the bidirectional full-control switch comprises two IGBT devices connected in reverse series or two MOSFETs connected in reverse series. 3 The buck-boost-based multi-level inverter circuit according to claim 1, wherein the ninth switching element and the tenth switching element are fully controlled switching elements or diodes; wherein, the diode The anode of the diode is used as the first end of the switching element, and the cathode of the diode is used as the second end of the switching element. 4 The multi-level inverter circuit based on buck-boost according to claim 1, wherein each fully-controlled switching element in the step-down inverter unit and the step-up inverter unit is selected as N-channel A MOSFET or a P-channel MOSFET or an IGBT device, wherein: when each of the fully-controlled switching elements is an N-channel MOSFET, the source of the N-channel MOSFET serves as the first end of the fully-controlled switching element, and The drain of the N-channel MOSFET is used as the second end of the fully-controlled switching element, and the gate of the N-channel MOSFET is used as the control end of the fully-controlled switching element; when each of the fully-controlled switching elements is selected as a P-channel MOSFET The drain of the P-channel MOSFET serves as the first end of the fully-controlled switching element, the source of the P-channel MOSFET serves as the second end of the fully-controlled switching element, and the gate of the P-channel MOSFET serves as the fully-controlled switching element. When the IGBT device is selected for each of the fully-controlled switching elements, the emitter of the IGBT device is used as the first end of the fully-controlled switching element, and the collector of the IGBT device is used as the fully-controlled switching element At the second end of the IGBT device, the base of the IGBT device serves as the control end of the fully-controlled switching element. 5 . An inverter system, characterized by comprising the buck-boost-based multi-level inverter circuit according to any one of claims 1-4 and for controlling the buck-boost-based multi-level inverter circuit A controller that turns on or off each fully-controlled switching element in the variable circuit, and the controller controls the turn-on or turn-off of each fully-controlled switching element in the buck-boost-based multi-level inverter circuit to achieve multiple power Flat AC output. | [ZH CN110768556B]: 一种基于升降压的多电平逆变电路以及逆变系统 技术领域 [0001]本发明涉及电力电子逆变电路技术领域，尤其涉及一种基于升降压的多电平逆变 电路以及逆变系统。 背景技术 [0002]随着社会的发展，人们对不可再生资源的需求越来越多，不可以再生资源是可以 被使用完的，由此石油、煤炭等化石不可再生能源被人们使用，变得越来越少。因此，目前能 源危机和能源污染步步逼近，获取新型能源已经变得十分迫切，以风能和太阳能为代表的 分布式发电技术以及以电池和超级电容为代表的分布式储能技术越来越受到世界各国的 高度重视。这些新兴能源和新技术的发展和应用高度依赖于电力电子逆变装置的性能。现 有电力电子逆变装置大部分是采用两电平逆变电路实现的，而两电平逆变电路本身具有谐 波含量高和效率低等缺陷。 [0003]随着电力电子技术的高速发展，目前的电力电子逆变装置大部分是采用多电平逆 变电路实现电源的转换，多电平逆变电路的优点包括输出电压谐波含量少、器件电压应力 低、电磁干扰少和效率较高等。而典型的多电平逆变电路包括二极管钳位型、电容钳位型和 H桥级联型。其中二极管钳位型和电容钳位型在多电平逆变电路中存在电路钳位复杂且不 具备自主升压的问题，而H桥级联型的多电平逆变电路需要多个独立的直流电源，使得多电 平逆变电路电路复杂。 [0004]因此，针对上述情况，如何设计出电路结构简单、输入电源数量少且具备自主升压 能力的多电平逆变电路成为本领域技术人员亟待解决的重要技术问题。 发明内容 [0005]本发明实施例提供了一种基于升降压的多电平逆变电路以及逆变系统，用于解决 现有多电平逆变电路的需要多个输入直流电源且不会自动升降压的技术问题。 [0006]为了实现上述目的，本发明实施例提供如下技术方案： [0007] 一种基于升降压的多电平逆变电路，包括直流电源、降压逆变单元、升压逆变单 元、交流输出端和控制器； [0008] 所述直流电源用于提供直流电源； [0009] 所述降压逆变单元与所述直流电源并联连接，所述降压逆变单元的降压输出端与 所述交流输出端的第一端连接； [0010] 所述升压逆变单元与所述直流电源并联连接，所述升压逆变单元的升压输出端与 所述交流输出端的第二端连接； [0011]其中，所述降压逆变单元和所述升压逆变单元中均包括多个全控开关元件，各个 所述全控开关元件的控制端均还与控制器连接，所述控制器控制所述降压逆变单元和所述 升压逆变单元中的各个所述全控开关元件的导通或关断，以实现所述交流输出端输出多电 平交流电。 [0012]优选地，所述降压逆变单元包括第一全控开关元件、第二全控开关元件、第一开关 元件、第一电容器和第二电容器； [0013]所述第一全控开关元件的第一端与所述第一电容器的第一端连接并作为所述降 压逆变单元的第一连接端，所述第二全控开关元件的第二端与所述第二电容器的第二端连 接并作为所述降压逆变单元的第二连接端，所述第一全控开关元件的第二端分别与所述第 二全控开关元件的第一端和所述第一开关元件的第一端连接并作为所述降压逆变单元的 降压输出端，所述第一电容器的第二端分别与所述第二电容器的第一端和所述第一开关元 件的第二端连接； [0014] 所述降压逆变单元的第一连接端与所述直流电源的负极连接，所述降压逆变单元 的第二连接端与所述直流电源的正极连接。 [0015]优选地，所述第一开关元件为双向全控开关。其中，所述双向全控开关包括两个反 向串联的IGBT器件或两个反向串联的MOSFET。 [0016]优选地，所述第一开关元件包括第三全控开关元件、第四全控开关元件、第一二极 管和第二二极管； [0017]所述第三全控开关元件的第一端分别与所述第一二极管的阳极和所述第一全控 开关元件的第二端连接，所述第一二极管的阴极和所述第二二极管的阳极连接并作为所述 第一开关元件的第二端； [0018]所述第二二极管的阴极分别与所述第二全控开关元件的第一端和所述第四全控 开关元件的第二端连接，所述第四全控开关元件的第一端与所述第三全控开关元件的第二 端连接并作为所述降压逆变单元的降压输出端。 [0019]优选地，所述第一开关元件包括第三全控开关元件、第四全控开关元件、第五全控 开关元件、第六全控开关元件和第三电容器； [0020]所述第三全控开关元件的第一端分别与所述第五全控开关元件的第一端、所述第 一全控开关元件的第二端和所述第三电容器的第一端连接，所述第五全控开关元件的第二 端和所述第六全控开关元件的第一端连接并作为所述第一开关元件的第二端； [0021]所述第六全控开关元件的第二端分别与所述第二全控开关元件的第一端、所述第 三电容器的第二端和所述第四全控开关元件的第二端连接，所述第四全控开关元件的第一 端与所述第三全控开关元件的第二端连接并作为所述降压逆变单元的降压输出端。 [0022]优选地，所述升压逆变单元包括第七全控开关元件、第八全控开关元件、第九开关 元件、第十开关元件、第十一全控开关元件、第十二全控开关元件、第四电容器和第五电容 器 ； [0023]所述第七全控开关元件的第一端与所述第十开关元件的第二端连接并作为所述 升压逆变单元的第一端，所述第十开关元件的第一端分别与所述第四电容器的第一端和所 述第十一全控开关元件的第一端来接，所述第十一全控开关元件的第二端与所述第十二全 控开关元件的第一端连接并作为所述升压逆变单元的升压输出端，所述第十二全控开关元 件的第二端分别与所述第五电容器的第一端和所述第九开关元件的第二端连接，所述第九 开关元件的第一端与所述第八全控开关元件的第二端连接并作为所述升压逆变单元的第 二端，所述第八全控开关元件的第一端与所述第七全控开关元件的第二端连接后再分别与 所述第四电容器的第二端和所述第五电容器的第一端连接； [0024]所述升压逆变单元的第一端与所述直流电源的负极连接，所述升压逆变单元的第 二端与所述直流电源的正极连接。 [0025]优选地，所述第九开关元件和所述第十开关元件为全控开关元件或二极管。其中， 所述二极管的阳极作为开关元件的第一端，所述二极管的阴极作为开关元件的第二端。 [0026] 优选地，所述降压逆变单元和所述升压逆变单元中的各个全控开关元件均选用N 沟道MOSFET或P沟道MOSFET或IGBT器件，其中： [0027] 当各个所述全控开关元件均选用N沟道MOSFET时，所述N沟道MOSFET的源极作为全 控开关元件的第一端，所述N沟道MOSFET的漏极作为全控开关元件的第二端，所述N沟道 MOSFET的栅极作为全控开关元件的控制端； [0028] 当各个所述全控开关元件均选用P沟道MOSFET时，所述P沟道MOSFET的漏极作为全 控开关元件的第一端，所述P沟道MOSFET的源极作为全控开关元件的第二端，所述P沟道 MOSFET的栅极作为全控开关元件的控制端； [0029]当各个所述全控开关元件均选用IGBT器件时，所述IGBT器件的发射极作为全控开 关元件的第一端，所述IGBT器件的集电极作为全控开关元件的第二端，所述IGBT器件的基 极作为全控开关元件的控制端。 [0030] 一种逆变系统，包括上述所述的基于升降压的多电平逆变电路及用于控制所述基 于升降压的多电平逆变电路中各个全控开关元件导通或关断的控制器，所述控制器控制所 述基于升降压的多电平逆变电路中的各个全控开关元件导通或关断实现多电平交流电的 输出。 [0031]从以上技术方案可以看出，本发明实施例具有以下优点：该基于升降压的多电平 逆变电路将一个直流电源输出的电压通过降压逆变单元和升压逆变单元上各个全控开关 元件的导通或截止转换成多电平的交流电从交流输出端输出，使得采用一个电源输入实现 了多电平交流电的输出，并且该基于升降压的多电平逆变电路的电路结构简单，解决了现 有多电平逆变电路的需要多个输入直流电源且不会自动升降压的技术问题。 附图说明 [0032]为了更清楚地说明本发明实施例或现有技术中的技术方案，下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本 发明的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可 以根据这些附图获得其它的附图。 [0033]图1为本发明实施例所述的基于升降压的多电平逆变电路的框架示意图。 [0034]图2a为本发明实施例所述的基于升降压的多电平逆变电路降压逆变单元实施例 一的电路图。 [0035]图2b为本发明实施例所述的基于升降压的多电平逆变电路降压逆变单元实施例 二的电路图。 [0036]图2c为本发明实施例所述的基于升降压的多电平逆变电路降压逆变单元实施例 三的电路图。 [0037]图3为本发明实施例所述的基于升降压的多电平逆变电路双向全控开关的电路 图。 [0038]图4a为本发明实施例所述的基于升降压的多电平逆变电路升压逆变单元实施例 一的电路图。 [0039]图4b为本发明实施例所述的基于升降压的多电平逆变电路升压逆变单元实施例 二的电路图。 [0040]图5为本发明实施例所述的基于升降压的多电平逆变电路的电路图。 [0041]图6为本发明实施例所述的基于升降压的多电平逆变电路的开关逻辑图。 具体实施方式 [0042]为使得本发明的发明目的、特征、优点能够更加的明显和易懂，下面将结合本发明 实施例中的附图，对本发明实施例中的技术方案进行清楚、完整地描述，显然，下面所描述 的实施例仅仅是本发明一部分实施例，而非全部的实施例。基于本发明中的实施例，本领域 普通技术人员在没有做出创造性劳动前提下所获得的所有其它实施例，都属于本发明保护 的范围。 [0043]本申请实施例提供了一种基于升降压的多电平逆变电路以及逆变系统，用于解决 现有多电平逆变电路的需要多个输入直流电源且不会自动升降压的技术问题。 [0044] 实施例一： [0045]如图1所示，图1为本发明实施例所述的基于升降压的多电平逆变电路的框架示意 图。 [0046]本发明实施例提供了一种基于升降压的多电平逆变电路，包括直流电源10、降压 逆变单元20、升压逆变单元30、交流输出端Uo和控制器40；所述直流电源用于提供直流电 源；降压逆变单元20与直流电源10并联连接，降压逆变单元10的降压输出端21与交流输出 端Uo的第一端连接;升压逆变单元30与直流电源10并联连接，升压逆变单元30的升压输出 端31与交流输出端Uo的第二端连接;降压逆变单元20和升压逆变单元30中均包括多个全控 开关元件，各个全控开关元件的控制端均还与控制器40连接，控制器40控制降压逆变单元 20和升压逆变单元30中的各个全控开关元件的导通或关断，以实现交流输出端Uo输出多电 平交流电。 [0047]需要说明的是，全控开关元件可以为IGBT器件，也可以为N沟道或P沟道的MOSFET 器件，也可以选用其他类型的开关管，只要符合全控开关的原理即可，本申请在此不做特别 的限定。其中，交流输出端Uo用于与负载连接。直流电源10输出的电压为Vdc。具体地，降压逆 变单元20和升压逆变单元30中的各个全控开关元件均可以选用N沟道MOSFET，也可以选用P 沟道MOSFET，也可以选用IGBT器件，当各个全控开关元件均选用N沟道MOSFET时，N沟道 MOSFET的源极作为全控开关元件的第一端，N沟道MOSFET的漏极作为全控开关元件的第二 端，N沟道MOSFET的栅极作为全控开关元件的控制端。当各个全控开关元件均选用P沟道 MOSFET时，P沟道MOSFET的漏极作为全控开关元件的第一端，P沟道MOSFET的源极作为全控 开关元件的第二端，P沟道MOSFET的栅极作为全控开关元件的控制端。当各个全控开关元件 均选用IGBT器件时，IGBT器件的发射极作为全控开关元件的第一端，IGBT器件的集电极作 为开关元件的第二端，IGBT器件的基极作为全控开关元件的控制端。各个全控开关元件的 控制端均与控制器40连接，控制器40用于控制各个全控开关元件的导通或关断，以实现多 电平交流电的输出。 [0048]本发明实施例中的基于升降压的多电平逆变电路将一个直流电源输出的电压通 过降压逆变单元和升压逆变单元上各个全控开关元件的导通或截止转换成多电平的交流 电从交流输出端输出，使得采用一个电源输入实现了多电平交流电的输出，并且该基于升 降压的多电平逆变电路的电路结构简单，解决了现有多电平逆变电路的需要多个输入直流 电源且不会自动升降压的技术问题。 [0049]需要说明的是，多电平交流电的电压是指输出电压不但极性可以在正负之间变 化，而且输出电压可以按阶梯的形式逐个电平递增然后递减，使得输出电压波形逼近正弦 波形。 [0050]如图2a至图2c所示，图2a为本发明实施例所述的基于升降压的多电平逆变电路降 压逆变单元实施例一的电路图；图2b为本发明实施例所述的基于升降压的多电平逆变电路 降压逆变单元实施例二的电路图；图2c为本发明实施例所述的基于升降压的多电平逆变电 路降压逆变单元实施例三的电路图。 [0051] 本发明的一个实施例中，降压逆变单元20包括第一全控开关元件S1、第二全控开 关元件S2、第一开关元件、第一电容器C1和第二电容器C2。 [0052]第一全控开关元件S1的第一端与第一电容器C1的第一端连接并作为降压逆变单 元20的第一连接端，第二全控开关元件S2的第二端与第二电容器C2的第二端连接并作为降 压逆变单元20的第二连接端，第一全控开关元件S1的第二端分别与第二全控开关元件S2的 第一端和第一开关元件的第一端连接并作为降压逆变单元20的降压输出端21，第一电容器 C1的第二端分别与第二电容器C2的第一端和第一开关元件的第二端连接;降压逆变单元20 的第一连接端与直流电源10的负极连接，降压逆变单元20的第二连接端与直流电源10的正 极连接。 [0053] 需要说明的是，第一电容器C1和第二电容器C2均可以优选选用电解电容器，也可 以选用其他类型的电容，只要符合第一电容器C1和第二电容器C2的原理即可，本申请在此 不做特别的限定。 [0054]在降压逆变单元20的实施例一中，如图2a所示，第一开关元件为双向全控开关。 [0055]需要说明的是，如图3所示，双向全控开关主要可以由两个反向串联的IGBT器件组 成，双向全控开关也可以由两个反向串联的MOSFET组成。 [0056]在降压逆变单元20的实施例二中，如图2b所示，第一开关元件包括第三全控开关 元件S3、第四全控开关元件S4、第一二极管D1和第二二极管D2；第三全控开关元件S3的第一 端分别与第一二极管D1的阳极和第一全控开关元件S1的第二端连接，第一二极管D1的阴极 和第二二极管的阳极连接并作为第一开关元件的第二端；第二二极管D2的阴极分别与第二 全控开关元件S2的第一端和第四全控开关元件S4的第二端连接，第四全控开关元件S4的第 一端与第三全控开关元件S3的第二端连接并作为降压逆变单元20的降压输出端21。 [0057]需要说明的是，二极管可以选用其他类型的二极管，只要符合第一二极管D1和第 二二极管D2的原理即可，本申请在此不做特别的限定。 [0058]在降压逆变单元20的实施例三中，如图2c所示，第一开关元件包括第三全控开关 元件S3、第四全控开关元件S4、第五全控开关元件S5、第六全控开关元件S6和第三电容器 C3；第三全控开关元件S3的第一端分别与第五全控开关元件S5的第一端、第一全控开关元 件S2的第二端和第三电容器C3的第一端连接，第五全控开关元件S5的第二端和第六全控开 关元件S6的第一端连接并作为第一开关元件的第二端;第六全控开关元件S6的第二端分别 与第二全控开关元件S2的第一端、第三电容器C3的第二端和第四全控开关元件S4的第二端 连接，第四全控开关元件S4的第一端与第三全控开关元件S3的第二端连接并作为降压逆变 单元20的降压输出端21。 [0059]需要说明的是，第三电容器C3可以优先选用电解电容，也可以选用其他类型的电 容，只要符合第三电容器C3的原理即可，本申请在此不做特别的限定。 [0060]如图4a和图4b所示，图4a为本发明实施例所述的基于升降压的多电平逆变电路升 压逆变单元实施例一的电路图；图4b为本发明实施例所述的基于升降压的多电平逆变电路 升压逆变单元实施例二的电路图。 [0061] 本发明实施例的一个实施例中，升压逆变单元30包括第七全控开关元件S7、第八 全控开关元件S8、第九开关元件S9、第十开关元件S10、第十一全控开关元件S11、第十二全 控开关元S12、第四电容器S4和第五电容器S5；第七全控开关元件S7的第一端与第十开关元 件S10的第二端连接并作为升压逆变单元30的第一端，第十开关元件S10的第一端分别与第 四电容器C4的第一端和第十一全控开关元件S11的第一端来接，第十一全控开关元件S11的 第二端与第十二全控开关元件S12的第一端连接并作为升压逆变单元30的升压输出端31， 第十二全控开关元件S12的第二端分别与第五电容器C5的第一端和第九开关元件S9的第二 端连接，第九开关元件S9的第一端与第八全控开关元件S8的第二端连接并作为升压逆变单 元30的第二端，第八全控开关元件S8的第一端与第七全控开关元件S7的第二端连接后再分 别与第四电容器C4的第二端和第五电容器C5的第一端连接;升压逆变单元30的第一端与直 流电源10的负极连接，升压逆变单元30的第二端与直流电源10的正极连接。 [0062] 需要说明的是，第四电容器C4和第五电容器C5均可以优选选用电解电容器，也可 以选用其他类型的电容，只要符合第四电容器C4和第五电容器C5的原理即可，本申请在此 不做特别的限定。如图4a所示，第九开关元件S9和第十开关元件S10均优选为全控开关元 件。如图4b所示，第九开关元件S9和第十开关元件S10均优选为二极管，该二极管的阳极作 为开关元件的第一端，该二极管的阴极作为开关元件的第二端。其中，二极管可以选用其他 类型的二极管，只要符合第九开关元件S9和第十开关元件S10的原理即可，本申请在此不做 特别的限定。 [0063]如图5和图6所示，图5为本发明实施例所述的基于升降压的多电平逆变电路的电 路图，图6为本发明实施例所述的基于升降压的多电平逆变电路的开关逻辑图。 [0064]本发明的实施例中，直流电源10输出的电压为Vdc，如图5和图6所示，降压逆变单元 20中的第一开关元件采用双向全控开关BS，升压逆变单元30中的第九开关元件S9和第十开 关元件S10采用二极管为例进行说明。若开通第一全控开关元件S1、第八全控开关元件S8和 第十二全控开关元件S12,其他的开关元件全部关断，交流输出端Uo输出的电压为+2Vdc。 [0065]若开通双向全控开关BS、第八全控开关元件S8和第十二全控开关元件S12,其他的 开关元件全部关断，交流输出端Uo输出的电压为+1.5Vdc。 [0066] 若开通第一全控开关元件S1、第七全控开关元件S7和第十二全控开关元件S12,其 他的开关元件全部关断，交流输出端Uo输出的电压为+Vdc。 [0067]若开通双向全控开关BS、第七全控开关元件S7和第十二全控开关元件S12,其他的 开关元件全部关断，交流输出端Uo输出的电压为0.5Vdc。 [0068]若开通第二全控开关元件S2、第七全控开关元件S7和第十二全控开关元件S12,其 他的开关元件全部关断,交流输出端Uo输出的电压为0。 [0069] 若开通双向全控开关BS、第八全控开关元件S8和第十一全控开关元件S11，其他的 开关元件全部关断，交流输出端Uo输出的电压为-0.5Vdc。 [0070] 若开通第一全控开关元件S1、第七全控开关元件S7和第十一全控开关元件S11，其 他的开关元件全部关断，交流输出端Uo输出的电压为-Vdc。 [0071]若开通双向全控开关BS、第七全控开关元件S7和第十一全控开关元件S11，其他的 开关元件全部关断，交流输出端Uo输出的电压为-1.5Vdc。 [0072]若开通第二全控开关元件S2、第七全控开关元件S7和第十一全控开关元件S11，其 他的开关元件全部关断，交流输出端Uo输出的电压为-2Vdc。 [0073]如图6所示和上述得知，该基于升降压的多电平逆变电路的输出电压可以从2Vde、T.5Vde逐级增加到+2Vde，然后再逐级减小到-2Vde，再往返增减实现多电平交流电的输 出，因此，直流电源的输出电压为Vdc，通过该基于升降压的多电平逆变电路输出交流电的幅 值为2Vde。第一电容器C1和第二电容器C2具有相同电容值，第一电容器C1和第二电容器C2串 联后再与直流电源10并联，使得第一电容器C1和第二电容器C2的电压相同并等于直流电源 10电压的一半，即Vdc/2 ；第一全控开关元件S1、第二全控开关元件S2和双向全控开关BS分时 导通;相对于第一电容器C1和第二电容器C2连接点的电位，降压逆变单元20的降压输出端 21的电压可在0和土Vdc/2这三种电平之间交替变化;第七全控开关元件S7和第八全控开关 元件S8互补交替导通，使得第四电容器C4和第五电容器C5分时与直流电源10并联，并使得 第四电容器C4和第五电容器C5的电压等于直流电源10的电压Vdc；第十一全控开关元件S11 和第十二全控开关元件S12也互补交替导通;根据第七全控开关元件S7、第八全控开关元件 S8、第十一全控开关元件S11和第十二全控开关元件S12的不同导通循序，升压逆变单元30 的升压输出端31的电压可在土Vdc/2和土3Vde/2这四种电平之间交替变化;于是，根据第一 全控开关元件S1、第二全控开关元件S2、双向全控开关BS、第七全控开关元件S7、第八全控 开关元件S8、第十一全控开关元件S11和第十二全控开关元件S12的不同开关状态的组合， 使得该基于升降压的多电平逆变电路可通过两个降压输出端21和升压输出端31输出0、士 Vdc/2、土 Vdc、土 3Vde/2和土 2Vde这九种不同交流电平。 [0074] 实施例二： [0075]本发明的实施例还提供了一种逆变系统，包括上述的基于升降压的多电平逆变电 路及用于控制该基于升降压的多电平逆变电路中各个全控开关元件导通或关断的控制器 40,控制器40控制该基于升降压的多电平逆变电路中的各个全控开关元件导通或关断实现 多电平交流电的输出。 [0076]需要说明的是，该基于升降压的多电平逆变电路已在实施例一中详细描述了，在 本实施例中不在一一阐述。 [0077]所属领域的技术人员可以清楚地了解到，为描述的方便和简洁，上述描述的系统， 装置和单元的具体工作过程，可以参考前述方法实施例中的对应过程,在此不再赘述。 [0078]在本申请所提供的几个实施例中，应该理解到，所揭露的系统，装置和方法，可以 通过其它的方式实现。例如，以上所描述的装置实施例仅仅是示意性的，例如，所述单元的 划分，仅仅为一种逻辑功能划分，实际实现时可以有另外的划分方式，例如多个单元或组件 可以结合或者可以集成到另一个系统，或一些特征可以忽略，或不执行。另一点，所显示或 讨论的相互之间的耦合或直接耦合或通信连接可以是通过一些接口，装置或单元的间接耦 合或通信连接，可以是电性，机械或其它的形式。 [0079]所述作为分离部件说明的单元可以是或者也可以不是物理上分开的，作为单元显 示的部件可以是或者也可以不是物理单元，即可以位于一个地方，或者也可以分布到多个 网络单元上。可以根据实际的需要选择其中的部分或者全部单元来实现本实施例方案的目 的。 [0080]另外，在本发明各个实施例中的各功能单元可以集成在一个处理单元中，也可以 是各个单元单独物理存在，也可以两个或两个以上单元集成在一个单元中。上述集成的单 元既可以采用硬件的形式实现，也可以采用软件功能单元的形式实现。 [0081]所述集成的单元如果以软件功能单元的形式实现并作为独立的产品销售或使用 时，可以存储在一个计算机可读取存储介质中。基于这样的理解，本发明的技术方案本质上 或者说对现有技术做出贡献的部分或者该技术方案的全部或部分可以以软件产品的形式 体现出来，该计算机软件产品存储在一个存储介质中，包括若干指令用以使得一台计算机 设备(可以是个人计算机，服务器，或者网络设备等)执行本发明各个实施例所述方法的全 部或部分步骤。而前述的存储介质包括：U盘、移动硬盘、只读存储器(ROM，Read - Only Memory)、随机存取存储器(RAM，Random Access Memory)、磁碟或者光盘等各种可以存储程 序代码的介质。 [0082]以上所述，以上实施例仅用以说明本发明的技术方案，而非对其限制;尽管参照前 述实施例对本发明进行了详细的说明，本领域的普通技术人员应当理解:其依然可以对前 述各实施例所记载的技术方案进行修改，或者对其中部分技术特征进行等同替换;而这些 修改或者替换，并不使相应技术方案的本质脱离本发明各实施例技术方案的精神和范围。 CN 110768556 Β [EN CN110768556B]: Technical field of multi-level inverter circuit and inverter system based on buck-boost [0001] The present invention relates to the technical field of power electronic inverter circuits, and more particularly to a multi-level inverter circuit and an inverter system based on buck-boost. Background technique [0002] With the development of society, people have more and more demand for non-renewable resources, and non-renewable resources can be used up. As a result, fossil non-renewable energy sources such as petroleum and coal are used by people and become more and more popular. Less. Therefore, the current energy crisis and energy pollution are approaching, and access to new energy sources has become very urgent. Distributed power generation technologies represented by wind and solar energy, and distributed energy storage technologies represented by batteries and supercapacitors are becoming more and more popular. All countries in the world attach great importance to it. The development and application of these emerging energy and new technologies are highly dependent on the performance of power electronic inverter devices. Most of the existing power electronic inverter devices are realized by using a two-level inverter circuit, and the two-level inverter circuit itself has defects such as high harmonic content and low efficiency. [0003] With the rapid development of power electronic technology, most of the current power electronic inverter devices use multi-level inverter circuits to achieve power conversion. The advantages of multi-level inverter circuits include low output voltage harmonic content, The device has low voltage stress, less electromagnetic interference and higher efficiency. The typical multi-level inverter circuit includes diode clamp type, capacitor clamp type and H-bridge cascade type. Among them, the diode clamp type and the capacitor clamp type have the problem of complex circuit clamping and no autonomous boost in the multi-level inverter circuit, while the H-bridge cascaded multi-level inverter circuit requires multiple independent The DC power supply makes the multi-level inverter circuit complicated. [0004] Therefore, in view of the above situation, how to design a multi-level inverter circuit with a simple circuit structure, a small number of input power sources, and an autonomous boost capability has become an important technical problem to be solved by those skilled in the art. Summary of the invention [0005] Embodiments of the present invention provide a multi-level inverter circuit and an inverter system based on buck-boost, which are used to solve the existing multi-level inverter circuit that requires multiple input DC power sources and does not automatically rise. The technical problem of step-down. [0006] In order to achieve the foregoing objectives, the embodiments of the present invention provide the following technical solutions: [0007] A multi-level inverter circuit based on buck-boost, including a DC power supply, a step-down inverter unit, a step-up inverter unit, an AC output terminal, and a controller; [0008] The DC power supply is used to provide a DC power supply; [0009] The step-down inverter unit is connected in parallel with the DC power supply, and the step-down output end of the step-down inverter unit is connected to the first end of the AC output end; [0010] The step-up inverter unit is connected in parallel with the DC power supply, and the step-up output end of the step-up inverter unit is connected to the second end of the AC output end; [0011] Wherein, the step-down inverter unit and the step-up inverter unit each include a plurality of fully-controlled switching elements, and the control end of each of the fully-controlled switching elements is also connected to a controller, and the control The controller controls the turn-on or turn-off of each of the fully-controlled switching elements in the step-down inverter unit and the step-up inverter unit, so as to realize that the AC output terminal outputs multi-level AC power. [0012] Preferably, the step-down inverter unit includes a first fully-controlled switching element, a second fully-controlled switching element, a first switching element, a first capacitor, and a second capacitor; [0013] The first end of the first full control switching element is connected to the first end of the first capacitor and serves as the first connection end of the step-down inverter unit. The second end is connected to the second end of the second capacitor and serves as the second connection end of the step-down inverter unit, and the second end of the first full control switching element is connected to the second full control switch respectively. The first end of the element is connected to the first end of the first switching element and serves as the step-down output end of the step-down inverter unit. The second end of the first capacitor is respectively connected to the first end of the second capacitor. One end is connected to the second end of the first switching element; [0014] The first connection end of the step-down inverter unit is connected to the negative electrode of the direct current power supply, and the second connection end of the step-down inverter unit is connected to the positive electrode of the direct current power supply. [0015] Preferably, the first switching element is a bidirectional full control switch. Wherein, the bidirectional full control switch includes two IGBT devices connected in reverse series or two MOSFETs connected in reverse series. [0016] Preferably, the first switching element includes a third fully-controlled switching element, a fourth fully-controlled switching element, a first diode, and a second diode; [0017] The first end of the third fully-controlled switching element is respectively connected to the anode of the first diode and the second end of the first fully-controlled switching element, and the cathode of the first diode Connected to the anode of the second diode and used as the second end of the first switching element; [0018] The cathode of the second diode is respectively connected to the first end of the second fully-controlled switching element and the second end of the fourth fully-controlled switching element. The first end is connected to the second end of the third fully-controlled switching element and serves as the step-down output end of the step-down inverter unit. [0019] Preferably, the first switching element includes a third fully-controlled switching element, a fourth fully-controlled switching element, a fifth fully-controlled switching element, a sixth fully-controlled switching element, and a third capacitor; [0020] The first terminal of the third fully-controlled switching element is respectively connected to the first terminal of the fifth fully-controlled switching element, the second terminal of the first fully-controlled switching element, and the third capacitor of the third capacitor. One end is connected, and the second end of the fifth full control switch element is connected to the first end of the sixth full control switch element and serves as the second end of the first switch element; [0021] The second end of the sixth full control switching element is respectively connected to the first end of the second full control switching element, the second end of the third capacitor, and the fourth full control switching element. Two ends are connected, and the first end of the fourth full control switching element is connected to the second end of the third full control switching element and serves as the step-down output end of the step-down inverter unit. [0022] Preferably, the boost inverter unit includes a seventh full-control switching element, an eighth full-control switching element, a ninth switching element, a tenth switching element, an eleventh full-control switching element, and a twelfth full-control switching element. Controlling the switching element, the fourth capacitor and the fifth capacitor; [0023] The first end of the seventh full-control switching element is connected to the second end of the tenth switching element and serves as the first end of the step-up inverter unit, and the first end of the tenth switching element is The terminals are respectively connected to the first terminal of the fourth capacitor and the first terminal of the eleventh fully-controlled switching element, and the second terminal of the eleventh fully-controlled switching element is connected to the twelfth fully-controlled switching element. The first end of the switching element is connected and used as the boost output end of the boost inverter unit, and the second end of the twelfth fully-controlled switching element is respectively connected to the first end of the fifth capacitor and the first end of the fifth capacitor. The second end of the nine switching element is connected, and the first end of the ninth switching element is connected to the second end of the eighth fully-controlled switching element and serves as the second end of the boost inverter unit. The first end of the eight full-control switching element is connected to the second end of the seventh full-control switching element and then to the second end of the fourth capacitor and the first end of the fifth capacitor respectively; [0024] The first end of the step-up inverter unit is connected to the negative electrode of the direct current power supply, and the second end of the step-up inverter unit is connected to the positive electrode of the direct current power supply. [0025] Preferably, the ninth switching element and the tenth switching element are fully controlled switching elements or diodes. Wherein, the anode of the diode serves as the first end of the switching element, and the cathode of the diode serves as the second end of the switching element. [0026] Preferably, each fully-controlled switching element in the step-down inverter unit and the step-up inverter unit is selected as an N-channel MOSFET or a P-channel MOSFET or an IGBT device, wherein: [0027] When the N-channel MOSFET is selected for each of the fully-controlled switching elements, the source of the N-channel MOSFET serves as the first end of the fully-controlled switching element, and the drain of the N-channel MOSFET serves as the fully-controlled The second end of the switching element, the gate of the N-channel MOSFET is used as the control end of the fully-controlled switching element; [0028] When each of the fully-controlled switching elements is selected as a P-channel MOSFET, the drain of the P-channel MOSFET is used as the first end of the fully-controlled switching element, and the source of the P-channel MOSFET is used as the fully-controlled The second end of the switching element, the gate of the P-channel MOSFET is used as the control end of the fully-controlled switching element; [0029] When IGBT devices are selected for each of the fully-controlled switching elements, the emitter of the IGBT device is used as the first end of the fully-controlled switching element, and the collector of the IGBT device is used as the second end of the fully-controlled switching element , The base of the IGBT device serves as the control terminal of the fully-controlled switching element. [0030] An inverter system, including the above-mentioned buck-boost-based multi-level inverter circuit and for controlling the conduction of each fully-controlled switching element in the buck-boost-based multi-level inverter circuit Or an off controller, the controller controls each fully-controlled switching element in the buck-boost-based multi-level inverter circuit to be turned on or off to realize the output of multi-level alternating current. [0031] It can be seen from the above technical solutions that the embodiment of the present invention has the following advantages: the multi-level inverter circuit based on buck-boost passes the voltage output by a DC power supply through the buck inverter unit and the boost inverter unit The on or off of each fully-controlled switching element is converted into multi-level AC output from the AC output terminal, so that a power input is used to realize the output of multi-level AC, and the multi-level inverter based on buck-boost The circuit structure of the circuit is simple, which solves the technical problem of the existing multi-level inverter circuit that requires multiple input DC power supplies and does not automatically step up and down. Description of the drawings [0032] In order to more clearly explain the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the drawings that need to be used in the description of the embodiments or the prior art. Obviously, in the following description The drawings are merely some embodiments of the present invention. For those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative labor. [0033] FIG. 1 is a schematic framework diagram of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0034] FIG. 2a is a circuit diagram of a step-down inverter unit of a step-down inverter unit of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0035] FIG. 2b is a circuit diagram of a second embodiment of a step-down inverter unit of a step-down inverter unit based on a buck-boost multi-level inverter circuit according to an embodiment of the present invention. [0036] FIG. 2c is a circuit diagram of Embodiment 3 of a step-down inverter unit of a step-down inverter unit based on a step-up and step-down multi-level inverter circuit according to an embodiment of the present invention. [0037] FIG. 3 is a circuit diagram of a bidirectional full-control switch of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0038] FIG. 4a is a circuit diagram of a first embodiment of a step-up inverter unit of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0039] FIG. 4b is a circuit diagram of a second embodiment of a step-up inverter unit of a multi-level buck-boost-based inverter circuit according to an embodiment of the present invention. [0040] FIG. 5 is a circuit diagram of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0041] FIG. 6 is a switch logic diagram of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. Detailed ways [0042] In order to make the objectives, features, and advantages of the present invention more obvious and understandable, the technical solutions in the embodiments of the present invention will be described clearly and completely in conjunction with the accompanying drawings in the embodiments of the present invention. It is obvious that The embodiments described below are only a part of the embodiments of the present invention, but not all of the embodiments. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0043] The embodiments of the present application provide a multi-level inverter circuit and an inverter system based on buck-boosting, which are used to solve the existing multi-level inverter circuit that requires multiple input DC power sources and does not automatically rise. The technical problem of step-down. [0044] Embodiment One: [0045] As shown in FIG. 1, FIG. 1 is a schematic diagram of a framework of a multi-level inverter circuit based on buck-boost according to an embodiment of the present invention. [0046] The embodiment of the present invention provides a multi-level inverter circuit based on buck-boost, including a DC power supply 10, a step-down inverter unit 20, a step-up inverter unit 30, and an AC output terminal UoAnd the controller 40; the DC power supply is used to provide DC power; the step-down inverter unit 20 is connected in parallel with the DC power supply 10, and the step-down output terminal 21 of the step-down inverter unit 10 and the AC output terminal UoThe first terminal is connected; the boost inverter unit 30 is connected in parallel with the DC power supply 10, the boost output terminal 31 of the boost inverter unit 30 and the AC output terminal UoThe second end is connected; the step-down inverter unit 20 and the step-up inverter unit 30 each include a plurality of fully-controlled switching elements, and the control ends of each fully-controlled switching element are also connected to the controller 40, and the controller 40 controls the step-down Each fully-controlled switching element in the voltage inverter unit 20 and the boost inverter unit 30 is turned on or off to realize the AC output terminal UoOutput multi-level alternating current. [0047] It should be noted that the fully-controlled switching element may be an IGBT device, or an N-channel or P-channel MOSFET device, and other types of switching tubes may also be selected, as long as it conforms to the principle of fully-controlled switching. This application is not specifically limited here. Among them, the AC output terminal UoUsed to connect with the load. The output voltage of the DC power supply 10 is Vdc. Specifically, each fully-controlled switching element in the step-down inverter unit 20 and the step-up inverter unit 30 can be selected as N-channel MOSFETs, P-channel MOSFETs, or IGBT devices. When N-channel MOSFETs are selected as the components, the source of the N-channel MOSFET is used as the first end of the fully-controlled switching element, the drain of the N-channel MOSFET is used as the second end of the fully-controlled switching element, and the gate of the N-channel MOSFET As the control end of the full control switching element. When the P-channel MOSFET is selected for each fully-controlled switching element, the drain of the P-channel MOSFET is used as the first end of the fully-controlled switching element, and the source of the P-channel MOSFET is used as the second end of the fully-controlled switching element. The gate of the MOSFET serves as the control terminal of the full-control switching element. When IGBT devices are selected for each fully-controlled switching element, the emitter of the IGBT device is used as the first end of the fully-controlled switching element, the collector of the IGBT device is used as the second end of the switching element, and the base of the IGBT device is used as the fully-controlled switching element The control end. The control end of each full-control switching element is connected to the controller 40, and the controller 40 is used to control the on or off of each full-control switching element, so as to realize the output of multi-level alternating current. [0048] The multi-level inverter circuit based on buck-boost in the embodiment of the present invention turns on or off the voltage output from a DC power supply through the buck inverter unit and the full-control switching element on the boost inverter unit. The converted multi-level AC power is output from the AC output end, so that one power input is used to realize the output of multi-level AC power, and the circuit structure of the multi-level inverter circuit based on buck-boost is simple, which solves the existing problems. The level inverter circuit requires multiple input DC power supplies and does not automatically increase and decrease the voltage. [0049] It should be noted that the voltage of multi-level alternating current means that not only the polarity of the output voltage can be changed between positive and negative, but the output voltage can be increased and then decreased level by level in the form of a ladder, so that the output voltage waveform is close to sine. Waveform. [0050] As shown in FIGS. 2a to 2c, FIG. 2a is a circuit diagram of Embodiment 1 of a step-down inverter unit of a multi-level buck-boost-based inverter circuit according to an embodiment of the present invention; FIG. 2b is an implementation of the present invention The circuit diagram of the second embodiment of the step-down inverter unit of the multi-level inverter circuit based on buck-boost according to the example; The circuit diagram of the third embodiment of the variable unit. [0051] In an embodiment of the present invention, the step-down inverter unit 20 includes a first fully-controlled switching element S1, a second fully-controlled switching element S2, a first switching element, a first capacitor C1, and a second capacitor C2. [0052] The first end of the first full control switching element S1 is connected to the first end of the first capacitor C1 and serves as the first connection end of the step-down inverter unit 20, and the second end of the second full control switching element S2 is connected to the first end of the step-down inverter unit 20. The second terminal of the second capacitor C2 is connected and used as the second connection terminal of the step-down inverter unit 20. The second terminal of the first fully-controlled switching element S1 is respectively connected to the first terminal and the first terminal of the second fully-controlled switching element S2. The first end of the switching element is connected and used as the step-down output terminal 21 of the step-down inverter unit 20, and the second end of the first capacitor C1 is respectively connected to the first end of the second capacitor C
[KO KR101723094B1]: ＭＭＣ 컨버터의 서브모듈 제어기용 전원장치 [EN EP3242389B1]: POWER SUPPLY DEVICE FOR SUB-MODULE CONTROLLER OF MMC CONVERTER [FR EP3242389B1]: DISPOSITIF D'ALIMENTATION ÉLECTRIQUE POUR CONTRÔLEUR DE SOUS-MODULE DE CONVERTISSEUR MMC [DE EP3242389B1]: STROMVERSORGUNGSVORRICHTUNG FÜR SUBMODULSTEUERGERÄT EINES MMC-WANDLERS [PT BR112017013953A2]: aparato de alimentação de energia para um controlador de submódulo de um conversor multinível modular | [KO KR101723094B1]: 본 발명은 고압전 직류송전(HVDC)시스템과 연계되는 모듈러 멀티레벨 컨버터(MMC)의 서브모듈 제어기에 구동전원을 공급하도록 하는 MMC 컨버터의 서브모듈 제어기용 전원장치에 관한 것이다. 본 발명에 따른 전원장치는, 상호 간에 직렬연결된 MMC 컨버터의 서브모듈 내부에 DC전압을 저장하는 N개(N≥2,정수)의 에너지저장부와, 상기 N개의 에너지저장부에 브릿지 형태로 병렬로 연결된 다수의 전력용반도체를 포함하는 브릿지회로부; 및 상기 N개의 에너지저장부 중 n개(1≤n | EP3242389B1 | 2017-11-08 2018-06-06 2021-09-22 | EP15875669A | 2015-12-29 2015-12-29 2015-12-29 | KR20140192750A, 2014-12-29 KR2015014402W, 2015-12-29 KR20140192750A, 2014-12-29 KR2015014402W, 2015-12-29 KR20140192750A, 2014-12-29 KR2015014402W, 2015-12-29 | WO2016108575A1: 2016-07-07 KR101723094B1: 2017-04-18 EP3242389B1: 2021-09-22 US10177652B2: 2019-01-08 BR112017013953A2: 2018-02-20 | HYOSUNG CORP 주식회사 효성 HYOSUNG HEAVY IND CORP | PARK JUNG SOO JUNG HONG JU KIM JUNE SUNG LEE DOO YOUNG CHOI JONG YUN PARK JUNG-SOO JUNG HONG-JU KIM JUNE-SUNG LEE DOO-YOUNG CHOI JONG-YUN DOO YOUNG LEE HONG JU JUNG JONG YUN CHOI JUNE SUNG KIM JUNG SOO PARK | H02M7/19: I H02J1/00: I H02M7/49: I H02M1/08: I H02M3/06: I H02M1/00: N H02M7/483: N | H02M1/08: I H02M7/49: I H02M7/19: I H02M1/0006: A H02M7/4835: A H02J1/00: I H02M3/06: I Y02E60/60: A | JP2013255422A JP2011024392A WO2014091801A1 US2014203645A1 KR101410731B1 EP2549634A1 EP2458726A1 JPH0851770A JP4969614B2 | CN106533234A CN106533234 106533234 WO2020141838A3 WO2020141838 2020/141838 WO2020/141838A3 WO2018124523A3 WO2018124523 2018/124523 WO2018/124523A3 KR20180075340A KR20180075340 1020180075340 KR1020180075340A KR10-2018-0075340A WO2019132437A1 WO2019132437 2019/132437 WO2019/132437A1 US10461630B2 US10461630 10461630 US2019028019A1 US2019028019 20190028019 US20190028019A1 US11075587B2 US11075587 11075587 | [KO KR101723094B1]: 삭제 상호 간에 직렬연결된 MMC 컨버터의 서브모듈 내부에 DC전압을 저장하는 N개(N≥2,정수)의 에너지저장부와, 상기 N개의 에너지저장부에 각각 병렬로 연결되고 상호간에 직렬로 연결된 다수의 전력용반도체를 포함하는 브릿지회로부; 상기 N개의 에너지저장부 중 n개(1≤n&lt;N)의 직렬연결된 에너지저장부의 일단에 형성된 제1출력단자와, m개(n&lt;m≤N)의 직렬연결된 에너지저장부의 일단에 형성된 제2출력단자 중 어느 하나를 스위칭하는 스위칭부; 및 상기 스위칭부의 스위칭에 따라 상기 제1출력단자 또는 제2출력단자를 통해 출력된 전압을 저전압으로 변환하여 서브모듈 제어기로 공급하는 DC/DC컨버터; 를 포함하고, 상기 서브모듈의 입력전압이 0V부터 기설정된 최대전압(Vmax)의 범위로 증가하는 도중 상기 스위칭부는 상기 서브모듈 제어기의 초기기동시부터 기설정된 제1전압까지는 상기 제2출력단자(X4)로 스위칭하여 상기 m개의 직렬연결된 에너지저장부에 저장된 전압이 상기 DC/DC컨버터로 공급되도록 하고, 상기 제1전압에 도달한 이후에는 상기 제1출력단자(X3)로 스위칭을 변경하여 상기 n개의 직렬연결된 에너지저장부에 저장된 전압이 상기 DC/DC컨버터로 공급되도록 하는 MMC 컨버터의 서브모듈 제어기용 전원장치. 삭제 제2항에 있어서, 상기 브릿지회로부는 하프브릿지회로 또는 풀브릿지회로 중 선택된 어느 하나를 포함하는 MMC 컨버터의 서브모듈 제어기용 전원장치. [EN EP3242389B1]: A power supply apparatus (200) for a sub-module controller of a sub-module of a Modular Multilevel Converter, MMC, comprising: a bridge circuit unit (210) including N, N≥2, integer, energy storage units (211) configured to store charges to a DC voltage in the sub-module of the MMC, and multiple power semiconductor devices (212) respectively connected in parallel with the N energy storage units (211) in a form of a bridge and connected in series with each other;characterized ina switching unit (220) adapted to switch any one of a first output terminal (X3) formed at a first end of n, 1≤n&lt;N, series-connected energy storage units, among the N energy storage units (211), and a second output terminal (X4) formed at a first end of m, n&lt;m≤N, series-connected energy storage units; anda DC/DC converter (230) adapted to convert a voltage, output through the first output terminal (X3) or the second output terminal (X4) depending on the switching state of the switching unit (220), into a low voltage required to drive the sub-module controller, and supplying the lower voltage to the sub-module controller. The power supply apparatus (200) of claim 1, wherein the switching unit (220) is configured to perform switching to make a connection to the second output terminal (X4) during a period from an initial operation to a preset first voltage, thus enabling a voltage stored in the m energy storage units to be supplied to the DC/DC converter (230), and to change switching to make a connection to the first output terminal (X3) during a period after the first voltage, thus enabling a voltage stored in the n energy storage units to be supplied to the DC/DC converter (230). The power supply apparatus (200) of claim 1 or 2, wherein the bridge circuit unit (210) comprises any one selected from a half-bridge circuit and a full-bridge circuit. [DE EP3242389B1]: Stromversorgungsvorrichtung (200) für eine Untermodul-Steuereinrichtung eines Untermoduls eines modularen Mehrstufenumrichters, MMC, aufweisend: eine Brückenschaltungseinheit (210), aufweisend N, wobei N ≥ 2 und eine ganze Zahl, Energiespeichereinheiten (211), die konfiguriert sind, um Ladungen zu einer Gleichspannung im Untermodul des MMC zu speichern, und mehrere Leistungshalbleiterbauelemente (212), die jeweils parallel zu den N Energiespeichereinheiten (211) in Form einer Brücke geschaltet und in Reihe miteinander geschaltet sind,gekennzeichnet durcheine Schalteinheit (220), die angepasst ist, um irgendeines von einem ersten Ausgangsanschluss (X3), der an einem ersten Ende von n, wobei 1 ≤ n &lt; N, in Reihe geschalteten Energiespeichereinheiten unter den N Energiespeichereinheiten (211) ausgebildet ist, und einem zweiten Ausgangsanschluss (X4), der an einem ersten Ende von m, wobei n &lt; m ≤ N, in Reihe geschalteten Energiespeichereinheiten ausgebildet ist, zu schalten, undeinen DC/DC-Wandler (230), der angepasst ist, um eine durch den ersten Ausgangsanschluss (X3) oder den zweiten Ausgangsanschluss (X4) in Abhängigkeit vom Schaltzustand der Schalteinheit (220) ausgegebene Spannung in eine Niederspannung umzuwandeln, die zum Ansteuern der Untermodul-Steuereinrichtung erforderlich ist, und die Niederspannung an die Untermodul-Steuereinrichtung zuführt. Stromversorgungsvorrichtung (200) gemäß Anspruch 1, wobei die Schalteinheit (220) konfiguriert ist, um während einer Periode von einem anfänglichen Betrieb bis zu einer voreingestellten ersten Spannung ein Schalten durchzuführen, um eine Verbindung mit dem zweiten Ausgangsanschluss (X4) herzustellen, wodurch ermöglicht wird, dass eine in den m Energiespeichereinheiten gespeicherte Spannung an den DC/DC-Wandler (230) zugeführt wird, und das Schalten zu ändern, um während einer Periode nach der ersten Spannung eine Verbindung mit dem ersten Ausgangsanschluss (X3) herzustellen, wodurch ermöglicht wird, dass eine in den n Energiespeichereinheiten gespeicherte Spannung dem DC/CD-Wandler (230)zugeführt wird. Stromversorgungsvorrichtung (200) gemäß Anspruch 1 oder 2, wobei die Brückenschaltungseinheit (210) irgendeines aufweist, das aus einer Halbbrückenschaltung und einer Vollbrückenschaltung ausgewählt ist. [FR EP3242389B1]: Appareil d'alimentation électrique (200) pour un système de commande de sous-module d'un sous-module d'un Convertisseur Multiniveaux Modulaire, MMC, comprenant : une unité de circuit en pont (210) comprenant N, un nombre entier, N≥2, unités de stockage d'énergie (211) configurées pour stocker des charges à une tension CC dans le sous-module du MMC, et de multiples dispositifs à semi-conducteur électriques (212) respectivement branchés en parallèle avec les N unités de stockage d'énergie (211) sous la forme d'un pont et branchés en série les uns avec les autres ;caractérisé parune unité de commutation (220) apte à commuter n'importe laquelle d'une première borne de sortie (X3) formée à une première extrémité de n, 1≤n&lt;N, unités de stockage d'énergie branchées en série, parmi les N unités de stockage d'énergie (211), et une seconde borne de sortie (X4) formée à une première extrémité de m, n&lt;m≤N, unités de stockage d'énergie branchées en série ; etun convertisseur CC/CC (230) apte à convertir une tension, émise à travers la première borne de sortie (X3) ou la seconde borne de sortie (X4) en fonction de l'état de commutation de l'unité de commutation (220), en une basse tension requise pour commander le système de commande du sous-module, et fournissant la tension inférieure au système de commande de sous-module. Appareil d'alimentation électrique (200) selon la revendication 1, dans lequel l'unité de commutation (220) est configurée pour réaliser une commutation afin de se connecter à la seconde borne de sortie (X4) pendant une période allant d'un fonctionnement initial à une première tension préétablie, en permettant ainsi de fournir une tension stockée dans les m unités de stockage d'énergie au convertisseur CC/CC (230), et de changer la commutation pour permettre une connexion à la première borne de sortie (X3) pendant une période après la première tension, en permettant ainsi à une tension stockée dans les n unités de stockage d'énergie d'être alimentée au convertisseur CC/CC (230). Appareil d'alimentation électrique (200) selon la revendication 1 ou 2, dans lequel l'unité de circuit en pont (210) comprend n'importe quel élément sélectionné parmi un circuit en demi-pont et un circuit en pont intégral. | [KO KR101723094B1]: ＭＭＣ 컨버터의 서브모듈 제어기용 전원장치{POWER DEVICE FOR SUB-MODULE CONTROLLER OF MMC CONVERTER} 본 발명은 서브모듈 제어기용 전원장치에 관한 것으로서, 특히 고압전 직류송전(HVDC: High Voltage Direct Current)시스템과 연계되는 모듈러 멀티레벨 컨버터(MMC: Modular Multilevel Converter)의 서브모듈(sub-module) 제어기에 구동전원을 공급하도록 하는 MMC 컨버터의 서브모듈 제어기용 전원장치에 관한 것이다. 일반적으로, 초고압 직류송전(HVDC) 시스템에서는 발전소에서 생산되는 교류전력을 직류로 변환시켜 송전하고 수전단에서 교류로 재변환하여 부하에 전력을 공급하도록 한다. 이러한 HVDC 시스템은 전압승압을 통하여 효율적이고 경제적인 전력전송이 가능하고 이종계통 연계, 장거리 고효율 송전 등의 장점을 갖는다. HVDC 시스템에는 전력송전 및 무효전력 보상을 위해 MMC 컨버터가 연계된다. 이러한 MMC 컨버터에는 다수의 서브모듈(sub-module)이 직렬로 연결된다. MMC 컨버터에서 서브모듈은 매우 중요한 요소로서 별도 마련된 제어기에 의해 제어되는데, 서브모듈의 고전압을 서브모듈 제어기의 구동전원으로 이용하기 위해서는 서브모듈 제어기에 필요한 저전압으로 변환하는 전원장치가 필요하다. 도 1에는 MMC 컨버터의 등가회로도이고, 도 2는 종래의 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도이다. 주지된 바와 같이 MMC 컨버터는 1개 이상의 상모듈(phase module)(1)로 구성되고 각 상모듈(1)에는 다수의 서브모듈(10)이 직렬로 연결된다. 또한, 각 상모듈(1)은 직류전압측을 정(+) 및 부(-)의 직류전압 모선 P 및 N에 각각 접속시킨다. 이들 직류전압 P-N 모선 간에는 직류 고전압이 존재한다. 각각의 서브모듈(10)은 두 개의 접속단자(X1,X2)가 형성된다. 종래의 MMC 컨버터의 서브모듈 제어기용 전원장치(20)는 에너지저장부(21)와 그 에너지저장부(21)에 다수의 직렬연결된 저항(22)이 병렬로 연결되고, 그 중 일부 저항에 DC/DC컨버터(23)가 연결된다. 이러한 서브모듈 제어기용 전원장치(20)가 HVDC 시스템에 연계된 MMC 컨버터에 적용되는 경우 에너지저장부(23)에 저장된 수~수십㎸의 고전압을 서브모듈 제어기에 필요한 수~수십V의 저전압으로 변환해야 한다. 이를 위해 종래는 에너지저장부(21)에 병렬로 연결된 다수의 저항(22)을 이용한 저항분압방식을 사용한다. 즉, 에너지저장부(21)에 충전된 전압을 서로 직렬로 연결된 다수의 저항(R1~R3) 중 일부 저항(R3)에 걸리는 전압으로 분압하여 저전압으로 변환하도록 한다. 하지만, 이러한 종래의 전원장치(20)는 분압을 위한 저항(R1~R3)으로 인해 불필요한 손실이 발생하는 문제점이 있다. 본 발명은 HVDC 시스템과 연계되는 MMC 컨버터의 다수의 서브모듈이 내부 고전압을 입력받아 서브모듈 제어기의 구동에 필요한 저전압으로 변환하여 서브모듈 제어기로 제어전원을 공급함에 있어서 불필요한 손실을 최소화하도록 하는 MMC 컨버터의 서브모듈 제어기용 전원장치를 제공하는데 그 목적이 있다. 본 발명의 일 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치는, 상호 간에 직렬연결된 MMC 컨버터의 서브모듈 내부에 DC전압을 저장하는 N개(N≥2,정수)의 에너지저장부와, 상기 N개의 에너지저장부에 브릿지 형태로 병렬로 연결된 다수의 전력용반도체를 포함하는 브릿지회로부; 및 상기 N개의 에너지저장부 중 n개(1≤n&lt;N)의 직렬연결된 에너지저장부의 양단에 형성된 출력단자로부터 출력된 전압을 저전압으로 변환하여 서브모듈 제어기로 공급하는 DC/DC컨버터를 포함한다. 또한, 본 발명의 다른 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치는, 상호 간에 직렬연결된 MMC 컨버터의 서브모듈 내부에 DC전압을 저장하는 N개(N≥2,정수)의 에너지저장부와, 상기 N개의 에너지저장부에 각각 병렬로 연결되고 상호간에 직렬로 연결된 다수의 전력용반도체를 포함하는 브릿지회로부; 상기 N개의 에너지저장부 중 n개(1≤n&lt;N)의 직렬연결된 에너지저장부의 일단에 형성된 제1출력단자와, m개(n&lt;m≤N)의 직렬연결된 에너지저장부의 일단에 형성된 제2출력단자 중 어느 하나를 스위칭하는 스위칭부; 및 상기 스위칭부의 스위칭에 따라 상기 제1출력단자 또는 제2출력단자를 통해 출력된 전압을 저전압으로 변환하여 서브모듈 제어기로 공급하는 DC/DC컨버터를 포함하고, 상기 서브모듈의 입력전압이 0V부터 기설정된 최대전압(Vmax)의 범위로 증가하는 도중 상기 스위칭부는 상기 서브모듈 제어기의 초기기동시부터 기설정된 제1전압까지는 상기 제2출력단자(X4)로 스위칭하여 상기 m개의 직렬연결된 에너지저장부에 저장된 전압이 상기 DC/DC컨버터로 공급되도록 하고, 상기 제1전압에 도달한 이후에는 상기 제1출력단자(X3)로 스위칭을 변경하여 상기 n개의 직렬연결된 에너지저장부에 저장된 전압이 상기 DC/DC컨버터로 공급되도록 한다. 삭제 본 발명에서, 상기 브릿지회로부는 하프브릿지회로 또는 풀브릿지회로 중 선택된 어느 하나를 포함한다. 본 발명에 의하면 MMC 컨버터의 서브모듈용 전원제어장치 내부의 각종 소자에서 발생하는 손실을 최소화할 수 있다. 또한, 본 발명에 의하면 분압저항을 이용한 종래의 전원제어장치보다 훨씬 높은 효율을 유지할 수 있다. 도 1은 일반적인 MMC 컨버터의 등가회로도, 도 2는 종래의 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도, 도 3은 본 발명의 일 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도, 도 4는 본 발명의 다른 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도. 이하, 본 발명의 일부 실시 예들을 예시적인 도면을 통해 상세히 설명한다. 각 도면의 구성요소들에 참조부호를 부가함에 있어서, 동일한 구성요소들에 대해서는 비록 다른 도면상에 표시되더라도 가능한 한 동일한 부호를 가지도록 하고 있음에 유의해야 한다. 또한, 본 발명의 실시 예를 설명함에 있어, 관련된 공지 구성 또는 기능에 대한 구체적인 설명이 본 발명의 실시 예에 대한 이해를 방해한다고 판단되는 경우에는 그 상세한 설명은 생략한다. 또한, 본 발명의 실시 예의 구성요소를 설명하는 데 있어서, 제 1, 제 2, A, B, (a), (b) 등의 용어를 사용할 수 있다. 이러한 용어는 그 구성요소를 다른 구성 요소와 구별하기 위한 것일 뿐, 그 용어에 의해 해당 구성요소의 본질이나 차례 또는 순서 등이 한정되지 않는다. 어떤 구성요소가 다른 구성요소에 "연결", "결합" 또는 "접속"된다고 기재된 경우, 그 구성요소는 그 다른 구성요소에 직접적으로 연결되거나 접속될 수 있지만, 각 구성요소 사이에 또 다른 구성요소가 "연결", "결합" 또는 "접속"될 수도 있다고 이해되어야 할 것이다. 도 3a 및 도 3b는 본 발명의 일 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도이다. 본 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치(100)는 1개 이상의 상모듈(phase module)을 포함하는 MMC 컨버터에 적용된다. 상모듈은 서로 직렬연결된 다수의 서브모듈을 포함하며 직류전압측을 정(+) 및 부(-)의 직류전압 모선 P 및 N에 각각 접속시킨다. 다수의 서브모듈은 두 입력단자(X1,X2)를 통해 서로 직렬연결되며 DC전압을 내부에 상호 간에 직렬로 연결된 에너지저장부(111)에 저장한다. 이러한 서브모듈은 제어기(미도시)에 의해 동작이 제어되며, 본 발명에 따른 전원장치(100)는 이러한 에너지저장부(111)에 저장된 고전압(수~수십㎸)을 저전압(수~수십V)으로 변환하여 서브모듈 제어기의 구동전원으로 공급하도록 한다. 본 발명의 일 실시 예에 따른 전원장치(100)는 브릿지회로부(110) 및 DC/DC컨버터(120)를 포함하여 구성된다. 브릿지회로부(110)는 N개의 에너지저장부(111) 및 다수의 전력용반도체(112)를 포함한다. N개(N≥2,정수)의 에너지저장부(111)는 상호간에 서로 직렬로 연결되고 DC전압을 저장한다. 다수의 전력용반도체(112)는 N개의 에너지저장부(111)에 브릿지 형태로 병렬로 연결된다. 본 실시 예에서 브릿지회로부(110)는 하프브릿지(half bridge) 회로 또는 풀브릿지(full bridge) 회로를 포함할 수 있다. 또한, 에너지저장부는 DC전압을 저장하는 소자로서 예컨대 커패시터 등으로 구현될 수 있고, 전력용반도체(112)는 전류의 흐름을 스위칭하는 소자로서 예컨대 IGBT, FET, 트랜지스터 등을 사용할 수 있다. 도 3a는 N개의 에너지저장부(111)와 다수의 전력용반도체(112)가 하프브릿지회로를 구성하는 예를 도시하고 도 3b는 N개의 에너지저장부(111)와 다수의 전력용반도체(112)가 풀브릿지회로를 구성하는 예를 도시하고 있다. 구체적으로, 도 3a에 도시된 하프브릿지회로의 일례에서는 N개의 에너지저장부(111)가 상호 간에 직렬로 연결되고, 상호 간에 직렬로 연결된 2개의 전력용반도체(112)가 이들 N개의 직렬연결된 에너지저장부(111)에 병렬로 연결되어 하프브릿지회로를 구성한다. 이러한 전력용반도체(112)는 턴온(turn-on)/턴오프(turn-off)제어가능한 파워반도체스위치(1121) 및 이에 병렬연결된 환류다이오드(1122)를 포함한다. 전력용반도체(112)는 제어부(미도시)의 제어신호에 의해 턴온/턴오프가 제어된다. 또한, 하프브릿지회로의 두 전력용반도체(112) 중 어느 하나의 전력용반도체의 양단에 제1입력단자(X1)와 제2입력단자(X2)가 형성되어 다른 서브모듈들과 직렬 연결된다. 도면에 일례로 전력용반도체(112)가 2개로 예시되었으나 본 발명은 이에 한정되지 않는다. 도 3b에 도시된 풀브릿지회로의 일례에서는 N개의 에너지저장부(111)가 상호간에 직렬로 연결되고, 상호간에 병렬로 연결된 두 쌍의 전력용반도체(112)의 직렬연결이 이들 N개의 직렬연결된 에너지저장부(111)에 병렬로 각각 연결되어 풀브릿지회로를 구성한다. 이러한 전력용반도체(112)는 제어부(미도시)의 제어신호에 의해 턴온/턴오프될 수 있다. 또한, 풀브릿지회로에서 각각 쌍을 이루는 전력용반도체(112)의 각 중성점에 제1입력단자(X1)와 제2입력단자(X2)가 각각 형성된다. 도면에는 일례로 전력용반도체(112)가 4개로 예시되었으나 본 발명은 이에 한정되지 않는다. DC/DC컨버터(120)는 N개의 에너지저장부(111) 중 일부인 n개(1≤n&lt;N)의 직렬연결된 에너지저장부(111)의 양단의 전압을 저전압으로 변환하여 후단의 서브모듈 제어기로 공급한다. 도 3a 및 도 3b에 도시된 일례에서는 설명의 편의상 N=5로 설정하여 각각 하프브릿지회로 및 풀브릿지회로를 구성하고 있다. 도시된 바와 같이, 하프브릿지회로는 5개의 에너지저장부(111)와 2개의 전력용반도체(112)를 포함하고 풀브릿지회로는 5개의 에너지저장부(111)와 4개의 전력용반도체(112)를 포함한다. DC/DC컨버터(120)는 5개의 에너지저장부(111) 중에 2개(n=2)의 직렬연결된 에너지저장부의 양단에 출력단자가 형성되고 상기 출력단자로부터 출력되는 전압을 공급받아 서브모듈 제어기(미도시)에 필요한 저전압으로 변환하여 출력한다. 상기에서 n=2는 물론 설명을 위한 일 예시이며 도 3의 (a)에서 n은 1~4 중 어느 하나가 될 수도 있다. 이러한 저전압 변환과정은 풀브릿지회로에도 동일하게 적용된다. 이와 같이 본 발명의 일 실시 예에 따른 전원장치(100)는 MMC 컨버터의 서브모듈의 내부에 제공된 다수의 에너지저장부(111)에 저장된 고전압을 이용하여 서브모듈 제어기의 구동전원으로 공급하되, 다수의 에너지저장부(111)에 저장된 고전압의 일부를 DC/DC컨버터(120)에서 공급받아 저전압으로 변환하여 서브모듈 제어기에의 구동전원으로 공급하도록 한다. 이로써 종래기술에서 저항분압을 이용함으로써 발생하는 발열 및 손실 문제를 해결할 수 있게 된다. 도 4는 본 발명의 다른 실시 예에 따른 MMC 컨버터의 서브모듈 제어기용 전원장치의 회로도이다. 도 4를 참조하면, 본 발명의 다른 실시 예에 따른 전원장치(200)는 브릿지회로부(210), 스위칭부(220) 및 DC/DC컨버터(230)를 포함하여 구성된다. 브릿지회로부(210)와 DC/DC컨버터(230)은 도 3의 브릿지회로부(110)와 DC/DC컨버터(120)와 동일하다. 따라서, 브릿지회로부(210)는 N개의 에너지저장부(211) 및 다수의 전력용반도체(212)를 이용하여 하프브릿지회로 또는 풀브릿지회로로 구현될 수 있다. 다만, 도 4에 도시된 전원장치(200)는 도 3에 도시된 전원장치(100) 비해 출력단자가 형성되는 위치가 일부 상이하다. 이를 하기에서 상세하게 설명하기로 한다. 본 발명의 다른 실시 예에 따른 전원장치(200)는 브릿지회로부(210)와 DC/DC컨버터(230)에서 전류의 흐름을 스위칭하는 스위칭부(220)를 더 포함한다. 이러한 스위칭부(220)는 브릿지회로부(210) 내 N개의 에너지저장부(211) 중 n개(1≤n&lt;N)의 직렬연결된 에너지저장부의 일단에 형성된 제1출력단자(X3)와, m개(n&lt;m≤N)의 직렬연결된 에너지저장부의 일단에 형성된 제2출력단자(X4) 중 어느 하나를 DC/DC컨버터(230)와 연결되도록 스위칭한다. 도 4에 도시된 일례에서는 설명의 편의상 N=5로 설정된 하프브릿지회로의 예시도를 나타낸다. 이러한 하프브릿지회로는 5개의 에너지저장부(211)와 2개의 전력용반도체(212)를 포함한다. 물론 도 3에서와 같이 브릿지회로부(210)는 풀브릿지회로로 구성될 수도 있다. 이때, 제1출력단자(X3)는 5개의 에너지저장부(211) 중 2개(n=2)의 직렬연결된 에너지저장부의 일단에 형성되고, 다른 제2출력단자(X4)는 5개(m=N=5)의 직렬연결된 에너지저장부의 일단에 형성되어 있다. 물론, 상기한 n=2, m=5(N)는 설명을 위한 일 예시이며, 다른 예로서 n=1~4 중 어느 하나가 될 수 있으며, m도 2~5 중 어느 하나가 될 수 있다. 다만, m은 n보다 큰 것이 바람직하다. 왜냐하면 기동 초기에 낮은 DC전압에서는 상대적으로 고전압이 충전된 m개의 에너지저장부의 전압을 DC/DC컨버터(230)에서 저전압으로 변환하도록 하고, 이후에 일정한 시간이 경과한 후 높은 DC전압에서는 상대적으로 저전압이 충전된 n개의 에너지저장부의 전압을 DC/DC컨버터(230)에서 저전압으로 변환하기 위한 것이다. 여기서, 스위칭부(220)는 5개의 에너지저장부(211) 중 2개의 직렬연결된 에너지저장부의 일단에 형성된 제1출력단자(X3)와, 5개의 직렬연결된 에너지저장부의 일단에 형성된 제2출력단자(X4) 중 어느 한 출력단자가 DC/DC컨버터(230)와 연결되도록 스위칭한다. 이때, 바람직하게는 초기에 제2출력단자(X4)를 DC/DC컨버터(230)와 연결하도록 스위칭하고, 이후에 일정시점에서 제1출력단자(X3)를 DC/DC컨버터(230)와 연결하도록 스위칭한다. 구체적으로, 본 실시 예에 따른 전원장치(200)가 MMC 컨버터에 적용되는 경우 서브모듈의 DC전압은 0V부터 기설정된 최대전압(Vmax)의 범위로 증감한다. 전원장치(200)의 초기 기동시부터 기설정된 제1전압까지는 제2출력단자(X4)로 스위칭하여 상대적으로 더 많은 개수의 직렬연결된 에너지저장부에 저장된 전압, 즉 상대적으로 더 큰 전압이 DC/DC컨버터(230)로 공급되도록 함으로써 빨리 안정적인 전원공급이 이루어지도록 하고, 제1전압 이후에는 제1출력단자(X3)로 스위칭을 변경하여 상대적으로 더 작은 개수의 직렬연결된 에너지저장부에 저장된 전압, 즉 상대적으로 더 작은 전압이 DC/DC컨버터(230)로 공급되도록 함으로써 고전압에 의한 회로의 부담을 줄이도록 한다. DC/DC컨버터(230)에서는 이와 같이 공급된 전압을 서브모듈 제어기의 구동에 필요한 저전압으로 변환하여 서브모듈 제어기로 공급하게 된다. 이와 같이 본 발명의 일 실시 예에 따른 전원장치(200)는 MMC 컨버터의 서브모듈의 내부에 제공된 다수의 에너지저장부(211)에 저장된 고전압을 이용하여 서브모듈 제어기의 구동전원으로 공급하되, 초기 기동시에는 상대적으로 더 많은 에너지저장부(211)에 저장된 고전압을 DC/DC컨버터(120)에서 공급받아 저전압으로 변환하여 서브모듈 제어기에의 구동전원으로 공급하도록 하고, 일정시점 이후부터는 상대적으로 더 적은 에너지저장부(211)에 저장된 저전압을 DC/DC컨버터(120)에서 공급받아 저전압으로 변환하여 서브모듈 제어기에의 구동전원으로 공급하도록 한다. 이로써 종래기술에서 저항분압을 이용함으로써 발생하는 발열 및 손실 문제를 해결할 수 있게 된다. 이상에서, 본 발명의 실시 예를 구성하는 모든 구성 요소들이 하나로 결합하거나 결합하여 동작하는 것으로 설명되었다고 해서, 본 발명이 반드시 이러한 실시 예에 한정되는 것은 아니다. 즉, 본 발명의 목적 범위 안에서라면, 그 모든 구성 요소들이 하나 이상으로 선택적으로 결합하여 동작할 수도 있다. 또한, 이상에서 기재된 "포함하다", "구성하다" 또는 "가지다" 등의 용어는, 특별히 반대되는 기재가 없는 한, 해당 구성 요소가 내재할 수 있음을 의미하는 것이므로, 다른 구성 요소를 제외하는 것이 아니라 다른 구성 요소를 더 포함할 수 있는 것으로 해석되어야 한다. 기술적이거나 과학적인 용어를 포함한 모든 용어들은, 다르게 정의되지 않는 한, 본 발명이 속하는 기술 분야에서 통상의 지식을 가진 자에 의해 일반적으로 이해되는 것과 동일한 의미가 있다. 사전에 정의된 용어와 같이 일반적으로 사용되는 용어들은 관련 기술의 문맥상의 의미와 일치하는 것으로 해석되어야 하며, 본 발명에서 명백하게 정의하지 않는 한, 이상적이거나 과도하게 형식적인 의미로 해석되지 않는다. 이상의 설명은 본 발명의 기술 사상을 예시적으로 설명한 것에 불과한 것으로서, 본 발명이 속하는 기술 분야에서 통상의 지식을 가진 자라면 본 발명의 본질적인 특성에서 벗어나지 않는 범위에서 다양한 수정 및 변형이 가능할 것이다. 따라서, 본 발명에 개시된 실시 예들은 본 발명의 기술 사상을 한정하기 위한 것이 아니라 설명하기 위한 것이고, 이러한 실시 예에 의하여 본 발명의 기술 사상의 범위가 한정되는 것은 아니다. 본 발명의 보호 범위는 아래의 청구범위에 의하여 해석되어야 하며, 그와 동등한 범위 내에 있는 모든 기술 사상은 본 발명의 권리범위에 포함되는 것으로 해석되어야 할 것이다. 110,210 : 에너지저장부 120,230 : DC/DC컨버터 220 : 스위칭부 [EN EP3242389B1]: Technical Field The present invention generally relates to a power supply apparatus for a sub-module controller and, more particularly, to a power supply apparatus for a sub-module controller of a Modular Multilevel Converter (MMC), which supplies driving power to the sub-module controller of an MMC connected to a High Voltage Direct Current (HVDC) system. Background Art Generally, in High Voltage Direct Current (HVDC) systems, Alternating Current (AC) power produced in a power plant is converted into DC power and the DC power is transmitted, and a power receiving stage re-converts the DC power into AC power and supplies the AC power to a load. Such an HVDC system is advantageous in that power may be efficiently and economically transmitted via voltage boosting, and in that connections between heterogeneous systems and long-distance high-efficiency power transmission are possible. A Modular Multilevel Converter (MMC) is connected to an HVDC system to realize power transmission and reactive power compensation. In the MMC, multiple sub-modules are connected in series with each other. In the MMC, sub-modules are very important components and are controlled by a separately provided controller. To use the high voltage from sub-modules as driving power for the sub-module controller, there is required a power supply apparatus, which converts the high voltage into the low voltage required for the sub-module controller. FIG. 1 is an equivalent circuit diagram of an MMC, and FIG. 2 is a circuit diagram of a conventional power supply apparatus for a sub-module controller of an MMC. As is well-known in the art, the MMC is composed of one or more phase modules 1, and multiple sub-modules 10 are connected in series with each other in each phase module 1. Further, respective DC voltage terminals of each phase module 1 are connected to positive (+) and negative (-) DC voltage buses P and N. A high DC voltage is present between the DC voltage P and N buses. In each sub-module 10, two connection terminals X1 and X2 are formed. A conventional power supply apparatus 20 for the sub-module controller of the MMC includes an energy storage unit 21 and multiple series-connected resistors 22, connected in parallel with the energy storage unit 21, wherein a DC/DC converter 23 is connected to some of the series-connected resistors. When the power supply apparatus 20 for the sub-module controller is applied to an MMC that is connected to an HVDC system, a high voltage of several to several tens of kV, stored in the energy storage unit 21, must be converted into a low voltage of several to several tens of V required for the sub-module controller. For this, in the conventional technology, a resistor voltage-dividing scheme using multiple resistors 22 connected in parallel with the energy storage unit 21 is used. That is, the voltage charged in the energy storage unit 21 is divided into voltages including a voltage across some resistor R3, among the multiple series-connected resistors R1 to R3, and is thus converted into a low voltage. However, the conventional power supply apparatus 20 is problematic in that unnecessary loss occurs due to the use of the resistors R1 to R3 for voltage division, EP 2 549 634 A1 discloses that when an electric power conversion apparatus formed by connecting a plurality of cells each using a semiconductor switching element in a cascade manner is controlled, it is necessary to communicate between the cells and a central controller. However, an increase in the number of cells increases the amount of information to be communicated and the load imposed on information processing. EP 2 458 726 A1 discloses a power conversion device, wherein among the optical fiber cables used in control/communication, at least the majority of high-voltage optical fiber cables with a dielectric strength against the output voltages of a plurality of cells can be eliminated and thus a low-voltage optical fiber cable with a dielectric strength against the output voltage of one cell can be used. Furthermore, here, the length required for the optical fiber cable can be reduced. A controller of the power conversion device comprising a plurality of cascade-connected cells comprises a central controller, and a cell controller with the same potential as each cell, the cell controller being installed in the vicinity of each cell, wherein the central controller and each cell controller are daisy-chained using an optical fiber cable. JP H08 51770 A discloses that a gate drive circuit for semiconductor switch comprises a series circuit of capacitors connected in parallel with the snubber capacitor of a semiconductor switch, and an energy collection circuit for charging a storage capacitor, serving as a power supply for a gate drive circuit comprising the series circuit of the capacitors with a low voltage. Disclosure Technical Problem An object of the present invention is to provide a power supply apparatus for a sub-module controller of an MMC, which minimizes unnecessary loss when multiple sub-modules in an MMC connected to an HVDC system receive an internal high voltage, convert the high voltage into a low voltage required to drive the sub-module controller, and supply the low voltage to the sub-module controller as control power. Technical Solution A power supply apparatus for a sub-module controller of a Modular Multilevel Converter (MMC) according to claim 1 is provided. Further embodiments are described in the dependent claims. A power supply apparatus for a sub-module controller of a MMC according to the present invention includes a bridge circuit unit including N (N≥2, integer) energy storage units for storing a DC voltage in a sub-module of the MMC, and multiple power semiconductor devices respectively connected in parallel with the N energy storage units in a form of a bridge and connected in series with each other; a switching unit for switching any one of a first output terminal formed at a first end of n (1≤n&lt;N) series-connected energy storage units, among the N energy storage units, and a second output terminal formed at a first end of m (n&lt;m≤N) series-connected energy storage units; and a DC/DC converter for converting a voltage, output through the first output terminal or the second output terminal depending on switching of the switching unit, into a low voltage, and supplying the low voltage to the sub-module controller. In the present invention, the switching unit may be configured to perform switching to make a connection to the second output terminal during a period from an initial operation to a preset first voltage, thus enabling a voltage stored in the m energy storage units to be supplied to the DC/DC converter, and to change switching to make a connection to the first output terminal during a period after the first voltage, thus enabling a voltage stored in the n energy storage units to be supplied to the DC/DC converter. In the present invention, the bridge circuit unit may include any one selected from a half-bridge circuit and a full-bridge circuit. Advantageous Effects According to the present invention, loss occurring in various types of components included in a power supply apparatus for sub-module controller in an MMC may be minimized. Further, according to the present invention, efficiency much higher than that of the conventional power supply apparatus using voltage-dividing resistors may be realized. Description of Drawings FIG. 1 is an equivalent circuit diagram of a typical MMC; FIG. 2 is a circuit diagram showing a conventional power supply apparatus for a sub-module controller of an MMC; FIG. 3 is a circuit diagram showing a power supply apparatus for a sub-module controller forming background art; and FIG. 4 is a circuit diagram showing a power supply apparatus for a sub-module controller of an MMC according to the present invention. Best Mode Embodiments of the present invention are described with reference to the accompanying drawings in order to describe the present invention in detail so that those having ordinary knowledge in the technical field to which the present invention pertains can easily practice the present invention. It should be noted that the same reference numerals are used to designate the same or similar elements throughout the drawings. In the following description of the present invention, detailed descriptions of known functions and configurations which are deemed to make the gist of the present invention obscure will be omitted. Further, terms such as "first", "second", "A", "B", "(a)", and "(b)" may be used to describe the components of the present invention. These terms are merely used to distinguish relevant components from other components, and the substance, sequence or order of the relevant components is not limited by the terms. It should be understood that a representation indicating that a first component is "linked", "coupled", or "connected" to a second component includes not only the case where the first component is directly coupled or connected to the second component but also cases where a third component is "linked", "coupled" or "connected" between the first and second components. FIGS. 3a and 3b are circuit diagrams showing a power supply apparatus for a sub-module controller of an MMC according to background art, and are presented here merely for illustrative purposes. A power supply apparatus 100 for a sub-module controller of an MMC according to the present invention is applied to an MMC having one or more phase modules. Each phase module includes multiple series-connected sub-modules, and DC voltage terminals thereof are connected to positive (+) and negative (-) DC voltage buses P and N, respectively. The multiple sub-modules are connected in series with each other through two input terminals X1 and X2, and store a DC voltage in energy storage units 111 connected in series with each other in the power supply apparatus. The operations of such sub-modules are controlled by a controller (not shown), and the power supply apparatus 100 according to the present invention is configured to convert a high voltage (several to several tens of kV), stored in the energy storage units 111, into a low voltage (several to several tens of V), and supply the low voltage to the sub-module controller as driving power. FIG. 4 is a circuit diagram showing a power supply apparatus for a sub-module controller of an MMC according to the present invention. Referring to FIG. 4, a power supply apparatus 200 according to the present invention includes a bridge circuit unit 210, a switching unit 220, and a DC/DC converter 230. The bridge circuit unit 210 and the DC/DC converter 230 are identical to the bridge circuit unit 110 and the DC/DC converter 120 of FIG. 3. Therefore, the bridge circuit unit 210 may be implemented as a half-bridge circuit or a full-bridge circuit using N energy storage units 211 and multiple power semiconductor devices 212. However, the power supply apparatus 200 shown in FIG. 4 differs slightly from the power supply apparatus 100 shown in FIG. 3 as to the position at which output terminals are formed. This will be described in detail later. The power supply apparatus 200 according to the present invention further includes a switching unit 220 for switching the flow of current in the bridge circuit unit 210 and the DC/DC converter 230. Such a switching unit 220 performs switching so that any one of a first output terminal X3, formed at a first end of n (1≤n&lt;N) series-connected energy storage units among N energy storage units 211 in the bridge circuit unit 210, and a second output terminal X4, formed at a first end of m (n&lt;m&lt;N) series-connected energy storage units, is connected to the DC/DC converter 230. In the example shown in FIG. 4, a half-bridge circuit, in which N = 5 is preset, is illustrated for the convenience of description. The half-bridge circuit includes five energy storage units 211 and two power semiconductor devices 212. Of course, as shown in FIG. 3, the bridge circuit unit 210 may be implemented as a full-bridge circuit. In this case, the first output terminal X3 is formed at the first end of two (n=2) series-connected energy storage units among five energy storage units 211, and the other second output terminal X4 is formed at the first end of five (m = N = 5) series-connected energy storage units. Of course, in the above description, n=2 and m=5(N) are only examples for description, and, as another example, n may be any one integer from 1 to 4, and m may be any one integer from 2 to 5. However, it is preferable that m be greater than n. The reason for this is that, at a low DC voltage in initial operation, the DC/DC converter 230 converts the voltage of m energy storage units, in which a relatively high voltage is charged, into a low voltage, and at a high DC voltage generated after a predetermined period of time has elapsed, the DC/DC converter 230 converts the voltage of n energy storage units, in which a relatively low voltage is charged, into a low voltage. Here, the switching unit 220 performs switching so that any one of the first output terminal X3, formed at the first end of two series-connected energy storage units, among five energy storage units 211, and the second output terminal X4, formed at the first end of the five series-connected energy storage units, is connected to the DC/DC converter 230. Here, preferably, switching is performed such that the second output terminal X4 is initially connected to the DC/DC converter 230 and such that, since then, the first output terminal X3 is connected to the DC/DC converter 230 at a predetermined time. More specifically, when the power supply apparatus 200 according to the present embodiment is applied to an MMC, the DC voltage of the sub-modules increases or decreases in a range from 0 V to a preset maximum voltage (Vmax). During a period from the initial operation of the power supply apparatus 200 to a preset first voltage, switching to make a connection to the second output terminal X4 is performed, so that the voltage stored in a relatively large number of series-connected energy storage units, that is, a relatively high voltage, is supplied to the DC/DC converter 230, thus enabling the supply of power to be stably performed. After the first voltage, switching is changed to make a connection to the first output terminal X3, so that the voltage stored in a relatively small number of series-connected energy storage units, that is, a relatively low voltage, is supplied to the DC/DC converter 230, thus reducing the high-voltage burden on the circuit. The DC/DC converter 230 converts the voltage supplied in this way into the low voltage required to drive the sub-module controller and supplies the low voltage to the sub-module controller. In this way, the power supply apparatus 200 according to the embodiment of the present invention is configured to supply driving power to the sub-module controller using the high voltages, stored in the multiple energy storage units 211 provided in each MMC sub-module, wherein, during initial driving, the high voltage stored in a relatively large number of energy storage units 211 is supplied from the DC/DC converter 120 and is converted into a low voltage, and the low voltage is supplied to the sub-module controller as driving power, and wherein, since a predetermined time, a low voltage stored in a relatively small number of energy storage units 211 is supplied from the DC/DC converter 120 and is converted into a low voltage, and the low voltage is supplied to the sub-module controller as the driving power. In this way, the problem of heat generation and loss appearing in the conventional technology due to the use of voltage-dividing resistors may be solved. In the above description, although a description has been made such that all components constituting embodiments of the present invention are combined into a single component or are operated with the components being combined with each other, the present invention is not limited to those embodiments. Further, it should be understood that terms such as "comprise", "include" or "have" are merely intended to indicate that the corresponding component is internally present, unless a description to the contrary is specifically pointed out in context, and are not intended to exclude the possibility that other components may be additionally included. Unless differently defined, all terms used here including technical or scientific terms have the same meanings as the terms generally understood by those skilled in the art to which the present invention pertains. The terms identical to those defined in generally used dictionaries should be interpreted as having meanings identical to contextual meanings of the related art, and are not interpreted as being ideal or excessively formal meanings unless they are definitely defined in the present specification. The protection scope of the present invention should be defined by the accompanying claims.
[DE EP3556000B1]: MODUL FÜR MODULAREN MEHRPUNKTUMRICHTER MIT KURZSCHLIESSER UND KONDENSATORSTROMBEGRENZUNG [EN EP3556000B1]: MODULE FOR MODULAR MULTILEVEL CONVERTER WITH CROWBAR AND CAPACITOR CURRENT LIMITATION [FR EP3556000B1]: MODULE D'UN CONVERTISSEUR MODULAIRE MULTI-NIVEAUX AVEC COURT-CIRCUITEUR ET LIMITEUR DE COURANT DU CONDENSATEUR [ZH CN211930497U]: 变换器模块和电压中间电路变换器 | [DE WO2018149493A1]: Die Erfindung betrifft ein Umrichtermodul (7) für einen Spannungszwischenkreisumrichter (1) mit einer Leistungshalbleiterschaltung (101) mit wenigstens zwei Leistungshalbleiterschaltern (102, 104), einem Energiespeicher (106) in einer Parallelschaltung zu der Leistungshalbleiterschaltung sowie einer Schutzvorrichtung (108) umfassend einen steuerbaren Schutz-Halbleiter (109), der in einer Parallelschaltung zum Energiespeicher angeordnet ist. Die Erfindung zeichnet sich dadurch aus, dass die Schutzvorrichtung ferner einen Strombegrenzer (114) zum Begrenzen von Stoßströmen umfasst, der in Reihe zum Energiespeicher angeordnet ist. Ferner betrifft die Erfindung einen Spannungszwischenkreisumrichter mit dem Umrichtermodul. [EN CN211930497U]: The utility model relates to a converter module and a voltage intermediate circuit converter. Converter module (7) for a voltage intermediate circuit converter (1) and having:-a converter module (7) for a voltage intermediate circuit converter (1); a power semiconductor circuit (101) with at least two power semiconductor switches (102, 104), an energy store (106) in the circuit in parallel with the power semiconductor circuit, and a protection device (108) comprising a controllable protection semiconductor (109) which is arranged in the circuit in parallel with the energy store. The protectiondevice is characterized in that the protection device further comprises a current limiter (114) used for limiting impact current, and the current limiter and the energy storage device are arranged inseries. Furthermore, the voltage intermediate circuit converter has a converter module. [FR WO2018149493A1]: L'invention concerne un module convertisseur (7), destiné à un convertisseur de tension indirect (1), comprenant un circuit à semi-conducteur de puissance (101) muni d'au moins deux commutateurs à semi-conducteur de puissance (102, 104), un accumulateur d'énergie (106) dans un circuit parallèle au circuit à semi-conducteur de puissance et un dispositif de protection (108) comprenant un semi-conducteur de protection commandable (109) disposé dans un circuit parallèle avec l'accumulateur d'énergie. L'invention est caractérisée en ce que le dispositif de protection comprend en outre un limiteur de courant (114), destiné à limiter des courants de choc, qui est disposé en série avec l'accumulateur d'énergie. En outre, l'invention concerne un convertisseur de tension indirect muni du module convertisseur. [ZH CN211930497U]: 本实用新型涉及一种变换器模块和一种电压中间电路变换器。变换器模块(7)用于电压中间电路变换器(1)并且具有：带有至少两个功率半导体开关(102，104)的功率半导体电路(101)，与功率半导体电路并联的电路中的能量存储器(106)，以及包括可控保护半导体(109)的保护装置(108)，该可控保护半导体布置在与能量存储器并联的电路中。本实用新型的特征在于，保护装置还包括用于限制冲击电流的限流器(114)，该限流器与能量存储器串联地布置。此外，电压中间电路变换器具有变换器模块。 | WO2018149493A1 | 2018-08-23 | EP2017053374W | 2017-02-15 | EP2017053374W, 2017-02-15 | WO2018149493A1: 2018-08-23 EP3556000B1: 2021-06-23 CN211930497U: 2020-11-13 | SIEMENS AG SIEMENS ENERGY GLOBAL GMBH & CO KG | ECKEL HANS-GÜNTER JUNGHANS CHRISTOPH SCHMITT DANIEL HANS-GUNTER ECKEL CHRISTOPH JUNGHANS DANIEL SCHMITT | H02M1/32: I H02M7/483: I | H02M1/32: I H02M7/4835: I | WO2013044961A1 US2014226374A1 WO2016203517A1 JP2013169088A WO2016128643A1 WO2014090272A1 DE10323220A1 WO2016155837A1 | EP3621190A1 EP3621190 3621190 WO2020173566A1 WO2020173566 2020/173566 WO2020/173566A1 | [DE EP3556000B1]: Umrichtermodul (7a) für einen Spannungszwischenkreisumrichter (1) mit - einer Leistungshalbleiterschaltung (101) mit wenigstens zwei Leistungshalbleiterschaltern (102, 104)- einem Energiespeicher (106) in einer Parallelschaltung zu der Leistungshalbleiterschaltung(101), sowie- einer Schutzvorrichtung (108) umfassend einen steuerbaren Schutz-Halbleiter (109), der in einer Parallelschaltung zum Energiespeicher (106) angeordnet ist, die Schutzvorrichtung (108) ferner einen Strombegrenzer (114) zum Begrenzen von Stoßströmen umfasst, der in Reihe zum Energiespeicher (106) angeordnet ist dadurch gekennzeichnet, dass der Strombegrenzer (114)- eine Primärwicklung (120), die in Reihe zum Energiespeicher (106) angeordnet ist, sowie- eine Sekundärwicklung (121) umfasst, wobei die Sekundärwicklung (121) und die Primärwicklung (120) magnetisch gekoppelt sind und die Sekundärwicklung (121) widerstandsbehaftet kurzgeschlossen ist, wobei der Schutz-Halbleiter (109), die Primärwicklung (120) und die Sekundärwicklung (121) in einem mechanischen Spannverband (122) fixiert sind. Umrichtermodul (7a) nach einem der vorangehenden Ansprüche, wobei die Leistungshalbleiterschaltung (101) in einem Modulgehäuse (123) und die Schutzvorrichtung (108) außerhalb des Modulgehäuses (123) angeordnet sind. Umrichtermodul (7a) nach einem der vorangehenden Ansprüche, wobei der Schutz-Halbleiter (109) einen Gate-Anschluss (110) aufweist, der mit einer Ansteuerschaltung (111) verbunden ist, die induktiv mit einer Verbindungsleitung (112) zwischen dem Energiespeicher (106) und der Leistungshalbleiterschaltung (101) gekoppelt ist. Umrichtermodul (7a) nach Anspruch 3, wobei die Ansteuerschaltung (111) eine Sensorwicklung (111a) umfasst, die um oder an der Verbindungsleitung (112) angeordnet ist. Umrichtermodul (7a) nach einem der Ansprüche 3 oder 4, wobei die Ansteuerschaltung (111) eine Kapazität (117) umfasst, die zwischen dem Gate-Anschluss (110) und einem Kathoden-Anschluss (118) des Schutz-Halbleiters (109) angeordnet ist. Umrichtermodul (7a) nach einem der Ansprüche 3 bis 5, wobei die Ansteuerschaltung (111) einen Diac (116) umfasst, der mit dem Gate-Anschluss (110) des Schutz-Halbleiters (109) verbunden ist. Umrichtermodul (7a) nach einem der Ansprüche 3 bis 6, wobei die Ansteuerschaltung (111) ein Widerstandselement (115) umfasst. Umrichtermodul (7a) nach einem der vorangehenden Ansprüche, wobei die Leistungshalbleiter (102, 104) der Leistungshalbleiterschaltung (101) in einer Halbbrückenschaltung oder einer Vollbrückenschaltung miteinander verbunden sind. Spannungszwischenkreisumrichter (1) mit einer Mehrzahl von Umrichterarmen (6a-f), wobei jeder Umrichterarm (6a-f) eine Reihenschaltung von Schaltmodulen umfasst, wobei wenigstens eines der Schaltmodule ein Umrichtermodul (7a) nach einem der Ansprüche 1 bis 8 ist. [EN EP3556000B1]: Converter module (7a) for a voltage source converter (1) having - a power semiconductor circuit (101) having at least two power semiconductor switches (102, 104)- an energy store (106) in a parallel circuit with the power semiconductor circuit (101), and- a protective device (108) comprising a controllable protective semiconductor (109), which is arranged in a parallel circuit with the energy store (106), the protective device (108) also comprises a current limiter (114) for limiting surge currents and which is arranged in series with the energy store (106), characterized in that the current limiter (114) comprises- a primary winding (120), which is arranged in series with the energy store (106), and- a secondary winding (121), wherein the secondary winding (121) and the primary winding (120) are magnetically coupled and the secondary winding (121) is shortcircuited in a resistive manner, wherein the protective semiconductor (109), the primary winding (120) and the secondary winding (121) are fixed in a mechanically clamped stack (122). Converter module (7a) according to the preceding claim, wherein the power semiconductor circuit (101) is arranged in a module housing (123) and the protective device (108) is arranged outside of the module housing (123). Converter module (7a) according to one of the preceding claims, wherein the protective semiconductor (109) has a gate terminal (110), which is connected to a drive circuit (111), which is inductively coupled to a connecting line (112) between the energy store (106) and the power semiconductor circuit (101). Converter module (7a) according to Claim 3, wherein the drive circuit (111) comprises a sensor winding (111a), which is arranged around or on the connecting line (112). Converter module (7a) according to one of Claims 3 or 4, wherein the drive circuit (111) comprises a capacitance (117), which is arranged between the gate terminal (110) and a cathode terminal (118) of the protective semiconductor (109). Converter module (7a) according to one of Claims 3 to 5, wherein the drive circuit (111) comprises a diac (116), which is connected to the gate terminal (110) of the protective semiconductor (109). Converter module (7a) according to one of Claims 3 to 6, wherein the drive circuit (111) comprises a resistance element (115) . Converter module (7a) according to one of the preceding claims, wherein the power semiconductors (102, 104) of the power semiconductor circuit (101) are connected to one another in a half-bridge circuit or a full-bridge circuit. Voltage source converter (1) having a plurality of converter arms (6a-f), wherein each converter arm (6a-f) comprises a series circuit of switching modules, wherein at least one of the switching modules is a converter module (7a) according to one of Claims 1 to 8. [FR EP3556000B1]: Module (7a) d'un convertisseur (1) de tension à circuit intermédiaire, comprenant : - un circuit (101) à semi-conducteur de puissance ayant au moins deux interrupteurs (102, 104) à semi-conducteur de puissance- un accumulateur (106) d'énergie dans un circuit en parallèle avec le circuit (101) à semi-conducteur de puissance, ainsi que- un système (108) de protection, comprenant un semi-conducteur (109) de protection pouvant être commandé, qui est monté suivant un circuit en parallèle avec l'accumulateur (106) d'énergie, le système (108) de protection comprenant en outre un limiteur (114) de courant pour limiter des courants d'acoup, qui est monté en série avec l'accumulateur (106) d'énergie caractérisé ce que le limiteur (114) de courant comprend : - un enroulement (120) primaire, qui est monté en série avec l'accumulateur (106) d'énergie, ainsi que- un enroulement (121) secondaire, dans lequel l'enroulement 121 secondaire et l'enroulement (120) primaire sont couplés magnétiquement et l'enroulement (121) secondaire est court-circuité à résistance, le semi-conducteur (109) de protection, l'enroulement (120) primaire et l'enroulement (121) secondaire étant immobilisés en un assemblage (122) mécanique de serrage. Module (7a) de convertisseur suivant l'une des revendications précédentes, dans lequel le circuit (101) à semi-conducteur de puissance est disposé dans un boîtier (123) du module et le système (108) de protection est disposé à l'extérieur du boîtier 123 du module. Module (7a) suivant l'une des revendications précédentes dans lequel le semi-conducteur (109) de protection a une borne (110) de grille, qui est reliée à un circuit (111) d'excitation, qui est couplé inductivement à une ligne (112) de liaison entre l'accumulateur 106 d'énergie et le circuit 101 à semi-conducteur de puissance. Module (7a) suivant la revendication 3, dans lequel le circuit (101) d'excitation comprend un enroulement (111) de capteur, qui est monté autour ou sur la ligne (112) de liaison. Module (7a) suivant l'une des revendications 3 ou 4, dans lequel le circuit (111) d'excitation comprend une capacité (117), qui est montée entre la borne (110) de grille et une borne (118) de cathode du semi-conducteur (109) de protection. Module (7a) suivant l'une des revendications 3 à 5, dans lequel le circuit (111) d'excitation comprend un diac (116), qui est connecté à la borne (110) de grille du semi-conducteur (109) de protection. Module (7a) suivant l'une des revendications 3 à 6, dans lequel le circuit (111) d'excitation comprend un élément (115) de résistance. Module (7a) suivant l'une des revendications précédentes dans lequel les semi-conducteurs (102, 104) de puissance du circuit (101) à semi-conducteur de puissance sont connectés entre eux en un circuit à demi-pont ou en un circuit à pont complet. Convertisseur (1) de tension à circuit intermédiaire ayant une pluralité de bras (6a-f) de convertisseur, chaque bras (6a-f) de convertisseur comprenant un circuit série de modules de coupure, dans lequel au moins l'un des modules de coupure est un module (7a) de convertisseur suivant l'une des revendications 1 à 8. [ZH CN211930497U]: 1 .一种变换器模块(7,7a),所述变换器模块用于电压中间电路变换器⑴并且具有： - 带有至少两个功率半导体开关(102，104)的功率半导体电路(101)， - 与所述功率半导体电路(101)并联的电路中的能量存储器(106)，以及 - 包括可控保护半导体(109)的保护装置(108)，所述可控保护半导体布置在与所述能 量存储器(106)并联的电路中， 其特征在于， 所述保护装置(108)还包括用于限制冲击电流的限流器(114)，所述限流器与所述能量 存储器(106)串联地布置。 2 .根据权利要求1所述的变换器模块(7a)，其特征在于，所述限流器(114)包括： -初级绕组(120)，所述初级绕组与所述能量存储器(106)串联地布置，以及 -次级绕组(121)，其中所述次级绕组(121)和所述初级绕组(120)磁性耦合并且所述次 级绕组(121)以带有电阻的方式短路。 3 .根据权利要求1所述的变换器模块(7a)，其特征在于，所述限流器(114)包括由电阻 元件(R)和电感(L)构成的并联电路。 4 .根据权利要求2所述的变换器模块(7a)，其特征在于，所述保护半导体(109)、所述初 级绕组(120)和所述次级绕组(121)以机械的紧固连接(122)固定。 5 .根据权利要求1至4中任一项所述的变换器模块(7a)，其特征在于，所述功率半导体 电路(101)布置在模块壳体(123)中，并且所述保护装置(108)布置在所述模块壳体(123)外 部。 6 .根据权利要求1所述的变换器模块⑺，其特征在于，所述保护半导体(109)具有栅极 接头(110)，所述栅极接头与控制电路(111)连接，所述控制电路与所述能量存储器(106)和 所述功率半导体电路(101)之间的连接线(112)电感地耦合。 7 .根据权利要求6所述的变换器模块⑺，其特征在于，所述控制电路(111)包括传感器 绕组(111a)，所述传感器绕组在所述连接线(112)附近或在所述连接线(112)处布置。 8 .根据权利要求6所述的变换器模块⑺，其特征在于，所述控制电路(111)包括电容 (117)，所述电容布置在保护半导体(109)的栅极接头(110)和阴极接头(118)之间。 9 .根据权利要求6至8中任一项所述的变换器模块⑺，其特征在于，所述控制电路 (111)包括双向触发二极管(116)，所述双向触发二极管与保护半导体(109)的栅极接头 (110)连接。 10 .根据权利要求6至8中任一项所述的变换器模块⑺，其特征在于，所述控制电路 (111)包括第一电阻(115)。 11 .根据权利要求1至4中任一项所述的变换器模块⑺，其特征在于，所述功率半导体 电路(101)的功率半导体开关(102,104)以半桥电路或全桥电路彼此连接。 12 .一种电压中间电路变换器(1)，所述电压中间电路变换器具有多个变换器臂(6af)，其特征在于，每个变换器臂(6a-f)包括开关模块的串联电路，其中开关模块中的至少一 个是根据权利要求1至10中任一项所述的变换器模块(7,7a)。 | [DE EP3556000B1]: Die Erfindung betrifft ein Umrichtermodul für einen Spannungszwischenkreisumrichter mit einer Leistungshalbleiterschaltung mit wenigstens zwei Leistungshalbleiterschaltern, einem Energiespeicher in einer Parallelschaltung zu der Leistungshalbleiterschaltung sowie einer Schutzvorrichtung umfassend einen steuerbaren Schutz-Halbleiter, der in einer Parallelschaltung zum Energiespeicher angeordnet ist. Ein solches Umrichtermodul ist aus der DE 10 323 220 A1 bekannt. Die Leistungshalbleiterschaltung des bekannten Umrichtermoduls ist als eine Vollbrückenschaltung ausgebildet. Sie umfasst zwei Reihenschaltungen von jeweils zwei Leistungshalbleiterschalteinheiten, die jeweils einen ein- und ausschaltbaren Halbleiterschalter sowie eine dazu antiparallele Freilaufdiode aufweisen. Die externen Anschlüsse der Vollbrückenschaltung sind mit Potenzialpunkten zwischen den Leistungshalbleiterschalteinheiten jeder Reihenschaltung angeordnet. Zugleich ist in einer Parallelschaltung zu Leistungshalbleiterschaltung ein Energiespeicher in Form eines Kondensators angeordnet. Der Schutz-Halbleiter des bekannten Umrichtermoduls ist eine Rückschwingdiode bzw. ein Thyristor. Bei einem Fehlerfall im Umrichtermodul, beispielsweise einem Schaltversagen eines der Halbleiterschalter der Leistungshalbleiterschaltung, kann innerhalb des Umrichtermoduls ein Kurzschluss entstehen. In einem solchen Fall kann es insbesondere zu einer schlagartigen Entladung des Energiespeichers kommen. Ohne besondere Schutzmaßnahmen können dabei Stromamplituden eines Kurzschlussstromes durch die Leistungshalbleiterschaltung von über 1 MA auftreten. Ein solcher Kurzschlussstrom kann zu einer Explosion in der Leistungshalbleiterschaltung und zur Beschädigung bzw. Zerstörung der Halbleiterschalter führen. Zudem kann die Explosionsenergie zum Verbiegen oder Reißen von Stromschienen und zu einer Beschädigung eines Gehäuses der Leistungshalbleiterschaltung führen. Der Schutz-Halbleiter des bekannten Umrichtermoduls ist dazu vorgesehen, in einem solchen Fehlerfall den Kurzschlussstrom zu übernehmen. Mittels des Schutz-Halbleiters wird der Energiespeicher im Fehlerfall niederohmig kurzgeschlossen, so dass die Leistungshalbleiterschaltung durch die Entladung des Energiespeichers nicht in Mitleidenschaft gezogen wird. Das bekannte Umrichtermodul ist ein Teil eines modularen Mehrstufenumrichters, der eine Mehrzahl von Umrichterarmen bzw. Umrichterzweigen umfasst. Die Umrichterarme des bekannten Mehrstufenumrichters erstrecken sich jeweils zwischen einem eingangsseitigen und einem ausgangsseitigen Wechselspannungsanschluss des Mehrstufenumrichters. Jeder Umrichterarm umfasst eine Reihenschaltung der Umrichtermodule. Ein solcher modularer Mehrstufenumrichter weist die vorteilhafte Eigenschaft auf, dass die mittels des modularen Mehrstufenumrichters eine mehrstufige Ausgangsspannung nahezu beliebiger Form erzeugt werden kann. Die Anzahl der erzeugbaren Stufen der Ausgangsspannung ist durch die Anzahl der Umrichtermodule in den Umrichterarmen bestimmt. Ein weiterer Vorteil des modularen Mehrstufenumrichters ist, dass in einem Fehlerfall eines der Umrichtermodule mittels einer Überbrückung dieses fehlerhaften Umrichtermoduls die Betriebsfähigkeit des modularen Mehrstufenumrichters weiterhin sichergestellt werden kann. In dem Beitrag von NICOLAS P LABBE: "An innovative currentlimiting device for automotive micro-hybrid starter motors", ELECTRICAL MACHINES (ICEM), 2012 XXTH 05 INTERNATIONAL CONFERENCE ON, IEEE, 2. September 2012 ist eine Schaltung beschrieben, die eine seriell in die Leitung eingefügte Primärwicklung umfasst, deren zugehörige Sekundärwicklung widerstandsbehaftet kurzgeschlossen ist. Aus der WO 2013/044961 A1 ist ein Schaltmodul für einen Umrichter bekannt, bei dem die Ansteuerschaltung des Schutzthyristors, der im Schaltmodul parallel zum Energiespeicher ist, eine Induktivität umfasst, die in Reihe zum Energiespeicher geschaltet ist. In der US 2014/0226374 A1 ist ein weites Schaltmodul mit einer Schutzschaltung für den Energiespeicher offenbart. Aus der WO 2016/203517 A1 und der JP 2013 169088 A ist jeweils eine Schaltung mit einem Schutzthyristor in Parallelschaltung zum Energiespeicher bekannt. In der JP 2013 169088 A wird darüber hinaus ein Spannverband für den Schutzthyristor offenbart. In der WO 2016/128643 A1 ist eine Begrenzungsschaltung für ein Motorfahrzeug mit einem Transformator beschrieben, dessen Primärwicklung seriell in eine Leitung und dessen Sekundärwicklung widerstandsbehaftet kurzgeschlossen ist. Die WO 2014/090272 A1 beschreibt ein Schaltmodul mit einer RL-Parallelschaltung in Reihe zum Energiespeicher. Die Aufgabe der vorliegenden Erfindung besteht darin, ein eingangs genanntes Umrichtermodul mit einer weiter verbesserten Schutzvorrichtung vorzuschlagen. Die Aufgabe wird durch ein Umrichtermodul gemäß Anspruch 1 gelöst. Bei einer unkontrollierten Entladung des Energiespeichers im Fehlerfall kann mittels des Strombegrenzers die Amplitude des Kurzschlussstroms begrenzt werden. Auf diese Weise können die negativen Auswirkungen des Kurzschlussstromes minimiert werden. Mittels des Strombegrenzers kann ein Stoßstrom, der im Fehlerfall im Gleichspannungszwischenkreis des Umrichtermoduls auftritt, begrenzt werden. Auf diese Weise kann vorteilhaft eine Zerstörung des Schutz-Halbleiters aufgrund eines hohen Stoßstromes vermieden werden, die ansonsten zu Austritt von Lichtbögen und Bruchstücken von Bauteilen führen kann. Als Gleichspannungszwischenkreis des Umrichtermoduls wird in diesem Zusammenhang der Stromkreis bezeichnet, der den Energiespeicher und die Leistungshalbleiterschaltung umfasst. Zweckmäßigerweise ist der Strombegrenzer derart ausgelegt, dass er in einem Normalbetrieb des Umrichtermoduls niederinduktiv ist. Die strombegrenzende Eigenschaft des Strombegrenzers tritt geeigneterweise nur in einem Fehlerfall auf. Zweckmäßigerweise ist der Schutz-Halbleiter in einem Normalbetrieb sperrend. Somit hat der Schutz-Halbleiter im Normalbetrieb keinen Einfluss auf die Arbeit des Umrichtermoduls bzw. des gesamten Stromrichters. Der Schutz-Halbleiter kann beispielsweise ein Thyristor oder ein anderer ansteuerbarer Halbleiterschalter sein. Der Schutz-Halbleiter kann dann im Fehlerfall gezündet, also eingeschaltet, werden. Nach der Zündung führt der hohe Kurzschlussstrom durch den Halbleiterschalter beispielsweise dazu, dass dieser durchlegiert, so dass ein dauerhafter niederohmiger Strompfad für den Kurzschlussstrom erzeugt ist. Gemäß der Erfindung umfasst der Strombegrenzer eine Primärwicklung, die in Reihe zum Energiespeicher angeordnet ist, sowie eine Sekundärwicklung, wobei die Sekundärwicklung und die Primärwicklung magnetisch gekoppelt sind und die Sekundärwicklung widerstandsbehaftet kurzgeschlossen ist. Somit entspricht der Strombegrenzer einem sekundärseitig kurzgeschlossenen Transformator. Die Primärseite des Transformators ist aktiver Bestandteil des Gleichspannungszwischenkreises des Umrichtermoduls. Im Fehlerfall transformiert die Primärwicklung die aufgrund des steilen Stromanstiegs aufgenommene Spannung in die Sekundärwicklung, welche dabei durch ihren ohmschen Widerstand einen Teil der aufgenommenen elektrischen Energie in Wärme umwandelt. Der induktive Anteil der Primärwicklung sorgt für eine Begrenzung der Stromanstiegsgeschwindigkeit bzw. des Stoßstromes, wobei die über den Strombegrenzer erzeugte Gegenspannung die Amplitude des Kurzschlussstromes begrenzt. Zudem kann durch die im Kurzschlussfall erhöhte Induktivität auch die Frequenz des Kurzschlussstromes verringert werden. Auf diese Weise kann vorteilhaft eine Aussendung hochfrequenter magnetischer Felder reduziert werden, wodurch eine Störung benachbarter elektronischer Baugruppen minimiert werden kann. Darüber ist es möglich, mittels des Strombegrenzers zwischen 50% und 90% der im Gleichspannungszwischenkreis des Umrichtermoduls gespeicherten Energie dissipativ abzubauen. Gemäß der Erfindung sind der Schutz-Halbleiter, die Primärwicklung und die Sekundärwicklung in einem mechanischen Spannverband fixiert. Der Schutz-Halbleiter, die Primärwicklung und die Sekundärwicklung des Strombegrenzers sind miteinander mechanisch verspannt. Dadurch kann eine besonders kompakte und mechanisch robuste Bauweise für die Schutzvorrichtung erreicht werden. Durch den kompakten Aufbau kann der Platzbedarf reduziert und damit auch ein Kostenvorteil erreicht werden. Vorzugsweise sind die Leistungshalbleiterschaltung in einem Modulgehäuse und die Schutzvorrichtung außerhalb des Modulgehäuses angeordnet. Auf diese Weise sind der innere Aufbau der Leistungshalbleiterschaltung und der Schutzvorrichtung voneinander unabhängig, so dass auch bereits vorhandene, nicht erfindungsgemäße Umrichtermodule mit der Schutzvorrichtung aufgerüstet werden können. Dieser Aufbau bringt somit einen Kostenvorteil bei der Herstellung des Umrichtermoduls. Bevorzugt weist der Schutz-Halbleiter einen Gate-Anschluss (Gate) auf, der mit einer Ansteuerschaltung verbunden ist, die induktiv mit einer Verbindungsleitung zwischen dem Energiespeicher und der Leistungshalbleiterschaltung gekoppelt ist. Der Schutz-Halbleiter ist bevorzugt ein ansteuerbarer Halbleiterschalter. Die Ansteuerschaltung ist mit dem Steueranschluss bzw. dem Gate des Schutz-Halbleiters verbunden und übernimmt die Ansteuerung des Schutz-Halbleiters. Die induktive Kopplung bewirkt, dass bei einem starken Stromanstieg im Gleichspannungszwischenkreis des Umrichtermoduls ein Strom in der Ansteuerschaltung induziert wird. Der Strom in der Ansteuerschaltung ist geeigneterweise dazu geeignet, den Schutz-Halbleiter zu zünden. Auf diese Weise ist eine einfache und zugleich wirksame Steuerung des Schutz-Halbleiters bereitgestellt. Die induktive Kopplung kann durch eine Sensorwicklung realisiert sein, die um oder an der Verbindungsleitung angeordnet beziehungsweise geführt ist. Die Sensorwicklung ist beispielsweise derart angeordnet, dass die von der Sensorwicklung aufgespannte Fläche parallel zu einer Fläche ist, die von der Zwischenkreisschaltung aufgespannt ist. Dies sorgt für eine besonders zuverlässige induktive Kopplung der Ansteuerschaltung. Die induktive Kopplung ist geeigneterweise derart eingerichtet, dass ein Anstieg eines Kurzschlussstromes oberhalb 200 kA/µs zu einer Zündung des Schutz-Halbleiters führt. Damit führen insbesondere kleine Fehlerströme von 10 kA bis 20 kA, die betriebsbedingt im Umrichtermodul auftreten können, nicht zu einer (unnötigen) Zündung des Schutzhalbleiers. Vorzugsweise umfasst die Ansteuerschaltung eine Kapazität, die zwischen dem Gate-Anschluss und einem Kathoden-Anschluss (Kathode) des Schutz-Halbleiters angeordnet ist. Die Kapazität ist dazu eingerichtet ist, durch die Abgabe einer in der Kapazität gespeicherten Energie, den Schutz-Halbleiter einzuschalten beziehungsweise zu zünden. Die Kapazität weist bevorzugt einen Kapazitätswert zwischen 10 Mikrofarad und 50 Mikrofarad auf. Bevorzugt umfasst die Ansteuerschaltung einen Diac (auch als Zweichrichtungsdiode bezeichnet), der mit dem Gate-Anschluss des Schutz-Halbleiters verbunden ist. Anstelle des Diac ist auch jeder andere geeignete spannungsgesteuerte Schalter einsetzbar. Der Diac ist dazu eingerichtet, oberhalb einer vorbestimmten Spannungsschwelle leitend zu sein. Unterhalb der Spanungsschwelle bleibt der Diac sperrend. Die Spannungsschwelle kann zwischen 1 V und 100 V liegen, bevorzugt zwischen 10 V und 50 V. Mittels des Diacs kann vorteilhaft vermieden werden, dass kleine Spannungsschwankungen zum Zünden des Schutz-Halbleiters führen. Nach dem Überschreiten der Spannnungsschwelle bleibt der Diac niederohmig leitend, solange Strom fließt. Die Ansteuerschaltung kann ferner ein Widerstandselement zur Strombegrenzung eines Stromes durch die Ansteuerschaltung umfassen. Ein Widerstandswert des Widerstandselements liegt bevorzugt zwischen 0,1 Ohm und 1 Ohm. Die Kapazität und das Widerstandselement üben gemeinsam eine Filterfunktion als Tiefpass aus. Die Leistungshalbleiter der Leistungshalbleiterschaltung können beispielsweise in einer Halbbrückenschaltung oder einer Vollbrückenschaltung miteinander verbunden sein. Gemäß einer Ausführungsvariante mit Vollbrückenschaltung weist die Leistungshalbleiterschaltung vier ein- und abschaltbare Leistungshalbleiter auf, die so mit dem Energiespeicher verschaltet sind, dass an Ausgangsklemmen des Umrichtermoduls eine an dem Energiespeicher abfallende Energiespeicherspannung, eine Nullspannung oder aber die inverse Energiespeicherspannung erzeugbar ist. Gemäß einer weiteren Ausführungsvariante mit Halbbrückenschaltung weist die Leistungshalbleiterschaltung zwei abschaltbare Leistungshalbleiter auf, die so mit dem Energiespeicher verschaltet sind, dass an Ausgangsklemmen des Schaltmoduls eine an dem Energiespeicher abfallende Energiespeicherspannung oder eine Nullspannung erzeugbar ist. Die Erfindung betrifft ferner einen Spannungszwischenkreisumrichter mit einer Mehrzahl von Umrichterarmen, wobei jeder Umrichterarm eine Reihenschaltung von Schaltmodulen umfasst. Ein solcher Spannungszwischenkreisumrichter, der ein modularer Mehrstufenumrichter ist, ist aus der bereits zuvor genannten DE 10 323 220 A1 bekannt. Dort erstrecken sich die Umrichterarme zwischen jeweils zugeordneten Wechselspannungsanschlüssen des Mehrstufenumrichters. Die Schaltmodule weisen jeweils eine Leistungshalbleiterschaltung in Vollbrückenausführung auf. Ein modularer Mehrstufenumrichter, dessen Umrichterarme sich jeweils zwischen einem Gleichspannungspol und einem Wechselspannungsanschluss des Zwischenkreisumrichters erstrecken, ist aus der WO 2016/155837 A1 bekannt. Die Schaltmodule des Mehrstufenumrichters der WO 2016/155837 A1 weisen jeweils eine Leistungshalbleiterschaltung in Halbbrückenausführung auf. Die Aufgabe der Erfindung besteht darin, einen artgemäßen Spannungszwischenkreisumrichter vorzuschlagen, der möglichst zuverlässig ist. Die Aufgabe wird durch einen Spannungszwischenkreisumrichter nach Anspruch 9 gelöst. Die Vorteile des erfindungsgemäßen Spannungszwischenkreisumrichters ergeben sich insbesondere aus den zuvor beschriebenen Vorteilen des erfindungsgemäßen Umrichtermoduls. Insbesondere die in einem Fehlerfall erreichte Zuverlässigkeit des erfindungsgemäßen Umrichtermoduls erhöht bei dessen Einsatz in einem Spannungszwischenkreisumrichter die Zuverlässigkeit der gesamten Anordnung. Alle zuvor im Zusammenhang mit dem erfindungsgemäßen Umrichtermodul beschriebenen Merkmale und Ausführungsvarianten können selbstverständlich auch beim erfindungsgemäßen Spannungszwischenkreisumrichter einzeln oder in Kombination realisiert werden. Die Erfindung soll im Folgenden anhand der Figuren 1 bis 4 weiter erläutert werden. Figur 1 zeigt ein Ausführungsbeispiel eines erfindungsgemäßen Spannungszwischenkreisumrichters in einer schematischen Darstellung;Figur 2 zeigt ein Umrichtermodul in einer schematischen Darstellung, welches nicht in den Schutzumfang der Ansprüche fällt;Figur 3 zeigt ein Ausführungsbeispiel einer Ansteuerschaltung für ein erfindungsgemäßes Umrichtermodul in einer schematischen Darstellung.Figur 4 zeigt ein Ausführungsbeispiel eines erfindungsgemäßen Umrichtermoduls in einer schematischen Darstellung. Figur 1 zeigt einen Zwischenkreisumrichter 1, der modularen Mehrstufenumrichter (MMC) ist. Der MMC 1 weist einen ersten Gleichspannungspol 2 und einen zweiten Gleichspannungspol 3. Der erste und der zweite Gleichspannungspol 2 bzw. 3 sind mit einer Gleichspannungsverbindung 4 verbunden, die zum Verbinden des MMC mit einem Gleichspannungsnetz dient. Der MMC 1 weist ferner einen Wechselspannungsanschluss 5 auf, der zum Anschluss des MMC 1 an ein dreiphasiges Wechselspannungsnetz eingerichtet ist. Zwischen jedem der beiden Gleichspannungspole 2, 3 und dem Wechselspannungsanschluss 5 erstrecken sich sechs gleichartig aufgebaute Umrichterarme 6a-f. Der Phasenzweig 6a umfasst eine Reihenschaltung gleichartig aufgebauter zweipoliger Umrichtermodule 7. Die Anzahl der Umrichtermodule 7 ist grundsätzlich beliebig und auf die jeweilige Anwendung angepasst, was in Figur 1 durch die unterbrochenen Linien 9 angedeutet ist. In einer Reihenschaltung zu den Umrichtermodule 7 ist jeweils eine Glättungsdrossel 8 angeordnet. Auf den Aufbau der Umrichtermodule 7 wird in der nachfolgenden Figur 2 näher eingegangen. Figur 2 zeigt im Einzelnen ein Umrichtermodul 7 welches nicht in den Schutzumfang der Ansprüche fällt. Das Umrichtermodul 7 umfasst eine Leistungshalbleiterschaltung in Form einer Halbbrückenschaltung 101. Die Halbbrückenschaltung 101 weist zwei Anschlüsse X1 und X2 auf. Der Anschluss X1 kann beispielsweise die Leistungshalbleiterschaltung 101 mit dem Anschluss X2 einer Leistungshalbleiterschaltung eines weiteren Umrichtermoduls 7 verbinden, so dass eine Reihenschaltung der Umrichtermodule 7 gebildet ist. Die Leistungshalbleiterschaltung 101 umfasst einen ersten Halbleiterschalter 102 in Form eines Bipolartransistors mit isolierter Gate-Elektrode (IGBT), dem eine Freilaufdiode 103 antiparallel geschaltet ist. Ferner umfasst die Halbbrückenschaltung 101 einen zweiten Halbleiterschalter 104 in Form eines IGBT, dem eine Freilaufdiode 105 antiparallel geschaltet ist. Die Durchlassrichtung der beiden Halbleiterschalter 102 und 104 ist gleichgerichtet. Der erste Anschluss X1 ist an einem Potenzialpunkt 113 zwischen den beiden Halbleiterschaltern 102 und 104 angeordnet. Der zweite Anschluss X2 ist mit dem Emitter des zweiten Halbleiterschalters 104 verbunden. Parallel zu den beiden Halbleiterschaltern 102, 104 ist ein Energiespeicher in Form eines Leistungskondensators 106 angeordnet. Durch eine geeignete Ansteuerung der Halbleiterschalter 102, 104 kann, bei einer durch einen Pfeil 107 angedeuteten Betriebsstromrichtung, der Kondensator 106 zugeschaltet oder überbrückt werden, so dass an den Anschlüssen X1, X2 entweder die am Kondensator 106 abfallende Spannung Uc oder eine Spannung null abfällt. Das Umrichtermodul 7 umfasst ferner eine Schutzvorrichtung 108 mit einem Schutz-Halbleiter in Form eines Thyristors 109, der parallel zum Energiespeicher 107 angeordnet ist. Das Gate 110 des Thyristors 109 ist mit einer Ansteuerschaltung 111 verbunden, die induktiv an eine Verbindungsleitung 112 zwischen dem Energiespeicher 106 und der Leistungshalbleiterschaltung 101 gekoppelt ist. Auf die Einzelheiten des Aufbaus der Ansteuerschaltung 111 wird in der nachfolgenden Figur 3 näher eingegangen. Die induktive Kopplung wird mittels einer Stromschleife lila realisiert, die derart ausgestaltet ist, dass die durch die Stromschleife 111a aufgespannte Fläche in etwa parallel zu der von der Parallelschaltung des Kondensators 106 und des Thyristors 109 aufgespannte Fläche liegt. Die Ansteuerschaltung 111 umfasst darüber hinaus eine Bauelementenanordnung 111b. Die Schutzvorrichtung 108 umfasst ferner einen Strombegrenzer 114. Der Strombegrenzer 114 umfasst eine Parallelschaltung eines Widerstandselements R und einer Induktivität L. Figur 3 zeigt den Aufbau der Ansteuerschaltung 108 für das Umrichtermodul 7 der Figuren 1, 2 und 4, wobei gleiche und gleichartige Bauelemente in allen Figuren 1 bis 4 mit gleichen Bezugszeichen versehen sind. Die Bauelementenanordnung 111b umfasst einen Widerstand 115 und einen Diac 116, die zwischen Gate 110 des Thyristors 109 und der Stromschleife 111a angeordnet sind. Ferner ist ein Kondensator 117 parallel zur Stromschleife 111a und zwischen dem Gate 110 und einer Kathode 118 des Thyristors 109 vorgesehen. Bei einer fehlerverursachten, schlagartigen Entladung des Kondensators 106 induziert ein starker Anstieg eines Kurzschlussstroms durch die Verbindungsleitung 112 eine Spannung in der Stromschleife 111a. Sobald die Spannung einen vorbestimmten Schwellwert von 30 V überschreitet, wird der Diac 116 leitend, so dass der Thyristor 109 über dessen Gate 110 gezündet wird. Der Kurzschlussstrom wird damit über den Thyristor 109 geleitet, so dass die Leistungshalbleiterschaltung 101 vor einer Beschädigung bewahrt wird. Die Energie aus dem Kondensator 106 kann mittels des Strombegrenzers 114 abgebaut und in Wärme umgewandelt werden. In Figur 4 ist ein Umrichtermodul 7a dargestellt, das eines oder mehrere der Umrichtermodule 7 in Figur 1 ersetzen kann. Im Unterschied zum Umrichtermodul 7 der Figur 2 umfasst das Umrichtermodul 7a eine Schutzvorrichtung 108a. Die Schutzvorrichtung 108a umfasst einen Strombegrenzer 114a mit einer Primärwicklung 120, die in Reihe zum Energiespeicher 106 angeordnet ist, sowie eine Sekundärwicklung 121, die kurzgeschlossen ist, ohne dass der Widerstand der Sekundärwicklung null ist (die Enden der Sekundärwicklung sind beispielsweise miteinander verbunden). Die Primär- und die Sekundärwicklung 120 beziehungsweise 121 sind miteinander magnetisch gekoppelt. Darüber hinaus sind der Thyristor 109, die Primär- und die Sekundärwicklung 120 beziehungsweise 121 miteinander in einem mechanischen Spannverband 122 verspannt und fixiert. Der Spannverband 122 ist außerhalb eines Gehäuses 123 der Leistungshalbleiterschalter 101 angeordnet. Die Ansteuerschaltung des Thyristors 109 entspricht in ihrem Aufbau derjenigen aus Figur 3. [EN EP3556000B1]: The invention relates to a converter module for a voltage intermediate circuit converter with a power semiconductor circuit with at least two power semiconductor switches, an energy storage device in a parallel connection to the power semiconductor circuit and a protective device comprising a controllable protective semiconductor which is arranged in a parallel connection with the energy storage device. Such a converter module is from DE 10 323 220 A1 known. The power semiconductor circuit of the known converter module is designed as a full bridge circuit. It comprises two series circuits of two power semiconductor switching units each, each having a semiconductor switch that can be switched on and off and a free-wheeling diode antiparallel to it. The external connections of the full bridge circuit are arranged with potential points between the power semiconductor switching units of each series circuit. At the same time, an energy store in the form of a capacitor is arranged in a parallel connection to the power semiconductor circuit. The protective semiconductor of the known converter module is a resonance diode or a thyristor. In the event of a fault in the converter module, for example a switching failure of one of the semiconductor switches in the power semiconductor circuit, a short circuit can occur within the converter module. In such a case, the energy store can in particular be suddenly discharged. Without special protective measures, current amplitudes of a short-circuit current through the power semiconductor circuit of more than 1 MA can occur. Such a short-circuit current can lead to an explosion in the power semiconductor circuit and to damage or destruction of the semiconductor switch. In addition, the explosion energy can bend or tear busbars and damage a housing of the power semiconductor circuit. The protective semiconductor of the known converter module is provided to take over the short-circuit current in such a fault case. In the event of a fault, the energy store is short-circuited with low resistance by means of the protective semiconductor, so that the power semiconductor circuit is not affected by the discharge of the energy store. The known converter module is part of a modular multi-stage converter which comprises a plurality of converter arms or converter branches. The converter arms of the known multistage converter each extend between an input-side and an output-side AC voltage connection of the multistage converter. Each converter arm comprises a series connection of the converter modules. Such a modular multi-stage converter has the advantageous property that a multi-stage output voltage of almost any form can be generated by means of the modular multi-stage converter. The number of output voltage levels that can be generated is determined by the number of converter modules in the converter arms. Another advantage of the modular multi-stage converter is that, in the event of a fault in one of the converter modules, the operability of the modular multi-stage converter can continue to be ensured by bridging this faulty converter module. In the post by NICOLAS P LABBE: "An innovative currentlimiting device for automotive micro-hybrid starter motors", ELECTRICAL MACHINES (ICEM), 2012 XXTH 05 INTERNATIONAL CONFERENCE ON, IEEE, September 2, 2012 a circuit is described which comprises a primary winding inserted in series into the line, the associated secondary winding of which is resistively short-circuited. From the WO 2013/044961 A1 a switching module for a converter is known in which the control circuit of the protective thyristor, which is parallel to the energy store in the switch module, comprises an inductance which is connected in series with the energy store. In the US 2014/0226374 A1 a further switching module with a protective circuit for the energy store is disclosed. From the WO 2016/203517 A1 and the JP 2013 169088 A a circuit with a protective thyristor in parallel with the energy store is known. In theJP 2013 169088 A a tensioning association for the protective thyristor is also disclosed. In the WO 2016/128643 A1 describes a limiting circuit for a motor vehicle with a transformer whose primary winding is short-circuited in series in a line and whose secondary winding is resistive. The WO 2014/090272 A1 describes a switching module with an RL parallel connection in series with the energy store. The object of the present invention is to propose a converter module mentioned at the beginning with a further improved protective device. The object is achieved by a converter module according to claim 1. In the event of an uncontrolled discharge of the energy store in the event of a fault, the amplitude of the short-circuit current can be limited by means of the current limiter. In this way the negative effects of the short-circuit current can be minimized. The current limiter can be used to limit a surge current that occurs in the DC intermediate circuit of the converter module in the event of a fault. In this way, destruction of the protective semiconductor due to a high surge current can advantageously be avoided, which can otherwise lead to the emergence of arcs and fragments of components. In this context, the DC voltage intermediate circuit of the converter module is the electrical circuit that comprises the energy store and the power semiconductor circuit. The current limiter is expediently designed in such a way that it is low-inductive in normal operation of the converter module. The current-limiting property of the current limiter suitably only occurs in the event of a fault. The protective semiconductor is expediently blocking in normal operation. This means that the protective semiconductor has no influence on the work of the converter module or the entire converter during normal operation. The protective semiconductor can be, for example, a thyristor or another controllable semiconductor switch. The protective semiconductor can then be ignited, i.e. switched on, in the event of a fault. After ignition, the high short-circuit current through the semiconductor switch causes it to break down, for example, so that a permanent low-resistance current path is generated for the short-circuit current. According to the invention, the current limiter comprises a primary winding, which is arranged in series with the energy store, and a secondary winding, the secondary winding and the primary winding being magnetically coupled and the secondary winding being resistively short-circuited. The current limiter thus corresponds to a transformer short-circuited on the secondary side. The primary side of the transformer is an active part of the DC link of the converter module. In the event of a fault, the primary winding transforms the voltage absorbed due to the steep increase in current into the secondary winding, which converts part of the electrical energy absorbed into heat due to its ohmic resistance. The inductive component of the primary winding limits the rate of increase in current or the surge current, with the counter voltage generated by the current limiter limiting the amplitude of the short-circuit current. In addition, the increased inductance in the event of a short circuit can also reduce the frequency of the short circuit current. In this way, the emission of high-frequency magnetic fields can advantageously be reduced, as a result of which interference with neighboring electronic assemblies can be minimized. In addition, it is possible to dissipatively dissipate between 50% and 90% of the energy stored in the DC voltage intermediate circuit of the converter module by means of the current limiter. According to the invention, the protective semiconductor, the primary winding and the secondary winding are fixed in a mechanical tensioning association. The protective semiconductor, the primary winding and the secondary winding of the current limiter are mechanically braced with one another. As a result, a particularly compact and mechanically robust design can be achieved for the protective device. Due to the compact design, the space requirement can be reduced and thus a cost advantage can also be achieved. The power semiconductor circuit is preferably arranged in a module housing and the protective device is arranged outside the module housing. In this way, the internal structure of the power semiconductor circuit and the protective device are independent of one another, so that converter modules that are already present and not according to the invention can also be upgraded with the protective device. This structure thus brings a cost advantage in the manufacture of the converter module. The protective semiconductor preferably has a gate connection (gate) which is connected to a control circuit which is inductively coupled to a connecting line between the energy store and the power semiconductor circuit. The protective semiconductor is preferably a controllable semiconductor switch. The control circuit is connected to the control connection or the gate of the protective semiconductor and takes over the control of the protective semiconductor. The inductive coupling has the effect that a current is induced in the control circuit in the event of a strong increase in current in the DC voltage intermediate circuit of the converter module. The current in the control circuit is suitably suitable for igniting the protective semiconductor. In this way, a simple and at the same time effective control of the protective semiconductor is provided. The inductive coupling can be implemented by a sensor winding which is arranged or guided around or on the connecting line. The sensor winding is arranged, for example, in such a way that the area spanned by the sensor winding is parallel to an area spanned by the intermediate circuit circuit. This ensures a particularly reliable inductive coupling of the control circuit. The inductive coupling is suitably set up in such a way that an increase in a short-circuit current above 200 kA / μs leads to ignition of the protective semiconductor. In particular, small residual currents of 10 kA to 20 kA, which can occur in the converter module due to operation, do not lead to an (unnecessary) ignition of the protective semilayer. The control circuit preferably comprises a capacitance which is arranged between the gate connection and a cathode connection (cathode) of the protective semiconductor. The capacitance is set up to switch on or ignite the protective semiconductor by releasing an energy stored in the capacitance. The capacitance preferably has a capacitance value between 10 microfarads and 50 microfarads. The control circuit preferably comprises a diac (also referred to as a bidirectional diode) which is connected to the gate connection of the protective semiconductor. Instead of the diac, any other suitable voltage-controlled switch can also be used. The diac is set up to be conductive above a predetermined voltage threshold. The diac remains blocking below the voltage threshold. The voltage threshold can be between 1 V and 100 V, preferably between 10 V and 50 V. The diac can advantageously prevent small voltage fluctuations from triggering the
[ZH WO2021047130A1]: 基于模块化多电平换流器的大功率电机驱动系统 [EN US11121641B1]: High-power machine drive system based on modular multilevel converter [FR WO2021047130A1]: SYSTÈME D'ENTRAÎNEMENT DE MOTEUR HAUTE PUISSANCE À BASE DE CONVERTISSEUR MULTINIVEAU MODULAIRE | [ZH WO2021047130A1]: 一种基于模块化多电平换流器的大功率电机驱动系统，属于发电、变电或配电的技术领域。大功率电机驱动系统由模块化多电平换流器（1）与多脉波交交变频器（2）组成，模块化多电平换流器（1）输出相位互差2π/k的k相高频交流电压，多脉波交交变频器（2）输出低频电压驱动对应电机。该驱动系统将模块化多电平换流器（1）与多脉波交交变频器（2）相结合，通过采用高频运行的模块化多电平换流器（1）减少模块化多电平换流器（1）储能电容容量、体积和重量，增加模块化多电平换流器（1）直流侧电压等级，提高驱动系统容量；通过采用多脉波交交变频器（2）保证电机侧输出波形质量，并实现对电机的低频控制，适用于大功率低速电机的驱动。 [EN US11121641B1]: The present invention discloses a high-power machine drive system based on a modular multilevel converter (MMC), which belongs to the technical field of power generation, power transformation, or power distribution. The high-power machine drive system consists of a modular multilevel converter and a multi-pulse cycloconverter. The MMC outputs k phases of high-frequency AC voltages with a phase difference of 2π/k, and the multi-pulse cycloconverter outputs a low-frequency voltage to drive a corresponding machine. According to the present invention, the MMC is combined with the multi-pulse cycloconverter, and by adopting the MMC that operates at a high frequency, the capacity, the volume, and the weight of the energy storage capacitor of the MMC are reduced, the voltage level at the DC side of the MMC is increased, and the capacity of the drive system is increased. By adopting the multi-pulse cycloconverter, quality of an output waveform at a machine side can be guaranteed, thereby implementing low frequency control on the machine. The present invention may be adapted to drive a high-power low-speed machine. [FR WO2021047130A1]: L'invention concerne un système d'entraînement de moteur haute puissance à base de convertisseur multiniveau modulaire qui se rapporte au domaine technique de la production d'énergie, de la transformation ou de la distribution d'énergie. Le système d'entraînement de moteur haute puissance est composé d'un convertisseur multiniveau modulaire (1) et d'un convertisseur de fréquence c.a.-c.a. à ondes multi-impulsions (2). Le convertisseur multiniveau modulaire (1) délivre en sortie une tension alternative haute fréquence en phase k qui a une différence de phase de 2π/k. Le convertisseur de fréquence c.a./c.a. à ondes multi-impulsions (2) délivre en sortie une tension basse fréquence pour entraîner un moteur correspondant. Dans le système d'entraînement, le convertisseur multiniveau modulaire (1) est combiné au convertisseur de fréquence c.a./c.a. à ondes multi-impulsions (2) et, au moyen de l'utilisation du convertisseur multiniveau modulaire (1) fonctionnant à une fréquence élevée, la capacité de capacité de stockage d'énergie, le volume et le poids du convertisseur multiniveau modulaire (1) sont réduits, le niveau de tension côté continu du convertisseur multiniveau modulaire (1) est augmenté et la capacité du système d'entraînement est améliorée ; et au moyen de l'utilisation du convertisseur de fréquence c.a./c.a. à ondes multi-impulsions (2), la qualité de la forme d'onde de sortie côté moteur est assurée et la commande à basse fréquence du moteur est obtenue, ce qui est approprié pour entraîner des moteurs à haute puissance et à faible vitesse. | US11121641B1 | 2021-08-26 2021-09-14 | US202017265474A | 2020-01-02 2020-01-02 | CN201910851440A, 2019-09-10 CN2020070007W, 2020-01-02 CN201910851440A, 2019-09-10 CN2020070007W, 2020-01-02 | CN110611460B: 2020-11-06 WO2021047130A1: 2021-03-18 US11121641B1: 2021-09-14 | UNIV SOUTHEAST 东南大学 | DENG FUJIN JIANG PENGYUAN HU YIHUA | H02P5/74: I H02P27/08: I H02M7/483: I H02M1/00: I | H02P5/74: I H02P27/08: I H02M1/0095: I H02M7/4833: I | CN103795301A CN106602885A CN107276107A CN109889059A US2019222159A1 CN110611460A CN109474008A EP1306964A1 CN108599603A CN101079578A US5903066A US2018083550A1 | WO2021047130A1 WO2021047130 2021/047130 WO2021/047130A1 | [ZH WO2021047130A1]: 基于模块化多电平换流器的大功率电机驱动系统,其特征在于,包括: 模块化多电平换流器,各相桥臂接同一直流母线,输出相位互差2π/k的k相高频交流电压,由k组反并联晶闸管组成每相晶闸管模块的多脉波交交变频器,每相晶闸管模块的输入端接相位互差2π/k的k相高频交流电压,输出变频后的交流电至待驱动的大功率电机,载波生成模块,根据模块化电平变换器输出的k相高频交流电压的相位角生成k组反并联晶闸管对应的载波信号,转速矢量控制器,根据电机转速及其参考值、多脉波交交变频器输出至电机的交流电流、模块化电平变换器输出的相位互差2π/k的k相高频交流电压生成各相晶闸管模块所对应的电压调制信号,多脉波调制器,结合多脉波交交变频器输出侧电流的方向对k组反并联晶闸管对应的载波信号和各相晶闸管模块所对应的电压调制信号进行多脉波调制生成多脉波交交变频器各相晶闸管模块的触发脉冲。 根据权利要求1所述基于模块化多电平换流器的大功率电机驱动系统,其特征在于,模块化多电平换流器输出的k相高频交流电压的调制信号为:y i=m 1sin[2πf mmct-2π(i-1)/k+θ mmc],y i为i相高频交流电压的调制信号,m 1为调制系数,f mmc为MMC输出电压频率,θ mmc为第一相高频交流电压相位角。 根据权利要求1所述基于模块化多电平换流器的大功率电机驱动系统,其特征在于,k组反并联晶闸管中第i组反并联晶闸管对应的载波信号W i为:W i=sin[2πf mmct-πi/k+θ mmc]。 根据权利要求1所述基于模块化多电平换流器的大功率电机驱动系统,其特征在于,结合多脉波交交变频器输出侧电流的方向对k组反并联晶闸管对应的载波信号和各相晶闸管模块所对应的电压调制信号进行多脉波调制的方法为: 在多脉波交交变频器输出侧电流为正向时闭锁所有反组晶闸管,在多脉波交交变频器输出侧电流为反向时闭锁所有正组晶闸管; 对于晶闸管模块中未闭锁的正组晶闸管,比较k组反并联晶闸管对应的载波信号的下降沿和该相晶闸管模块所对应的电压调制信号,载波信号小于电压调制信号时持续发送触发脉冲,反之不发送触发脉冲,对于晶闸管模块中未闭锁的反组晶闸管,比较k组反并联晶闸管对应的载波信号的上升沿和该相晶闸管模块所对应的电压调制信号,载波信号大于电压调制信号时持续发送触发脉冲,反之不发送触发脉冲。 根据权利要求3所述基于模块化多电平换流器的大功率电机驱动系统,其特征在于,模块化电平变换器输出的k相高频交流电压的相位角通过PLL获取。 [EN US11121641B1]: 1. A high-power machine drive system based on a modular multilevel converter, comprising: a modular multilevel converter, arms of all phases being connected to a same DC bus, and the modular multilevel converter outputting k phases of high-frequency AC voltages with a phase difference of 2π/k; a multi-pulse cycloconverter whose thyristor modules of all phases consist of k groups of anti-parallel thyristors, input ends of the thyristor modules of all phases being connected to the k phases of high-frequency AC voltages with the phase difference of 2π/k, and the multi-pulse cycloconverter outputting a frequency-converted AC power to a to-be-driven high-power machine;a carrier generation module configured to generate carrier signals corresponding to the k groups of anti-parallel thyristors according to phase angles of the k phases of high-frequency AC voltages output by the modular multilevel converter,a speed vector controller configured to generate voltage modulation signals corresponding to the thyristor modules of all phases according to a machine speed and a reference value thereof, an AC current output from the multi-pulse cycloconverter to the machine, and the k phases of high-frequency AC voltages with the phase difference of 2π/k output by the modular multilevel converter;a multi-pulse modulator configured to generate trigger pulses of the thyristor modules of all phases of the multi-pulse cycloconverter by performing multi-pulse modulation on the carrier signals corresponding to the k groups of anti-parallel thyristors and the voltage modulation signals corresponding to the thyristor modules of all phases in combination with a current direction at an output side of the multi-pulse cycloconverter. 2. The high-power machine drive system based on a modular multilevel converter according to claim 1, wherein the modulation signals of the k phases of high-frequency AC voltages output by the modular multilevel converter are: yi=m1 sin[2πfmmct−2π(i−1)/k], wherein yi is a modulation signal of an i-phase high-frequency AC voltage, m1 is a modulation coefficient, and fmmc is a frequency at which the MMC outputs a voltage. 3. The high-power machine drive system based on a modular multilevel converter according to claim 1, wherein a carrier signal Wi corresponding to an ith group of anti-parallel thyristors in the k groups of anti-parallel thyristors is: Wi=sin[2πfmmct−+θmmc−π(2i−3)/k], wherein fmmc is a frequency at which the MMC outputs a voltage, and θmmc are phase angles of the k phases of high-frequency AC voltages output by the modular multilevel converter. 4. The high-power machine drive system based on a modular multilevel converter according to claim 1, wherein a method of performing multi-pulse modulation on the carrier signals corresponding to the k groups of anti-parallel thyristors and the voltage modulation signals corresponding to the thyristor modules of all phases in combination with the current direction at the output side of the multi-pulse cycloconverter comprises: locking all the groups of reversely connected thyristors when the current at the output side of the multi-pulse cycloconverter is in a forward direction, and locking all the groups of forward connected thyristors when the current at the output side of the multi-pulse cycloconverter is in a reverse direction;for all the unlocked groups of forward connected thyristors in the thyristor module, comparing falling edges of the carrier signals corresponding to the k groups of anti-parallel thyristors with the voltage modulation signals corresponding to the thyristor module of the phase, and continuously sending trigger pulses when the carrier signals are less than the voltage modulation signals, or otherwise skipping sending the trigger pulses;for all the unlocked groups of reversely connected thyristors in the thyristor module, comparing rising edges of the carrier signals corresponding to the k groups of anti-parallel thyristors with the voltage modulation signals corresponding to the thyristor module of the phase, and continuously sending trigger pulses when the carrier signals are greater than the voltage modulation signals, or otherwise skipping sending the trigger pulses. 5. The high-power machine drive system based on a modular multilevel converter according to claim 3, wherein the phase angles of the k phases of high-frequency AC voltages output by the modular multilevel converter are obtained through a phase-locked loop (PLL). | [ZH WO2021047130A1]: 基于模块化多电平换流器的大功率电机驱动系统 技术领域 本发明公开了基于模块化多电平换流器的大功率电机驱动系统,涉及多电平电力电子变换器技术,属于发电、变电或配电的技术领域。 背景技术 模块化多电平换流器(Modular Multilevel Converter,MMC)相比于传统两电平或三电平换流器,具有模块化程度高、功率大、能量传输效率高、交流侧输出电压谐波含量低、可实现冗余控制等优点,适用于高电压、大功率场合,目前在高压直流输电、轨道交通、中压电机驱动等领域已经得到了广泛的应用。 理论研究表明,MMC各子模块电容电压波动大小与交流侧输出频率成反比关系,若利用MMC直接驱动大功率低速电机将造成较大的子模块电容电压波动,影响交流侧输出波形质量,严重时甚至会影响MMC以及电机的正常运行。为抑制子模块电容电压波动,通常采取增大电容容量的方式,但同时造成了电容体积和重量占比过大、系统建造维护成本过高的问题,限制了MMC在中、高压电机驱动领域的应用。 目前,通常采用三电平型变频器或单元级联型变频器驱动大功率低速电机。三电平型变频器主电路结构简单易于实现,但因输出侧电压为三电平谐波含量大且输出电压范围受功率器件耐压条件的限制而无法适用于功率等级较高的情况。单元级联型变频器输入侧采用移相变压器解决了输出侧电压谐波含量大的问题,同时通过功率单元级联使得单个功率器件耐压要求降低,易于实现高压变频。但是各功率单元由于基础电位不同必须采用多线圈隔离变压器进行绝缘隔离,系统结构较为复杂。 为改善现有大功率低速电机驱动方案的缺陷,欲采用MMC驱动电路实现大功率电机的低速驱动。然而,MMC的低频电压波动制约了MMC在大功率电机低速驱动的应用。针对MMC低频电压波动问题,传统的解决方案为注入高频共模电压或注入特定次桥臂环流,然而此类方案可能会对MMC系统的谐波、电压应力、损耗等产生不利影响,从而对电机谐波、损耗等产生不利影响。又有一些技术通过改变MMC系统结构的方式改善其低频电压波动问题,然而此类方法需 要对MMC的控制方式做出调整,较为复杂。此外,现有MMC驱动电路驱动大功率低速电机的方法仅仅改善电机启动阶段的电容电压波动,电机启动后MMC通常运行于低频(如50Hz)下,故电容的容量、体积和重量并未得到有效得减少。 发明内容 本发明的发明目的是针对上述背景技术的不足,提供了基于模块化多电平换流器的大功率电机驱动系统,通过采用高频运行的MMC减少MMC储能电容容量、体积和重量,增加MMC直流侧电压等级,提高驱动系统容量,通过采用多脉波交交变频器保证电机侧输出波形质量,并实现对电机的低频控制,解决了MMC直接驱动大功率低速电机存在的电容电压波动过大的技术问题,克服了现有MMC驱动电路虽能改善直接驱动方案的缺陷但却影响电机谐波和损耗或者需要改变MMC控制方式的缺陷。 本发明为实现上述发明目的采用如下技术方案: 基于模块化多电平换流器的大功率电机驱动系统由模块化多电平换流器、多脉波交交变频器、载波生成模块、转速矢量控制器、多脉波调制器组成。MMC含有k相交流侧输出,且换流器每相含有上下两个桥臂,每个桥臂包含n个相同的SM子模块以及一个桥臂电感,每相直流侧均与同一直流母线相连,换流器第k相交流侧输出与各多脉波交交变频器第k相输入相连接。多脉波交交变频器分为零式结构与桥式结构两类,相比于桥式结构的交交变频器而言,零式结构交交变频器所需晶闸管仅为桥式结构的一半,故其成本更低,控制更简单可靠,而且更容易实现自然无环流控制。故本发明中多脉波交交变频器采用零式拓扑结构,其由三相内部拓扑结构相同的晶闸管模块构成,多脉波交交变频器第k相输入与各相晶闸管模块中第k组反并联晶闸管相连,多脉波交交变频器输出侧与对应三相电机1~m相连。载波生成模块根据模块化电平变换器输出的k相高频交流电压的相位角生成k组反并联晶闸管对应的载波信号。转速矢量控制器根据电机转速及其参考值、多脉波交交变频器输出至电机的交流电流、模块化电平变换器输出的相位互差2π/k的k相高频交流电压生成各相晶闸管模块所对应的电压调制信号。多脉波调制器结合多脉波交交变频器输出侧电流的方向对k组反并联晶闸管对应的载波信号和各相晶闸管模块所对应的电压调制信号进行多脉波调制生成多脉波交交变频器各相晶闸管模块的触发脉冲。 作为本发明的一种改进,三相内部拓扑结构相同的晶闸管模块均包含k组反并联晶闸管,各组反并联晶闸管包括晶闸管。 基于模块化多电平换流器的大功率电机驱动系统的控制方法包括以下步骤:MMC输出相位互差2π/k的k相高频交流电压,多脉波交交变频器输出低频电压驱动对应电机。具体步骤如下: (1)模块化多电平换流器采用高频调制方式,交流侧输出相位互差2π/k的k相高频交流电压。其中,第i相调制信号为y i=m 1sin[2πf mmct-2π(i-1)/k+θ mmc]。m 1为调制系数,取准许的最大值,以便MMC输出最大电压;f mmc为MMC输出电压频率,通常取几百赫兹(如300Hz);θ mmc为第一相高频交流电压相位角。 (2)利用锁相环(PLL)得到MMC交流输出侧高频交流电压相位角θ mmc,生成k组反并联晶闸管各自对应载波W 1~W k。其中,第i组反并联晶闸管所对应载波为W i=sin[2πf mmct-πi/k+θ mmc]。 (3)三相低速运行电机1~m均采取转速矢量控制,以三相电机m为例,其控制方法为,根据三相电机实际转速n、转速参考值n ref、电机侧三相电流i am,i bm,i cm、高频交流电压u m1~u mk,得到多脉波交交变频器输出侧三相电压调制信号y maref,y mbref,y mcref。 (4)将载波W 1~W k与A相晶闸管模块所对应调制信号y maref进行交交变频器多脉波调制,得到A相k组反并联晶闸管的触发脉冲S 1_1a、S 2_1a......S 1_ka、S 2_ka;将载波W 1~W k与B相晶闸管模块所对应调制信号y mbref进行交交变频器多脉波调制,得到B相k组反并联晶闸管的触发脉冲S 1_1b、S 2_1b......S 1_kb、S 2_kb;将载波W 1~W k与C相晶闸管模块所对应调制信号y mcref进行交交变频器多脉波调制,得到C相k组反并联晶闸管的触发脉冲S 1_1c、S 2_1c......S 1_kc、S 2_kc;驱动各相晶闸管模块内的正反组晶闸管,从而输出低频电压驱动电机m,其余三相电机控制方法类似。 本发明采用上述技术方案,具有以下有益效果: (1)本发明解决了MMC直接驱动大功率低速电机电容电压波动过大的问题,由于MMC各子模块电容电压波动大小与交流侧输出频率成反比关系,若利用MMC直接驱动大功率低速电机,将造成较大的子模块电容电压波动。现有方 案采取增大电容容量的方式,抑制子模块电容电压波动在允许范围内,但同时造成了电容体积和重量占比过大、系统建造维护成本过高的问题。而本发明将MMC与多脉波交交变频器相结合组成大功率电机驱动系统,在保证电机侧输出波形质量的同时,MMC运行频率可控制在几百赫兹水平,与现有方案相比,能够显著减少MMC储能电容容量、降低MMC储能电容体积和重量。 (2)本发明使得系统高度模块化,易于系统根据容量要求进行拓展,本发明利用MMC模块化的特点,可根据实际驱动系统容量要求确定MMC具体相数以及各相桥臂所需包含的子模块数量,使得系统高度模块化,更具有实际工程价值。同时通过增加各相桥臂所包含子模块数量,能够显著降低单个功率器件耐压要求。通过增加交交变频器脉波数量,能够显著改善电机侧输出波形质量,保证电机平稳安全运行。本发明使得系统高度模块化,易于系统根据容量要求进行拓展,这是本发明与现有其它大功率低速电机驱动方案的本质区别。 (3)本发明基于现有的MMC模块实现大功率低速电机的驱动,无需改变MMC基本结构,因而不需要调整MMC的相关控制方法,整个控制方案简单,易于理解与实施。 (4)本发明利用系统模块化特点,可进行冗余控制,能够大大提高系统的可靠性。 附图说明 图1(a)是本发明的大功率电机驱动系统结构图,图1(b)是A相晶闸管模块系统结构图,图1(c)是SM模块结构图。 图2是本发明的大功率电机驱动系统控制框图。 图中标号说明:1、模块化多电平换流器,1-1、SM子模块,1-2、桥臂电感,1-3、直流母线,2、多脉波交交变频器,2-1、A相晶闸管模块,VT 1_1a、VT 1_2a、VT 1_3a、VT 1_ka为A相晶闸管模块中的第1、第2、第3、第k正组晶闸管,VT 2_1a、VT 2_2a、VT 2_3a、VT 2_ka为A相晶闸管模块中的第1、第2、第3、第k反组晶闸管。 具体实施方式 为了加深对本发明的认识和理解,下面结合附图和具体实施方式进一步介绍该技术方案。 如图1(a)所示,基于模块化多电平换流器的大功率电机驱动系统由模块 化多电平换流器1与多脉波交交变频器2组成,MMC含有k相交流侧输出,且换流器每相含有上下两个桥臂,每个桥臂包含n个相同的SM子模块1-1以及一个桥臂电感1-2。子模块采用半桥拓扑结构,也可以是全桥、钳位双子模块等其他拓扑结构。每相直流侧均与同一直流母线1-3相连,换流器第k相交流侧输出与各多脉波交交变频器第k相输入相连接。此外,上述MMC拓扑结构中相数k与每个桥臂所包含子模块数n由驱动系统容量等设计指标确定。多脉波交交变频器均采用零式拓扑结构,由三相内部拓扑结构相同的晶闸管模块构成,A相晶闸管模块2-1图1(b)所示。各晶闸管模块包含k组反并联晶闸管,各组反并联晶闸管包括晶闸管VT 1_i与VT 2_i。多脉波交交变频器第k相输入与各相晶闸管模块中第k组反并联晶闸管相连,多脉波交交变频器输出侧与对应三相电机1~m相连。 基于模块化多电平换流器的大功率电机驱动系统如图2所示,包括:模块化多电平换流器、多脉波交交变频器、载波生成模块、转速矢量控制器、多脉波调制器。模块化多电平换流器的各相桥臂接同一直流母线,输出相位互差2π/k的k相高频交流电压;多脉波交交变频器的每相晶闸管模块由k组反并联晶闸管组成,每相晶闸管模块的输入端接相位互差2π/k的k相高频交流电压,输出变频后的交流电至待驱动的大功率电机;载波生成模块根据模块化电平变换器输出的k相高频交流电压的相位角生成k组反并联晶闸管对应的载波信号;转速矢量控制器根据电机转速及其参考值、多脉波交交变频器输出至电机的交流电流、模块化电平变换器输出的相位互差2π/k的k相高频交流电压生成各相晶闸管模块所对应的电压调制信号;多脉波调制器结合多脉波交交变频器输出侧电流的方向对k组反并联晶闸管对应的载波信号和各相晶闸管模块所对应的电压调制信号进行多脉波调制生成多脉波交交变频器各相晶闸管模块的触发脉冲。 该系统的控制方法为模块化多电平换流器、多脉波交交变频器以及三相电机之间的协调控制方案,包括:MMC输出相位互差2π/k的k相高频交流电压,多脉波交交变频器输出低频电压驱动对应电机。具体包括以下步骤: (1)模块化多电平换流器采用高频调制方式,通过将各相调制信号y i(i=1,2,...k)与高频等腰三角载波进行比较,得到各相上桥臂(下桥臂)需要投入的子模块个数n iu_on(n il_on)。其中,第i相调制信号y i=m 1sin[2πf mmct-2π(i-1)/k+θ mmc]。m 1为调制系数,取准许的最大值,以便MMC输出最大电压;f mmc为MMC输出 电压频率,通常取几百赫兹;θ mmc为第一相高频交流电压相位角。然后分别对各相上桥臂(下桥臂)子模块电容电压进行升序排序,当桥臂电流i iu(i il)为正,投入电容电压最低的n iu_on(n il_on)个子模块,当桥臂电流i iu(i il)为负,投入电容电压最高的n iu_on(n il_on)个子模块,使得MMC交流侧输出相位互差2π/k的k相高频交流电压。 (2)利用锁相环(PLL)得到MMC交流输出侧高频交流电压相位角θ mmc,生成k组反并联晶闸管各自对应载波W 1~W k。其中,第i组反并联晶闸管所对应载波为W i=sin[2πf mmct-πi/k+θ mmc]。 (3)三相低速运行电机1~m均采取转速矢量控制,以三相电机m为例,其控制方法为,根据三相电机实际转速n、转速参考值n ref、电机侧三相电流i am,i bm,i cm、高频交流电压u m1~u mk,得到多脉波交交变频器输出侧三相电压调制信号y maref,y mbref,y mcref。 (4)将载波W 1~W k与A相晶闸管模块所对应调制信号y maref进行交交变频器多脉波调制,得到A相k组反并联晶闸管的触发脉冲S 1_1a、S 2_1a......S 1_ka、S 2_ka;将载波W 1~W k与B相晶闸管模块所对应调制信号y mbref进行交交变频器多脉波调制,得到B相k组反并联晶闸管的触发脉冲S 1_1b、S 2_1b......S 1_kb、S 2_kb;将载波W 1~W k与C相晶闸管模块所对应调制信号y mcref进行交交变频器多脉波调制,得到C相k组反并联晶闸管的触发脉冲S 1_1c、S 2_1c......S 1_kc、S 2_kc;驱动各相晶闸管模块内的正反组晶闸管,从而输出低频电压驱动电机m,其余三相电机控制方法类似。 其中,步骤(4)中交交变频器多脉波调制方法,以A相晶闸管模块为例进行分析(其余两相模块类似),具体为: (a)对于A相晶闸管模块中所有正组晶闸管VT 1_1a~VT 1_ka,各自触发脉冲S 1_1a~S 1_ka分别通过将载波W 1~W k下降沿与调制信号y maref进行比较得到,若载波小于调制信号,持续发送触发脉冲,反之不发送触发脉冲。 (b)对于A相晶闸管模块中所有反组晶闸管VT 2_1a~VT 2_ka,各自触发脉冲S 2_1a~S 2_ka分别通过将载波W 1~W k上升沿与调制信号y maref进行比较得到,若载波大于调制信号,持续发送触发脉冲,反之不发送触发脉冲。 (c)若变频器输出侧电流方向i am&gt;0,则所有反组晶闸管VT 2_1a~VT 2_ka闭锁, 若变频器输出侧电流方向i am&lt;0,则所有正组晶闸管VT 1_1a~VT 1_ka闭锁。 本发明尤其适用于大功率低速电机驱动,与现有的方法相比,本发明将MMC与多脉波交交变频器相结合,通过采用高频运行的MMC减少MMC储能电容容量、体积和重量,增加MMC直流侧电压等级,提高驱动系统容量;通过采用多脉波交交变频器保证电机侧输出波形质量,并实现对电机的低频控制。 需要说明的是上述实施例并非用来限定本发明的保护范围,在上述技术方案的基础上所作出的等同变换或替代均落入本发明权利要求所保护的范围。 [EN US11121641B1]: BACKGROUND Technical Field The present invention discloses a high-power machine drive system based on a modular multilevel converter, and relates to the technology of a multilevel power electronic converter, which belongs to the technical field of power generation, power transformation, or power distribution. Related Art Compared with traditional two-level or three-level converters, a modular multilevel converter (MMC) has the advantages of high modularity, high power, high energy transmission efficiency, low harmonics of the AC side output voltage, capability of implementing redundancy control, and the like, which is suitable for high-voltage and high-power applications and currently has been widely used in fields such as high voltage DC transmission, rail transit, medium voltage machine drive, and the like. A theoretical research shows that a fluctuation of a capacitor voltage of each sub-module of the MMC is inversely proportional to the AC side output frequency. If the MMC is used to directly drive a high-power low-speed machine, large fluctuations of the capacitor voltage of the sub-module may be caused, which affects the quality of the AC side output waveform, and may even affect the normal operation of the MMC and the machine in severe cases. In order to suppress the fluctuation of the capacitor voltage of the sub-module, the method of increasing the capacitor capacity is usually adopted, which also causes a high proportion of volume and weight of the capacitor and high system construction and maintenance costs, which limits the application of the MMC in the field of medium and high voltage machine drive. Currently, a three-level power converter or a unit cascade power converter is usually used to drive a high-power low-speed machine. A main circuit structure of three-level power converter is simple and easy to operate, but cannot be applied to the situation with higher power level because the three-level output voltage has a large harmonic content and the output voltage range is limited by the withstand voltage conditions of power devices. A phase-shifting transformer is adopted at an input side of the unit cascade power converter to solve the problem of high harmonics of the voltage at the output side. In addition, the voltage withstand requirement of a single power device is reduced through the cascade of power units, so that high-voltage power conversion can be easily implemented. However, due to the difference between basic potentials of the power units, a multi-coil isolation transformer is required to be adopted for insulation, and the system structure is relatively complicated. In order to improve the defects of the existing driving solution of the high-power low-speed machine, a MMC driving circuit is to be adopted to realize the low-speed driving of the high-power machine. However, the low-frequency voltage fluctuation of the MMC restricts the application of the MMC in low-speed driving of the high-power machine. For the problem of the low-frequency voltage fluctuation of the MMC, the traditional solution is to inject a high-frequency common-mode voltage or inject a selected circulating current. However, such a solution may have adverse effects on the harmonics, voltage stress, and loss of the MMC system, thereby causing adverse effects on the harmonics and loss of the machine. There are also some technologies that can alleviate the problem of the low-frequency voltage fluctuation by changing the structure of the MMC system. However, such methods need to adjust the MMC control method, which is more complicated. In addition, the existing method of driving a high-power low-speed machine through the MMC drive circuit only improves the fluctuation of the capacitor voltage during the machine start-up phase. After the machine is started, the MMC usually operates at a low frequency (such as 50 Hz), and therefore the capacity, the volume, and the weight of the capacitor are not effectively reduced. SUMMARY The purpose of the present invention is to provide a high-power machine drive system based on a modular multilevel converter for the shortcomings of the above background technology, and reduce the capacity, the volume, and the weight of the energy storage capacitor of the MMC by adopting the MMC operating at high frequency, and increase the voltage level at the DC side of the MMC, and increase the capacity of the drive system. A multi-pulse cycloconverter is used to ensure the quality of an output waveform at a machine side, and implement low-frequency control on the machine, which solves the problem of larger fluctuations of a capacitor voltage during direct drive of the high-power low-speed machine by the MMC, and overcomes the defect that the existing MMC drive circuit affects the machine harmonics and loss or needs to change the MMC control method although capable of improving the defects of the solution of direct drive. In order to achieve the objective of the present invention, the following technical solution is adopted in the present invention. A high-power machine drive system based on a modular multilevel converter consists of a modular multilevel converter, a multi-pulse cycloconverter, a carrier generation module, a speed vector controller, and a multi-pulse modulator. The MMC includes k phases of AC side outputs, and each phase of the converter includes upper and lower arms, each of the arms includes n identical sub-modules and an arm inductor, the DC side of each phase is connected to the same DC bus, and the kth phase of AC side output of the converter is connected to the kth phase of input of each of the multi-pulse cycloconverters. The multi-pulse cycloconverters are divided into a zero-type structure and a bridge-type structure. Compared with the cycloconverter with the bridge-type structure, the thyristor required by the cycloconverter with the zero-type structure is only half of that required by the bridge-type structure, and therefore the costs are lower, the control is simpler and more reliable, and it is easier to realize natural non-circulating current control. Therefore, in the present invention, the multi-pulse cycloconverter adopts a zero-type topology structure, which is composed of three-phase thyristor modules with the same internal topology structure. The kth phase of input of the multi-pulse cycloconverter is connected to the kth group of anti-parallel thyristors in thyristor modules of all phases, and an output side of the multi-pulse cycloconverter is connected to corresponding three-phase machines 1-m. The carrier generation module generates carrier signals corresponding to k groups of anti-parallel thyristors according to phase angles of the k phases of high-frequency AC voltages output by the modular multilevel converter. The speed vector controller generates voltage modulation signals corresponding to the thyristor modules of all phases according to a machine speed and a reference value thereof, an AC current output from the multi-pulse cycloconverter to the machine, and the k phases of high-frequency AC voltages with the phase difference of 2π/k output by the modular multilevel converter. The multi-pulse modulator generates trigger pulses of the thyristor modules of all phases of the multi-pulse cycloconverter by performing multi-pulse modulation on the carrier signals corresponding to the k groups of anti-parallel thyristors and the voltage modulation signals corresponding to the thyristor modules of all phases in combination with a current direction at an output side of the multi-pulse cycloconverter. As an improvement of the present invention, three-phase thyristor modules with the same internal topology structure all include k groups of anti-parallel thyristors, and each group of anti-parallel thyristors includes thyristors. A method for controlling a high-power machine drive system based on a modular multilevel converter includes the following steps. The MMC outputs k phases of high-frequency AC voltages with a phase difference of 2π/k, and the multi-pulse cycloconverter outputs a low-frequency voltage to drive a corresponding machine. Specifically, the steps are shown below. (1) The MMC adopts a high frequency modulation mode, and an AC side outputs k phases of high-frequency AC voltages with a phase difference of 2π/k. An ith phase of modulation signal is yi=m1 sin[2πfmmct−2π(i−1)/k+θmmc]. m1 is a modulation coefficient, which is an allowed maximum value, so that the MMC can output the maximum voltage. fmmc is a frequency at which the MMC outputs a voltage, which is usually several hundred Hz (such as 300 Hz). θmmc is a phase angle of a first phase of high frequency AC voltage. (2) A phase-locked loop (PLL) is used to obtain the phase angle θmmc of the high-frequency AC voltage on the AC output side of the MMC, and carriers W1-Wk respectively corresponding to k groups of anti-parallel thyristors are generated. The carriers corresponding to the ith group of anti-parallel thyristors are Wi=sin[2πfmmct−πi/k+θmmc]. (3) Three-phase low-speed operating machines 1-m all adopt speed vector control. The three-phase machine m is used as an example. The control method thereof is obtaining three-phase voltage modulation signals ymaref, ymbref, and ymcref at the output side of the multi-pulse cycloconverter according to an actual speed n of the three-phase machine, a reference value nref of the speed, three-phase currents iam, ibm, and icm at a machine side, and high-frequency AC voltages um1-umk. (4) Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymaref corresponding to a phase A thyristor module, to obtain trigger pulses S1_1a, S2_1a, . . . , S1_ka, S2_ka of phase A k groups of anti-parallel thyristors. Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymbref corresponding to a phase B thyristor module, to obtain trigger pulses S1_1b, S2_1b, . . . , S1_kb, S2_kb of phase B k groups of anti-parallel thyristors. Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymcref corresponding to a phase C thyristor module, to obtain trigger pulses S1_1c, S2_1c, . . . , S1_kc, S2_kc of phase C k groups of anti-parallel thyristors. Groups of forward connected thyristors and reversely connected thyristors in each phase of the thyristor module are driven by these trigger pulses, thereby outputting the low-frequency voltage to drive the machine m. The control method for the remaining three-phase machines is similar. The present invention has the following beneficial effects by adopting the above technical solution. (1) According to the present invention, the problem of larger fluctuations of the capacitor voltage during direct drive of the high-power low-speed machine by the MMC is solved. Since the fluctuation of a capacitor voltage of each sub-module of the MMC is inversely proportional to the AC side output frequency. If the MMC is used to directly drive the high-power low-speed machine, large fluctuations of the capacitor voltage of the sub-module may be caused. The existing solution adopts the method of increasing the capacitance of the capacitor to suppress the fluctuation of the capacitor voltage of the sub-module within the allowable range, which also causes the problem of larger proportions of the volume and the weight of the capacitor and higher system construction and maintenance costs. However, according to the present invention, the MMC is combined with the multi-pulse cycloconverter to form a high-power machine drive system. While ensuring the quality of the output waveform on the machine side, the operating frequency of the MMC can be controlled at the level of several hundred hertz. Compared with the existing solution, the capacity of an energy storage capacitor of the MMC can be significantly reduced, and the volume and weight of the energy storage capacitor of the MMC are reduced. (2) According to the present invention, the system is highly modularized and is easily expanded according to the capacity requirements. The MMC has the characteristic of modularization, a specific phase number of the MMC and the number of sub-modules required to be included in all phases of arms can be determined according to the actual drive system capacity requirements, so that the system is highly modularized and has more practical engineering value. In addition, by increasing the number of sub-modules included in all phases of arms, the withstand voltage requirement of a single power device can be significantly reduced. By increasing the number of pulses of the cycloconverter, the quality of the output waveform at the machine side can be significantly improved, thereby ensuring stable and safe operation of the machine. According to the present invention, the system is highly modularized, and the system is easy to expand according to the capacity requirements, which is the essential difference between the present invention and other existing solutions of high-power low-speed machine driving. (3) According to the present invention, based on the existing MMC module, driving of the high-power low-speed machine is implemented without changing the basic structure of the MMC, and therefore there is no need to adjust the related control method of the MMC. The whole control solution is simple and easy to understand and implement. (4) According to the present invention, through the modularity of the system, redundant control can be performed, which can greatly improve the reliability of the system. BRIEF DESCRIPTION OF THE DRAWINGS FIG. 1 (a) is a structural diagram of a high-power machine drive system according to the present invention, FIG. 1 (b) is a system structure diagram of phase A thyristor module, and FIG. 1 (c) is a structural diagram of the sub-module. FIG. 2 is a control block diagram of a high-power machine drive system according to the present invention. REFERENCE NUMERALS 1. Modular multilevel converter, 1-1. Sub-module, 1-2. Arm inductor, 1-3. DC bus, 2. Multi-pulse cycloconverter, 2-1. Phase-A thyristor module, VT1_1a, VT1_2a, VT1_3a, and VT1_ka are the first group of forward connected thyristors, the second group of forward connected thyristors, the third group of forward connected thyristors, and the kth group of forward connected thyristors in the phase A thyristor module, and VT2_1a, VT2_2a, VT2_3a, and VT2_ka are the first group of reversely connected thyristors, the second group of reversely connected thyristors, the third group of reversely connected thyristors, and the kth group of reversely connected thyristors in the phase A thyristor module. DETAILED DESCRIPTION In order to deepen the knowledge and understanding of the present invention, the technical solution is further introduced below with reference to the accompanying drawings and specific embodiments. As shown in FIG. 1 (a), a high-power machine drive system based on a modular multilevel converter (MMC) consists of a modular multilevel converter 1 and a multi-pulse cycloconverter 2. The MMC includes k phases of AC side outputs, and each phase of the converter includes upper and lower arms, and each of the arms includes n identical sub-modules 1-1 and an arm inductor 1-2. The sub-module is a half-bridge topology structure, or may be other topology structures such as a full-bridge sub-module, a clamp double sub-module, and the like. DC sides of all the phases are all connected to the same DC bus 1-3, and the kth phase of AC side output of the converter is connected to the kth phase of input of each of the multi-pulse cycloconverters. Moreover, in the above MMC topology, the number k of phases and the number n of sub-modules included in each of the arms are determined by design indicators such as the capacity of the drive system. The multi-pulse cycloconverter adopts the zero-type topology structure, which is composed of three-phase thyristor modules with the same internal topological structure. The phase A thyristor module 2-1 is shown in FIG. 1 (b). Each of the thyristor modules includes k groups of anti-parallel thyristors, and each group of anti-parallel thyristors includes thyristors VT1_i and VT2_i. The kth phase of input of the multi-pulse cycloconverter is connected to the kth group of anti-parallel thyristors in thyristor modules of all phases, and an output side of the multi-pulse cycloconverter is connected to corresponding three-phase machines 1-m. A high-power machine drive system based on a modular multilevel converter is shown in FIG. 2, including: a modular multilevel converter (MMC), a multi-pulse cycloconverter, a carrier generation module, a speed vector controller, and a multi-pulse modulator. The arms of all phases of the MMC are connected to a same DC bus, and the MMC outputs k phases of high-frequency AC voltages with a phase difference of 2π/k. All phases of thyristor modules of the multi-pulse cycloconverter consist of k groups of anti-parallel thyristors, input ends of the thyristor modules of all the phases are connected to the k phases of high-frequency AC voltages with the phase difference of 2π/k, and the multi-pulse cycloconverter outputs a frequency-converted AC power to a to-be-driven high-power machine. The carrier generation module generates carrier signals corresponding to the k groups of anti-parallel thyristors according to phase angles of the k phases of high-frequency AC voltages output by the modular multilevel converter. The speed vector controller generates voltage modulation signals corresponding to the thyristor modules of all phases according to a machine speed and a reference value thereof, an AC current output from the multi-pulse cycloconverter to the machine, and the k phases of high-frequency AC voltages with the phase difference of 2π/k output by the modular multilevel converter. The multi-pulse modulator generates trigger pulses of the thyristor modules of all phases of the multi-pulse cycloconverter by performing multi-pulse modulation on the carrier signals corresponding to the k groups of anti-parallel thyristors and the voltage modulation signals corresponding to the thyristor modules of all phases in combination with the current direction at an output side of the multi-pulse cycloconverter. The control method of the system is a coordinated control solution between the MMC, the multi-pulse cycloconverter, and the three-phase machine, including the following steps. The MMC outputs k phases of high-frequency AC voltages with a phase difference of 2π/k, and the multi-pulse cycloconverter outputs a low-frequency voltage to drive a corresponding machine. The method specifically includes the following steps. (1) The modular multilevel converter adopts a high frequency modulation mode. By comparing modulation signals yi (i=1, 2, . . . , k) with a high-frequency isosceles triangle carrier, the number of sub-modules niu_on (nil_on) that need to be input by upper arms (lower arms) of all phases can be achieved. An ith phase of modulation signal is yi=m1 sin[2πfmmct−2π(i−1)/k+θmmc]. m1 is a modulation coefficient, which is an allowed maximum value, so that the MMC can output the maximum voltage. fmmc is a frequency at which the MMC outputs a voltage, which is usually several hundred Hz. θmmc is a phase angle of a first phase of high frequency AC voltage. Then capacitor voltages of the upper arm (lower arm) sub-modules of all phases are sorted in ascending order. When the arm current iiu (iil) is positive, the number niu_on (nil_on) of sub-modules with the lowest capacitor voltage are input. When the arm current (iii) is negative, the number niu_on (nil_on) of sub-modules with the highest capacitor voltage are input, so that the AC side of the MMC outputs k phases of high-frequency AC voltages with a phase difference of 2π/k. (2) A phase-locked loop (PLL) is used to obtain the phase angle θmmc of the high-frequency AC voltage on the AC output side of the MMC, and carriers W1-Wk respectively corresponding to k groups of anti-parallel thyristors are generated. The carriers corresponding to the ith group of anti-parallel thyristors are Wi=sin[2πfmmct−πi/k+θmmc]. (3) Three-phase low-speed operating machines 1-m all adopt speed vector control. The three-phase machine m is used as an example. The control method thereof is obtaining three-phase voltage modulation signals ymaref, ymbref, and ymcref at the output side of the multi-pulse cycloconverter according to an actual speed n of the three-phase machine, a reference value nref of the speed, three-phase currents iam, ibm, and icm at a machine side, and high-frequency AC voltages um1-umk. (4) Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymaref corresponding to a phase A thyristor module, to obtain trigger pulses S1_1a, S2_1a, . . . , S1_ka, S2_ka of phase A k groups of anti-parallel thyristors. Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymbref corresponding to a phase B thyristor module, to obtain trigger pulses S1_1b, S2_1b, . . . , S1_kb, S2_kb of phase B k groups of anti-parallel thyristors. Multi-pulse cycloconverter modulation is performed on the carrier waves W1-Wk and the modulation signal ymcref corresponding to a phase C thyristor module, to obtain trigger pulses S1_1c, S2_1e, . . . , S1_kc, S2_kc of phase C k groups of anti-parallel thyristors. Groups of forward connected thyristors and reversely connected thyristors in each phase of the thyristor module are driven by these trigger pulses, thereby outputting the low-frequency voltage to drive the machine m. The control method for the remaining three-phase machines is similar. The method of multi-pulse cycloconverter modulation in step (4) is analyzed by using the phase A thyristor module as an example (the other two-phase modules are similar), which is specifically as follows. (a) For all the groups of forward connected thyristors VT1_1a-VT1_ka in the phase A thyristor module, respective trigger pulses S1_1a-S1_ka are obtained by respectively comparing falling edges of the carriers W1-Wk with the modulation signal ymaref If the carrier is less than the modulation signal, the trigger pulse is continuously sent, otherwise the trigger pulse is not sent. (b) For all the groups of reversely connected thyristors VT2_1a-VT2_ka in the phase A thyristor module, respective trigger pulses S2_1a-S2_ka are obtained by respectively comparing rising edges of the carriers W1-Wk with the modulation signal ymaref. If the carrier is greater than the modulation signal, the trigger pulse is continuously sent, otherwise the trigger pulse is not sent. (c) If the current direction iam at the output side of the cycloconverter is greater than 0, all the groups of reversely connected thyristors VT2_1a-VT2_ka are locked; and if the current direction iam at the output side of the cycloconverter is less than 0, all the groups of forward connected thyristors VT1_1a-VT1_ka are locked. The present invention is especially suitable for high-power low-speed machine drive. Compared with the existing method, according to the present invention, the MMC is combined with the multi-pulse cycloconverter, and by adopting the MMC that operates at a high frequency, the capacity, the volume, and the weight of the energy storage capacitor of the MMC are reduced, the voltage level at the DC side of the MMC is increased, and the capacity of the drive system is increased. By adopting the multi-pulse cycloconverter, quality of an output waveform at a machine side can be guaranteed, thereby implementing low frequency control on the machine. It should be noted that the above embodiments are not used to limit the protection scope of the present invention, and equivalent changes or substitutions made on the basis of the above technical solutions fall within the protection scope of the claims of the present invention.
[ZH CN110350571B]: 一种提升柔性直流输电交流侧故障穿越能力的控制方法 [EN CN110350571B]: Control method for improving AC side fault ride-through capability of flexible DC transmission | [ZH CN110350571B]: 本发明公开了一种提升柔性直流输电交流侧故障穿越能力的控制方法，该方法为：以电容值可变的等效电容对模块化多电平换流站上下桥臂进行数学建模获得数学模型，根据该数学模型，分析得出MMC换流站交直流侧实时功率值与MMC换流站直流侧电压值之间的解析关系，根据该解析关系推导出交流侧发生故障时换流站交直流侧功率之间的不平衡程度与直流侧电压跌落量之间的关系，再根据该关系，确定换流站功率调整实时目标值。本发明明显降低换流站交直流侧的功率不平衡程度，从而减轻已有的外环功率控制和内环电流控制的功率调节压力，间接提升了已有控制策略的控制效果，能够很好的提高直流电压的稳定性。 [EN CN110350571B]: The invention discloses a control method for improving flexible DC power transmission AC side fault ride-through capability, The method comprises the steps: the mathematical model of the upper and lower bridge arms of a modular multi-level converter station is established through mathematical modeling by using equivalent capacitance with variable capacitance, the analytic relationship between thereal-time power value of the AC/DC side of MMC converter station and the voltage value of the DC side of the MMC converter station is obtained according to the mathematical model, the relationship between the imbalance degree between AC and DC side power of the converter station and the DC side voltage sag is deduced according to the analytic relationship, and then the real-time target value of converter station power adjustment is determined according to the relationship. The AC/DC side power imbalance degree of the converter station is obviously reduced, the power adjustment pressure of theexisting outer loop power control and the inner loop current control is reduced, the control effect of the existing control strategy is indirectly improved and the stability of the DC voltage can be greatly improved. | CN110350571B | 2019-10-18 2020-10-02 | CN201910637804A | 2019-07-15 2019-07-15 | CN201910637804A, 2019-07-15 CN201910637804A, 2019-07-15 | CN110350571B: 2020-10-02 | GUIZHOU POWER GRID CO LTD 贵州电网有限责任公司 | CHEN DUNHUI LIN CHENHUI GAO JIPU WANG MIAN DAI QIJI LIU BIN WANG YU ZHANG LI FAN QIANG | H02J3/36: I H02J3/24: I H02J3/48: I | H02J3/24: I H02J3/36: I H02J3/48: I H02J2003/007: A Y02E60/60: A | CN103414179A CN104022522A WO2015102060A1 CN105391032A CN108365624A | CN110943635A CN110943635 110943635 | [ZH CN110350571B]: L 一种提升柔性直流输电交流侧故障穿越能力的控制方法，其特征在于：该方法为：以 电容值可变的等效电容对模块化多电平换流站上下桥臂进行数学建模获得数学模型，根据 该数学模型，分析得出MMC换流站交直流侧实时功率值与MMC换流站直流侧电压值之间的解 析关系，根据该解析关系推导出交流侧发生故障时换流站交直流侧功率之间的不平衡程度 与直流侧电压跌落量之间的关系，再根据该关系,确定换流站功率调整实时目标值;该方法 的具体步骤如下： 将上桥臂与下桥臂分别用一个电容值可变的电容来进行等效，设a相的上桥臂等效电 容玛⑴、a相下桥臂的等效电容为第⑺，得到如下式： 射⑺= α⑴= 2C ?/(1 -sin((w/)) 2C N(l + sin(&amp;)) ¢1) 式中N为上下桥臂投入的子模块数量之和,C为单个子模块的电容值，3为系统角频率、 t为时间； 将换流站上桥臂和下桥臂流过电流一个完整的变化周期划分为四个阶段,结合式(1), 得到换流站直流电压A Un的变化解析表达式,如下： Δ0 /V乃(/COS(e)一4ί) 曲 2c⑦ ⑵ 式中ί为流过上桥臂和下桥臂的交流基波分量的幅值,i为流经上下桥臂的直流分量大 小的三分之一，夕为电压电流相角差； 在原有MMC换流站控制框架之前添加一个控制环节，该控制环节用于对原来输入换流 站控制环节的功率控制目标值进行优化处理； 设桥臂子模块电容值C,投入子模块数为N,直流电压初始值为Uo,直流电压最大允许增 加量为A Umax,在时间t内桥臂电容存储能量的增量为： _ CA* , CUQUm Cmax Ν C3) 故障过程中的功率不平衡程度满足： AEcWAEcmax (4) 设两端柔性直流输电系统中换流站1为定电压控制站,换流站2为功率调节站，当换流 站1发生交流侧故障时,换流站2的输入功率Pin大幅下降，换流站2的输出功率Pout也跟着下 降,Pout与Pin之间出现功率不平衡,导致换流站2直流侧电压跌落,设跌落量为Δ Ude ,直流电 压初始值为Uo,根据式(3),换流站2的电容能量减少量为： Ν 2N ¢5) 根据能量守恒有： C6) CN 110350571 Β 将式⑹两边同时求导得: 当换流站1发生故障时,换流站1侧的功率支撑能力不足,换流站2的功率控制参考值应 该跟着换流站1侧注入功率同步递减，直到电压恢复稳定后，直流侧电压变化率趋近于零, 换流站2的功率控制指令值刚好与此时换流站1交流侧的注入功率相等，当功率注入端出现 交流侧故障时,换流站2的功率控制指令值为： % = &amp;厂3)&lt; ¢8) 式中S为电压稳定控制系数，保证故障情况下，功率调整过程中，换流站2侧控制功率指 令值小于换流站1侧的功率支撑能力。 CN 110350571 Β [EN CN110350571B]: L A control method for improving the fault ride-through capability of the AC side of the flexible DC transmission, which is characterized in that: the method is: mathematically modeling the upper and lower arms of the modular multilevel converter station with an equivalent capacitor with a variable capacitance value Mathematical model. According to this mathematical model, the analytical relationship between the real-time power value of the AC and DC side of the MMC converter station and the voltage value of the DC side of the MMC converter station is analyzed and derived, and the converter station when the AC side fails is derived from the analytical relationship The relationship between the degree of imbalance between the AC and DC side power and the amount of voltage drop on the DC side, and then determine the real-time target value of the converter station power adjustment based on this relationship; the specific steps of this method are as follows: Connect the upper bridge arm to the lower bridge The arms are respectively equivalent with a capacitor with a variable capacitance value. Set the equivalent capacitance of the upper arm of phase a and the equivalent capacitance of the lower arm of phase a as , and the following equation is obtained: = α= 2C ?/(1 -sin((w/)) 2C N(l + sin(&amp;)) ¢1) where N is the sum of the number of sub-modules input by the upper and lower bridge arms, and C is the capacitance value of a single sub-module, 3 is the system angular frequency, and t is the time; a complete cycle of current flowing through the upper and lower bridge arms of the converter station is divided into four stages, combined with formula (1), the DC voltage A Un of the converter station is obtained Change the analytical expression as follows: Δ0 /VNai(/COS(e)One4ί) song2c Where ί is the amplitude of the fundamental AC component flowing through the upper and lower bridge arms, i is one-third of the magnitude of the DC component flowing through the upper and lower arms, and is the voltage and current phase angle difference; in the original MMC A control link is added before the control frame of the converter station, which is used to optimize the power control target value of the original input to the control link of the converter station; Set the capacitance value of the bridge arm submodule C, the number of input submodules is N, DC The initial value of the voltage is Uo, the maximum allowable increase in DC voltage is A Umax, and the increase in the stored energy of the bridge arm capacitance during time t is: _ CA*, CUQUm Cmax Ν C3) The power imbalance during the fault process meets: AEcWAEcmax (4) In the two-end flexible DC transmission system, converter station 1 is a constant voltage control station, and converter station 2 is a power regulation station. When converter station 1 has an AC side failure, the input power Pin of converter station 2 The output power Pout of converter station 2 also drops. There is a power imbalance between Pout and Pin, which causes the DC side voltage of converter station 2 to drop. Set the amount of drop to Δ Ude and the initial value of DC voltage to Uo. Equation (3), the capacitance energy reduction of converter station 2 is: Ν 2N ¢5) According to the conservation of energy: C6) CN 110350571 Β Deriving both sides of equation at the same time: When converter station 1 fails, the power support capacity of converter station 1 is insufficient, and the power control reference value of converter station 2 should be decreased synchronously with the injected power of converter station 1 until the voltage is stabilized. The rate of change approaches zero, and the power control command value of converter station 2 is exactly equal to the injected power of the AC side of converter station 1 at this time. When the AC side failure occurs at the power injection end, the power control command value of converter station 2 For:% = &amp;Factory 3)&lt; ¢8) Where S is the voltage stability control coefficient, which ensures that in the event of a fault, the control power command value of the converter station 2 side is less than the power support capacity of the converter station 1 during the power adjustment process. CN 110350571 Β | [ZH CN110350571B]: 一种提升柔性直流输电交流侧故障穿越能力的控制方法 技术领域 [0001]本发明属于基于MMC换流器的两端或者多端柔性直流输电系统技术领域,具体涉 及一种提升柔性直流输电交流侧故障穿越能力的控制方法。 背景技术 [0002] 我国的能源分布和负荷分布不匹配，能源富余区域与重负荷区域距离较远，为了 实现能源的高效配置和充分利用，必须发展大容量远距离输电技术，同时直流异步互联还 有避免大面积连锁故障发生、消除低频振荡问题、不会加重交流电网短路电流水等作用。模 块化多电平柔性直流输电技术具有占地面积小、无换相失败问题、结构多变、方便扩展等诸 多优良特性，因此在直流电能传输及区域交流电网互联方面具有非常广阔的应用前景。目 前我国在上海、南澳、舟山以及厦门等地已开展和建设了一批柔性直流输电工程，美国建设 的跨湾工程(Trans Bay Cable Project,TBC)以及法国―西班牙的电网互联工程(INELFE) 也采用了柔性直流输电技术。 [0003] 柔性直流输电系统稳定运行的关键在于直流电压的稳定性，目前针对柔性直流输 电系统已经提出了诸多成熟的控制方法和策略,对于两端柔性直流输电系统一般采用定电 压站和定功率站相配合的控制方法，对于多端柔性直流输电系统常采用主从控制、下垂控 制等方法。这些控制方法在进行功率调整时都有一个可控裕度，当交流侧发生严重故障时, 由于故障瞬间换流站交直流侧交换功率产生很大的不平衡，这种不平衡的程度会超过已有 控制方法的功率调整可控裕度，出现调节能力不足，导致直流侧电压失稳，换流站退出运 行。 发明内容 [0004]本发明要解决的技术问题是:提供一种提升柔性直流输电交流侧故障穿越能力的 控制方法，以解决现有技术中存在的问题。 [0005]本发明采取的技术方案为:一种提升柔性直流输电交流侧故障穿越能力的控制方 法，该方法为：以电容值可变的等效电容对模块化多电平换流站上下桥臂进行数学建模获 得数学模型，根据该数学模型，分析得出MMC换流站交直流侧实时功率值与MMC换流站直流 侧电压值之间的解析关系,根据该解析关系推导出交流侧发生故障时换流站交直流侧功率 之间的不平衡程度与直流侧电压跌落量之间的关系，再根据该关系，确定换流站功率调整 实时目标值。 [0006] 一种提升柔性直流输电交流侧故障穿越能力的控制方法，该方法的具体步骤如 下： [0007]将上桥臂与下桥臂分别用一个电容值可变的电容来进行等效，设a相的上桥臂等 效电容1⑺、a相下桥臂的等效电容为，得到如下关系式： CN 110350571 Β [0008] 2C Ca(t) =-----------2C C；⑴=———.. N(l + sin(&amp;)) ¢1) [0009]式中N为上下桥臂投入的子模块数量之和,C为单个子模块的电容值，3为系统角 频率、t为时间； [0010]将换流站上桥臂和下桥臂流过电流一个完整的变化周期划分为四个阶段,结合式 (1),得到换流站直流电压A Ude的变化解析表达式,如下： [0011] Δ%,=世缥也竺 ⑵ [0012]式中I为流过上桥臂和下桥臂的交流基波分量的幅值,i为流经上下桥臂的直流分 量大小的三分之一，。为电压电流相角差； [0013] 根据式(2)可知，直流侧电压的波动主要是由直流侧和交流侧的注入电流即注入 功率的不平衡程度决定的，基于此,在原有MMC换流站控制框架之前添加一个控制环节，该 控制环节用于对原来输入换流站控制环节的功率控制目标值进行优化处理,从而减少换流 器交直流侧的功率传输不平衡程度，抑制直流电压波动； [0014]设桥臂子模块电容值C,投入子模块数为N,直流电压初始值为Uo,直流电压最大允 许增加量为AUmax,考虑到子模块电容的电压均衡控制，近似认为投入子模块电压均匀分 配,在时间t内桥臂电容存储能量的增量为： [0015] 二四也A* 2N N (3) [0016] 为了保证直流电压变化量不超过AUmax,故障过程中的功率不平衡程度满足： [0017] Δ Ec‹ Δ Ec max (4) [0018]设两端柔性直流输电系统中换流站1为定电压控制站,换流站2为功率调节站，当 换流站1发生交流侧故障时,换流站2的输入功率Pin大幅下降,换流站2的输出功率Pout也跟 着下降,Pout与Pin之间出现功率不平衡,导致换流站2直流侧电压跌落,设跌落量为A Ude ,直 流电压初始值为Uo，根据式(3),换流站2的电容能量减少量为： [0019] C5) [0020]根据能量守恒有: [0021] ^Pou,dt-^Pindt = \Ec [0022] 将式(6)两边同时求导得: [0023] (6) [0024]当换流站1发生故障时,换流站1侧的功率支撑能力不足，所以换流站2的功率控制 参考值应该跟着换流站1侧注入功率同步递减，从而减小换流站2的功率，这样才能保证直 CN 110350571 Β 流侧电压不会因为功率无法平衡而出现失稳，直到电压恢复稳定后,直流侧电压变化率趋 近于零，换流站2的功率控制指令值刚好与此时换流站1交流侧的注入功率相等，根据上述 分析，当功率注入端出现交流侧故障时，换流站2的功率控制指令值为： [0025] = ¢8) [0026] 式中δ为电压稳定控制系数，保证故障情况下，功率调整过程中，换流站2侧控制功 率指令值小于换流站1侧的功率支撑能力,这样电压才能稳定在设定指令值上。当柔性直流 系统发生交流侧故障时，进入功率控制目标值处理环节，将稳定运行状态下的功率控制目 标值Pref修改为故障状态下的功率控制目标值P'ref。 [0027]本发明首先用电容等效的方法对典型柔直换流站桥臂进行数学建模，进而分析直 流侧电压与不同工况及故障情况下交直流侧功率不平衡情况之间的关系，然后提出了一种 可以根据换流站实际运行工况自动调整功率控制指令值，降低交直流侧功率不平衡度的动 态功率控制方法，该方法的应用可以在交流侧发生故障时，根据实际交换功率的不平衡程 度，实时修正功率控制站的功率控制目标值，使得故障时换流站的功率调整量始终不超过 所采用控制方法的可调裕度，这样就避免了故障时直流侧电压大幅跌落，出现失稳,使得柔 性直流输电系统在交流侧故障时仍然能够保持一定的电能输送，当交流侧故障消失时，自 动回复正常运行状态。该调整策略不需要站间通信，不改变原有换流站功率控制系统的内 环和外环结构，只是在原有换流站控制系统之外附加一个功率控制环节，可以与现有的不 同换流站功率控制策略配合使用,所以在两端和多端柔直系统中均可应用。 [0028]本发明的有益效果：与现有技术相比，本发明过自动降低交流侧故障时换流站交 直流侧的功率调整量，保证该调整量处于控制系统的功率可调裕度之内，从而保证发生交 直流侧故障时，不出现直流电压失稳。 附图说明 [0029] 图1为MMC典型拓扑结构图； [0030]图2为基于MMC换流站的两端柔性直流输电系统结构示意图； [0031]图3为柔性直流输电系统中功率定功率控制站交直流侧传输功率关系示意图； [0032]图4典型的柔性直流输电有功功率控制系统流程示意图； [0033]图5为在本发明所采用控制策略下的柔性直流输电系统有功功率控制流程示意 图。 具体实施方式 [0034]下面结合附图及具体的实施例对本发明进行进一步介绍。 [0035]实施例1：如图卜5所示，一种提升柔性直流输电交流侧故障穿越能力的控制方法, 该方法为：以电容值可变的等效电容对模块化多电平换流站上下桥臂进行数学建模获得数 学模型，根据该数学模型，分析得出MMC换流站交直流侧实时功率值与MMC换流站直流侧电 压值之间的解析关系，根据该解析关系推导出交流侧发生故障时换流站交直流侧功率之间 的不平衡程度与直流侧电压跌落量之间的关系,再根据该关系，确定换流站功率调整实时 CN 110350571 Β 目标值。 [0036]构建MMC的基本控制框架，对于外环功率控制环节，如果是多端柔性直流输电系 统，可以采用下垂控制或者主从控制，对于两端柔性直流输电系统，则可采用定功率控制， 根据不同换流站的运行特性选取ΡΙ参数;而对于内环电流控制可以采用当下比较典型的带 内部环流抑制的控制框架。本发明将在MMC基本控制框架之外附加一个控制环节，该环节主 要处理MMC外环功率控制的输入量：功率控制目标值。该环节需要采集换流站当前运行功 率、换流站子模块数、换流站子模块电容、换流站直流电压初始值、换流站直流电压变化率 等状态信息，然后利用这些状态信息计算并输出一个功率控制目标值作为MMC功率外环控 制环节的输入，本质上相当于在原有的MMC外环功率控制环节之外附加了一个增益系数随 换流站实时运行工况动态变化的增益环节，相当于该增益环节与原来的外环功率控制环节 一起形成新的外环功率控制环节。 [0037] 一种抑制柔性直流输电直流电压波动的功率控制方法，具体步骤如下： [0038]如图1为典型的MMC换流站拓扑结构图，考虑到虽然上下桥臂所有子模块的充放电 电流在运行过程中是实时变化的，而且包含直流、一次、二次等各种分量，但是在同一时刻 同一桥臂上的所有子模块电容的充放电电流是相等的,而且由于上下桥臂的投入子模块数 量也是实时变化的，本发明将上桥臂与下桥臂分别用一个电容值可变的电容来进行等效。 设a相的上桥臂等效电容C；⑺、a相下桥臂的等效电容为然⑴,经过分析推导可得到如下 关系式: [0039] 玛⑺= £：«) = 2。 NQ-sinQ)) 2。 7V(l + sin((y/)) Ci) [0040]式中N为上下桥臂投入的子模块数量之和,C为单个子模块的电容值。 [0041]本发明将换流站上下桥臂流过电流一个完整的变化周期划分为四个阶段,集合式 ⑴，可以推导出换流站直流电压的变化解析表达式，如下: [0042] Δί/Α. =— 「一(2) [0043]式中I为流过上下桥臂的交流基波分量的幅值,i为流经上下桥臂的直流分量大小 的三分之一。 [0044] 根据式(2)可知，直流侧电压的波动主要是由直流侧和交流侧的注入电流即注入 功率的不平衡程度决定的，本发明基于此,在原有MMC换流站控制框架之前添加一个控制环 节，该环节主要作用是对原来输入换流站控制环节的功率控制目标值进行优化处理，从而 减少换流器交直流侧的功率传输不平衡程度,抑制直流电压波动。 [0045]设桥臂子模块电容值C,投入子模块数为N,直流电压初始值为Uo,直流电压最大允 许增加量为AUmax,考虑到子模块电容的电压均衡控制，近似认为投入子模块电压均匀分 配。在时间t内桥臂电容存储能量的增量为： [0046] = CAk + Β0A4ax (3) 'a 2N N [0047] 为了保证直流电压变化量不超过AUmax,故障过程中的功率不平衡程度应满足： [0048] Δ Ec‹ Δ Ec max (4) [0049]下面以两端柔性直流输电系统为例对本发明进行论述。图2为典型的两端柔性直 流输电系统示意图，其中换流站1为定电压控制站,换流站2为功率调节站。图3为换流站2的 交直流侧功率交换示意图。当换流站1发生交流侧故障时,Pin大幅下降,Pout也跟着下降,Pout 与Pin之间出现功率不平衡,导致换流站2直流侧电压跌落,设跌落量为Δ Ude,直流电压初始 值为Uo。根据式⑶，换流站2的电容能量减少量为： [0050] =3x[—--次卢J (5 ) [0051]根据能量守恒有： [0052] 以，山—以山=Α4 (6) [0053] 将式⑹两边同时求导得： 5—牛 ⑺ [0055]当换流站1发生故障时,换流站1侧的功率支撑能力不足，所以换流站2的功率控制 参考值应该跟着换流站1侧注入功率同步递减，从而减小换流站2的功率，这样才能保证直 流侧电压不会因为功率无法平衡而出现失稳，直到电压恢复稳定后,直流侧电压变化率趋 近于零，换流站2的功率控制指令值刚好与此时换流站1交流侧的注入功率相等。根据上述 分析，当功率注入端出现交流侧故障时，换流站2的功率控制指令值可设计为： [0056] % ;以,-3x(广。X嘴小5 (8) [0057] 式中δ为电压稳定控制系数，保证故障情况下，功率调整过程中，换流站2侧控制功 率指令值小于换流站1侧的功率支撑能力，这样电压才能稳定在设定指令值上。 [0058]图4为典型的柔性直流输电有功功率控制系统框图，图5为本发明提出的加入功率 调整附加环节之后的有功功率控制系统框图，首先加入一个柔性直流输电故障识别环节, 当柔性直流系统发生交流侧故障时，进入功率控制目标值处理环节,将稳定运行状态下的 功率控制目标值Pref修改为故障状态下的功率控制目标值P'ref。图中有功功率外环控制环 节和电流内环控制环节可以参照已有的典型控制系统构建。 [0059]与现有的提升MMC运行直流电压稳定性的控制方法相比，本发明并没有对已有的 外环功率控制和内环电流控制作出原则上的修改，而是在已有的功率控制环节之前附加了 一个根据换流站当前运行工况自适应调整的增益环节,该改动可以明显降低换流站交直流 侧的功率不平衡程度，从而减轻已有的外环功率控制和内环电流控制的功率调节压力，间 接提升了已有控制策略的控制效果，能够很好的提高直流电压的稳定性。 [0060]以上所述，仅为本发明的具体实施方式,但本发明的保护范围并不局限于此，任何 熟悉本技术领域的技术人员在本发明揭露的技术范围内，可轻易想到变化或替换,都应涵 盖在本发明的保护范围之内，因此，本发明的保护范围应以所述权利要求的保护范围为准。 [EN CN110350571B]: A control method for improving the AC side fault ride-through capability of flexible direct current transmissionTechnical field [0001] The present invention belongs to the technical field of two-terminal or multi-terminal flexible DC transmission systems based on MMC converters, and specifically relates to a control method for improving the fault ride-through capability of the AC side of the flexible DC transmission. Background technique [0002] my countrys energy distribution and load distribution do not match. The energy surplus area is far away from the heavy load area. In order to achieve efficient allocation and full utilization of energy, large-capacity long-distance power transmission technology must be developed. Large-area cascading failures occur, eliminate low-frequency oscillation problems, and will not aggravate the effects of short-circuit current in the AC grid. Modular multilevel flexible DC transmission technology has many excellent characteristics such as small footprint, no commutation failure, variable structure, and convenient expansion. Therefore, it has a very broad application prospect in DC power transmission and regional AC grid interconnection. At present, my country has carried out and constructed a number of flexible DC transmission projects in Shanghai, South Australia, Zhoushan, Xiamen and other places. The Trans Bay Cable Project (TBC) built in the United States and the French-Spanish grid interconnection project (INELFE) have also It adopts flexible DC transmission technology. [0003] The key to the stable operation of the flexible DC transmission system lies in the stability of the DC voltage. At present, many mature control methods and strategies have been proposed for the flexible DC transmission system. For the two-end flexible DC transmission system, constant voltage stations and constant power are generally used. The control method that the station cooperates, for the multi-terminal flexible direct current transmission system often adopts the method such as master-slave control, droop control and so on. These control methods have a controllable margin when performing power adjustments. When a serious failure occurs on the AC side, the AC and DC sides of the converter station will have a large imbalance due to the moment the failure occurs. The degree of this imbalance will exceed The power adjustment controllable margin of the existing control method has insufficient adjustment capability, which causes the DC side voltage to be unstable and the converter station to withdraw from operation. Summary of the invention [0004] The technical problem to be solved by the present invention is to provide a control method for improving the fault ride-through capability of the AC side of the flexible direct current transmission to solve the problems in the prior art. [0005] The technical solution adopted by the present invention is: a control method for improving the fault ride-through capability of the AC side of the flexible direct current transmission. The method is: using an equivalent capacitor with a variable capacitance value to connect the upper and lower bridges of the modular multilevel converter station The arm performs mathematical modeling to obtain a mathematical model. According to the mathematical model, the analytical relationship between the real-time power value of the AC and DC side of the MMC converter station and the voltage value of the DC side of the MMC converter station is analyzed, and the AC side is derived from the analytical relationship The relationship between the degree of imbalance between the AC and DC side power of the converter station and the voltage drop on the DC side when a fault occurs, and then determine the real-time target value of the converter station power adjustment based on this relationship. [0006] A control method for improving the fault ride-through capability of the AC side of a flexible DC transmission, the specific steps of the method are as follows: [0007] The upper bridge arm and the lower bridge arm are respectively equivalent with a variable capacitance capacitor, and the equivalent capacitance of the upper bridge arm of the a phase 1 and the equivalent capacitance of the lower bridge arm of the a phase are obtained as follows: Relationship: CN 110350571 Β [0008] 2C Ca(t) =-----------2C C;=.. N(l + sin(&amp;)) ¢1) [0009] In the formula, N is the sum of the number of sub-modules invested by the upper and lower bridge arms, C is the capacitance value of a single sub-module, 3 is the system angular frequency, and t is the time; [0010] A complete change cycle of the current flowing through the upper and lower bridge arms of the converter station is divided into four stages, combined with formula (1), the analytical expression for the change of the DC voltage A Ude of the converter station is obtained as follows: [0011] Δ%,=Shi Jing Ye Zhu2 [0012] In the formula, I is the amplitude of the fundamental AC component flowing through the upper and lower bridge arms, and i is one third of the magnitude of the DC component flowing through the upper and lower bridge arms. Is the voltage and current phase angle difference; [0013] According to equation (2), it can be seen that the fluctuation of the DC side voltage is mainly determined by the imbalance degree of the injected current, that is, the injected power, on the DC side and the AC side. Based on this, one is added before the original MMC converter station control framework. The control link is used to optimize the power control target value originally input to the control link of the converter station, thereby reducing the unbalanced degree of power transmission on the AC and DC sides of the converter and suppressing DC voltage fluctuations; [0014] Suppose the bridge arm sub-module capacitance value C, the number of input sub-modules is N, the initial value of the DC voltage is Uo, and the maximum allowable increase in the DC voltage is AUmax. Considering the voltage balance control of the sub-module capacitance, it is approximately regarded as the input sub-module The voltage is evenly distributed, and the increase in the stored energy of the bridge arm capacitance in time t is: [0015] Er Si Ye A* 2N N (3) [0016] In order to ensure that the DC voltage change does not exceed AUmax, the power imbalance during the fault process satisfies: [0017] Δ Ec Δ Ec max (4) [0018] In the two-terminal flexible DC transmission system, the converter station 1 is the constant voltage control station, and the converter station 2 is the power regulation station. When the AC side failure occurs in the converter station 1, the input power Pin of the converter station 2 is large Decrease, the output power Pout of converter station 2 also decreases. There is a power imbalance between Pout and Pin, which causes the DC side voltage of converter station 2 to drop. Set the drop amount to A Ude and the initial value of DC voltage to Uo. (3) The capacitance energy reduction of converter station 2 is: [0019] C5) [0020] According to the conservation of energy: [0021] ^Pou,dt-^Pindt = \Ec [0022] Deriving both sides of equation (6) simultaneously: [0023] (6) [0024] When the converter station 1 fails, the power support capacity of the converter station 1 is insufficient, so the power control reference value of the converter station 2 should be decreased synchronously with the injected power of the converter station 1 to reduce the commutation Station 2s power, so as to ensure straight CN 110350571 Β The voltage on the current side will not lose stability due to unbalanced power, until the voltage is restored to stability, the rate of change of the voltage on the DC side approaches zero, and the power control command value of converter station 2 is exactly the same as that of the AC side of converter station 1 at this time. The injected power is equal. According to the above analysis, when the AC side fault occurs at the power injection end, the power control command value of converter station 2 is: [0025] = ¢8) [0026] where δ is the voltage stability control coefficient, to ensure that in the case of a fault, during the power adjustment process, the control power command value of the converter station 2 side is less than the power support capacity of the converter station 1 side, so that the voltage can be stabilized at the set command Value. When the AC-side failure of the flexible DC system occurs, the power control target value processing link is entered, and the power control target value Pref in the stable operation state is modified to the power control target value P'ref in the fault state. [0027] The present invention first uses the capacitance equivalent method to mathematically model the bridge arms of a typical flexible-to-DC converter station, and then analyzes the relationship between the DC side voltage and the AC and DC side power imbalance under different operating conditions and fault conditions , And then proposed a dynamic power control method that can automatically adjust the power control command value according to the actual operating conditions of the converter station to reduce the power imbalance of the AC and DC sides. The application of this method can be based on the actual The unbalanced degree of the exchange power, the real-time correction of the power control target value of the power control station, so that the power adjustment amount of the converter station in the event of a failure does not exceed the adjustable margin of the adopted control method, thus avoiding the DC side voltage in the event of a failure A large drop and instability have enabled the flexible DC transmission system to maintain a certain amount of power transmission when the AC side fails. When the AC side failure disappears, it will automatically return to normal operation. This adjustment strategy does not require inter-station communication, does not change the inner and outer loop structures of the original converter station power control system, but only adds a power control link to the original converter station control system, which can be different from the existing ones. The flow station power control strategy is used in conjunction, so it can be applied in both ends and multi-end flexible straightening systems. [0028] The beneficial effects of the present invention: Compared with the prior art, the present invention automatically reduces the power adjustment amount on the AC and DC sides of the converter station when the AC side fails, and ensures that the adjustment amount is within the power adjustable margin of the control system. In order to ensure that there is no DC voltage instability in the event of a fault on the AC and DC side. BRIEF DESCRIPTION OF THE DRAWINGS [0029] Figure 1 is a diagram of a typical topology of MMC; [0030] FIG. 2 is a schematic diagram of the structure of a two-end flexible DC transmission system based on MMC converter stations; [0031] FIG. 3 is a schematic diagram of the transmission power relationship between the AC and DC sides of the power constant power control station in the flexible DC transmission system; [0032] FIG. 4 is a schematic flow diagram of a typical flexible DC transmission active power control system; [0033] FIG. 5 is a schematic diagram of the active power control flow of the flexible DC transmission system under the control strategy adopted in the present invention. detailed description [0034] The present invention will be further introduced below in conjunction with the drawings and specific embodiments. [0035] Embodiment 1: As shown in FIG. 1-5, a control method for improving the fault ride-through capability of the AC side of a flexible DC transmission, the method is: the equivalent capacitor with a variable capacitance is used for modular multilevel commutation The upper and lower bridge arms of the station are mathematically modeled to obtain a mathematical model. According to the mathematical model, the analytical relationship between the real-time power value of the AC and DC side of the MMC converter station and the voltage value of the DC side of the MMC converter station is obtained, and the analytical relationship is derived The relationship between the degree of unbalance between the AC and DC side power of the converter station and the voltage drop on the DC side when the AC side fails, and then determine the real-time power adjustment of the converter station based on this relationship CN 110350571 Β Target value. [0036] Construct the basic control framework of MMC. For the outer loop power control link, if it is a multi-terminal flexible DC transmission system, droop control or master-slave control can be adopted. For the two-terminal flexible DC transmission system, constant power control can be adopted. The operating characteristics of different converter stations select PI parameters; for inner loop current control, the current typical control framework with internal circulation suppression can be used. In the present invention, a control link is added to the MMC basic control framework, and this link mainly deals with the input quantity of the MMC outer loop power control: the power control target value. This link needs to collect status information such as the current operating power of the converter station, the number of sub-modules of the converter station, the capacitance of the sub-modules of the converter station, the initial value of the DC voltage of the converter station, and the rate of change of the DC voltage of the converter station, and then use these status information to calculate And output a power control target value as the input of the MMC power outer loop control link, which is essentially equivalent to adding a gain link in which the gain coefficient changes dynamically with the real-time operating conditions of the converter station in addition to the original MMC outer loop power control link. , Equivalent to this gain link and the original outer loop power control link form a new outer loop power control link. [0037] A power control method for suppressing DC voltage fluctuations of flexible DC transmission, the specific steps are as follows: [0038] Figure 1 is a typical MMC converter station topology diagram, considering that although the charging and discharging currents of all sub-modules of the upper and lower bridge arms change in real time during operation, and include DC, primary, secondary, etc. However, at the same time, the charge and discharge currents of all sub-module capacitors on the same bridge arm are equal, and since the number of input sub-modules of the upper and lower bridge arms also changes in real time, the present invention uses the upper and lower bridge arms separately A variable capacitance capacitor is equivalent. Suppose the equivalent capacitance C of the upper bridge arm of phase a; The equivalent capacitance of the lower bridge arm of phase a is what it is. , after analysis and deduction, the following relationship can be obtained: [0039] Ma = £: «) = 2。 NQ-sinQ)) 2。 7V(l + sin((y/)) Ci) [0040] In the formula, N is the sum of the number of sub-modules invested by the upper and lower bridge arms, and C is the capacitance value of a single sub-module. [0041] The present invention divides a complete change cycle of the current flowing through the upper and lower bridge arms of the converter station into four stages, collective formula (1), and the analytical expression for the change of the DC voltage of the converter station can be derived, as follows: [0042] Δί/Α. =- "One (2) [0043] where I is the amplitude of the fundamental AC component flowing through the upper and lower bridge arms, and i is one third of the magnitude of the DC component flowing through the upper and lower bridge arms. [0044] According to formula (2), the fluctuation of the DC side voltage is mainly determined by the imbalance degree of the injected current, that is, the injected power, on the DC side and the AC side. The present invention is based on this, before the original MMC converter station control framework Add a control link, the main function of this link is to optimize the power control target value of the original input to the converter station control link, thereby reducing the unbalanced degree of power transmission on the AC and DC sides of the converter and suppressing DC voltage fluctuations. [0045] Suppose the bridge arm sub-module capacitance value C, the number of input sub-modules is N, the initial value of the DC voltage is Uo, and the maximum allowable increase of the DC voltage is AUmax. Considering the voltage balance control of the sub-module capacitance, it is approximately regarded as the input sub-module The voltage is evenly distributed. The increment of the energy stored in the bridge arm capacitance in time t is: [0046] = CAk + Β0A4ax (3)'a 2N N [0047] In order to ensure that the DC voltage change does not exceed AUmax, the power imbalance during the fault process should meet: [0048] Δ Ec Δ Ec max (4) [0049] The present invention is discussed below by taking a two-terminal flexible direct current transmission system as an example. Figure 2 is a schematic diagram of a typical two-terminal flexible DC transmission system, where converter station 1 is a constant voltage control station, and converter station 2 is a power regulation station. Figure 3 is a schematic diagram of power exchange on the AC and DC sides of the converter station 2. When a fault occurs on the AC side of converter station 1, Pin drops sharply, and Pout also drops accordingly. There is a power imbalance between Pout and Pin, which causes the DC side voltage of converter station 2 to drop, set the amount of drop as Δ Ude, and the initial DC voltage The value is Uo. According to formula (3), the capacitance energy reduction of converter station 2 is: [0050] =3x[---Time Lu J (5) [0051] According to the conservation of energy: [0052] Yi, mountain-Yishan=Α4 (6) [0053] Deriving both sides of equation (6) at the same time: 5-Cattle [0055] When the converter station 1 fails, the power support capacity of the converter station 1 is insufficient, so the power control reference value of the converter station 2 should be decreased synchronously with the injected power of the converter station 1 to reduce the commutation The power of station 2 can ensure that the DC side voltage will not lose stability due to unbalanced power. After the voltage is restored to stability, the rate of change of the DC side voltage approaches zero, and the power control command value of converter station 2 just matches this When the injection power of the AC side of converter station 1 is equal. According to the above analysis, when the AC side failure occurs at the power injection end, the power control command value of the converter station 2 can be designed as: [0056] %; to, -3x (wide. X mouth small 5 (8) [0057] where δ is the voltage stability control coefficient, to ensure that in the case of a fault, during the power adjustment process, the control power command value of the converter station 2 side is less than the power support capacity of the converter station 1 side, so that the voltage can be stabilized at the set command Value. [0058] FIG. 4 is a block diagram of a typical flexible DC transmission active power control system, and FIG. 5 is a block diagram of the active power control system proposed by the present invention after adding an additional link for power adjustment. First, a flexible DC transmission fault identification link is added. When a fault occurs on the AC side of the system, the system enters the power control target value processing link, and the power control target value Pref in the stable operation state is modified to the power control target value P'ref in the fault state. The active power outer loop control link and the current inner loop control link in the figure can be constructed by referring to the existing typical control system. [0059] Compared with the existing control method for improving the DC voltage stability of MMC operation, the present invention does not modify the existing outer loop power control and inner loop current control in principle. Before the control link, a gain link that is adaptively adjusted according to the current operating conditions of the converter station is added. This change can significantly reduce the power imbalance on the AC and DC sides of the converter station, thereby reducing the existing outer loop power control and inner loop The power regulation pressure of current control indirectly improves the control effect of the existing control strategy, and can well improve the stability of the DC voltage. [0060] The above are only specific embodiments of the present invention, but the protection scope of the present invention is not limited thereto. Any person skilled in the art can easily think of changes or changes within the technical scope disclosed by the present invention. All replacements shall be covered by the protection scope of the present invention. Therefore, the protection scope of the present invention shall be subject to the protection scope of the claims.
[EN US10944321B2]: Multi-level switching power converter, and controller circuit and control method thereof [ZH CN111211667B]: 多阶切换式电源转换电路、其控制电路与控制方法 | [EN US10944321B2]: A multi-level switching power converter includes a multi-level power stage circuit which converts an input power to an output power. The power stage circuit includes an inductor, a conversion capacitor and plural power switches. The controller circuit controls the multi-level power stage circuit and includes: a feedback pulse generator circuit which generates a trigger pulse; a first timer circuit and a second timer circuit which determine a first time period and a second time period respectively according to the trigger pulse; and an adjusting circuit which adjusts the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage. [ZH CN111211667B]: 一种多阶切换式电源转换电路、其控制电路与控制方法。该多阶切换式电源转换电路包括：多阶功率级电路以及控制电路，多阶功率级电路用以转换输入电源而产生输出电源，其包括转换电容器、电感器及多个功率开关；控制电路用以控制多阶功率级电路；控制电路包括：反馈脉冲产生电路用以产生触发脉冲；计时电路以及另一计时电路，分别根据触发脉冲决定第一时段及第二时段，以控制多阶功率级电路；以及调整电路，用以根据转换电容器的跨压与参考电压的差值而调整第一时段，使得转换电容器的跨压的平均值大致上等于参考电压的位准。 | US2020161959A1 | 2021-03-09 2020-05-21 | US201916653940A | 2019-10-15 2019-10-15 | CN201811381770A, 2018-11-20 CN201811381770A, 2018-11-20 | US10944321B2: 2021-03-09 CN111211667B: 2021-01-26 | RICHTEK TECHNOLOGY CORP 立锜科技股份有限公司 | CHUANG YUNG-CHUN HUANG TSUNG-WEI ZHUANG YONGJUN HUANG ZONGWEI | H02M3/158: I H02M3/07: I H02M1/08: I H02M1/00: I H02M1/088: I | H02M1/00: I H02M1/0003: A H02M3/07: I H02M3/158: I H02M1/0095: A | US2004095081A1 US2004095108A1 US2004095112A1 US2004095116A1 US2004095164A1 US2004095264A1 US2020161967A1 CN104052278A CN105939106A CN107112892A US9929653B1 CN208158430U | US10811962B2 US10811962 10811962 US11101734B2 US11101734 11101734 | [EN US10944321B2]: 1. A multi-level switching power converter, comprising: a multi-level power stage circuit, configured to operably convert an input power to an output power by multi-level power conversion; anda controller circuit, configured to operably control the multi-level power stage circuit;wherein the multi-level power stage circuit includes: an inductor, coupled between a switching node and a first node;a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; andplural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level;wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power;wherein the controller circuit includes: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power;a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse;plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; andan adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or(2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 2. The multi-level switching power converter of claim 1, wherein the controller circuit further includes another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. 3. The multi-level switching power converter of claim 1, wherein the timer circuit includes: a current source, configured to operably provide a predetermined current;a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current;a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; anda timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage;wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. 4. The multi-level switching power converter of claim 3, wherein the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period;(2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or(3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. 5. The multi-level switching power converter of claim 4, wherein the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or(2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage;wherein the adjusting output signal corresponds to the first adjusting signal. 6. The multi-level switching power converter of claim 1, wherein the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power stage circuit operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node;(2) a second state: the inductor being electrically connected between the ground level and the first node;(3) a third state: the inductor and the conversion capacitor being electrically connected in series between the ground level and the first node, wherein the terminal of the conversion capacitor is electrically connected to the ground level, and the other terminal of the conversion capacitor is electrically connected to the switching node; or(4) a fourth state: the inductor being electrically connected between the second node and the first node;wherein the first pulse modulation signal controls the power stage circuit to operate in the first state in the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the third state in the second time period; orthe first pulse modulation signal controls the power stage circuit to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the second state outside the second time period. 7. The multi-level switching power converter of claim 1, wherein: when the first node is coupled to the output power and the second node is coupled to the input power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an input voltage of the input power; orwhen the first node is coupled to the input power and the second node is coupled to the output power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power. 8. The multi-level switching power converter of claim 1, wherein the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; anda modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. 9. A controller circuit for use in controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, the multi-level power converter including: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power; the controller circuit comprising: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power;a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse;plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; andan adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or(2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 10. The controller circuit of claim 9, further comprising another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. 11. The controller circuit of claim 9, wherein the timer circuit includes: a current source, configured to operably provide a predetermined current;a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current;a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; anda timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage;wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. 12. The controller circuit of claim 11, wherein the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period;(2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or(3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. 13. The controller circuit of claim 12, wherein the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or(2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage;wherein the adjusting output signal corresponds to the first adjusting signal. 14. The controller circuit of claim 9, wherein the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power converter operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node;(2) a second state: the inductor being electrically connected between the ground level and the first node;(3) a third state: the inductor and the conversion capacitor being electrically connected in series between the ground level and the first node, wherein the terminal of the conversion capacitor is electrically connected to the ground level, and the other terminal of the conversion capacitor is electrically connected to the switching node; or(4) a fourth state: the inductor being electrically connected between the second node and the first node;wherein the first pulse modulation signal controls the power converter to operate in the first state in the first time period, and the second pulse modulation signal controls the power converter to operate in the third state in the second time period; orthe first pulse modulation signal controls the power converter to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power converter to operate in the second state outside the second time period. 15. The controller circuit of claim 9, wherein: when the first node is coupled to the output power and the second node is coupled to the input power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an input voltage of the input power; orwhen the first node is coupled to the input power and the second node is coupled to the output power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power. 16. The controller circuit of claim 9, wherein the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; anda modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. 17. A control method for controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, wherein the multi-level power converter includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power; the control method comprising: generating a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power;generating at least a first phase pulse and a second phase pulse according to the trigger pulse;determining a first time period and generating a first pulse modulation signal according to the first phase pulse and the first time period;determining a second time period and generating a second pulse modulation signal according to the second phase pulse and the second time period; andperforming one of the followings: adjusting the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; oradjusting the first time period according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. 18. The control method of claim 17, further comprising one of the followings: (1) adjusting the second time period according to the difference between the voltage across the conversion capacitor and the reference voltage such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or(2) adjusting the second time period according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage;wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. [ZH CN111211667B]: 1 .一种多阶切换式电源转换电路，包含： 一多阶功率级电路，用以通过多阶切换式电源转换的方式，转换一输入电源而产生一 输出电源；以及 一控制电路，用以控制该多阶功率级电路； 其中该多阶功率级电路包括： 一电感器，耦接于一切换节点与一第一节点之间； 一转换电容器，用以通过电容性分压方式产生至少一比例电位；以及 多个功率开关，耦接于该电感器与该转换电容器，该多个功率开关控制该电感器与该 转换电容器的耦接关系，使得该切换节点切换于该至少一比例电位、一第二节点与一第三 节点之间，以实现多阶切换式电源转换，其中该转换电容器的跨压决定该至少一比例电位； 其中该第一节点、该第二节点与该第三节点配置为以下之一： ⑴该第一节点耦接于该输出电源，该第二节点耦接于该输入电源，且该第三节点耦接 于一接地电位，以将该多阶功率级电路配置为一降压型； ⑵该第一节点耦接于该输入电源，该第二节点耦接于该输出电源，且该第三节点耦接 于该接地电位，以将该多阶功率级电路配置为一升压型;或者 ⑶该第一节点耦接于该接地电位，该第二节点耦接于该输入电源，且该第三节点耦接 于该输出电源，以将该多阶功率级电路配置为一反相升降压型； 其中该控制电路包括： 一反馈脉冲产生电路，用以根据一输出相关信号以及一参考信号而产生一触发脉冲， 其中该输出相关信号相关于该输出电源； 一分相电路，用以根据该触发脉冲而产生至少一第一相位脉冲以及一第二相位脉冲； 多个计时电路，耦接于该分相电路，其中该多个计时电路的一计时电路，用以决定一第 一时段，且用以根据该第一相位脉冲及该第一时段而产生一第一脉冲调制信号，该多个计 时电路的另一计时电路，用以决定一第二时段，且用以根据该第二相位脉冲及该第二时段 而产生一第二脉冲调制信号，其中该第一脉冲调制信号及该第二脉冲调制信号用以控制该 多个功率开关，以实现多阶切换式电源转换；以及 一调整电路，用以进行以下操作之一：（1）根据该转换电容器的跨压与一参考电压的差 值而产生第一调整信号，以控制该计时电路而调整该第一时段，使得该转换电容器的跨压 的平均值大致上等于该参考电压的位准;或者⑵根据该切换节点的电压与该参考电压的 差值以及一占空比相关信号而产生第一调整信号，以控制该计时电路而调整该第一时段， 使得该比例电位大致上等于该参考电压的位准;其中该占空比相关信号相关于该多个功率 开关的占空比； 其中，该多个计时电路的该计时电路包括： 一电流源，用以提供一预设的电流； 一计时电容电路，根据一计时电流而产生一积分信号，其中该计时电流相关于该预设 的电流； 一计时比较电路，用以根据该积分信号及一阈值电压而产生一计时比较信号；以及 一计时逻辑电路，用以根据一计时输入信号以及该计时比较信号而产生一计时输出信 号，其具有一预设时段，其中该计时电路根据该计时电流、该计时电容电路的电容值，以及 该阈值电压的位准而决定该预设时段； 其中，该计时电路的该计时输入信号对应于该第一相位脉冲，该计时电路的该计时输 出信号对应于该第一脉冲调制信号，该预设时段对应于该第一时段。 2 .如权利要求1所述的多阶切换式电源转换电路，其中，该控制电路还包括另一调整电 路，用以进行以下操作之一：（1）根据该转换电容器的跨压与该参考电压的差值而产生第二 调整信号，以控制该另一计时电路而调整该第二时段，使得该转换电容器的跨压的平均值 大致上等于该参考电压的位准;或者⑵根据该切换节点的电压与该参考电压的差值以及 该占空比相关信号而产生该第二调整信号，以控制该另一计时电路而调整该第二时段，使 得该比例电位大致上等于该参考电压的位准;其中该第二调整信号调整该第二时段的方向 与该第一调整信号调整该第一时段的方向为互补。 3 .如权利要求1所述的多阶切换式电源转换电路，其中，该计时电路根据该第一调整信 号而通过以下方式至少之一而调整该第一时段： （1）该第一调整信号调整该计时电流以调整该第一时段； ⑵该第一调整信号调整该阈值电压以调整该第一时段;或者 （3）该第一调整信号模拟或数字切换方式调整该计时电容电路的电容值，以调整该第 一时段。 4 .如权利要求3所述的多阶切换式电源转换电路，其中，该调整电路包括以下至少之 一 ⑴一转导电路，用以进行以下操作之一：（1a）根据该转换电容器的跨压与该参考电压 的差值而产生一调整输出信号;或者（1b）根据该切换节点的电压与该参考电压的差值以及 该占空比相关信号而产生该调整输出信号，其中该调整输出信号为电流形式，其分流耦接 于该电流源与该计时电容电路，用以调整该计时电流;或者 ⑵一电压增益电路，用以进行以下操作之一：（2a）根据该转换电容器的跨压与该参考 电压的差值而产生该调整输出信号;或者（2b）根据该切换节点的电压与该参考电压的差值 以及该占空比相关信号而产生该调整输出信号，其中该调整输出信号为电压形式，用以调 整该阈值电压； 其中该调整输出信号对应于该第一调整信号。 5 .如权利要求1或2中的任一项所述的多阶切换式电源转换电路，其中： 该第一脉冲调制信号及该第二脉冲调制信号控制该多个功率开关，使该功率级电路操 作于以下状态之一： ⑴第一状态:使该电感器与该转换电容器电性串联于该第二节点与该第一节点之间， 该转换电容器的一端电连接于该切换节点，该转换电容器的另一端电连接于该第二节点； ⑵第二状态:使该电感器电连接于该第三节点与该第一节点之间； ⑶第三状态:使该电感器与该转换电容器电性串联于该第三节点与该第一节点之间， 该转换电容器的该端电连接于该第三节点，该转换电容器的另一端电连接于该切换节点； 或者 ⑷第四状态:使该电感器电连接于该第二节点与该第一节点之间； 其中该第一脉冲调制信号控制该功率级电路于该第一时段内操作于该第一状态，且该 第二脉冲调制信号控制该功率级电路于该第二时段内操作于该第三状态;或者，该第一脉 冲调制信号控制该功率级电路于该第一时段之外操作于该第四状态，且该第二脉冲调制信 号控制该功率级电路于该第二时段之外操作于该第二状态。 6 .如权利要求1所述的多阶切换式电源转换电路，其中： 当该多阶功率级电路配置为该降压型时，该切换节点切换于该输入电源及该比例电位 之间、或该切换节点切换于该接地电位及该比例电位之间，其中该参考电压的位准为该输 入电源的一输入电压的1/2； 当该多阶功率级电路配置为该升压型时，该切换节点切换于该输出电源及该比例电位 之间、或该切换节点切换于该接地电位及该比例电位之间，其中该参考电压的位准为该输 出电源的一输出电压的1/2；或者 当该多阶功率级电路配置为该反相升降压型时，该切换节点切换于该输出电源及该比 例电位之间、或该切换节点切换于该输入电源及该比例电位之间，其中该参考电压的位准 为该输入电压与该输出电压的差值的1/2。 7 .如权利要求1所述的多阶切换式电源转换电路，其中，该反馈脉冲产生电路包括： 一误差放大电路，用以根据该输出相关信号以及该参考信号的差值而产生一误差放大 信号；以及 一调制比较电路，用以比较该误差放大信号与一斜坡信号而产生该触发脉冲。 8 .一种控制电路，用以控制一多阶切换式电源转换电路，该多阶切换式电源转换电路 包括一多阶功率级电路，用以通过多阶切换式电源转换的方式，转换一输入电源而产生一 输出电源;其中该多阶功率级电路包括:一电感器，耦接于一切换节点与一第一节点之间； 一转换电容器，用以通过电容性分压方式产生至少一比例电位；以及多个功率开关，耦接于 该电感器与该转换电容器，该多个功率开关控制该电感器与该转换电容器的耦接关系，使 得该切换节点切换于该至少一比例电位、一第二节点与一第三节点之间，以实现多阶切换 式电源转换，其中该转换电容器的跨压决定该至少一比例电位;其中该第一节点、该第二节 点与该第三节点配置为以下之一：（1）该第一节点耦接于该输出电源，该第二节点耦接于该 输入电源，且该第三节点耦接于一接地电位，以将该多阶功率级电路配置为一降压型；（2） 该第一节点耦接于该输入电源，该第二节点耦接于该输出电源，且该第三节点耦接于该接 地电位，以将该多阶功率级电路配置为一升压型；或者⑶该第一节点耦接于该接地电位， 该第二节点耦接于该输入电源，且该第三节点耦接于该输出电源，以将该多阶功率级电路 配置为一反相升降压型；该控制电路包含： 一反馈脉冲产生电路，用以根据一输出相关信号以及一参考信号而产生一触发脉冲， 其中该输出相关信号相关于该输出电源； 一分相电路，用以根据该触发脉冲而产生至少一第一相位脉冲以及一第二相位脉冲； 多个计时电路，耦接于该分相电路，其中该多个计时电路的一计时电路，用以决定一第 一时段，且用以根据该第一相位脉冲及该第一时段而产生一第一脉冲调制信号，该多个计 时电路的另一计时电路，用以决定一第二时段，且用以根据该第二相位脉冲及该第二时段 而产生一第二脉冲调制信号，其中该第一脉冲调制信号及该第二脉冲调制信号用以控制该 多个功率开关，以实现多阶切换式电源转换；以及 一调整电路，用以进行以下操作之一：（1）根据该转换电容器的跨压与一参考电压的差 值而产生第一调整信号，以控制该计时电路而调整该第一时段，使得该转换电容器的跨压 的平均值大致上等于该参考电压的位准;或者⑵根据该切换节点的电压与该参考电压的 差值以及一占空比相关信号而产生第一调整信号，以控制该计时电路而调整该第一时段， 使得该比例电位大致上等于该参考电压的位准;其中 该占空比相关信号相关于该多个功率开关的占空比； 其中，该多个计时电路的该计时电路包括： 一电流源，用以提供一预设的电流； 一计时电容电路，根据一计时电流而产生一积分信号，其中该计时电流相关于该预设 的电流； 一计时比较电路，用以根据该积分信号及一阈值电压而产生一计时比较信号；以及 一计时逻辑电路，用以根据一计时输入信号以及该计时比较信号而产生一计时输出信 号，其具有一预设时段，其中该计时电路根据该计时电流、该计时电容电路的电容值，以及 该阈值电压的位准而决定该预设时段； 其中，该计时电路的该计时输入信号对应于该第一相位脉冲，该计时电路的该计时输 出信号对应于该第一脉冲调制信号，该预设时段对应于该第一时段。 9 .如权利要求8所述的控制电路，还包含另一调整电路，用以进行以下操作之一：（1）根 据该转换电容器的跨压与该参考电压的差值而产生第二调整信号，以控制该另一计时电路 而调整该第二时段，使得该转换电容器的跨压的平均值大致上等于该参考电压的位准;或 者⑵根据该切换节点的电压与该参考电压的差值以及该占空比相关信号而产生该第二调 整信号，以控制该另一计时电路而调整该第二时段，使得该比例电位大致上等于该参考电 压的位准;其中该第二调整信号调整该第二时段的方向与该第一调整信号调整该第一时段 的方向为互补。 10 .如权利要求8所述的控制电路，其中，该计时电路根据该第一调整信号而通过以下 方式至少之一而调整该第一时段： （1）该第一调整信号调整该计时电流以调整该第一时段； ⑵该第一调整信号调整该阈值电压以调整该第一时段;或者 （3）该第一调整信号模拟或数字切换方式调整该计时电容电路的电容值，以调整该第 一时段。 11 .如权利要求10所述的控制电路，其中，该调整电路包括以下至少之一： ⑴一转导电路，用以进行以下操作之一：（1a）根据该转换电容器的跨压与该参考电压 的差值而产生一调整输出信号;或者（1b）根据该切换节点的电压与该参考电压的差值以及 该占空比相关信号而产生该调整输出信号，其中该调整输出信号为电流形式，其分流耦接 于该电流源与该计时电容电路，用以调整该计时电流;或者 ⑵一电压增益电路，用以进行以下操作之一：（2a）根据该转换电容器的跨压与该参考 电压的差值而产生该调整输出信号;或者（2b）根据该切换节点的电压与该参考电压的差值 以及该占空比相关信号而产生该调整输出信号，其中该调整输出信号为电压形式，用以调 整该阈值电压； 其中该调整输出信号对应于该第一调整信号。 12 .如权利要求8或9中的任一项所述的控制电路，其中： 该第一脉冲调制信号及该第二脉冲调制信号控制该多个功率开关，使该功率级电路操 作于以下状态之一： ⑴第一状态:使该电感器与该转换电容器电性串联于该第二节点与该第一节点之间， 该转换电容器的一端电连接于该切换节点，该转换电容器的另一端电连接于该第二节点； ⑵第二状态:使该电感器电连接于该第三节点与该第一节点之间； ⑶第三状态:使该电感器与该转换电容器电性串联于该第三节点与该第一节点之间， 该转换电容器的该端电连接于该第三节点，该转换电容器的另一端电连接于该切换节点； 或者 ⑷第四状态:使该电感器电连接于该第二节点与该第一节点之间； 其中该第一脉冲调制信号控制该功率级电路于该第一时段内操作于该第一状态，且该 第二脉冲调制信号控制该功率级电路于该第二时段内操作于该第三状态;或者，该第一脉 冲调制信号控制该功率级电路于该第一时段之外操作于该第四状态，且该第二脉冲调制信 号控制该功率级电路于该第二时段之外操作于该第二状态。 13 .如权利要求8所述的控制电路，其中： 当该多阶功率级电路配置为该降压型时，该切换节点切换于该输入电源及该比例电位 之间、或该切换节点切换于该接地电位及该比例电位之间，其中该参考电压的位准为该输 入电源的一输入电压的1/2； 当该多阶功率级电路配置为该升压型时，该切换节点切换于该输出电源及该比例电位 之间、或该切换节点切换于该接地电位及该比例电位之间，其中该参考电压的位准为该输 出电源的一输出电压的1/2；或者 当该多阶功率级电路配置为该反相升降压型时，该切换节点切换于该输出电源及该比 例电位之间、或该切换节点切换于该输入电源及该比例电位之间，其中该参考电压的位准 为该输入电压与该输出电压的差值的1/2。 14 .如权利要求8所述的控制电路，其中，该反馈脉冲产生电路包括： 一误差放大电路，用以根据该输出相关信号以及该参考信号的差值而产生一误差放大 信号；以及 一调制比较电路，用以比较该误差放大信号与一斜坡信号而产生该触发脉冲。 15 .一种控制方法，用以控制一多阶切换式电源转换电路，该多阶切换式电源转换电路 包括一多阶功率级电路，用以通过多阶切换式电源转换的方式，转换一输入电源而产生一 输出电源;其中该多阶功率级电路包括:一电感器，耦接于一切换节点与一第一节点之间； 一转换电容器，用以通过电容性分压方式产生至少一比例电位；以及多个功率开关，耦接于 该电感器与该转换电容器，该多个功率开关控制该电感器与该转换电容器的耦接关系，使 得该切换节点切换于该至少一比例电位、一第二节点与一第三节点之间，以实现多阶切换 式电源转换，其中该转换电容器的跨压决定该至少一比例电位;其中该第一节点、该第二节 点与该第三节点配置为以下之一：（1）该第一节点耦接于该输出电源，该第二节点耦接于该 输入电源，且该第三节点耦接于一接地电位，以将该多阶功率级电路配置为一降压型；（2） 该第一节点耦接于该输入电源，该第二节点耦接于该输出电源，且该第三节点耦接于该接 地电位，以将该多阶功率级电路配置为一升压型；或者⑶该第一节点耦接于该接地电位， 该第二节点耦接于该输入电源，且该第三节点耦接于该输出电源，以将该多阶功率级电路 配置为一反相升降压型；该控制方法包含： 根据一输出相关信号以及一参考信号而产生一触发脉冲，其中该输出相关信号相关于 该输出电源； 根据该触发脉冲而产生至少一第一相位脉冲以及一第二相位脉冲； 决定一第一时段，且根据该第一相位脉冲及该第一时段而产生一第一脉冲调制信号； 决定一第二时段，且根据该第二相位脉冲及该第二时段而产生一第二脉冲调制信号， 其中该第一脉冲调制信号及该第二脉冲调制信号用以控制该多个功率开关，以实现多阶切 换式电源转换；以及 根据该转换电容器的跨压与一参考电压的差值以调整该第一时段，使得该转换电容器 的跨压的平均值大致上等于该参考电压的位准;或者，根据该切换节点的电压与该参考电 压的差值以及一占空比相关信号调整该第一时段，使得该比例电位大致上等于该参考电压 的位准;其中该占空比相关信号相关于该多个功率开关的占空比； 其中，产生该第一脉冲调制信号的步骤包括： 将一计时信号积分而产生一积分信号； 比较该积分信号及一阈值而产生一计时比较信号；以及 根据一计时输入信号以及该计时比较信号而产生一计时输出信号，其具有一预设时 段，其中该预设时段根据该计时信号以及该阈值的位准而决定； 其中，该计时输入信号对应于该第一相位脉冲，该计时输出信号对应于该第一脉冲调 制信号，该预设时段对应于该第一时段。 16 .如权利要求15所述的控制方法，还包含:根据该转换电容器的跨压与该参考电压的 差值而调整该第二时段，使得该转换电容器的跨压的平均值大致上等于该参考电压的位 准;或者，根据该切换节点的电压与该参考电压的差值以及该占空比相关信号而调整该第 二时段，使得该比例电位大致上等于该参考电压的位准;其中调整该第二时段的方向与调 整该第一时段的方向为互补。 | [EN US10944321B2]: CROSS REFERENCE The present invention claims priority to CN 201811381770.X, filed on Nov. 20, 2018. BACKGROUND OF THE INVENTION Field of Invention The present invention relates to a multi-level switching power converter. Particularly it relates to a multi-level switching power converter which can perform self-balance and self-calibration. The present invention also relates to a controller circuit and a control method for use in the multi-level switching power converter. Description of Related Art Relevant prior art documents are “A 50 MHz 5V 3W 90% Efficiency 3-Level Buck Converter with Real-Time Calibration, Xun Liu et. al, 2016 Symposium on VLSI Circuits Digest of Technical Papers”, “Analysis and Design Considerations of Integrated 3-Level Buck Converters, Xun Liu et. al, IEEE TRANSACTIONS ON CIRCUITS AND SYSTEMS Vol. 63, No. 5, May 2016”, “A 2 MHz 12-100 V 90% Efficiency Self-Balancing ZVS Reconfigurable Three-Level DC-DC Regulator With Constant-Frequency Adaptive-On-Time V2 Control and Nanosecond-Scale ZVS Turn-On Delay” and “Constant ON-Time 3-Level Buck Converter for Low Power Applications, Brian M. Cassidy et. al, IEEE, 2015”, which propose different approaches from the present invention. FIG. 1 shows a prior art 3-level switching power converter (3-level switching power converter 1) which employs the power switches (N1-N4), the conversion capacitor CF and the inductor L to convert the input power VIN to the output power VOUT by 3-level power conversion. More specifically, the switching node LX is switched among 3 levels of voltages (i.e. the input voltage VVI, the ground level and a proportion voltage level such as VVI/2) to achieve the 3-level power conversion. The prior art circuit in FIG. 1 has a drawback that the proportion voltage level may shift due to non-ideality or mismatch among circuits to cause extra power loss or un-stability of the switching frequency. FIG. 2 shows operating waveforms of the prior art multi-level switching power converter corresponding to FIG. 1. Ideally, the high level of the voltage of the switching node VLX is supposed to be equal to ½ of the input voltage, i.e. VVI/2, and the average of the voltage VCF across the conversion capacitor CF is also supposed to be equal to VVI/2. However, due to the aforementioned non-ideality, as shown in FIG. 2, the actual high level of the voltage of the switching node VLX is higher than VVI/2 during D1 period, and is lower than VVI/2 during D3 period. On the other hand, the average of the voltage VCF across the conversion capacitor CF is also shifted from the expected VVI/2, to be lower than VVI/2 as shown in FIG. 2. As described earlier, this issue causes extra power loss or un-stability of the switching frequency. Compared to the prior art in FIG. 1, the present invention is advantageous in that a self-calibration can be performed to keep the level of the voltage of the switching node VLX and the average of the voltage VCF across the conversion capacitor CF at expected levels, whereby the power loss can be reduced and the switching frequency can be kept stable. SUMMARY OF THE INVENTION From one perspective, the present invention provides a multi-level switching power converter, comprising: a multi-level power stage circuit, configured to operably convert an input power to an output power by multi-level power conversion; and a controller circuit, configured to operably control the multi-level power stage circuit; wherein the multi-level power stage circuit includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power; wherein the controller circuit includes: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. In one embodiment, the controller circuit further includes another adjusting circuit, configured to operate as one of the followings: (1) the another adjusting circuit generating a second adjusting signal according to the difference between the voltage across the conversion capacitor and the reference voltage to control the second timer circuit to adjust the second time period such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or (2) the another adjusting circuit generating the second adjusting signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, to control the second timer circuit to adjust the second time period such that the proportion voltage level is substantially equal to the level of the reference voltage; wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. In one embodiment, the timer circuit includes: a current source, configured to operably provide a predetermined current; a timer capacitor circuit, configured to operably generate an integration signal according to a timer current, wherein the timer current relates to the predetermined current; a timer comparison circuit, configured to operably generate a timer comparison signal according to the integration signal and a threshold voltage; and a timer logic circuit, configured to operably generate a timer output signal according to a timer input signal and the integration signal, wherein the timer output signal has a predetermined time period, and a time length of the predetermined time period is determined by the timer circuit according to the timer current, a capacitance of the timer capacitor circuit, and a level of the threshold voltage; wherein the timer input signal of the timer circuit corresponds to the first phase pulse, and the timer output signal corresponds to the first pulse modulation signal, and the predetermined time period corresponds to the first time period. In one embodiment, the timer circuit adjusts the first time period according to the first adjusting signal by at least one of the following ways: (1) the first adjusting signal adjusting the timer current to adjust the first time period; (2) the first adjusting signal adjusting the threshold voltage to adjust the first time period; or (3) the first adjusting signal adjusting the capacitance of the timer capacitor circuit in an analog or digital manner to adjust the first time period. In one embodiment, the adjusting circuit includes at least one of the followings: (1) a transconductor circuit, configured to operate as one of the followings: (1a) generating an adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (1b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in current form and provides a current branch shunted to the current source and the timer capacitor circuit to adjust the timer current; or (2) a voltage gain circuit, configured to operate as one of the followings: (2a) generating the adjusting output signal according to the difference between the voltage across the conversion capacitor and the reference voltage; or (2b) generating the adjusting output signal according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, wherein the adjusting output signal is in voltage form and is configured to adjust the threshold voltage; wherein the adjusting output signal corresponds to the first adjusting signal. In one embodiment, the first pulse modulation signal and the second pulse modulation signal control the plural power switches such that the power stage circuit operates in one of the following states: (1) a first state: the inductor and the conversion capacitor being electrically connected in series between the second node and the first node, wherein one terminal of the conversion capacitor is electrically connected to the switching node, and the other terminal of the conversion capacitor is electrically connected to the second node; (2) a second state: the inductor being electrically connected between the ground level and the first node; (3) a third state: the inductor and the conversion capacitor being electrically connected in series between the ground level and the first node, wherein the terminal of the conversion capacitor is electrically connected to the ground level, and the other terminal of the conversion capacitor is electrically connected to the switching node; or (4) a fourth state: the inductor being electrically connected between the second node and the first node; wherein the first pulse modulation signal controls the power stage circuit to operate in the first state in the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the third state in the second time period; or the first pulse modulation signal controls the power stage circuit to operate in the fourth state outside the first time period, and the second pulse modulation signal controls the power stage circuit to operate in the second state outside the second time period. In one embodiment, when the first node is coupled to the output power and the second node is coupled to the input power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein a level of the reference voltage is ½ of an input voltage of the input power; or when the first node is coupled to the input power and the second node is coupled to the output power, the switching node is switched between the output power and the proportion voltage level, or the switching node is switched between the ground level and the proportion voltage level, wherein the level of the reference voltage is ½ of an output voltage of the output power. In one embodiment, the feedback pulse generator circuit includes: an error amplifier circuit, configured to operably generate an error amplified signal according to the difference between the output related signal and the reference signal; and a modulation comparison circuit, configured to operably compare the error amplified signal and a ramp signal to generate the trigger pulse. From another perspective, the present invention provides a controller circuit for use in controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, the multi-level power converter including: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power; the controller circuit comprising: a feedback pulse generator circuit, configured to operably generate a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; a phase splitting circuit, configured to operably generate at least a first phase pulse and a second phase pulse according to the trigger pulse; plural timer circuits, coupled to the phase splitting circuit, wherein a first one of the plural timer circuits is configured to operably determine a first time period and generate a first pulse modulation signal according to the first phase pulse and the first time period, and a second one of the plural timer circuits is configured to operably determine a second time period and generate a second pulse modulation signal according to the second phase pulse and the second time period; and an adjusting circuit, configured to operate as one of the followings: (1) the adjusting circuit generating a first adjusting signal according to a difference between the voltage across the conversion capacitor and a reference voltage to control the timer circuit to adjust the first time period such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or (2) the adjusting circuit generating the first adjusting signal according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, to control the timer circuit to adjust the first time period such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. From another perspective, the present invention provides a control method for controlling a multi-level switching power converter to convert an input power to an output power by multi-level power conversion, wherein the multi-level power converter includes: an inductor, coupled between a switching node and a first node; a conversion capacitor, configured to operably generate at least one proportion voltage level by capacitive voltage division; and plural power switches, coupled to the inductor and the conversion capacitor, and configured to operably control the coupling arrangement of the inductor and the conversion capacitor, such that the switching node is switched among the at least one proportion voltage level, a ground level, and a second node, so that the multi-level power conversion is achieved, wherein a voltage across the conversion capacitor determines the at least one proportion voltage level; wherein the first node is coupled to the output power and the second node is coupled to the input power, or, the first node is coupled to the input power and the second node is coupled to the output power; the control method comprising: generating a trigger pulse according to an output related signal and a reference signal, wherein the output related signal relates to the output power; generating at least a first phase pulse and a second phase pulse according to the trigger pulse; determining a first time period and generating a first pulse modulation signal according to the first phase pulse and the first time period; determining a second time period and generating a second pulse modulation signal according to the second phase pulse and the second time period; and performing one of the followings: adjusting the first time period according to a difference between the voltage across the conversion capacitor and a reference voltage such that an average of the voltage across the conversion capacitor is substantially equal to a level of the reference voltage; or adjusting the first time period according to a difference between a voltage on the switching node and a reference voltage, and a duty ratio related signal, such that the proportion voltage level is substantially equal to a level of the reference voltage, wherein the duty ratio related signal relates to a duty ratio of the plural power switches. In one embodiment, the control method further comprises one of the followings: (1) adjusting the second time period according to the difference between the voltage across the conversion capacitor and the reference voltage such that the average of the voltage across the conversion capacitor is substantially equal to the level of the reference voltage; or (2) adjusting the second time period according to the difference between the voltage on the switching node and the reference voltage, and the duty ratio related signal, such that the proportion voltage level is substantially equal to the level of the reference voltage; wherein a direction of adjusting the second time period by the second adjusting signal is complementary to a direction of adjusting the first time period by the first adjusting signal. The objectives, technical details, features, and effects of the present invention will be better understood with regard to the detailed description of the embodiments below. BRIEF DESCRIPTION OF THE DRAWINGS FIG. 1 shows a schematic diagram of a prior art multi-level switching power converter. FIG. 2 shows operating waveforms of a prior art multi-level switching power converter. FIGS. 3A-3C show schematic diagrams of various embodiments of the multi-level switching power converter according to the present invention. FIGS. 4A-4B show operating waveforms corresponding to the embodiment shown in FIG. 3A. FIG. 5 shows schematic diagrams of four coupling states corresponding to the embodiment shown in 3A. FIGS. 6A-6B show schematic diagrams of two specific embodiments of the multi-level switching power converter according to the present invention. FIGS. 6C-6E show schematic diagrams of other specific embodiments of the multi-level switching power converter according to the present invention. FIG. 7 shows a schematic diagram of a specific embodiment of the feedback pulse generator circuit of the multi-level switching power converter according to the present invention. FIG. 8 shows operating waveforms of the multi-level switching power converter according to the present invention. FIG. 9 shows operating waveforms of the multi-level switching power converter according to the present invention. FIG. 10A shows a schematic diagram of a specific embodiment of the timer circuit of the multi-level switching power converter according to the present invention. FIG. 10B shows a schematic diagram of a specific embodiment of the timer logic circuit of the multi-level switching power converter according to the present invention. FIGS. 11A-11C show schematic diagrams of several specific embodiments of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIGS. 11D-11F show schematic diagrams of several specific embodiments of the timer capacitor circuit of the multi-level switching power converter according to the present invention. FIG. 11G shows a schematic diagram of another specific embodiment of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIGS. 12A-12B show schematic diagrams of several specific embodiments of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. FIG. 12C shows a schematic diagram of another specific embodiment of the timer circuit and the adjusting circuit of the multi-level switching power converter according to the present invention. DESCRIPTION OF THE PREFERRED EMBODIMENTS The drawings as referred to throughout the description of the present invention are for illustration only, to show the interrelations between the circuits and the signal waveforms, but not drawn according to actual scale. FIGS. 3A-3B show schematic diagrams of two embodiments of the multi-level switching power converter (multi-level switching power converter 3A and 3B) according to the present invention. As shown in FIGS. 3A-3B, each of the multi-level switching power converter (multi-level switching power converter 3A and 3B) comprises a multi-level power stage circuit 200 and a controller circuit 100. The multi-level power stage circuit 200 is configured to operably convert an input power VIN to an output power VOUT by multi-level power conversion. The controller circuit 100 is configured to operably control the multi-level power stage circuit 200. Still referring to FIGS. 3A-3B, the multi-level power stage circuit 200 includes an inductor L, at least one conversion capacitor (e.g. CF) and plural power switches (e.g. N1-N4). The inductor L is coupled between a switching node LX and a first node ND1. The conversion capacitor CF is configured to operably generate at least one proportion voltage level by capacitive voltage division (“Capacitive voltage division” will be explained in detail later). The plural power switches (N1-N4) are coupled to the inductor L and the conversion capacitor CF, and are configured to operably control the coupling arrangement of the inductor L and the conversion capacitor CF, such that the switching node LX is switched among the at least one proportion voltage level, a ground level, and a second node ND2, to achieve the multi-level power conversion, wherein the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. In one embodiment, as shown in FIG. 3A, the first node ND1 is coupled to the output power VOUT and the second node ND2 is coupled to the input power VIN. In this case, the multi-level switching power converter 3A is configured to be a buck (step-down) multi-level switching power converter. In another embodiment, as shown in FIG. 3B, the first node ND1 is coupled to the input power VIN and the second node ND2 is coupled to the output power VOUT. In this case, the multi-level switching power converter 3B is configured to be a boost (step-up) multi-level switching power converter. Note that the input capacitor CIN and the output capacitor COUT are coupled to the input power VIN and the output power VOUT respectively. The term “multi-level” used in the terms “multi-level switching power converter” and “multi-level power stage circuit” indicates that the switching node LX is switched among multiple levels, such as the aforementioned at least one proportion voltage level, the ground level and the second switching node ND2, so as to convert the input power VIN to the output power VOUT, whereby the multi-level power conversion is achieved. More specifically, the multi-level switching power converters 3A and 3B shown in FIGS. 3A and 3B are 3-level switching power converters (corresponding to buck and boost types respectively). Hereinafter for simplicity, the multi-level switching power converter of the present invention will be illustrated and explained using a buck type power converter (more specifically a 3-level buck type switching power converter) as an example, unless noted. FIGS. 4A-4B show operating waveforms corresponding to the embodiment shown in FIG. 3A. As shown in FIG. 4A, in this embodiment, the input power has an input voltage VVI and the output power VOUT has an output voltage VVO. When the duty ratio of the input voltage to the output voltage (i.e. VVO/VVI) is less than 50%, the voltage VLX on the switching node LX is switched between the ground level and the target value of the proportion voltage level (VVI/2). As shown in FIG. 4B, in this embodiment, when the duty ratio of the input voltage to the output voltage (i.e. VVO/VVI) is larger than 50%, the voltage VLX on the switching node LX is switched between the input voltage VVI and the target value of the proportion voltage level (VVI/2). In this embodiment, the level of the proportion voltage level is ½ of the input voltage VVI, i.e. VVI/2. As shown in FIG. 3A, when the first node ND1 is coupled to the input power VIN and the second node ND2 is coupled to the output power VOUT, the switching node LX is switched between the output power VOUT and the proportion voltage level, or the switching node LX is switched between the ground level and the proportion voltage level. In this embodiment, the proportion voltage level is ½ of the output voltage VVO of the output power VOUT, i.e. VVO/2. FIG. 5 shows schematic diagrams of four coupling states corresponding to the embodiment shown in 3A. Referring to FIGS. 3A and 5, the aforementioned “capacitive voltage division” means that the conversion capacitor CF is controlled to be coupled between the second node ND2 and the switching node LX (e.g. the first state as shown in FIG. 5), or to be coupled between the switching node LX and the ground voltage level (e.g. the third state as shown in FIG. 5), in a time-shared manner, thereby generating the at least one proportion voltage level (e.g. VVI/2) by the “capacitive voltage division”. In other words, the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. In the embodiments shown in FIGS. 3A, 4A and 4B, the target level of the voltage VCF across the conversion capacitor CF is VVI/2. In these embodiments, the proportion voltage level also is VVI/2. From another perspective, the multi-level switching power conversion achieved by the “capacitive voltage division” is characterized in that: during some of the time periods, the plural power switches control the inductor L and the conversion capacitor CF to be electrically connected in series between the first node ND1 and the second node ND2 (e.g. the first state shown in FIG. 5), while during other time periods, the plural power switches control the inductor L and the conversion capacitor CF to be electrically connected in series between the first node ND1 and the ground level (e.g. the third state shown in FIG. 5), such that the switching node LX is switched among the at least one proportion voltage level (e.g. VVI/2), the ground level, and the second node ND2, so that the multi-level power conversion is achieved, wherein the voltage VCF across the conversion capacitor CF determines the at least one proportion voltage level. Note that, in a boost type multi-level switching power converter (e.g. FIG. 3B), the “capacitive voltage division” is scaling-up; more specifically, the proportion voltage level is pumped to the voltage on the second node ND2 (e.g. corresponding to VVO as shown in FIG. 3B). That is, in the context of the present invention, “capacitive voltage division” can be scaling down (e.g. VVI/2) or scaling up (e.g. VVO) the proportion voltage level. According to the present invention, the multi-level switching power conversion achieved by the “capacitive voltage division” is not limited to the 3-level switching power conversion as illustrated in FIGS. 3A, 4A and 4B. In other embodiments, the multi-level switching power conversion achieved by the “capacitive voltage division” can be expanded to include more than 3 levels. For example, as shown in FIG. 3C, in one embodiment, the switching node LX (coupled to a terminal of the inductor L) can be switched among the second node (e.g. corresponding to the input voltage VIN), the ground level, a first proportion voltage level (e.g. VVI*(⅔)) and a second proportion voltage level (e.g. VVI*(⅓)), thereby achieving 4-level switching power conversion. More specifically, the power stage circuit 200 can be configured to include plural conversion capacitors (e.g. CF1 and CF2) for achieving 4-level “capacitive voltage division”. The controller circuit 100 generates a pulse modulation signal DX (which can include plural corresponding pulse modulation signals) to control the switch circuit 210. The switch circuit 210 includes the aforementioned plural power switches which are configured to perform the aforementioned switching. In this embodiment, the voltage VCF1 across the conversion capacitor CF1 and the voltage VCF2 across the conversion capacitor CF2 determine the first proportion voltage level and the second proportion voltage level by the capacitive voltage division. In one specific embodiment, as shown in FIG. 3A, the plural power switches includes a first power switch N1, a second power switch N2, a third power switch N3, and the fourth power switch N4. One terminal of the fourth power switch N4 and one terminal of the third power switch N3 are coupled to a upper node CF+. Another terminal of the fourth power switch N4 is coupled to the second node ND2. Another terminal of the third power switch N3 is coupled to the switching node LX. One terminal of the second power switch N2 and one terminal of the first power switch N1 are coupled to a lower node CF−. Another terminal of the second power switch N2 is coupled to the switching node LX. Another terminal of the first power switch N1 is coupled to the ground level. In this embodiment, the conversion capacitor CF is couple between the upper node CF+ and the lower node CF−. The inductor L is coupled between the switching node LX and the first node ND1. In this embodiment, the fourth power switch N4 and the first power switch N1 are configured to switch complementarily (e.g. controlled by the complementary driving signals DO and DOb). The third power switch N3 and the second power switch N2 are configured to switch complementarily (e.g. controlled by the complementary driving signals DS and DSb). As described earlier, this embodiment can achieve 3-level switching power conversion. The conversion capacitor CF provides the capacitive voltage division function. The configuration of the power stage circuit 200 shown in FIG. 3B is similar to the embodiment shown in FIG. 3A, so its details are not redundantly explained for simplicity. FIG. 6A shows a schematic diagram of one specific embodiment of the multi-level switching power converter (multi-level switching power converter 6A) according to the present invention. In this embodiment, the controller circuit 100 includes a feedback pulse generator circuit 110, a phase splitting circuit 120, plural timer circuits (e.g. 130 and 140), and an adjusting circuit (ADJ CKT) 150. FIG. 8 shows operating waveforms of the multi-level switching power converter according to the present invention (e
[DE WO2018153433A1]: MODULARER MULTILEVELSTROMRICHTER [EN US11050357B2]: Modular multilevel power converter in which electronic components of the converter are arranged on different vehicles [FR WO2018153433A1]: CONVERTISSEUR DE PUISSANCE MODULAIRE À PLUSIEURS NIVEAUX | [DE WO2018153433A1]: Die Erfindung betrifft einen modularen Multilevelstromrichter (500) mit ersten elektrischen Bauelementen (508), die auf einem ersten Fahrzeug (501) angeordnet sind, und mit zweiten elektrischen Bauelementen (509), die auf einem zweiten Fahrzeug (502) angeordnet sind. Dabei sind das erste Fahrzeug (501) und das zweite Fahrzeug (502) beabstandet voneinander aufgestellt. Die ersten elektrischen Bauelemente (508) und die zweiten elektrischen Bauelemente (509) sind mittels mehrerer erster Verbindungsleiter (518) elektrisch miteinander verbunden. [EN US11050357B2]: A modular multilevel power converter includes first electric components on a first vehicle and second electric components on a second vehicle. The first vehicle and the second vehicle are placed at a spacing distance from each other. The first electric components and the second electric components are electrically interconnected by a plurality of first connecting conductors. [FR WO2018153433A1]: L'invention concerne un convertisseur de puissance modulaire à plusieurs niveaux (500) comportant des premiers composants électriques (508) qui sont agencés sur un premier véhicule (501), et des seconds composants électriques (509) qui sont agencés sur un second véhicule (502). Le premier véhicule (501) et le second véhicule (502) sont installés à distance l'un de l'autre. Les premiers composants électriques (508) et les seconds composants électriques (509) sont connectés électriquement les uns aux autres au moyen de plusieurs premiers conducteurs de connexion (518). | WO2018153433A1 | 2018-08-30 | EP2017053916W | 2017-02-21 | EP2017053916W, 2017-02-21 | WO2018153433A1: 2018-08-30 US11050357B2: 2021-06-29 | SIEMENS AG | MANGOLD THOMAS PIESCHEL MARTIN STÜRMER UWE TEPE TOBIAS STUERMER UWE | H02M7/00: I H02M7/483: I H05K7/10: I H02M7/515: I H02M7/483: N | H02M7/003: I H02M1/327: A H02M7/4835: A H02M7/5152: I | US2013009591A1 WO2010118772A1 US2007093280A1 US10700617B1 US2020235582A1 US2021044216A1 US2010091434A1 CN202772592U CN202840300U CN202978747U WO2008098530A1 | WO2020047677A1 WO2020047677 2020/047677 WO2020/047677A1 US11081972B2 US11081972 11081972 | [DE WO2018153433A1]: Patentansprüche1. Modularer Multilevelstromrichter (500)- mit ersten elektrischen Bauelementen (508), die auf einem ersten Fahrzeug (501), insbesondere auf einem ersten LKW- Anhänger (501), angeordnet sind, - mit zweiten elektrischen Bauelementen (509), die auf einem zweiten Fahrzeug (502), insbesondere auf einem zweiten LKW- Anhänger (502), angeordnet sind, - wobei das erste Fahrzeug (501) und das zweite Fahrzeug (502) beabstandet voneinander aufgestellt sind und - wobei die ersten elektrischen Bauelemente (508) und die zweiten elektrischen Bauelemente (509) mittels mehrerer erster Verbindungsleiter (518) elektrisch miteinanderverbunden sind. 2. Modularer Multilevelstromrichter nach Anspruch 1,d a d u r c h g e k e n n z e i c h n e t , dass- die ersten elektrischen Bauelemente (508) eine Reihenschaltung von Modulen (1_1, 1_2, 1_3,..., l_n) aufweisen, wobei die Module jeweils mindestens zwei elektronischeSchaltelemente (202, 206) und einen elektrischenEnergiespeicher (210) aufweisen und- die zweiten elektrischen Bauelemente (509) mindestens eine elektrische Spule (LI, L3, L5) aufweisen. 3. Modularer Multilevelstromrichter nach Anspruch 1 oder 2, d a d u r c h g e k e n n z e i c h n e t , dass- die ersten elektrischen Bauelemente (508) in einem ersten Container (602) angeordnet sind, der auf dem ersten Fahrzeug befestigt (501) ist und/oder - die zweiten elektrischen Bauelemente (509) in einem zweiten Container (604) angeordnet sind, der auf dem zweiten Fahrzeug (502) befestigt ist. 4. Modularer Multilevelstromrichter nach einem dervorhergehenden Ansprüche,d a d u r c h g e k e n n z e i c h n e t , dass - an einem ersten Ende des ersten Fahrzeugs (501) eine erste elektrische Schnittstelle (512) zum Anschluss der erstenVerbindungsleiter (518) angeordnet ist und/oder - an einem ersten Ende des zweiten Fahrzeugs (502) eine zweite elektrische Schnittstelle (514) zum Anschluss der ersten Verbindungsleiter (518) angeordnet ist. 5. Modularer Multilevelstromrichter nach einem dervorhergehenden Ansprüche,d a d u r c h g e k e n n z e i c h n e t , dass - die erste elektrische Schnittstelle (512) mehrere lösbare elektrische Kontaktpaare (704) aufweist, die jeweils einen ersten elektrischen Kontakt (908) und einen zweitenelektrischen Kontakt (910) aufweisen, wobei die erstenKontakte (908) elektrisch mit den ersten elektrischenBauelementen (508) verbunden sind und die zweiten Kontakte (910) elektrisch jeweils mit einem der ersten Verbindungsleiter (518) verbunden sind und/oder - die zweite elektrische Schnittstelle (514) mehrere lösbare elektrische Kontaktpaare (704) aufweist, die jeweils einen ersten elektrischen Kontakt (908) und einen zweitenelektrischen Kontakt (910) aufweisen, wobei die erstenKontakte (908) elektrisch mit den zweiten elektrischenBauelementen (509) verbunden sind und die zweiten Kontakte (910) elektrisch jeweils mit einem der erstenVerbindungsleiter (518) verbunden sind. 6. Modularer Multilevelstromrichter nach Anspruch 5, d a d u r c h g e k e n n z e i c h n e t , dass - die elektrischen Kontaktpaare (704) jeweils als einSteckverbinder (704) ausgestaltet sind. 7. Modularer Multilevelstromrichter nach Anspruch 5 oder 6, d a d u r c h g e k e n n z e i c h n e t , dass - die ersten Kontakte (908) der ersten elektrischenSchnittstelle (512) elektrisch mit den ersten elektrischen Bauelementen (508) verbunden sind mittels erster elektrischer Kabel (522), die zumindest abschnittsweise an der Unterseite des ersten Fahrzeugs (501) verlaufen und durch an derUnterseite des ersten Containers (602) angeordneteAusnehmungen (904) hindurch in einen Innenraum des ersten Containers (501) hineingeführt sind und/oder - die ersten Kontakte (908) der zweiten elektrischenSchnittstelle (514) elektrisch mit den zweiten elektrischen Bauelementen (509) verbunden sind mittels zweiterelektrischer Kabel (524), die zumindest abschnittsweise an der Unterseite des zweiten Fahrzeugs (502) verlaufen und durch an der Unterseite des zweiten Containers (604)angeordnete Ausnehmungen (904) hindurch in einen Innenraum des zweiten Containers (604) hineingeführt sind. 8. Modularer Multilevelstromrichter nach einem dervorhergehenden Ansprüche,d a d u r c h g e k e n n z e i c h n e t , dass - der modulare Multilevelstromrichter (500) einenTransformator (532) aufweist, der auf einem dritten Fahrzeug (503) , insbesondere auf einem dritten LKW-Anhänger (503) , angeordnet ist,- wobei das dritte Fahrzeug (503) und das zweite Fahrzeug (502) beabstandet voneinander aufgestellt sind und - wobei der Transformator (532) und die zweiten elektrischen Bauelemente (509) mittels mehrerer zweiter Verbindungsleiter (530) elektrisch miteinander verbunden sind. 9. Modularer Multilevelstromrichter nach Anspruch 8,d a d u r c h g e k e n n z e i c h n e t , dass - an einem zweiten Ende des zweiten Fahrzeugs (502) eine dritte elektrische Schnittstelle (528) zum Anschluss der zweiten Verbindungsleiter (530) angeordnet ist und - die zweiten Verbindungsleiter (530) mit der drittenelektrischen Schnittstelle (528) verbunden sind. 10. Modularer Multilevelstromrichter nach Anspruch 9, d a d u r c h g e k e n n z e i c h n e t , dass - die erste elektrische Schnittstelle (512), die zweite elektrische Schnittstelle (514) und die dritte elektrische Schnittstelle (528) gleichartig aufgebaut sind. 11. Modularer Multilevelstromrichter nach einem dervorhergehenden Ansprüche,d a d u r c h g e k e n n z e i c h n e t , dass - der modulare Multilevelstromrichter (500) eineKühleinrichtung (560) aufweist, die auf einem viertenFahrzeug (504), insbesondere auf einem vierten LKW-Anhänger (504), angeordnet ist,- wobei das vierte Fahrzeug (504) und das erste Fahrzeug (501) beabstandet voneinander aufgestellt sind und - wobei die Kühleinrichtung (560) und das erste Fahrzeug (501) mittels mindestens einer Kühlmittelleitung (558) miteinander verbunden sind. 12. Modularer Multilevelstromrichter nach einem der Ansprüche 2 bis 11,d a d u r c h g e k e n n z e i c h n e t , dass - die zwei elektronischen Schaltelemente (202,206) der Module in einer Halbbrückenschaltung angeordnet sind, und/oder- die Module jeweils die zwei elektronischen Schaltelemente (202, 206) und zwei weitere elektronische Schaltelemente (302, 306) aufweisen, wobei die zwei elektronischenSchaltelemente (202, 206) und die zwei weiterenelektronischen Schaltelemente (302, 306) in einerVollbrückenschaltung angeordnet sind. 13. Modularer Multilevelstromrichter nach einem dervorhergehenden Ansprüche,d a d u r c h g e k e n n z e i c h n e t , dass - der modulare Multilevelstromrichter (500) mindestens zwei erste Fahrzeuge (501) aufweist, wobei die auf den beiden ersten Fahrzeugen (501) jeweils angeordneten erstenelektrischen Bauelemente (508) jeweils einer anderen Phase des Multilevelstromrichters (500) zugeordnet sind. 14. Blindleistungskompensationsanlage (401) mit einemmodularen Multilevelstromrichter (500) nach einem derAnsprüche 1 bis 13. 15. Verfahren zum Beeinflussen von elektrischem Strom mittels eines modularen Multilevelstromrichters (500), bei dem - der elektrische Strom von einem Energieübertragungsnetz (540) zu ersten elektrischen Bauelementen (508) und zu zweiten elektrischen Bauelementen (509) übertragen wird, wobei die ersten elektrischen Bauelemente (508) auf einem ersten Fahrzeug (501), insbesondere auf einem ersten LKW- Anhänger (501), angeordnet sind und die zweiten elektrischen Bauelemente (509) auf einem zweiten Fahrzeug (502),insbesondere auf einem zweiten LKW-Anhänger (502), angeordnet sind und die ersten elektrischen Bauelemente (508) und die zweiten elektrischen Bauelemente (509) Bestandteile des modularen Multilevelstromrichters (500) sind, und - von dem modularen Multilevelstromrichter (500) unterBeteiligung der ersten elektrischen Bauelemente (508) und der zweiten elektrischen Bauelemente (509) der elektrische Strom beeinflusst wird. 16. Verfahren nach Anspruch 15,d a d u r c h g e k e n n z e i c h n e t , dass - der elektrische Strom derart beeinflusst wird, dass eine Blindleistungskompensation des elektrischen Stromsdurchgeführt wird. [EN US11050357B2]: 1. A modular multilevel power converter, comprising: first electrical components arranged on a first vehicle;second electrical components arranged on a second vehicle;said first vehicle and said second vehicle being spaced apart from one another; anda plurality of first connecting conductors electrically connecting said first electrical components and said second electrical components to one another. 2. The modular multilevel power converter according to claim 1, wherein said first vehicle is a first truck trailer and said second vehicle is a second truck trailer. 3. The modular multilevel power converter according to claim 1, wherein: said first electrical components comprise a series connection of modules, each of said modules having at least two electronic switching elements and an electrical energy-storage device; andsaid second electrical components comprise at least one electrical coil. 4. The modular multilevel power converter according to claim 3, wherein: said at least two electronic switching elements of said modules are connected in a half-bridge circuit; oreach of said modules has said at least two electronic switching elements and two further electronic switching elements, said at least two electronic switching elements and said two further electronic switching elements being connected in a full-bridge circuit. 5. The modular multilevel power converter according to claim 1, wherein: said first electrical components are arranged in a first container which is fastened to said first vehicle; and/orsaid second electrical components are arranged in a second container which is fastened to said second vehicle. 6. The modular multilevel power converter according to claim 1, further comprising: a first electrical interface for connecting up said plurality of first connecting conductors, said first electrical interface being arranged at a first end of said first vehicle; and/ora second electrical interface for connecting up said plurality of first connecting conductors, said second electrical interface being arranged at a first end of said second vehicle. 7. The modular multilevel power converter according to claim 6, wherein: said first electrical interface comprises a plurality of detachable electrical contact pairs, each of said plurality of detachable electrical contact pairs of said first electrical interface having a first electrical contact electrically connected to a respective one of said plurality of first electrical components and a second electrical contact electrically connected to a respective one of said plurality of first connecting conductors; and/orsaid second electrical interface comprises a plurality of detachable electrical contact pairs, each of said plurality of detachable electrical contact pairs of said second electrical interface having a first electrical contact electrically connected to a respective one of said second electrical components and a second electrical contact electrically connected to a respective one of said plurality of first connecting conductors. 8. The modular multilevel power converter according to claim 7, wherein each of said plurality of detachable electrical contact pairs of said first electrical interface and each of said plurality of detachable electrical contact pairs of said second electrical interface is a plug connector. 9. The modular multilevel power converter according to claim 7, wherein: said first vehicle has an underside, said second vehicle has an underside, said first container has an interior space and an underside, and said second container has an interior space and an underside;said first electrical contacts of said first electrical interface are electrically connected to said first electrical components by way of first electrical cables which extend, at least in some sections thereof, on said underside of said first vehicle and are guided into said interior space of said first container through recesses formed in said underside of said first container; and/orsaid first electrical contacts of said second electrical interface are electrically connected to said second electrical components by way of second electrical cables which extend, at least in some sections thereof, on said underside of said second vehicle and are guided into said interior space of said second container through recesses formed in said underside of said second container. 10. The modular multilevel power converter according to claim 7, further comprising: a transformer arranged on a third vehicle;said third vehicle and said second vehicle being spaced apart from one another; andsaid transformer and said second electrical components being electrically connected to one another by way of a plurality of second connecting conductors. 11. The modular multilevel power converter according to claim 10, further comprising a third electrical interface for connecting up said plurality of second connecting conductors, said third electrical interface being arranged at a second end of said second vehicle and said plurality of second connecting conductors being connected to said third electrical interface. 12. The modular multilevel power converter according to claim 11, wherein said first electrical interface, said second electrical interface, and said third electrical interface are constructed identically. 13. The modular multilevel power converter according to claim 10, further comprising: a cooling device arranged on a fourth vehicle;said fourth vehicle and said first vehicle being spaced apart from one another; andat least one coolant line connecting said cooling device and said first vehicle to one another. 14. The modular multilevel power converter according to claim 13, wherein said third vehicle is a third truck trailer and said fourth vehicle is a fourth truck trailer. 15. The modular multilevel power converter according to claim 1, wherein said first vehicle is one of two first vehicles, each one of said two first vehicles carrying said first electrical components, and wherein said two first vehicles are respectively assigned to a different phase of the multilevel power converter. 16. A reactive-power compensation system, comprising a modular multilevel power converter according to claim 1. 17. A method for influencing electric current by way of a modular multilevel power converter, the method comprising: transmitting the electric current from a power-transmission network to first electrical components arranged on a first vehicle and to second electrical components arranged on a second vehicle, wherein the first electrical components and the second electrical components are constituent parts of the modular multilevel power converter; andinfluencing the electric current by the modular multilevel power converter with the participation of the first electrical components and of the second electrical components. 18. The method according to claim 17, wherein the first electrical components are arranged on a first vehicle and the second electrical components are arranged on a second vehicle. 19. The method according to claim 17, which comprises influencing the electric current to carry out a reactive-power compensation of the electrical current. | [DE WO2018153433A1]: Beschreibung Modularer Multilevelstromrichter Ein modularer Multilevelstromrichter ist eine leistungselektronische Schaltung zum Umwandeln von elektrischer Energie. Mit einem modularen Multilevelstromrichter kann beispielsweise Wechselstrom in Gleichstrom und Gleichstrom in Wechselstrom umgewandelt werden. Ein modularer Multilevelstromrichter weist eine Vielzahl von gleichartigen Modulen auf, welche elektrisch in Reihe geschaltet sind. Durch die elektrische Reihenschaltung der Module lassen sich hohe Ausgangsspannungen erreichen. Ein modularer Multilevelstromrichter ist einfach an unterschiedliche Spannungen anpassbar (skalierbar) und eine gewünschte Ausgangsspannung kann relativ genau erzeugt werden. Ein modularer Multilevelstromrichter kann vorteilhafterweise im Hochspannungsbereich eingesetzt werden, beispielsweise als Stromrichter bei einer Hochspannungs- Gleichstrom-Übertragungsanlage oder als Blindleistungskompensationsanlage . Für den Hoch- und Mittelspannungsbereich geeignete modulare Multilevelstromrichter weisen oftmals eine beträchtliche Größe auf. Der ortsfeste Aufbau eines solchen modularen Multilevelstromrichters stellt ein großes Investitionsvorhaben dar und dauert oftmals relativ lange. Ursachen dafür sind beispielsweise, dass eine lange Vorausplanung notwendig ist, dass Fundamente hergestellt, Gebäude gebaut und Kabel verlegt werden müssen. Diese Baumaßnahmen sind oft auch mit langwierigen Planungs- und Genehmigungsverfahren verbunden. Der Erfindung liegt die Aufgabe zugrunde, einen modularen Multilevelstromrichter und ein Verfahren zum Beeinflussen von elektrischem Strom mittels eines modularen Multilevelstromrichters anzugeben, die schnell an dem gewünschten Einsatzort realisiert werden können. Diese Aufgabe wird erfindungsgemäß gelöst durch einen modularen Multilevelstromrichter und durch ein Verfahren nach den unabhängigen Patentansprüchen. Vorteilhafte Ausführungsformen des Multilevelstromrichters und des Verfahrens sind in den abhängigen Patentansprüchen angegeben. Offenbart wird ein modularer Multilevelstromrichter - mit ersten elektrischen Bauelementen, die auf einem ersten Fahrzeug, insbesondere auf einem ersten LKW-Anhänger, angeordnet sind, - mit zweiten elektrischen Bauelementen, die auf einem zweiten Fahrzeug, insbesondere auf einem zweiten LKW- Anhänger, angeordnet sind, - wobei das erste Fahrzeug und das zweite Fahrzeug beabstandet voneinander aufgestellt sind und - wobei die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente mittels mehrerer erster (elektrischer) Verbindungsleiter elektrisch miteinander verbunden sind. Hierbei ist vorteilhaft, dass die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente jeweils auf einem Fahrzeug angeordnet sind. Dadurch können die ersten und die zweiten elektrischen Bauelemente jeweils mittels des Fahrzeugs schnell zu dem gewünschten Einsatzort transportiert werden. Weiterhin ist vorteilhaft, dass die Bauelemente auch während des Betriebs des Multilevelstromrichters auf dem jeweiligen Fahrzeug verbleiben. Zum Betrieb des Multilevelstromrichters sind das erste Fahrzeug und das zweite Fahrzeug beabstandet voneinander aufgestellt, und die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente sind mittels der ersten Verbindungsleiter miteinander elektrisch verbunden. Dadurch ist es vorteilhafterweise nicht notwendig, Fundamente, Gebäude oder ähnliche Infrastruktureinheiten zu errichten. Auch die zugehörigen Planungs- und Genehmigungsverfahren können entfallen. Dies ermöglicht es, den modularen Multilevelstromrichter sehr schnell an seinem gewünschten Einsatzort zu installieren und zum Einsatz zu bringen. Weiterhin ist vorteilhaft, dass auch modulare Multilevelstromrichter mit großen und schweren elektrischen Bauelementen auf diese Art realisiert werden können, weil die Bauelemente auf mehrere Fahrzeuge verteilt sind. Bei Bedarf kann der Multilevelstromrichter natürlich auch mehr als zwei Fahrzeuge aufweisen, die mittels Verbindungsleitern elektrisch miteinander verbunden sind. Der Begriff , elektrische Bauelemente λ wird im Rahmen der Beschreibung für klassische elektrische Bauelemente wie beispielsweise Spulen, Schalter oder Widerstände und auch für elektronische Bauelemente wie beispielsweise Transistoren, IGBTs oder Schaltkreise verwendet. Der modulare Multilevelstromrichter kann vorteilhafterweise so ausgestaltet sein, dass - die ersten elektrischen Bauelemente eine (elektrische) Reihenschaltung von Modulen aufweisen, wobei die Module jeweils mindestens zwei elektronische Schaltelemente und einen elektrischen Energiespeicher aufweisen, - und die zweiten elektrischen Bauelemente mindestens eine elektrische Spule aufweisen. Bei dieser Ausgestaltungsform sind auf dem ersten Fahrzeug und dem zweiten Fahrzeug wesentliche elektrische Bauelemente angeordnet, um einen ein- oder mehrphasigen Multilevelstromrichter zu realisieren. Der modulare Multilevelstromrichter kann auch so ausgestaltet sein, dass - die ersten elektrischen Bauelemente in einem ersten Container angeordnet sind, der auf dem ersten Fahrzeug befestigt ist und/oder - die zweiten elektrischen Bauelemente in einem zweiten Container angeordnet sind, der auf dem zweiten Fahrzeug befestigt ist. Zum Beispiel kann der modulare Multilevelstromrichter so ausgestaltet sein, dass - die Reihenschaltung von Modulen in einem ersten Container angeordnet ist, der auf dem ersten Fahrzeug befestigt ist und/oder - die Spule in einem zweiten Container angeordnet ist, der auf dem zweiten Fahrzeug befestigt ist. Der erste Container und der zweite Container bilden dabei vorteilhafterweise jeweils ein Gehäuse des Multilevelstromrichters ; sie schützen die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente vor Umgebungseinflüssen. Zusätzlich schützen die Container auch die Umwelt des Multilevelstromrichters vor potenziell gefährlichen physikalischen Größen, die an dem Multilevelstromrichter auftreten, wie beispielsweise vor hohen Spannungen, großen Strömen oder starken elektromagnetischen Feldern. Der Multilevelstromrichter kann so eingerichtet sein, dass - an einem ersten Ende des ersten Fahrzeugs eine erste elektrische Schnittstelle zum Anschluss der ersten Verbindungsleiter angeordnet ist und/oder - an einem ersten Ende des zweiten Fahrzeugs eine zweite elektrische Schnittstelle zum Anschluss der ersten Verbindungsleiter angeordnet ist. Mittels der ersten Schnittstelle und der zweiten Schnittstelle können vorteilhafterweise die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente elektrisch miteinander verbunden werden. Dabei ist vorteilhaft, dass die erste elektrische Schnittstelle und die zweite elektrische Schnittstelle jeweils an einem ersten Ende des jeweiligen Fahrzeuges angeordnet ist. Dadurch ist man beim Anschluss der ersten Verbindungsleiter sehr variabel: Die ersten Verbindungsleiter können vom Fahrzeug sowohl parallel zur Fahrtrichtung als auch im rechten Winkel zur Fahrtrichtung fortgeführt werden. Insbesondere können die ersten Verbindungsleiter vorteilhafterweise geradlinig vom Fahrzeug weggeführt werden, da durch die endseitige Anordnung der Schnittstelle an dem Fahrzeug in mehrere Richtungen ausreichend Platz für die geradlinige Verlegung der ersten Verbindungsleiter ist. Der Multilevelstromrichter kann so ausgestaltet sein, dass - die erste elektrische Schnittstelle mehrere lösbare elektrische Kontaktpaare aufweist, die jeweils einen ersten elektrischen Kontakt und einen zweiten elektrischen Kontakt aufweisen, wobei die ersten Kontakte elektrisch mit den ersten elektrischen Bauelementen verbunden sind und die zweiten Kontakte elektrisch jeweils mit einem der ersten Verbindungsleiter verbunden sind und/oder - die zweite elektrische Schnittstelle mehrere lösbare elektrische Kontaktpaare aufweist, die jeweils einen ersten elektrischen Kontakt und einen zweiten elektrischen Kontakt aufweisen, wobei die ersten Kontakte elektrisch mit den zweiten elektrischen Bauelementen verbunden sind und die zweiten Kontakte elektrisch jeweils mit einem der ersten Verbindungsleiter verbunden sind. Vorteilhafterweise weisen die beiden Schnittstellen also jeweils mehrere lösbare Kontaktpaare auf. Dabei ist besonders vorteilhaft, dass am Einsatzort beim Aufbau des Multilevelstromrichters lediglich die einander zugeordneten ersten Kontakte und zweiten Kontakte miteinander zu verbinden sind. Die elektrische Verbindung zwischen den ersten Kontakten und den ersten elektrischen Bauelementen (also die fahrzeugseitige elektrische Verbindung) kann schon bei der Installation der Bauelemente auf dem jeweiligen Fahrzeug vollständig hergestellt und geprüft werden. Dies kann in einer Werkhalle erfolgen; es ist am Einsatzort des Multilevelstromrichters nicht notwendig, diese ( fahrzeugseitigen) elektrischen Verbindungen zu verändern und/oder zu prüfen. Dadurch kann der Multilevelstromrichter am Einsatzort sehr einfach, schnell und mit wenig Personal aufgebaut und/oder in Betrieb genommen werden. Der Multilevelstromrichter kann so ausgestaltet sein, dass die elektrischen Kontaktpaare jeweils als ein Steckverbinder ausgestaltet sind. Mittels Steckverbindern lassen sich die elektrischen Verbindungsleiter besonders einfach und schnell mit den auf dem jeweiligen Fahrzeug befindlichen elektrischen Bauelementen verbinden. Der Multilevelstromrichter kann so ausgestaltet sein, dass - die ersten Kontakte der ersten elektrischen Schnittstelle elektrisch mit den ersten elektrischen Bauelementen verbunden sind mittels erster elektrischer Kabel, die zumindest abschnittsweise an der Unterseite des ersten Fahrzeugs verlaufen und durch an der Unterseite des ersten Containers angeordnete Ausnehmungen hindurch in einen Innenraum des ersten Containers hineingeführt sind und/oder - die ersten Kontakte der zweiten elektrischen Schnittstelle elektrisch mit den zweiten elektrischen Bauelementen verbunden sind mittels zweiter elektrischer Kabel, die zumindest abschnittsweise an der Unterseite des zweiten Fahrzeugs verlaufen und durch an der Unterseite des zweiten Containers angeordnete Ausnehmungen hindurch in einen Innenraum des zweiten Containers hineingeführt sind. Dabei ist besonders vorteilhaft, dass die ersten elektrischen Kabel an der Unterseite des ersten Fahrzeuges geschützt und sicher vor versehentlicher Veränderung oder Beschädigung verlegt sind. Weiterhin ist vorteilhaft, dass die ersten elektrischen Kabel durch an der Unterseite des ersten Containers angeordneten Ausnehmungen hindurch in den Innenraum des ersten Containers eingeführt sind. Dadurch kann durch diese Ausnehmungen keine oder nur wenig Feuchtigkeit (Regen, Schnee oder ähnliches) in den ersten Container eindringen. Diese Vorteile gelten natürlich auch für den zweiten Container entsprechend . Der Multilevelstromrichter kann so ausgestaltet sein, dass - der modulare Multilevelstromrichter einen Transformator aufweist, der auf einem dritten Fahrzeug, insbesondere auf einem dritten LKW-Anhänger, angeordnet ist, - wobei das dritte Fahrzeug und das zweite Fahrzeug beabstandet voneinander aufgestellt sind und - wobei der Transformator und die zweiten elektrischen Bauelemente mittels mehrerer zweiter (elektrischer) Verbindungsleiter elektrisch miteinander verbunden sind. Hierbei ist besonders vorteilhaft, dass der modulare Multilevelstromrichter einen eigenen Transformator aufweist und somit unabhängig von einem fest installierten Transformator am Einsatzort ist. Dadurch werden die Einsatzmöglichkeiten des Multilevelstromrichters deutlich vergrößert und der modulare Multilevelstromrichter kann durch Wahl eines geeigneten Transformators an unterschiedlichste Spannungsniveaus angepasst werden. Der Multilevelstromrichter kann auch so ausgestaltet sein, dass - an einem zweiten Ende des zweiten Fahrzeugs eine dritte elektrische Schnittstelle zum Anschluss der zweiten Verbindungsleiter angeordnet ist und - die zweiten Verbindungsleiter mit der dritten elektrischen Schnittstelle (elektrisch) verbunden sind. Dabei ist besonders vorteilhaft, dass an dem zweiten Fahrzeug die dritte elektrische Schnittstelle und die zweite elektrische Schnittstelle auch räumlich voneinander getrennt sind und damit Verwechselungen beim Anschluss der Verbindungsleiter vermieden werden. Außerdem kann durch die Anordnung der dritten elektrischen Schnittstelle und der zweiten elektrischen Schnittstelle an zwei (entgegengesetzten) Enden des zweiten Fahrzeugs die notwendige Länge der Verbindungsleiter minimiert werden. Der Multilevelstromrichter kann auch so ausgestaltet sein, dass - die erste elektrische Schnittstelle, die zweite elektrische Schnittstelle und die dritte elektrische Schnittstelle gleichartig aufgebaut sind. Dabei ist besonders vorteilhaft, dass das elektrische Verbinden der einzelnen Schnittstellen mittels elektrischer Verbindungsleiter am Einsatzort deutlich vereinfacht wird. Das am Einsatzort befindliche Personal braucht lediglich einmal das Prinzip der Schnittstelle zu verstehen und kann dann einfach und schnell die auf den Fahrzeugen angeordneten elektrischen Bauelemente mittels der Verbindungsleiter elektrisch miteinander verbinden. Der Multilevelstromrichter kann auch so ausgestaltet sein, dass - der modulare Multilevelstromrichter eine Kühleinrichtung aufweist, die auf einem vierten Fahrzeug, insbesondere auf einem vierten LKW-Anhänger, angeordnet ist, - wobei das vierte Fahrzeug und das erste Fahrzeug beabstandet voneinander aufgestellt sind und - wobei die Kühleinrichtung und das erste Fahrzeug mittels mindestens einer Kühlmittelleitung miteinander verbunden sind. Die auf dem vierten Fahrzeug angeordnete Kühleinrichtung ermöglicht es, den Multilevelstromrichter effektiv zu kühlen und daher auch bei großen benötigten elektrischen Leistungen zu verwenden. Der Multilevelstromrichter kann auch so ausgestaltet sein, dass - die zwei elektronischen Schaltelemente der Module in einer Halbbrückenschaltung angeordnet sind, und/oder - die Module jeweils die zwei elektronischen Schaltelemente und zwei weitere elektronische Schaltelemente aufweisen, wobei die zwei elektronischen Schaltelemente und die zwei weiteren elektronischen Schaltelemente in einer Vollbrückenschaltung angeordnet sind. Mittels dieser Halbbrückenschaltungen und/oder Vollbrückenschaltungen lassen sich vielfältige Konfigurationen von Multilevelstromrichtern realisieren . Der Multilevelstromrichter kann auch so ausgestaltet sein, dass - der modulare Multilevelstromrichter mindestens zwei erste Fahrzeuge aufweist, wobei die auf den beiden ersten Fahrzeugen jeweils angeordneten ersten elektrischen Bauelemente jeweils einer anderen Phase des Multilevelstromrichters zugeordnet sind. Mit einem derartigen Multilevelstromrichter lassen sich bevorzugt sehr große elektrische Leistungen verarbeiten. Dazu sind die elektrischen Bauelemente jeder elektrischen Phase auf einem oder mehreren dieser Phase zugeordneten ersten Fahrzeugen angeordnet. Dadurch lässt sich auch ein modularer Multilevelstromrichter mit sehr großen und sehr schweren elektrischen Bauelementen realisieren. Beispielsweise kann der Multilevelstromrichter ein dreiphasiger Multilevelstromrichter sein. Dieser dreiphasige Multilevelstromrichter kann drei erste Fahrzeuge aufweisen, wobei jedes der drei ersten Fahrzeuge jeweils die einer Phase zugeordneten ersten elektrischen Bauelemente trägt. Offenbart wird weiterhin eine Blindleistungskompensationsanlage mit einem modularen Multilevelstromrichter nach einer der vorstehend beschriebenen Varianten. Offenbart wird weiterhin ein Verfahren zum Beeinflussen von elektrischem Strom mittels eines modularen Multilevelstromrichters, bei dem - der elektrische Strom von einem Energieübertragungsnetz zu ersten elektrischen Bauelementen und zu zweiten elektrischen Bauelementen übertragen wird, wobei die ersten elektrischen Bauelemente auf einem ersten Fahrzeug, insbesondere auf einem ersten LKW-Anhänger, angeordnet sind und die zweiten elektrischen Bauelemente auf einem zweiten Fahrzeug, insbesondere auf einem zweiten LKW-Anhänger, angeordnet sind und die ersten elektrischen Bauelemente und die zweiten elektrischen Bauelemente Bestandteile des modularen Multilevelstromrichters sind, und - von dem modularen Multilevelstromrichter unter Beteiligung der ersten elektrischen Bauelemente und der zweiten elektrischen Bauelemente der elektrische Strom beeinflusst wird . Dieses Verfahren kann so ausgestaltet sein, dass - der elektrische Strom derart beeinflusst wird, dass eine Blindleistungskompensation des elektrischen Stroms durchgeführt wird. Es handelt sich also um ein Verfahren zur Blindleistungskompensation von elektrischem Strom mittels eines modularen Multilevelstromrichters. Der beschriebene Multilevelstromrichter und das beschriebene Verfahren weisen gleiche beziehungsweise gleichartige Vorteile auf. Im Folgenden wird die Erfindung anhand von Ausführungs¬ beispielen näher erläutert. Gleiche Bezugszeichen verweisen dabei auf gleiche oder gleich wirkende Elemente. Dazu ist in Figur 1 ein Ausführungsbeispiel eines modularen Multilevelstromrichters in einer Brückenschaltung, in Figur 2 ein Ausführungsbeispiel eines Moduls, in Figur 3 ein weiteres Ausführungsbeispiel eines Moduls, Figur 4 ein Ausführungsbeispiel einer Blindleistungs- Kompensationsanlage mit einem modularen Multilevelstromrichter, in Figur 5 ein Ausführungsbeispiel des modularen Multilevelstromrichters mit 6 Fahrzeugen, in Figur 6 ein Ausführungsbeispiel des ersten Fahrzeugs und des zweiten Fahrzeugs, Figur 7 das Ausführungsbeispiel des ersten Fahrzeugs in einer anderen Ansicht, in Figur 8 ein Ausführungsbeispiel der Schnittstelle, in Figur 9 das Ausführungsbeispiel der Schnittstelle in einer teilweise geschnittenen Ansicht, und Figur 10 das Ausführungsbeispiel des ersten Fahrzeugs und des zweiten Fahrzeugs in einer Ansicht von unten dargestellt . In Figur 1 ist ein Stromrichter 1 (Hochspannungs-Stromrichter 1) in Form eines modularen Multilevelstromrichters 1 (modular multilevel Converter, MMC) dargestellt. Dieser Multilevelstromrichter 1 weist einen ersten Wechselspannungsanschluss 5, einen zweiten Wechsel¬ spannungsanschluss 7 und einen dritten Wechselspannungs- anschluss 9 auf. Der erste Wechselspannungsanschluss 5 ist elektrisch mit einem ersten Phasenmodulzweig 11 und einem zweiten Phasenmodulzweig 13 verbunden. Der erste Phasenmodulzweig 11 und der zweite Phasenmodulzweig 13 bilden ein erstes Phasenmodul 15 des Stromrichters 1. Das dem ersten Wechselspannungsanschluss 5 abgewandte Ende des ersten Phasenmodulzweigs 11 ist mit einem ersten Gleichspannungs- anschluss 16 elektrisch verbunden; das dem ersten Wechselspannungsanschluss 5 abgewandte Ende des zweiten Phasenmodulzweigs 13 ist mit einem zweiten Gleichspannungsanschluss 17 elektrisch verbunden. Der erste Gleichspannungsanschluss 16 ist ein positiver Gleichspannungsanschluss; der zweite Gleichspannungsanschluss 17 ist ein negativer Gleichspannungsanschluss. Der zweite Wechselspannungsanschluss 7 ist mit einem Ende eines dritten Phasenmodulzweigs 18 und mit einem Ende eines vierten Phasenmodulzweigs 21 elektrisch verbunden. Der dritte Phasenmodulzweig 18 und der vierte Phasenmodulzweig 21 bilden ein zweites Phasenmodul 24. Der dritte Wechsel¬ spannungsanschluss 9 ist mit einem Ende eines fünften Phasenmodulzweigs 27 und mit einem Ende eines sechsten Phasenmodulzweigs 29 elektrisch verbunden. Der fünfte Phasenmodulzweig 27 und der sechste Phasenmodulzweig 29 bilden ein drittes Phasenmodul 31. Das dem zweiten Wechselspannungsanschluss 7 abgewandte Ende des dritten Phasenmodulzweigs 18 und das dem dritten Wechselspannungsanschluss 9 abgewandte Ende des fünften Phasenmodulzweigs 27 sind mit dem ersten Gleichspannungs- anschluss 16 elektrisch verbunden. Das dem zweiten Wechselspannungsanschluss 7 abgewandte Ende des vierten Phasen- modulzweigs 21 und das dem dritten Wechselspannungsanschluss 9 abgewandte Ende des sechsten Phasenmodulzweigs 29 sind mit dem zweiten Gleichspannungsanschluss 17 elektrisch verbunden. Der erste Phasenmodulzweig 11, der dritte Phasenmodulzweig 18 und der fünfte Phasenmodulzweig 27 bilden ein positivseitiges Stromrichterteil 32; der zweite Phasenmodulzweig 13, der vierte Phasenmodulzweig 21 und der sechste Phasenmodulzweig 29 bilden ein negativseitiges Stromrichterteil 33. Der erste Wechselspannungsanschluss 5, der zweite Wechsel- spannungsanschluss 7 und der dritte Wechselspannungsanschluss 9 sind über einen Transformator 35 und eine Schaltanlage 36 mit einem Energieübertragungsnetz 37 elektrisch verbunden. Jeder Phasenmodulzweig weist eine Mehrzahl von Modulen (1_1, 1_2, 1_3, 1_4 ... l_n; 2_1 ... 2_n; usw.) auf, welche (mittels ihrer galvanischen Stromanschlüsse) elektrisch in Reihe geschaltet sind. Solche Module werden auch als Submodule bezeichnet. Im Ausführungsbeispiel der Figur 1 weist jeder Phasenmodulzweig n Module auf. Die Anzahl der mittels ihrer galvanischen Stromanschlüsse elektrisch in Reihe geschalteten Module kann sehr verschieden sein, mindestens sind zwei Module in Reihe geschaltet, es können aber auch beispiels- weise 3, 50, 100 oder mehr Module elektrisch in Reihe geschaltet sein. Im Ausführungsbeispiel ist n = 36: der erste Phasenmodulzweig 11 weist also 36 Module 1_1, 1_2, 1_3, ··· 1_36 auf. Die anderen Phasenmodulzweige 13, 18, 21, 27 und 29 sind gleichartig aufgebaut. In jedem Phasenmodulzweig ist weiterhin eine Induktivität (Spule) LI bis L6 angeordnet. Von einer Steuereinrichtung des Stromrichters 1 werden optische Nachrichten beziehungsweise optische Signale über eine optische Kommunikationsverbindung (zum Beispiel über einen Lichtwellenleiter) zu den einzelnen Modulen 1_1 bis 6_n übertragen. Beispielsweise sendet die Steuereinrichtung an die einzelnen Module jeweils einen Sollwert zur Höhe der Ausgangsspannung, die das jeweilige Modul bereitstellen soll. Der beschriebene modulare Multilevelstromrichter weist also eine Vielzahl der genannten gleichartigen Module auf, welche elektrisch in Reihe geschaltet sind. Durch die elektrische Reihenschaltung der Module lassen sich hohe Ausgangs- Spannungen erreichen. Der Stromrichter ist einfach an unterschiedliche Spannungen anpassbar (skalierbar) und eine gewünschte Ausgangsspannung kann relativ genau erzeugt werden. Modulare Multilevelstromrichter werden oftmals im Hochspannungsbereich eingesetzt, beispielsweise als Stromrichter einer Hochspannungs-Gleichstrom- Übertragungsanlage oder als Blindleistungskompensationsanlage (Blindleistungskompensator) . Der Stromrichter 1 weist eine Kühleinrichtung 50 auf. Die Kühleinrichtung 50 weist einen Kühlmittelbehälter 52, eine Pumpe 54 (Kühlmittel-Pumpe 54) und einen Wärmeübertrager 56 (Wärmetauscher 56) . Der Kühlmittelbehälter 52, die Pumpe 54 und der Wärmeübertrager 56 sind durch Kühlmittelleitungen 60 mit den einzelnen Modulen 1_1 ... l_n, 3_1 ... 3_n, usw. des Stromrichters 1 verbunden. In dem Kühlmittelbehälter 52 befindet sich ein Vorrat an Kühlmittel 70. Das Kühlmittel 70 kann aus dem Kühlmittelbehälter 52 mittels der Pumpe 54 durch den Wärmeübertrager 56, durch die Module 1_1 ... l_n des ersten Phasenmodulzweigs 11 und danach wieder zurück zum Kühlmittelbehälter 52 gepumpt werden. Somit weist die Kühleinrichtung 50 einen Kühlmittelkreislauf 72 auf. Mittels des Kühlmittelkreislaufs 72 können also in den Modulen angeordnete Leistungshalbleiterbauelemente gleichzeitig gekühlt werden. Zur Kühlung der Leistungshalbleiterbauelemente der Module des zweiten Phasenmodulzweigs 13, des vierten Phasenmodulzweigs 21 und des sechsten Phasenmodulzweigs 29 existiert eine weitere Kühleinrichtung 80. Diese weitere Kühleinrichtung 80 ist identisch aufgebaut zu der Kühleinrichtung 50 des ersten, dritten und fünften Phasenmodulzweigs 11, 18 und 27. Selbstverständlich können auch sämtliche Module des Stromrichters 1 mittels einer einzigen Kühleinrichtung (d. h. mittels eines einzigen Kühlmittelbehälters 52, einer einzigen Pumpe 54 und eines einzigen Wärmeübertragers 56) gekühlt werden. Alternativ ist es auch möglich, mehr als zwei Kühleinrichtungen zur Kühlung der Module des Stromrichters 1 einzusetzen. In Figur 2 ist beispielhaft der Aufbau eines Moduls 201 dargestellt. Dabei kann es sich beispielsweise um das Modul 1_1 des ersten Phasenmodulzweigs 11 (oder auch um eines der anderen in Figur 1 dargestellten Module) handeln. Das Modul ist als ein Halbbrückenmodul 201 ausgestaltet. Das Modul 201 weist ein erstes ein- und abschaltbares elektronisches Schaltelement 202 mit einer ersten antiparallel geschalteten Diode 204 (erste Freilaufdiode 204) auf. Weiterhin weist das Modul 201 ein zweites ein- und abschaltbares elektronisches Schaltelement 206 mit einer zweiten antiparallel geschalteten Diode 208 (zweite Freilaufdiode 208) und einen elektrischen Energiespeicher 210 in Form eines elektrischen Kondensators 210 auf. Das erste elektronische Schaltelement 202 und das zweite elektronische Schaltelement 206 sind jeweils als ein IGBT ( insulated-gate bipolar transistor) ausgestaltet. Das erste elektronische Schaltelement 202 ist elektrisch in Reihe geschaltet mit dem zweiten elektronischen Schaltelement 206. Am Verbindungspunkt zwischen den beiden elektronischen Schaltelementen 202 und 206 ist ein erster (galvanischer) Modulanschluss 212 angeordnet. An dem Anschluss des zweiten Schaltelements 206, welcher dem Verbindungspunkt gegenüberliegt, ist ein zweiter (galvanischer) Modulanschluss 215 angeordnet. Der zweite Modulanschluss 215 ist weiterhin mit einem ersten Anschluss des Energiespeichers 210 verbunden; ein zweiter Anschluss des Energiespeichers 210 ist elektrisch verbunden mit dem Anschluss des ersten Schaltelements 202, der dem Verbindungspunkt gegenüberliegt. Der Energiespeicher 210 ist also elektrisch parallel geschaltet zu der Reihenschaltung aus dem ersten Schaltelement 202 und dem zweiten Schaltelement 206. Durch entsprechende Ansteuerung des ersten Schaltelements 202 und des zweiten Schaltelements 206 kann erreicht werden, dass zwischen dem ersten Modulanschluss 212 und dem zweiten Modulanschluss 215 entweder die Spannung des Energiespeichers 210 ausgegeben wird oder keine Spannung ausgegeben wird (d.h. eine Nullspannung ausgegeben wird) . Durch Zusammenwirken der Module der einzelnen Phasenmodulzweige kann so die jeweils gewünschte Ausgangsspannung des Stromrichters erzeugt werden. Die Ansteuerung des ersten Schaltelements 202 und des zweiten Schaltelements 206 erfolgt im Ausführungsbeispiel mittels der (oben erwähnten) von der Steuereinrichtung 48 des Stromrichters zu dem Modul übertragenen Nachricht beziehungsweise Signal. In Figur 3 ist ein weiteres Ausführungsbeispiel eines Moduls 301 des modularen Multilevelstromrichters 1 dargestellt. Bei diesem Modul 301 kann es sich beispielsweise um das Modul 1 2 (oder auch um eines der anderen in Figur 1 dargestellten Module) handeln. Neben den bereits aus Figur 2 bekannten ersten elektronischen Schaltelement 202, zweiten elektronischen Schaltelement 206, erster Freilaufdiode 204, zweiter Freilaufdiode 208 und Energiespeicher 210 weist das in Figur 3 dargestellte Modul 301 ein drittes elektronisches Schaltelement 302 mit einer antiparallel geschalteten dritten Freilaufiode 304 sowie ein viertes elektronisches Schaltelement 306 mit einer vierten antiparallel geschalteten Freilaufdiode 308 auf. Das dritte elektronische Schaltelement 302 und das vierte elektronische Schaltelement 306 sind jeweils als ein IGBT ausgestaltet. Im Unterschied zur Schaltung der Figur 2 ist der zweite Modulanschluss 315 nicht mit dem zweiten elektronischen Schaltelement 206 elektrisch verbunden, sondern mit einem Mittelpunkt einer elektrischen Reihenschaltung aus dem dritten elektronischen Schaltelement 302 und dem vierten elektronischen Schaltelement 306. Das Modul 301 der Figur 3 ist ein sogenanntes Vollbrücken- Modul 301. Dieses Vollbrücken-Modul 301 zeichnet sich dadurch aus, dass bei entsprechender Ansteuerung der vier elektronischen Schaltelemente zwischen dem ersten (galvanischen) Modulanschluss 212 und dem zweiten (galvanischen) Modulanschluss 315 wahlweise entweder die positive Spannung des Energiespeichers 210, die negative Spannung des Energiespeichers 210 oder eine Spannung des Wertes Null (Nullspannung) ausgegeben werden kann. Somit kann also mittels des Vollbrückenmoduls 301 die Polarität der Ausgangsspannung umgekehrt werden. Der Stromrichter 1 kann entweder nur Halbbrücken-Module 201, nur Vollbrücken-Module 301 oder auch Halbbrücken-Module 201 und Vollbrücken-Module 301 aufweisen. In Figur 4 ist ein Ausführungsbeispiel eines Stromrichters 401 dargestellt, welcher eine Blindleistungskompensationsanlage 401 ist. Dieser Stromrichter 401 weist lediglich die drei Phasenmodulzweige 11, 18 und 27 auf, welche drei Phasenmodule des Stromrichters bilden. Die Anzahl der Phasenmodule entspricht der Anzahl der Phasen eines Wechselspannungs-Energieübertragungsnetzes 37, an das der Stromrichter 401 mittels des Transformators 35 und der Schaltanlage 36 angeschlossen ist. Die drei Phasenmodule 11, 18 und 27 sind dreieckförmig miteinander verbunden, d.h. die drei Phasenmodule 11, 18 und 27 sind in einer Dreieckschaltung geschaltet. Jeder Eckpunkt der Dreieckschaltung ist mit jeweils einer Phasenleitung 415, 417 oder 419 des dreiphasigen Wechselspannungsnetzes 37 elektrisch verbunden. (Die drei Phasenmodule können in einem anderen Ausführungsbeispiel anstelle in Dreieckschaltung auch in einer Sternschaltung geschaltet sein.) Der Stromrichter 401 kann das Energieübertragungsnetz 37 mit Blindleistung versorgen oder Blindleistung aus dem Energieübertragungsnetz 37 entnehmen. In Figur 5 ist ein Ausführungsbeispiel eines modularen Multilevelstromrichters 500 dargestellt, dessen elektrische Bauelemente auf sechs Fahrzeugen angeordnet sind. Die elektrischen Bauelemente des Multilevelstromrichters 500 sind auf einem ersten Fahrzeug 501, einem zweiten Fahrzeug 502, einem dritten Fahrzeug 503, einem vierten Fahrzeug 504, einem fünften Fahrzeug 505 und einem sechsten Fahrzeug 506 angeordnet. Bei den Fahrzeugen handelt es sich jeweils um einen LKW-Anhänger. Alternativ kann es sich bei jedem der Fahrzeuge jedoch auch um ein anderes Fahrzeug handeln, beispielsweise um einen mit einem Motor ausgestatteten Lastkraftwagen oder um einen Eisenbahnwagen. Auf dem ersten Fahrzeug 501 sind erste elektrische Bauelemente 508 angeordnet. Bei diesen elektrischen Bauelementen 508 handelt es sich im Ausführungsbeispiel um die Reihenschaltungen der Module 1_1 bis l_n, 3_1 bis 3_n und 5_1 bis 5_n, vergleiche Figur 4. Auf dem zweiten Fahrzeug 502 sind zweite elektrische Bauelemente 509 angeordnet. Im Ausführungsbeispiel sind die zweiten elektrischen Bauelemente 509 elektrische Spulen (elektrische Drosseln, Drosselspulen, sogenannte Phasen-Drosselspulen) , insbesondere die in Figur 4 dargestellten elektrischen Spulen LI, L3 und L5. An einem ersten Ende des ersten Fahrzeugs 501 ist eine erste elektrische Schnittstelle 512 angeordnet. An einem ersten Ende des zweiten Fahrzeugs 502 ist eine zweite elektrische Schnittstelle 514 angeordnet. Die erste elektrische Schnittstelle 512 ist über erste Verbindungsleiter 518 mit der zweiten elektrischen Schnittstelle 514 elektrisch verbunden . Das erste Fahrzeug 501 und das zweite Fahrzeug 502 sind dabei parallel zueinander aufgestellt. Die ersten elektrischen Leiter 518, die die erste elektrische Schnittstelle 512 des ersten Fahrzeugs 501 und die zweite elektrische Schnittstelle 514 des zweiten Fahrzeugs 502 verbinden, verlaufen senkrecht zum ersten Fahrzeug 501 und zum zweiten Fahrzeug 502. So
[ES WO2018053660A1]: CONVERTIDOR MULTINIVEL PARA EL CONTROL Y TRANSMISIÓN DE LA ENERGÍA ELÉCTRICA [EN US11018600B2]: Multilevel converter for the control and transmission of electrical energy [FR EP3518412A4]: CONVERTISSEUR MULTINIVEAUX DESTINÉ À LA COMMANDE ET À LA TRANSMISSION D'ÉNERGIE ÉLECTRIQUE [DE EP3518412A4]: MEHRSTUFIGER UMRICHTER ZUR STEUERUNG UND ÜBERTRAGUNG VON ELEKTRISCHER ENERGIE | [ES WO2018053660A1]: Un convertidor multinivel que opera con menor cantidad de componentes, ahorrando costos, pérdidas, tamaño y peso, permitiendo la reducción de volumen y la accesibilidad al control y transformación de energía eléctrica, que comprende al menos una celda básica compuesta por: a) un primer interruptor de potencia que interconecta el bus positivo entre dicha al menos una celda básica y al menos otra celda básica conectadas en cascada entre sí y/o una celda básica y una fuente de tensión continua; b) un segundo interruptor de potencia que interconecta el bus negativo entre dicha al menos una celda básica y al menos otra celda básica conectadas en cascada entre sí; y/o una celda básica y la fuente de tensión continua del punto a); y c) un condensador con un tercer interruptor de potencia, ambos conectados en serie entre sí e interconectados entre el bus positivo y el negativo. [EN EP3518412A4]: A multilevel converter operating with fewer components saving costs, losses, size and weight, allowing the reduction of volume and accessibility to the control and transformation of electric power, comprising at least a basic cell formed by:a) a first power switch that interconnects the positive bus between said at least one basic cell and at least another basic cell connected in cascade each other and / or a basic cell and a continuous voltage source;b) a second power switch that interconnects the negative bus between said at least one basic cell and at least another basic cell connected in cascade each other; and / or a basic cell and the continuous voltage source of point a); andc) a capacitor with a third power switch, both of them being connected in series each other and interconnected between the positive and negative bus. [FR WO2018053660A1]: Un convertisseur multiniveaux qui fonctionne avec une quantité réduite de composants, en économisant les coûts, les pertes, la taille et le poids, permettant de réduire le volume et l'accessibilité à la commande et à la transformation de l'énergie électrique, qui comprend au moins une cellule basique composée : a) d'un premier interrupteur de puissance qui connecte entre eux le bus positif avec ladite au moins une cellule basique et au moins une autre cellule basique connectées en cascade entre elles et/ou une cellule basique et une source de tension continue; b) un deuxième interrupteur de puissance qui connecte entre eux le bus négatif et ladite au moins une cellule basique et au moins une autre cellule basique connectées en cascade entre elles; et/ou une cellule basique et la source de tension continue du point a); et c) un condensateur avec un troisième interrupteur de puissance, tout deux connectés en série entre eux et connectés entre le bus positif et le bus négatif. | EP3518412A4 | 2019-07-31 2020-04-29 | EP17852052A | 2017-09-20 2017-09-20 | CL2016002365A, 2016-09-20 CL2017050053W, 2017-09-20 CL2016002365A, 2016-09-20 CL2017050053W, 2017-09-20 | CL2016002365A1: 2017-02-17 WO2018053660A1: 2018-03-29 EP3518412A4: 2020-04-29 US11018600B2: 2021-05-25 | UNIV ANDRÉS BELLO UNIV ANDRES BELLO UNIV TECNICA FEDERICO SANTA MARIA UTFSM Universidad Andres Bello Universidad Tecnica Federico Santa Maria | NORAMBUENA VALDIVIA MARGARITA ANDREA RODRIGUEZ PÉREZ JOSÉ RAMÓN NORAMBUENA VALDIVIA MARGARITA RODRIGUEZ PÉREZ JOSÉ KOURO RAENER SAMIR KOURO RENAER SAMIR | H02M7/00: I H02M7/483: I H02M7/487: I H02M7/5387: I | H02M7/00: I H02M1/0095: A H02M7/4837: I H02M7/003: I H02M7/487: I H02M7/5387: I | JP2014064431A CN105337521A JP2013055753A EP0823772A1 WO2013186006A2 US7518892B2 US2015036398A1 US2016329832A1 US6697271B2 US9479075B2 ES2330569T3 WO2015041691A1 WO2015131931A1 |  | [ES WO2018053660A1]: REIVINDICACIONESUn convertidor multinivel que opera con menor cantidad de componentes, ahorrando costos, pérdidas, tamaño y peso, permitiendo la reducción de volumen y la accesibilidad al control y transformación de energía eléctrica, CARACTERIZADO porque comprende al menos una celda básica compuesta por: a. un primer interruptor de potencia que interconecta el bus positivo entre dicha al menos una celda básica y al menos otra celda básica conectadas en cascada entre sí; b. un segundo interruptor de potencia que interconecta el bus negativo entre dicha al menos una celda básica y al menos otra celda básica conectadas en cascada entre sí; y c. un condensador con un tercer interruptor de potencia, ambos conectados en serie entre sí e interconectados entre el bus positivo y el negativo. Un convertidor multinivel que opera con menor cantidad de componentes, ahorrando costos, pérdidas, tamaño y peso, permitiendo la reducción de volumen y la accesibilidad al control y transformación de energía eléctrica, CARACTERIZADO porque comprende al menos una celda básica compuesta por: a. un primer interruptor de potencia que interconecta el bus positivo entre dicha al menos una celda básica y una fuente de tensión continua; b. un segundo interruptor de potencia que interconecta el bus negativo entre dicha al menos una celda básica y una fuente de tensión continua; y c. un condensador con un tercer interruptor de potencia, ambos conectados en serie e interconectados entre el bus positivo y el negativo. El convertidor multinivel de la reivindicación 1 o 2, CARACTERIZADO porque la salida de cada fase del convertidor multinivel se obtiene en el punto medio de dos interruptores de potencia de salida conectados en serie entre sí y en paralelo entre el polo positivo y negativo de la última celda básica conectada del convertidor. El convertidor multinivel de la reivindicación 3, CARACTERIZADO porque la cantidad de niveles de tensión generados por fase de salida viene dada por: Nn = Nc + 2 Donde Nn corresponde al número de niveles de tensión obtenidos entre una fase de salida y el neutro del convertidor multinivel y Nc al número de celdas básicas que conforman el convertidor multinivel. El convertidor multinivel de la reivindicación 4, CARACTERIZADO porque la cantidad de niveles de tensión obtenidos es independiente de la cantidad de salidas empleadas, ya sea para una fase, tres fases, seis fases o Nf fases. [EN US11018600B2]: 1. A multilevel converter operating with fewer components saving costs, losses, size and weight, allowing the reduction of volume and accessibility to control and the transformation of electric power, wherein the multilevel converter comprises at least one basic cell formed by: a) a first power switch that interconnects a positive bus between at least two basic cells connected in cascade each other;b) a second power switch that interconnects a negative bus between at least two basic cells connected in cascade each other; andc) a capacitor with a third power switch connected in series and interconnected between the positive and negative bus wherein an output of each multilevel converter phase is obtained at a midpoint of two output power switches connected in series each other and in parallel between the positive and negative pole of the last basic cell connected of the converter and the number of voltage levels generated by output phase is given by: Nn=Nc+2 wherein Nn corresponds to the number of voltage levels obtained between an output phase and the multilevel converter neutral, and Nc to the number of basic cells that form the multi-level converter. 2. The multilevel converter according to claim 1, further comprising at least one additional basic cell formed by: i. a first power switch that interconnects a positive bus between said at least one additional basic cell and a continuous voltage source;ii. a second power switch that interconnects a negative bus between said at least one additional basic cell and the continuous voltage source; andiii. a capacitor with a third power switch connected in series and interconnected between the positive and negative bus. 3. The multilevel converter according to claim 2, characterized in that the output of each multilevel converter phase is obtained at a midpoint of two output power switches connected in series each other and in parallel between the positive and negative pole of the last basic cell connected of the converter. 4. The multilevel converter according to claim 1, wherein the number of voltage levels obtained is independent from the number of outputs used, whether for one phase, three phases, six phases or more phases. | [ES WO2018053660A1]: CONVERTIDOR MULTINIVEL PARA EL CONTROL Y TRANSMISIÓN DE LA ENERGÍA ELÉCTRICA CAMPO DE APLICACIÓN La presente invención se refiere a realizar la conversión de energía eléctrica operando con menor cantidad de componentes, ahorrando costos, pérdidas, tamaño y peso, permitiendo la reducción de volumen y la accesibilidad a la transformación de energía eléctrica para la utilización en diversa aplicaciones, más específicamente a un Convertidor Multinivel para el control y transformación de la energía eléctrica dentro del ámbito de la electrónica de potencia. DESCRIPCIÓN DEL ARTE PREVIO El desarrollo tecnológico experimentado por todos los ámbitos de nuestra sociedad en los últimos cuarenta años se debe en gran parte por el avance que ha alcanzado la electrónica de potencia. Esta rama de la tecnología es responsable de transformar los distintos modos de uso de la energía eléctrica para adaptarla a múltiples aplicaciones como el control de velocidad de motores eléctricos, funcionamiento de aparatos domésticos (electrodomésticos, ordenadores, etc.), equipos de comunicaciones, control de procesos y equipos industriales, así como en el ámbito de la generación, transporte, distribución y almacenamiento de energía eléctrica. En nuestra actual sociedad, la energía eléctrica constituye un pilar fundamental en las diversas actividades desarrolladas día a día, tanto la utilización como el transporte de la misma. La naturaleza de la energía eléctrica impone una serie de requisitos para su producción y transporte muy diferente a otros tipos de energía. Parámetros como la tensión, la forma de la señal, la frecuencia y el factor de potencia, llevan impuestos ciertos límites para garantizar la estabilidad de la red y el correcto suministro de la electricidad en los puntos de consumo. Sin embargo, la forma de generar energía eléctrica no es uniforme y cada fuente energética la produce de una forma particular, presentando una amplia variedad de valores de los distintos parámetros mencionados anteriormente. Los convertidores electrónicos alterna-continua (AC/DC) que alimentan las líneas de transporte en corriente continua y alterna de alta tensión (HVDC y HVAC) y los convertidores continua-continua (DC/DC) que adaptan la tensión de las baterías a los distintos circuitos microelectrónicos (automóviles eléctricos) son claros ejemplos de aplicación donde se requiere una transformación de la energía eléctrica con el mayor rendimiento posible. Un convertidor de energía es un sistema o equipo electrónico que tiene por objetivo la conversión de energía eléctrica entre dos formatos diferentes. Por ejemplo, obtener corriente continua a partir de corriente alterna. El concepto inicial de convertidor puede extenderse para incluir aspectos como: eficiencia, reversibilidad, grado de idealidad, fiabilidad, volumen o tecnología, por citar las más importantes. Los convertidores pueden clasificarse según diferentes criterios. Uno de los más comúnmente utilizados es agruparlos según el formato de las energías de entrada y salida. Básicamente y según este criterio pueden establecerse cuatro grandes grupos: • Convertidores AC/AC. • Convertidores AC/DC o rectificadores. • Convertidores DC/DC. • Convertidores DC/AC o inversores. La transmisión de energía eléctrica requiere en sus puntos de conexión y distribución, de equipos que transformen la energía de un medio a otro, estos equipos denominados Convertidores de Potencia, han sido ampliamente desarrollados y estudiados, siendo actualmente empleados aquellos que permiten la generación de tensión multinivel en la salida. Los convertidores multinivel incluyen un arreglo de semiconductores de potencia y capacitores como fuentes de tensión, la tensión generada a la salida tiene forma de onda escalonada considerando que los interruptores se cierran y se abren en tiempos diferentes, dependiendo del número de interruptores de potencia la tensión en la salida crece sumando la tensión de los capacitores, mientras que los interruptores de potencia soportan tensiones reducidas. Los convertidores multinivel alimentados en tensión han surgido como una nueva opción de convertidor para aplicaciones de alta potencia. Existen diferentes topologías de convertidores multinivel, sin embargo, se pueden clasificar en tres estructuras básicas: · Convertidor multinivel con diodo fijador (Diode-Clamped Converter o NPC (Neutral Point Clamped Con verter)). • Convertidor multinivel con condensadores flotantes (Flying Capacitor Converter). • Convertidor multinivel en cascada. {Cascade Full-Bridge Converter). Tabla 1 : Ventajas y Desventajas de Convertidores Multinivel La principal ventaja de los convertidores multinivel es la reducción de componentes armónicas en las variables eléctricas. Estos equipos son empleados también para la transformación de la energía en aplicaciones tales como motores y accionamientos. Existe una gran variedad de Convertidores Multinivel en el estado de la técnica, es así como la solicitud de patente CL 201202458, de fecha 04-09-2012, del inventor Ruiz Caballero Domingo Antonio, divulga un inversor multinivel híbrido reductor y/o elevador de tensión para aplicaciones en donde la tensión continua de entrada sea de bajo valor o de gran variación. El documento de patente EP20050405463, de fecha 07-02-2007, de los inventores Stefanutti Philippe; Zueger Harry; Hugo Nicolás; Dormía Georges; Descollaz Bernard, titulado "Transformer arrangement and multilevel converter", describe un convertidor multinivel, con dos niveles de convertidor (N=2), incluyendo cada nivel un convertidor primario conectado a un devanado primario de una unidad de transformador, un convertidor secundario conectado a un devanado secundario de la unidad de transformador y una estructura de núcleo de transformador que define un recorrido de flujo magnético cerrado para acoplar magnéticamente el devanado primario y secundario. El convertidor se caracteriza porque las estructuras del núcleo del transformador de una primera y segunda unidad del transformador forman un núcleo compartido con un retorno definiendo una sección compartida de los respectivos recorridos de flujo magnético cerrados de la unidad de transformador primario y secundario. El documento de patente US6697271 B2 de fecha 24-02-2004, del inventor Corzine Keith Alien, titulado "CASCADED MULTI-LEVEL H-BRIDGE DRIVE", describe un inversor de múltiples niveles que se construye conectando en cascada varios niveles de inversores con puente H, y proporciona diferentes entradas de tensión a los convertidores multinivel adicionales. Los valores de tensión se seleccionan con el fin de proporcionar un mayor número de niveles de salida. Esta disposición puede proporcionar hasta quince niveles de salida si se utilizan fuentes de tensión regenerativos y hasta once niveles de salida si se utiliza una fuente de tensión no renovable. El documento de solicitud de patente US201313955607, de fecha 31 -07-2013, de los inventores Andrew Alien Rockhill, Di Zhang, Luis José Garcés, titulado "Multilevel converter system", describe un convertidor de potencia que incluye al menos una fase con una pluralidad de unidades de conmutación, donde dichas unidades de conmutación están acopladas entre sí de una manera que al menos dos unidades de conmutación tienen diferentes tensiones de funcionamiento. El documento solicitud de patente WO2015131931 , de fecha 1 1 -09-2015, de los inventores Amel Lachichi; Frans Dijkhuizen; Mats Hyttinen; Muhammad Nawaz; Nan Chen, titulado "MULTILEVEL CONVERTER", divulga un convertidor multinivel que comprende un módulo de medio puente que tiene una unidad de condensadores y al menos dos interruptores, una unidad de puerta configurada para controlar los interruptores, un conductor eléctrico, al menos una primera y segunda porción terminal y una subcelda. El documento solicitud de patente WO2015041691 de fecha 26-03-2015, de los inventores Fan Shengfang; Xue Yaosuo, titulado "A NEW FOUR-LEVEL CONVERTER CELL TOPOLOGY FOR CASCADED MODULAR MULTILEVEL CONVERTERS", divulga un convertidor multinivel modular en cascada que tiene una pluralidad de convertidores de 4 niveles, donde cada fase AC genera las formas de onda de tensión de niveles múltiples compuestos de diferentes salida. Cada módulo es una fuente de tensión controlada. El número de niveles de tensión en el convertidor en cascada se determina por el número de módulos en cada fase y los niveles de tensión generados por cada módulo. Uno de los principales problemas que presentan hoy en día todos estos convertidores multinivel son su tamaño, peso y costo, los cuales limitan la accesibilidad y maniobrabilidad de los mismos. Esta problemática abre la posibilidad de introducir una nueva topología capaz de reducir su volumen, la cantidad de componentes empleados, el costo asociado y las pérdidas involucradas. BREVE DESCRIPCIÓN DE LAS FIGURAS La figura 1 muestra un convertidor trifásico conformado por dos celdas básicas de la presente invención. La figura 2A (Arte Previo) muestra un convertidor comercial back-to-back de 3 niveles. La figura 2B muestra el convertidor de la presente invención para el caso de 3 niveles y 6 fases, 3 de entrada y 3 de salida, lo que permite tener una conexión back-to-back. DESCRIPCIÓN DETALLADA DE LA INVENCIÓN La presente invención divulga un convertidor multinivel para realizar la conversión de energía eléctrica operando con menor cantidad de componentes ahorrando costos, pérdidas, tamaño y peso, permitiendo la reducción de volumen y la accesibilidad a la transformación de energía eléctrica para la utilización en diversa aplicaciones El convertidor multinivel de la presente invención comprende una celda básica formada por un condensador y tres interruptores de potencia (IGBT o MOSFET), cada celda aporta un nivel adicional a la salida. La salida del convertidor se genera a través de la conexión de dos interruptores de potencia por fase. Como muestra la figura 1 , las celdas básicas (1 1 ' y 1 1 ) están conectadas en cascada, donde cada calda básica (1 1 ' y 1 1 ) está formada por: a) un interruptor de potencia (S4 , St) que interconecta el bus positivo entre las celdas básicas (1 1 ', 1 1 ) en serie contiguas y/o entre una celda básica (1 1 ') y una fuente de tensión continua (representada por C3); b) un interruptor de potencia (S6 , S2) que interconecta el bus negativo entre las celdas básicas (1 1 ', 1 1 ) en serie contiguas y/o entre una celda básica (1 1 ') y la fuente de tensión continua del punto anterior (representada por C3); y c) un condensador (C1 , C2) con un interruptor de potencia (S5, S3) en serie conectados entre el bus positivo y el negativo. La salida (12) de cada fase del convertidor (1 ) se obtiene en el punto medio de dos interruptores de potencia conectados en serie entre sí y en paralelo entre el polo positivo y negativo de la última celda básica del convertidor. Así se tienen dos primeros interruptores de potencia (S7, S7) conectados en serie para la fase de salida A, dos segundos interruptores de potencia (S8, S8) conectados en serie para la fase de salida B y dos terceros interruptores de potencia (S9, S9) conectados en serie para la fase de salida C. Todos estos interruptores de potencia están conectados en paralelo a la última celda básica que posea el convertidor multinivel de la presente invención. La cantidad de niveles generados a la salida del convertidor viene dada por la ecuación: Nn = Nc + 2 Donde Nn corresponde al número de niveles obtenidos y Nc al número de celdas básicas que conforman el convertidor. Por lo tanto, cada celda básica conectada aporta un nivel adicional a la salida. La cantidad de niveles de tensión generados es independiente de la cantidad de salidas empleadas, ya sea para 1 fase, 3 fases, 6 fases o fases. Se requieren únicamente 3 celdas básicas conectadas en serie para tener 5 niveles de tensión en cada una de las fases de salida independiente del número que sean, lo único que varía al variar el número de fases de salida es la cantidad de interruptores de potencia en serie conectados en paralelo a la última celda básica conectada. La figura 1 muestra el detalle de la celda básica y de la configuración para tres salidas independientes (A, B, C) (convertidor trifásico). Dado que en este caso el convertidor está conformado por dos celdas básicas Nc = 2 la cantidad de niveles obtenidos en cada una de las fases corresponde a Nn = 4. El condensador C3 en la topología mostrada es el enlace de continua, el convertidor realiza la conversión de energía alterna a continua y viceversa. La figura 2A muestra dos convertidores comerciales de condensadores flotantes de tres niveles de tensión a una primera salida (21 ) y a una segunda salida (22). Cada uno de estos convertidores es idéntico al otro y poseen tres fases de salida: A, B, C en la primera salida (21 ) y U, V, W en la segunda salida (22), este tipo de configuración es conocida como conexión back-to-back (espalda con espalda), pues ambos convertidores están conectados a través del enlace de continua. En la figura 2A, este enlace de tensión continua se encuentra representado por el condensador C2. El convertidor de condensador flotante está compuesto por una celda básica (23) que se conforma con dos interruptores de potencia y un condensador. Finalmente la salida de cada fase está conformada por dos interruptores de potencia. En total, para una configuración back-to-back de un convertidor de condensadores flotantes de 3 niveles de tensión se requiere un total de 24 interruptores de potencia y 6 condensadores más el condensador de enlace de continua. La figura 2B muestra la topología de la presente invención en una configuración back- to-back con tres niveles de tensión a la salida de cada fase, tal como el convertidor de la figura 2A. Las salidas A, B, C en la primera salida (25) corresponden a las mismas tres fases mostradas en la primera salida (21 ) de la figura 2A, mientras que las salidas U, V, W en la segunda salida (26) corresponden a las tres fases mostradas en la segunda salida (22) de la figura 2A. La presente invención requiere de una celda básica (24) para generar tres niveles de tensión en cada salida del convertidor, tal como el convertidor de condensador flotante (23) de la figura 2A, la diferencia es que la invención propuesta solo requiere una celda, independiente de la cantidad de fases de salida requeridas, tal como se muestra en la figura 2B, mientras que la topología comercial requiere una celda por cada fase de salida (21 , 22). El condensador C2 de la figura 2B corresponde al condensador de enlace de continua entre la entrada A, B, C y la salida U, V, W. La tabla 2 muestra una comparación numérica de la cantidad de componentes para diversas topologías multinivel actualmente en el mercado y la propuesta de la presente invención. Tabla 2: Tabla comparativa de convertidores con 6 fases de salida (back-to-back) [EN US11018600B2]: RELATED APPLICATION This application Is a national phase entry under 35 USC 371 of International Patent Application No.: PCT/CL2017/050053 filed on 20 Sep. 2017, which claims priority from Chilean Application No. 2365-2016 filed on 20 Sep. 2016, the disclosures of which are incorporated in their entirety by reference herein. SCOPE The present invention refers to the conversion of electrical energy operating with fewer components, saving costs, losses, size and weight, allowing volume reduction and accessibility to the transformation of electrical energy for use in different applications, more specifically to a Multilevel Converter for the control and transformation of electrical energy within the scope of power electronics. DESCRIPTION OF PRIOR ART The technological development experienced by all areas of our society in the last forty years is mostly due to the progress made in power electronics. This branch of technology is responsible for transforming the different modes of use of electric power to adapt it to multiple applications such as speed control of electric motors, operation of household appliances (household appliances, computers, etc.), communications equipment, control of industrial processes and equipment, as well as in the field of generation, transport, distribution and storage of electrical energy. In our current society, electric power is a fundamental pillar in the different activities developed every day, both the use and transport of it. The nature of electric power imposes a number of requirements for its production and transport that are very different from other types of energy. Parameters such as voltage, the signal form, frequency and power factor are subject to certain limits in order to guarantee the stability of the network and the correct supply of electricity at points of consumption. The way of generating electrical energy, however, is not uniform and each energy source produces it in a particular way, presenting a wide variety of values for the different parameters mentioned above. The alternating-direct electronic converters (AC/DC) that feed the transport lines under high voltage direct and alternating current (HVDC and HVAC) and the direct-direct converters (DC/DC) that adapt the voltage of the batteries to the different microelectronic circuits (electric cars) are clear examples of application where a transformation of electrical energy with the highest possible output is required. An energy converter is an electronic equipment or system that aims to convert electrical energy between two different formats, as for example, obtaining direct current from alternating current. The initial concept of the converter can extend to include such aspects such as: efficiency, reversibility, ideality degree, reliability, volume or technology, as the most important. The converters can be classified according to different criteria. One of the most commonly used is to group them according to the format of the input and output energies. Basically and according to this criterion four large groups can be established: AC/AC converters.AC/DC converters or rectifiers.DC/DC converters.DC/AC converters or inverters. The transmission of electrical energy requires in its points of connection and distribution, of equipment that transform the energy from one medium to another. Said equipment, being called Power Converters, have been widely developed and studied, those that allow the generation of multilevel voltage at the output being currently used. The multilevel converters include an array of power semiconductors and capacitors as voltage sources; the voltage generated at the output has stepped wave form considering that the switches close and open at different times; depending on the number of power switches the voltage at the output grows adding the voltage of the capacitors, while the power switches support reduced voltages. Multi-level converters with voltage fed have emerged as a new converter option for high power applications. There are different topologies of multilevel converters; however, they can be classified into three basic structures: Diode-Clamped Converter or NPC (Neutral Point Clamped Converter)).Flying Capacitor Multilevel Converter.Cascade Full-Bridge Multilevel Converter). TABLE 1 Advantages and Disadvantages of Multilevel Converters TYPE OF CONVERTER ADVANTAGES DISADVANTAGES NPC Low content of harmonics Too much claimed converters Highly efficient converter Flow of actual power had to control Simple control method Depending on the way direct voltage is Obtained. unbalances can produce among capacitors Flying Capacitor The modular technology allows Excess number of capacitors increasing the number of levels at the output in a simple way Extra switching combination to The Converter control is balance the levels of voltage complex when ensuring the right balance of capacitors Control of actual and active power Cascade Full-Bridge Fewer number of componentes Independent DC sources are Redesigning the power stage is necessary for each cell not necessary The semiconductor devices handle only the voltage present in a DC source The main advantage of multilevel converters is the reduction of harmonic components in the electrical variables. Such equipment is also used for the transformation of energy in such applications as motors and drives. There is a wide variety of Multilevel Converters in the state of the art. This is how the patent application CL 201202458, dated Sep. 4, 2012, of the inventor Ruiz Caballero Domingo Antonio, discloses a hybrid inverter multilevel reducer and or voltage booster for applications wherein the continuous voltage input being of a low value or with a great variation. The patent document EP20050405463, dated Feb. 7, 2007, from the inventors Stefanutti Philippe; Zueger Harry; Hugo Nicolas; Dormia Georges; Descollaz Bernard, entitled “Transformer arrangement and multilevel converter”, describes a multilevel converter, with two converter levels (N=2), with each level including a primary converter connected to a primary winding of a transformer unit, a secondary converter connected to a secondary winding of the transformer unit, and a transformer core structure defining a closed magnetic flux path for magnetically coupling the primary and secondary windings. The converter is characterized in that the transformer core structures of a first and second transformer unit form a shared core with a return defining a shared section of the respective closed magnetic flux paths of the primary and secondary transformer unit. The patent document U.S. Pat. No. 6,697,271 B2 dated Feb. 24, 2004, from the inventor Corzine Keith Allen, entitled “CASCADED MULTI-LEVEL H-BRIDGE DRIVE”, describes a multi-level inverter that is constructed by cascading several levels of H bridge inverters, and provides different voltage inputs to the additional multilevel converters. The voltage values are selected in order to provide a greater number of output levels. This arrangement can provide up to fifteen output levels if regenerative voltage sources and up to eleven output levels are used if a non-renewable voltage source is used. The patent application document US201313955607, dated Jul. 31, 2013, from the inventors Andrew Allen Rockhill, Di Zhang, Luis Jose Garces, entitled “Multilevel converter system”, describes a power converter including at least one phase with a plurality of switching units, wherein said switching units are coupled together in such a way that at least two switching units have different operating voltages. The patent application document WO2015131931, dated Sep. 11, 2015, from the inventors Amel Lachichi; Frans Dijkhuizen; Mats Hytlinen; Muhammad Nawaz; Nan Chen, entitled “MULTILEVEL CONVERTER”, discloses a multilevel converter comprising a half-bridge module having a capacitor unit and at least two switches, a door unit configured to control the switches, an electrical conductor, at least one first and second terminal portion and a subcell. The patent application WO2015041691 dated Mar. 26, 2015, from the inventors Fan Shengfang; Xue Yaosuo, entitled “A NEW FOUR-LEVEL CONVERTER CELL TOPOLOGY FOR CASCADED MODULAR MULTILEVEL CONVERTERS”, discloses a cascaded modular multi-level converter having a plurality of 4-level converters, where each AC phase generates voltage waveforms of compound multiple levels with different output. Each module is a controlled voltage source. The number of voltage levels in the cascaded converter is determined by the number of modules in each phase and the voltage levels generated by each module. In addition, the JP 2014064431 document discloses a multilevel power conversion apparatus for generating an alternating current output converted from a DC voltage source into a plurality of voltage levels. To this effect, a circuit is proposed with first basic cells, where—in each cell—a switching element, a flying capacitor and a switching element are connected sequentially in series between positive and negative electrodes of continuous voltage sources. As for the expansion circuits, a second basic cell is connected in parallel with the flying capacitor of each first basic ceil and a second additional basic cell is connected in parallel with a flying capacitor of the second basic cell until a certain number of times to connect the same number of second basic cells. Each phase module has a switching element between each input terminal and an output terminal, and selectively control the switching element (on/off) to generate a potential of any input terminal from the output terminal. One of the current main problems of all these multilevel converters is their size, weight and cost, which limit their accessibility and maneuverability. In particular and from the aforementioned JP 2014064431 document. It is observed that the desired amount of voltage levels exclusively depends on the number of outputs used. Therefore, disadvantageously, independent sets of components for each output are required. That is, the basic cells cannot operate in two phases simultaneously without the need to repeat the set of components for each output, which implies having a large physical space to accommodate these components. This problem opens up the possibility of introducing a new topology capable of reducing its volume, the number of components used, the associated cost and the losses involved. BRIEF DESCRIPTION OF THE FIGURES FIG. 1 shows a three-phase converter formed by two basic cells of the present invention. FIG. 2A (Prior Art) shows a 3-level commercial back-to-back converter. FIG. 2B shows the converter of the present invention for the case of 3 levels and 6 phases, 3 inputs and 3 outputs, which allows having a back-to-back connection. DETAILED DESCRIPTION OF THE INVENTION The present invention discloses a multilevel converter to perform the conversion of electrical energy operating with fewer components saving costs, losses, size and weight, allowing the reduction of volume and accessibility to the transformation of electric power for use in various applications The multilevel converter of the present invention comprises a basic cell formed by a capacitor and three power switches (IGBT or MOSFET), each cell providing an additional level to the output. The output of the converter is generated through the connection of two power switches per phase. As shown in FIG. 1, the basic cells (11′ and 11) are connected in cascade, wherein each basic cell (11′ and 11) is formed by: a) a power switch (S4, S1) that interconnects the positive bus between the basic cells (11′, 11) in contiguous series and/or between a basic cell (11′) and a continuous voltage source (represented by VDC);b) a power switch (S6, S2) that interconnects the negative bus between the basic ceils (11′, 11) in contiguous series and/or between a basic cell (11′) and the continuous voltage source of the previous point (represented by VDC); andc) a capacitor (C1, C2) with a power switch (S5, S3) connected in series between the positive and negative bus. The output (12) of each phase of the converter (1) is obtained at the midpoint of two power switches connected in series with each other and in parallel between the positive and negative pole of the last basic cell of the converter. So, there are two first power switches (S7, S7) connected in series for the output phase A, two second power switches (S8, S8) connected in series for the output stage B and two third power switches (S9, S9) connected in series for the output phase C. All these power switches are connected in parallel to the last basic cell that has the multilevel converter of the present invention. The number of levels generated at the output of the converter is given by the equation: Nn=Nc+2 Wherein Nn corresponds to the number of levels obtained and Nc to the number of basic cells that form the converter. Therefore, each connected basic cell brings an additional level to the output. The number of voltage levels generated is independent of the number of outputs used, whether for 1 phase, 3 phases, 6 phases or Nf phases. Only 3 basic cells connected in series are required to have 5 voltage levels in each of the output phases regardless of the number they are; the only thing that varies with changing the number of output phases is the number of power switches in series connected in parallel to the last connected basic cell. FIG. 1 shows the detail of the basic cell and the configuration for three independent outputs (A, B, C) (three-phase converter). Since in this case the converter is made up of two basic cells Nc=2, the number of levels obtained in each of the phases corresponds to Nn=4. The capacitor C3 in the topology shown is the continuous link, the converter performing the conversion of alternate to continuous power and vice versa. FIG. 2A shows two commercial converters of floating capacitors of three voltage levels to a first output (21) and a second output (22). Each of these converters is identical to the other and has three output phases: A, B, C on the first output (21) and U, V, W on the second output (22); this type of configuration: is known as a back-to-back connection, since both converters are connected through the continuous link. In FIG. 2A, this continuous voltage link is represented by the VDC capacitor. The floating capacitor converter is composed of a basic cell (23) that is formed by two power switches and a capacitor. Finally, the output of each phase is made up of two power switches. In total, tor a back-to-back configuration of a floating capacitor converter with 3 voltage levels, a total of 24 power switches and 6 capacitors plus the continuous link capacitor are required. FIG. 2B shows the topology of the present invention in a back-to-back configuration with three voltage levels at the output of each phase, such as the converter of FIG. 2A. The outputs A, B, C in the first output (25) correspond to the same three phases shown in the first output (21) of FIG. 2A, while the outputs U, V, W in the second output (26) correspond to the thre
[ZH CN212726884U]: 一种模块化多电平换流器及换流站 [EN CN212726884U]: Modular multilevel converter and converter station | [ZH CN212726884U]: 本实用新型公开了一种模块化多电平换流器及换流站，所述模块化多电平换流器包括三相桥臂，每相桥臂包括上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联的换流器子模块，所述换流器子模块包括第一全控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中，所述第一全控型开关模块和第二全控型开关模块串联形成开关支路；所述开关支路、缓冲电路和第一电容相互并联；所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联的第一二极管。换流器中设有IGCT器件，实现了将换流器和负荷开关集成于一个换流站中，减小了换流站的体积和成本，实现换流站高度集成化，使得换流站可靠性高，且能广泛的应用到柔性直流输电系统中。 [EN CN212726884U]: The utility model discloses a modularized multi-level converter and a converter station, the modularized multi-level converter comprises a three-phase bridge arm, each phase bridge arm comprises an upper bridge arm and a lower bridge arm, the upper bridge arm and the lower bridge arm are provided with a plurality of cascaded converter sub-modules, and each cascaded converter sub-module is providedwith a plurality of cascaded converter sub-modules. Wherein the converter sub-module comprises a first full-control type switch module, a second full-control type switch module, a buffer circuit anda first capacitor, and the first full-control type switch module and the second full-control type switch module are connected in series to form a switch branch; the switch branch, the buffer circuit and the first capacitor are connected in parallel; each of the first full-control type switch module and the second full-control type switch module comprises an IGCT device and a first diode which is in anti-parallel connection with the IGCT device. The converter is internally provided with the IGCT device, the converter and the load switch are integrated in one converter station, the size and costof the converter station are reduced, high integration of the converter station is achieved, the reliability of the converter station is high, and the converter station can be widely applied to a flexible direct-current power transmission system. | CN212726884U | 2021-03-16 | CN202021597091U | 2020-08-04 | CN202021597091U, 2020-08-04 | CN212726884U: 2021-03-16 | CHINA THREE GORGES CORP UNIV TSINGHUA | ZENG RONG GUO MINGZHU ZHAO BIAO TANG BOJIN XU CHAOQUN ZHAI DONGLING YU ZHANQING SONG QIANG QU LU | H02M7/483: I H02M7/521: I |  |  |  | [ZH CN212726884U]: 1 .一种模块化多电平换流器，包括三相桥臂，每相桥臂包括上桥臂和下桥臂，所述上桥 臂和下桥臂设置有多个级联的换流器子模块，其特征在于，所述换流器子模块包括第一全 控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中， 所述第一全控型开关模块和第二全控型开关模块串联形成开关支路； 所述开关支路、缓冲电路和第一电容相互并联； 所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联的第 一二极管。 2 .根据权利要求1所述的模块化多电平换流器，其特征在于，所述第二全控型开关模块 并联在所述换流器子模块的输出端。 3 .根据权利要求2所述的模块化多电平换流器，其特征在于，所述换流器子模块中第一 全控型开关模块中的IGCT器件的阴极与第二全控型开关模块中的IGCT器件的阳极连接。 4 .根据权利要求1-3任一所述的模块化多电平换流器，其特征在于，所述缓冲电路包括 第一电感、第一电阻、第二二极管和第二电容，其中， 所述第一电感的第一端与分别与所述第一电容的第一端和第一电阻的第一端连接，其 第二端分别与第一全控型开关模块和第二二极管的正极连接； 第二二极管的负极分别与第一电阻的第二端和第二电容的第一端连接； 第二电容的第二端分别与第二全控型开关模块和第一电容的第二端连接。 5 .一种换流站，其特征在于，包括权利要求1所述的模块化多电平换流器、负荷开关和 第一电抗器，其中， 所述模块化多电平换流器与所述负荷开关的一端连接； 所述负荷开关的另一端与所述第一电抗器的一端连接。 6 .根据权利要求5所述的换流站，其特征在于，所述模块化多电平换流器还包括直流侧 和交流侧，其中， 所述模块化多电平换流器的直流侧正极通过依次连接负荷开关和第一电抗器后与直 流线路连接； 所述模块化多电平换流器的交流侧与交流电网连接。 7 .根据权利要求6所述的换流站，其特征在于，模块化多电平换流器中所有第一全控型 开关模块和第二全控型开关模块中的IGCT器件，用于在直流线路发生短路故障时，通过控 制第一全控型开关模块中的IGCT器件闭锁，第二全控型开关模块的IGCT器件导通，令交流 电网处于三相短路状态以及直流线路的直流端口电势为零，最终令故障电流停止上升。 8 .根据权利要求7所述的换流站，其特征在于，所述第一电抗器为平波电抗器。 9 .根据权利要求8所述的换流站，其特征在于，所述负荷开关为额定负荷开关，用于在 直流线路的故障电流达到负荷开关的额定电流值时，进行分闸切断故障电流。 10 .根据权利要求9所述的换流站，其特征在于，所述额定负荷开关为机械式负荷开关、 电子式负荷开关或混合式负荷开关。 [EN CN212726884U]: 1 A modular multi-level converter, comprising a three-phase bridge arm, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper bridge arm and the lower bridge arm are provided with a plurality of cascaded converters The sub-module is characterized in that the converter sub-module includes a first full-control switch module, a second full-control switch module, a buffer circuit and a first capacitor, wherein the first full-control switch module and The second full control switch module is connected in series to form a switch branch; the switch branch, the buffer circuit, and the first capacitor are connected in parallel with each other; the first full control switch module and the second full control switch module both include an IGCT device and The first diode in anti-parallel with it. 2 The modular multi-level converter according to claim 1, wherein the second fully-controlled switch module is connected in parallel to the output end of the converter sub-module. 3 The modular multilevel converter according to claim 2, wherein the cathode of the IGCT device in the first fully-controlled switch module in the converter sub-module and the second fully-controlled switch module The anode connection of the IGCT device in. 4 The modular multilevel converter according to any one of claims 1-3, wherein the buffer circuit includes a first inductor, a first resistor, a second diode, and a second capacitor, wherein: The first end of the first inductor is connected to the first end of the first capacitor and the first end of the first resistor, and the second end of the first inductor is connected to the first fully-controlled switch module and the second diode respectively. The cathode of the second diode is connected to the second end of the first resistor and the first end of the second capacitor respectively; the second end of the second capacitor is connected to the second fully-controlled switch module and the first capacitor, respectively The second end of the connection. 5 A converter station, characterized by comprising the modular multilevel converter, load switch and first reactor of claim 1, wherein the modular multilevel converter and the One end of the load switch is connected; the other end of the load switch is connected to one end of the first reactor. 6 The converter station according to claim 5, wherein the modular multilevel converter further comprises a DC side and an AC side, wherein the DC side anode of the modular multilevel converter The load switch and the first reactor are connected in sequence and then connected to the DC line; the AC side of the modular multilevel converter is connected to the AC power grid. 7 The converter station according to claim 6, characterized in that all the IGCT devices in the first full-control switch module and the second full-control switch module in the modular multilevel converter are used in direct current When a short-circuit fault occurs on the line, by controlling the IGCT device in the first full-control switch module to block, the IGCT device of the second full-control switch module is turned on, so that the AC power grid is in a three-phase short-circuit state and the DC port potential of the DC line is Zero, eventually stopping the fault current from rising. 8 The converter station of claim 7, wherein the first reactor is a smoothing reactor. 9 The converter station according to claim 8, wherein the load switch is a rated load switch, which is used to switch off the fault current when the fault current of the DC line reaches the rated current value of the load switch. 10 The converter station according to claim 9, wherein the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. | [ZH CN212726884U]: 一种模块化多电平换流器及换流站 技术领域 [0001]本实用新型属于电力输电领域，特别涉及一种模块化多电平换流器及换流站。 背景技术 [0002]柔性直流输电已经成为目前最有潜质的新型电力传输方式，并且已经在大容量输 电系统中得到了应用。模块化多电平换流器是目前最为主流的拓扑结构。现已投运的柔性 直流输电工程多是采用基于IGBT（Insulated Gate Bipolar Transistor：绝缘栅双极型晶 体管）的模块化多电平换流器，但是在直流故障清除方面有很大的实现困难，往往在直流短 路故障发生时会产生极大的直流短路故障电流，为此需要分断直流短路故障电流，需要极 大分断电流能力的直流断路器，此类直流断路器的造价高且体积非常巨大。因此，如图1所 示，换流站采用的是基于IGBT的模块化多电平换流器，且将换流器和断路器分别置于两个 独立的换流站中。 [0003]从而如何提供一种模块化多电平换流器以及能够实现换流站集成换流和开关一 体化的功能越来越成为亟待解决的技术问题。 实用新型内容 [0004]针对上述问题，本实用新型提供一种模块化多电平换流器及换流站，提高换流器 的可靠性以及实现了换流站集成换流和开关一体化的功能。 [0005]本实用新型的目的在于提供一种模块化多电平换流器，包括三相桥臂，每相桥臂 包括上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联的换流器子模块，所述换流器 子模块包括第一全控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中， [0006]所述第一全控型开关模块和第二全控型开关模块串联形成开关支路； [0007]所述开关支路、缓冲电路和第一电容相互并联； [0008]所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联 的第一二极管。 [0009]进一步地，所述第二全控型开关模块并联在所述换流器子模块的输出端。 [0010]进一步地，所述换流器子模块中第一全控型开关模块中的IGCT器件的阴极与第二 全控型开关模块中的IGCT器件的阳极连接。 [0011]进一步地，所述缓冲电路包括第一电感、第一电阻、第二二极管和第二电容，其中， [0012] 所述第一电感的第一端与分别与所述第一电容的第一端和第一电阻的第一端连 接，其第二端分别与第一全控型开关模块和第二二极管的正极连接； [0013]第二二极管的负极分别与第一电阻的第二端和第二电容的第一端连接； [0014]第二电容的第二端分别与第二全控型开关模块和第一电容的第二端连接。 [0015]本实用新型的另一目的在于提供一种换流站，包括上述所述的模块化多电平换流 器、负荷开关和第一电抗器，其中， [0016]所述模块化多电平换流器与所述负荷开关的一端连接； [0017] 所述负荷开关的另一端与所述第一电抗器的一端连接。 [0018] 进一步地，所述模块化多电平换流器还包括直流侧和交流侧，其中， [0019]所述模块化多电平换流器的直流侧正极通过依次连接负荷开关和第一电抗器后 与直流线路连接； [0020]所述模块化多电平换流器的交流侧与交流电网连接。 [0021]进一步地，模块化多电平换流器中所有第一全控型开关模块和第二全控型开关模 块中的IGCT器件，用于在直流线路发生短路故障时，通过控制第一全控型开关模块中的 IGCT器件闭锁，第二全控型开关模块的IGCT器件导通，令交流电网处于三相短路状态以及 直流线路的直流端口电势为零，最终令故障电流停止上升。 [0022] 进一步地，所述第一电抗器为平波电抗器。 [0023]进一步地，所述负荷开关为额定负荷开关，用于在直流线路的故障电流达到负荷 开关的额定电流值时，进行分闸切断故障电流。 [0024]进一步地，所述额定负荷开关为机械式负荷开关、电子式负荷开关或混合式负荷 开关。 [0025]本实用新型中的所述模块化多电平换流器中的第一全控型开关模块和第二全控 型开关模块均采用了IGCT器件，相比于IGBT，由于IGCT具有非常高的浪涌电流承受能力、通 态电流能力、正向阻断电压能力以及可靠性，并且还具有非常低的通态压降，从而使得模块 化多电平换流器具有电流大、阻断电压高、可靠性高、结构紧凑以及低导通损耗等优点。 [0026]进一步，换流站能够将模块化多电平换流器和负荷开关集成于一个站中，大幅减 小了换流站整体的体积和成本，实现了高度集成化和很高的经济性，可以在未来的柔性直 流输电系统中得到广泛的应用。 [0027] 此外，由于通过控制第一全控型开关模块中的IGCT器件闭锁，第二全控型开关模 块的IGCT器件导通，能够有效地令故障电流停止上升，从而负荷开关仅需要分断额定电流 大小的直流电流，从而也大幅减小了负荷开关所需的体积、用量和成本。且换流站中只需要 平波电抗器，平波电抗器电感值小，不需要考虑限流功能。 [0028]本实用新型的其它特征和优点将在随后的中阐述，并且，部分地从 中变得显而易见，或者通过实施本实用新型而了解。本实用新型的目的和其他优点可通过 在、权利要求书以及附图中所指出的结构来实现和获得。 附图说明 [0029]为了更清楚地说明本实用新型实施例或现有技术中的技术方案，下面将对实施例 或现有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图是本 实用新型的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动的前提下，还 可以根据这些附图获得其他的附图。 [0030]图1示出了现有技术中的一种换流站和断路器的结构示意图； [0031]图2示出了本实用新型实施例中的一种模块化多电平换流器的结构示意图； [0032]图3示出了本实用新型实施例中的一种换流站的结构示意图； [0033]图4示出了本实用新型实施例中的换流站中UMMC、UDC和iDC在控制过程中的变化曲 线图。 具体实施方式 [0034]为使本实用新型实施例的目的、技术方案和优点更加清楚，下面将结合本实用新 型实施例中的附图，对本实用新型实施例中的技术方案进行清楚、完整地说明，显然，所描 述的实施例是本实用新型一部分实施例，而不是全部的实施例。基于本实用新型中的实施 例，本领域普通技术人员在没有做出创造性劳动前提下所获得的所有其他实施例，都属于 本实用新型保护的范围。 [0035]如图2所示，本实用新型实施例中介绍了一种模块化多电平换流器，包括三相桥 臂，每相桥臂包括上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联换流器子模块，其 中，每相桥臂的上桥臂中的换流器子模块分别为n个，在图2中分别为：SMap1、SMap2…… SMapn，SMbp1、SMbp2……SMbpn，SMcp1、SMcp2 , 模块分别为n个，在图2中分别为:SMan1、SMan2 SMcpn。每相桥臂的下桥臂中的换流器子 SMann,SMbn1、SMbn2 SMbpnn,SMcn1、 SMcn2……SMcnn。进一步，所述换流器子模块包括第一全控型开关模块、第二全控型开关模 块、缓冲电路和第一电容。所述第一全控型开关模块包括IGCT（integrated Gate Commutated Thyristors：集成门极换流晶闸管）器件Sxi1及与其反并联的第一二极管Dxi1； 所述第二全控型开关模块包括IGCT器件Sxi2及与其反并联的第一二极管Dxi2；且所述第一全 控型开关模块和第二全控型开关模块串联形成开关支路;所述开关支路、缓冲电路和第一 电容Cxi相互并联。进一步，所述第一全控型开关模块和第二全控型开关模块串联时，所述 IGCT器件Sxi^IGCT器件Sxi2方向相同，即所述IGCT器件Sxi1的阴极与所述IGCT器件Sxi2的阳 极连接。所述模块化多电平换流器中的第一全控型开关模块和第二全控型开关模块均采用 了IGCT器件，相比于IGBT，由于IGCT具有非常高的浪涌电流承受能力、通态电流能力、正向 阻断电压能力以及可靠性，并且还具有非常低的通态压降，从而使得模块化多电平换流器 具有电流大、阻断电压高、可靠性高、结构紧凑以及低导通损耗等优点。 [0036]本实施例中，每个与IGCT器件反并联的第一二极管能够有效对故障电流进行反向 截止，从而保护所述IGCT器件。 [0037]进一步具体的，如图2所示，所述第二全控型开关模块并联在所述换流器子模块的 输出端，上桥臂和下桥臂上的多个换流器子模块均通过各自的输出端实现连接。进一步，所 述缓冲电路包括第一电感Lxis、第一电阻Rxis、第二二极管Dxis和第二电容Cxis，其中，所述第 一电感Lxis的第一端与分别与所述第一电容Cxi的第一端和第一电阻Rxis的第一端连接，其第 二端分别与第一全控型开关模块和第二二极管Dxis的正极连接;第二二极管的负极分别与 第一电阻Rxis的第二端和第二电容Cxis的第一端连接;第二电容Cxis的第二端分别与第二全 控型开关模块和第一电容Cxi的第二端连接。第一电容Cxi的第一端为正极，第二端为负极， 且电压采用Vc表示。采用缓冲电路，在模块化多电平换流器正常工作时，能够有效地抑制第 一全控型开关模块和/或第二全控型开关模块上电流或者电压的上升率。而模块化多电平 换流器工作在直流线路短路故障状态下时，由于采取了第一全控型开关模块中的IGCT器件 闭锁，第二全控型开关模块的IGCT器件导通的方法，所述缓冲电路在故障处理时处于旁路 状态。 [0038] 示出） [0039] 本实施例中，所述每相桥臂的上桥臂和下桥臂上还设置有第二电抗器（图2-3中未 且与相应桥臂上级联的多个换流器子模块串联。 如图3所示，本实用新型实施例中还介绍了一种换流站，所述换流站包括上述所述 的模块化多电平换流器以及负荷开关和第一电抗器，其中，所述模块化多电平换流器包括 直流侧和交流侧;所述模块化多电平换流器直流侧的正极与所述负荷开关的一端连接，所 述负荷开关的另一端与所述第一电抗器的一端连接，所述第一电抗器的另一端与直流线路 连接。进一步，所述模块化多电平换流器的负极与所述第一电抗器的另一端形成所述换流 站的直流端口，即为换流站的直流端口，通过该直流端口，实现所述换流站与直流线路连 接。所述模块化多电平换流器的交流侧形成换流站的交流端口与交流电网连接。本实用新 型实施例中的将换流器和负荷开关集成于一个换流站中，大幅减小了换流站整体的体积和 成本，实现了高度集成化和很高的经济性，可以在未来的柔性直流输电系统中得到广泛的 应用。此外，将上述所述的模块化多电平换流器应用到换流站中，从而使得基于IGCT的换流 站在面对直流短路故障时，能够实现直流故障自清除的功能，且能够很好地限制直流短路 故障电流的上升。 [0040]图3中，所述负荷开关为额定负荷开关。用于在直流线路的故障电流达到负荷开关 的额定电流值时，进行分闸切断故障电流。由于通过控制第一全控型开关模块中的IGCT器 件闭锁，第二全控型开关模块的IGCT器件导通，能够有效地令故障电流停止上升。负荷开关 仅需要分断额定电流大小的直流电流即可，从而也大幅减小了负荷开关所需的体积、用量 和成本。进一步，所述额定负荷开关为机械式负荷开关、电子式负荷开关或混合式负荷开 关。所述第一电抗器为平波电抗器。由于上述所述的模块化多电平换流器能够直接限制直 流线路短路故障时故障电流的上升，因此，本实用新型实施例中的换流器不需要配备大电 感值的电抗器用于限流，仅将电抗器用于平波。从而本实用新型实施例中的第一电抗器的 电感值小，无需考虑限流功能。但对于基于IGBT-MMC （Modular Multilevel Converter：模 块化多电平变流器），由于其无法限制故障时故障电流的快速上升，为此需要配备大电感值 的电抗器，用于限流，同时还利用电抗器来平波。 [0041] 本实用新型实施例中还介绍了一种上述所述换流站的控制方法，所述控制方法的 控制过程具体包括以下步骤： [0042] 1）t0时刻：假定在t0时刻发生直流线路短路故障，直流线路短路故障导致的故障 电流开始快速上升。 [0043] 2）t1时刻:检测到短路故障发生且换流器子模块保护动作时刻。当检测到直流线 路短路故障后，模块化多电平变流器中所有换流器子模块中的第一全控型开关模块的IGCT 器件Sxi1闭锁，第二全控型开关模块的IGCT器件Sxi2导通。具体的，t0〜t1时间段的长度为直 流线路发生短路故障后的延时时间，其中，t0〜t1时间段的长度为0.3ms （毫秒）。 [0044]当直流线路发生短路故障后，换流站中模块化多电平变流器的所有换流器子模块 中的第一全控型开关模块的IGCT器件Sxi1闭锁，第二全控型开关模块的IGCT器件Sxi2导通, 从而使得模块化多电平换流器交流侧连接的交流电网处于三相短路状态，具体的，相当于 通过模块化多电平换流器所有桥臂上的第二电抗器三相短路，换流站直流端口电势相当于 零，同时，所述模块化多电平变流器直流侧的电势也为零，且此时故障电流停止上升。 [0045] 3）t2时刻：负荷开关切断故障电流时刻，此时通过负荷开关的直流线路短路故障 的故障电流达到最大值。t1〜t2时间段的长度为负荷开关接收到动作命令并分开开关的时 间，t1〜t2时间段的长度约为3ms。负荷开关切断之后，隔绝了直流线路和模块化多电平换 流器，所述故障电流开始衰减，且自此，直流线路开始去游离。进一步，所述故障电流的最大 值为负荷开关额定电流值。 [0046] 4)t3时刻:模块化多电平换流器中所有换流器子模块中的第二全控型开关模块的 IGCT器件Sxi2的闭锁时刻。在负荷开关分断完故障电流之后，已不需要再通过IGCT器件主动 短路来钳制模块化多电平换流器直流侧端口的电压。因此，IGCT器件可以在所处的每相桥 臂的电流过零点或者小电流时控制关断，结束交流电网的三相短路状态，t2〜t3时间段的 长度为控制模块化多电平换流器闭锁的时间，t2〜t3时间段的长度小于10ms。本实用新型 实施例中，所述小电流为每相桥臂上的电流不大于IGCT器件重复可关断电流的预设值，所 述IGCT器件重复可关断电流的预设值为IGCT的重复可关断电流最大能力，市场占有率最高 的四英寸IGCT器件的重复可关断电流最大能力可以为4.5kA(千安培)，但不限于4.5kA, 5kA、6kA等都适用于本实用新型。 [0047] 5)t4时刻：模块化多电平换流器解除闭锁的时刻，此时重新打开所有换流器子模 块中的IGCT器件，即令所有IGCT器件Sxi/旧GCT器件Sxi2导通。模块化多电平换流器由闭锁 状态慢慢恢复电压到正常运行状态。恢复所述电压的过程往往需要一到两个周波，共约 40ms的时间。但只需保证在负荷开关重合闸之前已经完成恢复起电压即可。所述电压为模 块化多电平换流器正常运行时的额定直流电压。 [0048] 6)t5时刻:控制负荷开关重合闸的时刻。此时模块化多电平换流器已经解锁，且恢 复到正常运行时的电压。t2〜t5时间段的长度为直流线路去游离的时间，从而，t2〜t5时间 段的长度约为300ms。 [0049] 7)t6时刻：负荷开关完成重合的时刻，模块化多电平换流器恢复向直流侧传输功 率。t5〜t6时间段的长度为负荷开关重合闸的时间，对于机械式负荷开关，t5〜t6时间段的 长度约为15〜20ms。 [0050]通过上述控制过程,模块化多电平换流器的电压UMMC以及直流线路直流端口的电 压UDC和电流iDC的变化如图4所示。且控制过程中，涉及的每个时间段的长度时间长度均有 效地说明对本实用新型实施例中的换流站能够快速的对直流线路短路故障进行处理和恢 复，且可靠性更高。 [0051]将设置有IGCT器件的模块化多电平换流器和负荷开关共同布置于一个换流站内， 使得结构更紧凑，使得换流站同时具备换流和开关的功能。 [0052]尽管参照前述实施例对本实用新型进行了详细的说明，本领域的普通技术人员应 当理解:其依然可以对前述各实施例所记载的技术方案进行修改，或者对其中部分技术特 征进行等同替换；而这些修改或者替换，并不使相应技术方案的本质脱离本实用新型各实 施例技术方案的精神和范围。 [EN CN212726884U]: A modular multilevel converter and converter station technical field [0001] The present utility model belongs to the field of power transmission, and particularly relates to a modular multi-level converter and a converter station. Background technique [0002] Flexible direct current transmission has become the most promising new power transmission method at present, and it has been applied in large-capacity power transmission systems. Modular multilevel converters are currently the most mainstream topology. Most of the flexible DC transmission projects that have been put into operation use modular multilevel converters based on IGBTs (Insulated Gate Bipolar Transistor), but there are great difficulties in achieving DC fault clearance. Often when a DC short-circuit fault occurs, a large DC short-circuit fault current will be generated. For this reason, it is necessary to break the DC short-circuit fault current, and a DC circuit breaker with a great breaking current capability is required. This type of DC circuit breaker is expensive and very large. Therefore, as shown in Figure 1, the converter station uses IGBT-based modular multi-level converters, and the converter and circuit breaker are placed in two independent converter stations. [0003] Therefore, how to provide a modular multi-level converter and the functions that can realize the integrated converter and switch integration of the converter station has increasingly become an urgent technical problem to be solved. Utility model content [0004] In view of the above-mentioned problems, the present invention provides a modular multilevel converter and converter station, which improves the reliability of the converter and realizes the functions of integrated converter and switch integration of the converter station. [0005] The purpose of the present utility model is to provide a modular multi-level converter, including three-phase bridge arms, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper bridge arm and the lower bridge arm are arranged There are a plurality of cascaded converter sub-modules, and the converter sub-modules include a first full-control switch module, a second full-control switch module, a buffer circuit and a first capacitor, wherein [0006] the The first full control switch module and the second full control switch module are connected in series to form a switch branch; [0007] The switch branch, the buffer circuit and the first capacitor are connected in parallel with each other; [0008] The first full control switch module and the second full control switch module both include an IGCT device and a first diode connected in anti-parallel with the IGCT device. [0009] Further, the second fully-controlled switch module is connected in parallel to the output end of the converter sub-module. [0010] Further, the cathode of the IGCT device in the first full control switch module in the converter sub-module is connected to the anode of the IGCT device in the second full control switch module. [0011] Further, the snubber circuit includes a first inductor, a first resistor, a second diode, and a second capacitor, wherein, [0012] the first terminal of the first inductor is connected to the first The first end of the capacitor is connected to the first end of the first resistor, and the second end of the capacitor is respectively connected to the first full-control switch module and the anode of the second diode; [0013] The cathode of the second diode is respectively connected to the second end of the first resistor and the first end of the second capacitor; [0014] The second end of the second capacitor is respectively connected to the second fully-controlled switch module and the second end of the first capacitor. [0015] Another object of the present invention is to provide a converter station, including the above-mentioned modular multilevel converter, load switch and first reactor, wherein, [0016] The modular multilevel converter is connected to one end of the load switch; [0017] The other end of the load switch is connected to one end of the first reactor. [0018] Further, the modular multilevel converter further includes a DC side and an AC side, wherein, [0019] The positive pole of the DC side of the modular multilevel converter is connected to the DC line by sequentially connecting the load switch and the first reactor; [0020] The AC side of the modular multilevel converter is connected to an AC power grid. [0021] Further, the IGCT devices in all the first fully-controlled switch modules and the second fully-controlled switch modules in the modular multilevel converter are used to control the first The IGCT device in the full-control switch module is blocked, and the IGCT device of the second full-control switch module is turned on, so that the AC grid is in a three-phase short-circuit state and the DC port potential of the DC line is zero, and finally the fault current stops rising. [0022] Further, the first reactor is a smoothing reactor. [0023] Further, the load switch is a rated load switch, which is used to switch off the fault current when the fault current of the DC line reaches the rated current value of the load switch. [0024] Further, the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. [0025] The first fully-controlled switch module and the second fully-controlled switch module in the modular multi-level converter in the present utility model both use IGCT devices. Compared with IGBTs, IGCT has very High surge current withstand capability, on-state current capability, forward blocking voltage capability and reliability, and also has a very low on-state voltage drop, so that the modular multi-level converter has large current and blocking The advantages of high voltage, high reliability, compact structure and low conduction loss. [0026] Further, the converter station can integrate the modular multilevel converter and load switch into one station, which greatly reduces the overall volume and cost of the converter station, and achieves a high degree of integration and high economy. It can be widely used in future flexible DC transmission systems. [0027] In addition, by controlling the IGCT device in the first full-control switch module to be blocked, the IGCT device of the second full-control switch module is turned on, which can effectively stop the fault current from rising, so that the load switch only needs to be disconnected. The current size of the direct current also greatly reduces the volume, consumption and cost required by the load switch. Moreover, only the smoothing reactor is needed in the converter station, and the inductance of the smoothing reactor is small, so there is no need to consider the current limiting function. [0028] Other features and advantages of the present utility model will be described in the following, and partly become obvious from them, or understood by implementing the present utility model. The purpose and other advantages of the present invention can be realized and obtained through the structures indicated in the claims, the claims and the drawings. Description of the drawings [0029] In order to more clearly describe the embodiments of the present utility model or the technical solutions in the prior art, the following will briefly introduce the drawings that need to be used in the description of the embodiments or the prior art. Obviously, in the following description The accompanying drawings are some embodiments of the present invention. For those of ordinary skill in the art, without creative work, other drawings can be obtained from these drawings. [0030] FIG. 1 shows a structural schematic diagram of a converter station and a circuit breaker in the prior art; [0031] FIG. 2 shows a schematic structural diagram of a modular multilevel converter in an embodiment of the present invention; [0032] FIG. 3 shows a schematic structural diagram of a converter station in an embodiment of the present utility model; [0033] FIG. 4 shows the U in the converter station in the embodiment of the present utility model.MMC, UDCAnd iDCThe change curve in the control process. detailed description [0034] In order to make the purpose, technical solutions and advantages of the embodiments of the present utility model clearer, the technical solutions in the embodiments of the present utility model will be explained clearly and completely with reference to the drawings in the embodiments of the present utility model. Obviously , The described embodiments are part of the embodiments of the present utility model, but not all of the embodiments. Based on the embodiments of the present utility model, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present utility model. [0035] As shown in Figure 2, the embodiment of the present utility model introduces a modular multilevel converter, including three-phase bridge arms, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper The bridge arm and the lower bridge arm are provided with multiple cascaded converter sub-modules. Among them, there are n converter sub-modules in the upper bridge arm of each phase bridge arm. In Figure 2 they are respectively: SMap1, SMap2 ... SMapn, SMbp1, SMbp2...... SMbpn, SMcp1, SMcp2, there are n modules respectively, in Figure 2 they are: SMan1, SMan2 SMcpn. Inverter in the lower arm of each phase bridge arm SMann, SMbn1, SMbn2 SMbpnn,SMcn1, SMcn2......SMcnn. Further, the converter sub-module includes a first full-control switch module, a second full-control switch module, a buffer circuit and a first capacitor. The first fully controlled switch module includes an IGCT (integrated Gate Commutated Thyristors: integrated gate commutated thyristor) device Sxi1And the first diode D in anti-parallel with itxi1; The second fully-controlled switch module includes an IGCT device Sxi2And the first diode D in anti-parallel with itxi2And the first fully-controlled switch module and the second fully-controlled switch module are connected in series to form a switch branch; the switch branch, the buffer circuit and the first capacitor CxiParallel to each other. Further, when the first full control switch module and the second full control switch module are connected in series, the IGCT device Sxi^IGCT device Sxi2The direction is the same, that is, the IGCT device Sxi1The cathode and the IGCT device Sxi2The anode is connected. Both the first fully-controlled switch module and the second fully-controlled switch module in the modular multilevel converter use IGCT devices. Compared with IGBTs, IGCT has a very high surge current withstand capability, On-state current capability, forward blocking voltage capability and reliability, and also has a very low on-state voltage drop, so that the modular multi-level converter has large current, high blocking voltage, high reliability, and structure The advantages of compactness and low conduction loss. [0036] In this embodiment, each first diode antiparallel to the IGCT device can effectively reverse the fault current, thereby protecting the IGCT device. [0037] More specifically, as shown in FIG. 2, the second fully-controlled switch module is connected in parallel to the output end of the converter sub-module, and the multiple converter sub-modules on the upper bridge arm and the lower bridge arm are connected in parallel. The modules are all connected through their respective output terminals. Further, the buffer circuit includes a first inductor Lxis, The first resistance Rxis, The second diode DxisAnd the second capacitor Cxis, Wherein, the first inductor LxisThe first terminal and the first capacitor CxiThe first terminal and the first resistor RxisIs connected to the first end, and the second end is respectively connected to the first fully-controlled switch module and the second diode DxisThe anode of the second diode is connected to the anode; the cathode of the second diode is connected to the first resistor RxisThe second terminal and the second capacitor CxisThe first terminal is connected; the second capacitor CxisThe second terminal is respectively connected with the second fully-controlled switch module and the first capacitor CxiThe second end of the connection. The first terminal of the first capacitor Cxi is a positive electrode, and the second terminal is a negative electrode, and the voltage is represented by Vc. By adopting the buffer circuit, when the modular multi-level converter is working normally, it can effectively suppress the rising rate of current or voltage on the first full control switch module and/or the second full control switch module. When the modular multilevel converter works in the DC line short-circuit fault state, because the IGCT device in the first full-control switch module is blocked, and the IGCT device in the second full-control switch module is turned on, The buffer circuit is in a bypass state during fault processing. [0038] Shown) [0039] In this embodiment, a second reactor is also provided on the upper and lower bridge arms of each phase bridge arm (not shown in Figures 2-3 and cascaded with the corresponding upper bridge arm The multiple converter sub-modules are connected in series. As shown in Figure 3, the embodiment of the present utility model also introduces a converter station, the converter station includes the above-mentioned The modular multilevel converter as well as the load switch and the first reactor, wherein the modular multilevel converter includes a DC side and an AC side; the DC side of the modular multilevel converter The positive pole is connected to one end of the load switch, the other end of the load switch is connected to one end of the first reactor, and the other end of the first reactor is connected to a DC line. Further, the negative pole of the modular multilevel converter and the other end of the first reactor form the DC port of the converter station, that is, the DC port of the converter station, through which the DC port can realize all The converter station is connected to the DC line. The AC side of the modular multilevel converter forms the AC port of the converter station to connect to the AC power grid. In the embodiment of the utility model, the converter and load switch are integrated into one converter station, which greatly reduces the overall volume and cost of the converter station, realizes high integration and high economic efficiency, and can be used in the future It has been widely used in the flexible DC transmission system. In addition, the above-mentioned modular multi-level converter is applied to the converter station, so that when the IGCT-based converter station faces a DC short-circuit fault, it can realize the function of self-clearing the DC fault, and it can be very effective. Well limit the rise of DC short-circuit fault current. [0040] In Figure 3, the load switch is a rated load switch. It is used to open and cut off the fault current when the fault current of the DC line reaches the rated current value of the load switch. Since the IGCT device in the first full control switch module is controlled to be blocked, the IGCT device in the second full control switch module is turned on, which can effectively stop the fault current from rising. The load switch only needs to break the DC current of the rated current, thus greatly reducing the volume, consumption and cost required by the load switch. Further, the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. The first reactor is a smoothing reactor. Since the above-mentioned modular multilevel converter can directly limit the rise of the fault current when the DC line is short-circuited, the converter in the embodiment of the present invention does not need to be equipped with a reactor with a large inductance value for current limiting , Only use reactor for smooth wave. Therefore, the inductance value of the first reactor in the embodiment of the present invention is small, and there is no need to consider the current limiting function. But for IGBT-MMC (Modular Multilevel Converter: Modular Multilevel Converter), because it cannot limit the rapid rise of the fault current in the event of a fault, it is necessary to equip a reactor with a large inductance value for current limiting. A reactor is also used to smooth the waves. [0041] The embodiment of the utility model also introduces a control method of the above-mentioned converter station, and the control process of the control method specifically includes the following steps: [0042] 1) Time t0: Assume that a short-circuit fault of the DC line occurs at time t0, and the fault current caused by the short-circuit fault of the DC line starts to rise rapidly. [0043] 2) Time t1: the time when a short-circuit fault is detected and the protection of the converter sub-module is activated. When the DC line short-circuit fault is detected, the IGCT device S of the first fully-controlled switch module among all the converter sub-modules in the modular multi-level converterxi1Latching, IGCT device S of the second full control switch modulexi2Conduction. Specifically, the length of the time period from t0 to t1 is the delay time after a short-circuit fault occurs on the DC line, where the length of the time period from t0 to t1 is 0.3 ms (milliseconds). [0044] When a short-circuit fault occurs on the DC line, the IGCT device S of the first fully-controlled switch module among all the converter sub-modules of the modular multi-level converter in the converter stationxi1Latching, IGCT device S of the second full control switch modulexi2Turn on, so that the AC grid connected to the AC side of the modular multilevel converter is in a three-phase short-circuit state. Specifically, it is equivalent to three-phase through the second reactor on all the bridge arms of the modular multilevel converter Short circuit, the potential of the DC port of the converter station is equivalent to zero, and at the same time, the potential of the DC side of the modular multilevel converter is also zero, and the fault current stops rising at this time. [0045] 3) Time t2: the moment when the load switch cuts off the fault current, at this time the fault current of the short-circuit fault of the DC line through the load switch reaches the maximum value. The length of the time period t1~t2 is the time when the load switch receives the action command and separates the switches, and the length of the time period t1~t2 is about 3ms. After the load switch is cut off, the DC line and the modular multi-level converter are isolated, the fault current begins to attenuate, and since then, the DC line begins to be freed. Further, the maximum value of the fault current The value is the rated current value of the load switch. [0046] 4) Time t3: IGCT device S of the second fully-controlled switch module among all converter sub-modules in the modular multi-level converterxi2Moment of lock-up. After the load switch breaks the fault current, there is no need to actively short-circuit the IGCT device to clamp the voltage at the DC side port of the modular multilevel converter. Therefore, the IGCT device can be controlled to be turned off when the current of each phase bridge arm is at the zero-crossing point or when the current is small, and the three-phase short-circuit state of the AC grid is ended. The length of the t2~t3 period is to control the modular multi-level commutation The lock time of the device, the length of the time period t2~t3 is less than 10ms. In the embodiment of the present invention, the low current is that the current on each phase bridge arm is not greater than the preset value of the IGCT device's repetitive turn-off current, and the preset value of the IGCT device's repetitive turn-off current is the repetition of IGCT The maximum power-off current capability. The maximum repetitive power-off current capability of the four-inch IGCT device with the highest market share can be 4.5kA (kiloamps), but it is not limited to 4.5kA, 5kA, 6kA, etc., which are all applicable to this utility model. [0047] 5) Time t4: the time when the modular multilevel converter is unlocked. At this time, all IGCT devices in the converter sub-modules are reopened, that is, all IGCT devices Sxi/Old GCT device Sxi2Conduction. The modular multilevel converter slowly restores the voltage from the locked state to the normal operating state. The process of restoring the voltage often requires one to two cycles, a total of about 40 ms. However, it is only necessary to ensure that the voltage recovery has been completed before the load switch reclosing. The voltage is the rated DC voltage of the modular multilevel converter during normal operation. [0048] 6) Time t5: the time when the load switch is controlled to reclose. At this time, the modular multilevel converter has been unlocked and restored to the voltage during normal operation. The length of the time period from t2 to t5 is the time for the DC line to dissociate, and thus, the length of the time period from t2 to t5 is about 300 ms. [0049] 7) Time t6: At the time when the load switch completes the overlap, the modular multilevel converter resumes transmitting power to the DC side. The length of the time period from t5 to t6 is the time for the load switch to reclose. For a mechanical load switch, the length of the time period from t5 to t6 is about 15 to 20 ms. [0050] Through the above control process, the voltage U of the modular multilevel converterMMCAnd the voltage U of the DC port of the DC lineDCAnd current iDCThe changes are shown in Figure 4. In addition, in the control process, the length of each time period involved effectively shows that the converter station in the embodiment of the present invention can quickly handle and restore the DC line short-circuit fault, and has higher reliability. [0051] The modular multilevel converter and load switch equipped with IGCT devices are arranged together in a converter station, making the structure more compact, so that the converter station has both the functions of converter and switch. [0052] Although the present utility model has been described in detail with reference to the foregoing embodiments, those of ordinary skill in the art should understand that they can still modify the technical solutions described in the foregoing embodiments, or make equivalents to some of the technical features. Replacement; and these modifications or replacements do not cause the essence of the corresponding technical solutions to deviate from the spirit and scope of the technical solutions of the embodiments of the present invention.
[JA WO2021111502A1]: 電力変換装置 [EN WO2021111502A1]: POWER CONVERSION DEVICE [FR WO2021111502A1]: DISPOSITIF DE CONVERSION DE PUISSANCE | [JA WO2021111502A1]: 電圧評価値生成部（７００）は、電力変換器を構成する全ての変換器セルの蓄電要素の電圧（Ｖｃ）の検出値を受けて、全ての検出値の平均値とは異なる、全変換器セルの各蓄電素子の電圧評価値（Ｖｃｇ）を生成する。更に、電圧評価値生成部（７００）は、全ての変換器セルを予め区分した複数のグループの各々に含まれる複数個の変換器セルでの各蓄電素子の電圧評価値（Ｖｃｇ）を、当該複数個の変換器セルでの蓄電素子の電圧（Ｖｃ）の検出値の平均値を用いずに生成する。電圧マクロ制御部（６１０）は、電圧評価値（Ｖｃｇ）を用いて、全ての変換器セル、及び、各グループの変換器セルの蓄積エネルギの過不足を制御するための、少なくとも同一グループの複数の変換器セルに対して共通に設定される制御値（Ｉｚｒｅｆ）を算出する。 [EN WO2021111502A1]: According to the present invention, a voltage evaluation value generation unit (700) receives the detected values of voltages (Vc) of power storage elements of all converter cells constituting a power converter, and generates a voltage evaluation value (Vcg) of each of the power storage elements of all the converter cells, the voltage evaluation value being different from the average value of all the detected values. Further, the voltage evaluation value generation unit (700) generates the voltage evaluation value (Vcg) of each of power storage elements of a plurality of converter cells included in each of a plurality of groups obtained by dividing all the converter cells in advance, without using the average value of the detected values of the voltages (Vc) of the power storage elements of said plurality of converter cells. A voltage macro control unit (610) uses the voltage evaluation value (Vcg) to calculate a control value (Izref) to be commonly set for a plurality of converter cells of at least the same group, for controlling the excess or deficiency of the stored energy of all the converter cells and the converter cells of each group. [FR WO2021111502A1]: Selon la présente invention, une unité de génération de valeur d'évaluation de tension (700) reçoit les valeurs détectées de tensions (Vc) d'éléments de stockage de puissance de toutes les cellules de conversion constituant un convertisseur de puissance, et génère une valeur d'évaluation de tension (Vcg) de chacun des éléments de stockage de puissance de toutes les cellules de conversion, la valeur d'évaluation de tension étant différente de la valeur moyenne de toutes les valeurs détectées. En outre, l'unité de génération de valeur d'évaluation de tension (700) génère la valeur d'évaluation de tension (Vcg) de chacun des éléments de stockage de puissance d'une pluralité de cellules de conversion comprises dans chacun d'une pluralité de groupes obtenus par la division de toutes les cellules de conversion à l'avance, sans utiliser la valeur moyenne des valeurs détectées des tensions (Vc) des éléments de stockage de puissance de ladite pluralité de cellules de conversion. Une macro-unité de commande de tension (610) utilise la valeur d'évaluation de tension (Vcg) pour calculer une valeur de commande (Izref) à définir communément pour une pluralité de cellules de conversion d'au moins le même groupe, pour commander l'excès ou la déficience de l'énergie stockée de toutes les cellules de conversion et les cellules de conversion de chaque groupe. | WO2021111502A1 | 2021-06-10 | JP2019047045W | 2019-12-02 | JP2019047045W, 2019-12-02 | JP6768993B1: 2020-10-14 WO2021111502A1: 2021-06-10 | 三菱電機株式会社 MITSUBISHI ELECTRIC CORP | FUJIWARA SHUHEI KONO YOSHIYUKI UDA RYOSUKE KAJIYAMA TAKUYA FUJII TOSHIYUKI HAYASHI SHIGEO | H02M7/483: I H02M7/48: I | H02M7/48: I H02M7/483: I | WO2019138550A1 JP2019047713A JP2013121223A |  | [JA WO2021111502A1]: 互いにカスケード接続された複数の変換器セルを有するアームを少なくとも1つ含む電力変換器と、 前記電力変換器を制御する制御装置とを備え、 前記複数の変換器セルの各々は、 一対の入出力端子と、 複数のスイッチング素子と、 前記複数のスイッチング素子を介して前記入出力端子と電気的に接続される蓄電素子と、 前記蓄電素子の電圧を検出する電圧検出器とを有し、 前記制御装置は、 前記電力変換器を構成する全ての変換器セルによる前記蓄電素子の蓄積エネルギの過不足、及び、前記全ての変換器セルを予め区分した複数のグループの各々に含まれる複数個の変換器セルによる前記蓄電素子の蓄積エネルギの過不足の少なくとも一方を制御する電圧マクロ制御部と、 前記全ての変換器セルについての、それぞれの前記蓄電素子の電圧検出値の平均値とは異なる各前記蓄電素子の電圧評価値、及び、前記グループ毎の前記複数個の変換器セルについての、それぞれの前記蓄電素子の電圧検出値の平均値とは異なる各前記蓄電素子の電圧評価値の少なくとも一方を算出する電圧評価値生成部とを含み、 前記電圧マクロ制御部は、前記蓄積エネルギの過不足を制御するための、少なくとも前記複数個の変換器セルに対して共通に設定される制御値を、前記電圧評価値生成部からの前記電圧評価値に基づいて算出する、電力変換装置。 前記電圧評価値生成部は、少なくとも前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最大値を抽出する最大値抽出部を有し、 前記電圧評価値生成部は、前記最大値抽出部によって抽出された前記最大値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、少なくとも前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最小値を抽出する最小値抽出部を有し、 前記電圧評価値生成部は、前記最小値抽出部によって抽出された前記最小値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、少なくとも前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最大値を抽出する最大値抽出部と、 前記最大値抽出部と共通の前記複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最小値を抽出する最小値抽出部と、 前記最大値抽出部によって抽出された前記最大値と、前記最小値抽出部によって抽出された前記最小値との平均値を演算する平均値演算部とを有し、 前記電圧評価値生成部は、前記平均値演算部によって算出された前記平均値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、少なくとも前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最頻値を抽出する最頻値抽出部を有し、 前記電圧評価値生成部は、前記最頻値抽出部によって抽出された前記最頻値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、少なくとも前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力される代表値抽出部と、 一定周期で発生される乱数、又は、一定周期でカウントアップされるカウント値に従って前記複数個のうちの1個を選択するための選択信号を切り替える選択切替部とを有し、 前記代表値抽出部は、前記選択切替部からの前記選択信号に従って、前記複数個の電圧検出値のうちの1つの電圧検出値を代表値として抽出し、 前記電圧評価値生成部は、前記代表値抽出部によって抽出された前記代表値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電力変換装置は、 前記アーム毎に配置された電流検出器をさらに備え、 前記複数の変換器セルの各々において、前記複数のスイッチング素子は、前記アーム毎に設定された交流電圧指令値と、周期的なキャリア信号との比較に基づくパルス幅変調制御に従ってオンオフ制御され、 前記電圧評価値生成部は、前記グループ毎の前記電圧評価値を算出する評価値算出部を含み、 前記グループは、複数設けられた前記アームの各々に相当し、 前記評価値算出部は、 前記アーム毎に、前記電流検出器によって検出されたアーム電流と、当該アームの前記交流電圧指令値から求められる前記パルス幅変調制御での変調率指令値との乗算値の時間積分値を用いて、各前記蓄電素子の電圧推定値を算出する第1の電圧推定部を有し、 前記第1の電圧推定部は、前記時間積分値を、各前記アームに含まれる前記複数個の変換器セルの前記蓄電素子の容量値の合計で除算した値に従って前記電圧推定値を算出し、 前記電圧評価値生成部は、前記第1の電圧推定部によって抽出された前記電圧推定値を、当該グループの前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電力変換装置は、 前記電力変換器の入出力電力を検出するための検出器を更に備え、 前記電圧評価値生成部は、前記全ての変換器セルの前記電圧評価値を算出する評価値算出部を含み、 前記評価値算出部は、 前記入出力電力の時間積分値を用いて、前記全ての変換器セルの各前記蓄電素子の電圧推定値を算出する第2の電圧推定部を有し、 前記第2の電圧推定部は、前記時間積分値に対して、前記全ての変換器セルの前記蓄電素子の容量値の合計値で除算し、更に、各前記蓄電素子の電圧公称値で除算する演算に従って前記電圧推定値を算出し、 前記電圧評価値生成部は、前記第2の電圧推定部によって抽出された前記電圧推定値を、前記全ての変換器セルの前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、 異なる方式によって前記電圧評価値を算出する複数の評価値算出部と、 前記複数の評価値算出部による算出値のうちの1つの算出値を選択する出力選択回路とを含み、 前記出力選択回路は、前記電力変換器の動作状況に応じて前記1つの算出値の選択を切り替え、 前記電圧評価値生成部は、前記出力選択回路によって選択された前記1つの算出値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電圧評価値生成部は、 前記複数個の電圧検出値を入力されて、当該複数個の電圧検出値から異常値を除去する異常値除去部を更に含み、 前記評価値算出部には、前記異常値除去部によって処理された前記複数個の電圧検出値が入力される、請求項2~6のいずれか1項に記載の電力変換装置。 前記電圧評価値生成部は、 前記評価値算出部の出力値を通過させるフィルタを更に含み、 前記フィルタは、前記出力値を平均化する特性を有するように構成され、 前記電圧評価値生成部は、前記フィルタの出力値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項2~6及び10のいずれか1項に記載の電力変換装置。 前記電圧評価値生成部は、 前記評価値算出部の出力値を通過させるフィルタを更に含み、 前記フィルタは、前記出力値の変化分を抽出する特性を有するように構成され、 前記電圧評価値生成部は、前記フィルタの出力値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項7又は8に記載の電力変換装置。 前記電圧評価値生成部は、 異なる方式によって前記電圧評価値を算出する複数の評価値算出部と、 前記複数の評価値算出部のそれぞれからの複数の出力値をそれぞれ通過させる複数のフィルタと、 前記複数のフィルタのそれぞれの複数の出力信号に対して予め定められた複数のゲインをそれぞれ乗算した複数の乗算値を出力するゲイン乗算部と、 前記ゲイン乗算部から出力された前記複数の乗算値を加算して出力する加算部とを含み、 前記電圧評価値生成部は、前記加算部の出力値を前記電圧評価値として前記電圧マクロ制御部へ出力する、請求項1記載の電力変換装置。 前記電力変換装置は、 前記アーム毎に配置された電流検出器をさらに備え、 前記複数の変換器セルの各々において、前記複数のスイッチング素子は、前記アーム毎に設定された交流電圧指令値と、周期的なキャリア信号との比較に基づくパルス幅変調制御に従ってオンオフ制御され、 前記グループは、複数設けられた前記アームの各々に相当し、 前記複数の評価値算出部は、第1及び第2の評価値算出部を含み、 前記第1の評価値算出部は、 前記複数のグループのうちの同一のグループに含まれる前記複数個の変換器セルの前記電圧検出器による複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最大値を抽出する最大値抽出部と、 前記最大値抽出部と共通の前記複数個の電圧検出値を入力され、前記複数個の電圧検出値のうちの最小値を抽出する最小値抽出部と、 前記最大値抽出部によって抽出された前記最大値と、前記最小値抽出部によって抽出された前記最小値との平均値を演算する平均値演算部とを有し、 前記第1の評価値算出部は、前記平均値演算部が算出した前記平均値を出力し、 前記第2の評価値算出部は、 前記アーム毎に、前記電流検出器によって検出されたアーム電流と、当該アームの前記交流電圧指令値から求められる前記パルス幅変調制御での変調率指令値との乗算値の時間積分値を用いて、各前記蓄電素子の電圧推定値を算出する電圧推定部を有し、 前記電圧推定部は、前記時間積分値を、各前記アームに含まれる前記複数個の変換器セルの前記蓄電素子の容量値の合計で除算した値に従って前記電圧推定値を算出し、 前記第2の評価値算出部は、前記電圧推定部が算出した前記電圧推定値を出力し、 前記複数のフィルタは、 前記第1の評価値算出部の出力値を通過させる第1のフィルタと、 前記第2の評価値算出部の出力値を通過させる第2のフィルタとを含み、 前記第1のフィルタは、前記第1の評価値算出部の出力値を平均化する特性を有するように構成され、 前記第2のフィルタは、前記第2の評価値算出部の出力値の変化分を抽出する特性を有するように構成され、 前記複数のゲインは、 前記第1のフィルタの出力値と乗算される第1のゲインと、 前記第2のフィルタの出力値と乗算される第2のゲインとを含み、 前記第1及び第2のゲインの和は1.0であり、 前記加算部は、前記第1のゲインに係る第1の乗算値と、前記第2のゲインに係る第2の乗算値とを加算して出力する、請求項13記載の電力変換装置。 [EN WO2021111502A1]: A power converter including at least one arm having a plurality of converter cells cascaded to each other and a control device for controlling the power converter are provided, and each of the plurality of converter cells has a pair of input / output. The control includes a terminal, a plurality of switching elements, a power storage element electrically connected to the input / output terminal via the plurality of switching elements, and a voltage detector for detecting the voltage of the power storage element. The apparatus includes excess and deficiency of the stored energy of the power storage element by all the converter cells constituting the power converter, and a plurality of conversions included in each of a plurality of groups in which all the converter cells are divided in advance. The voltage macro control unit that controls at least one of the excess and deficiency of the stored energy of the power storage element by the instrument cell, and the voltage macro control unit that is different from the average value of the voltage detection values of the power storage elements for all the converter cells. At least one of the voltage evaluation value of the power storage element and the voltage evaluation value of each power storage element different from the average value of the voltage detection values of the power storage element for each of the plurality of converter cells in each group. Including the voltage evaluation value generator to be calculated The voltage macro control unit sets a control value commonly set for at least the plurality of converter cells for controlling excess or deficiency of the stored energy from the voltage evaluation value generation unit. A power converter that calculates based on the value. The voltage evaluation value generation unit includes at least an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the evaluation value calculation unit includes the plurality of evaluation value calculation units included in the same group among the plurality of groups. It has a maximum value extraction unit that inputs a plurality of voltage detection values by the voltage detector of the converter cell and extracts the maximum value among the plurality of voltage detection values, and the voltage evaluation value generation unit The power conversion device according to claim 1, wherein the maximum value extracted by the maximum value extraction unit is output to the voltage macro control unit as the voltage evaluation value. The voltage evaluation value generation unit includes at least an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the evaluation value calculation unit includes the plurality of evaluation value calculation units included in the same group among the plurality of groups. It has a minimum value extraction unit that inputs a plurality of voltage detection values by the voltage detector of the converter cell and extracts the minimum value among the plurality of voltage detection values, and the voltage evaluation value generation unit has a minimum value extraction unit. The power conversion device according to claim 1, wherein the minimum value extracted by the minimum value extraction unit is output to the voltage macro control unit as the voltage evaluation value. The voltage evaluation value generation unit includes at least an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the evaluation value calculation unit includes the plurality of evaluation value calculation units included in the same group among the plurality of groups. A maximum value extraction unit that inputs a plurality of voltage detection values by the voltage detector of the converter cell and extracts the maximum value among the plurality of voltage detection values, and the above-mentioned common to the maximum value extraction unit. A minimum value extraction unit that inputs a plurality of voltage detection values and extracts the minimum value among the plurality of voltage detection values, the maximum value extracted by the maximum value extraction unit, and the minimum value extraction unit. The voltage evaluation value generation unit has an average value calculation unit that calculates an average value with the minimum value extracted by the above, and the voltage evaluation value generation unit uses the average value calculated by the average value calculation unit as the voltage evaluation value. The power conversion device according to claim 1, which outputs to a voltage macro control unit. The voltage evaluation value generation unit includes at least an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the evaluation value calculation unit includes the plurality of evaluation value calculation units included in the same group among the plurality of groups. It has a most frequent value extraction unit that inputs a plurality of voltage detection values by the voltage detector of the converter cell and extracts the most frequent value among the plurality of voltage detection values, and generates the voltage evaluation value. The power conversion device according to claim 1, wherein the unit outputs the most frequent value extracted by the most frequent value extraction unit as the voltage evaluation value to the voltage macro control unit. The voltage evaluation value generation unit includes at least an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the evaluation value calculation unit includes the plurality of evaluation value calculation units included in the same group among the plurality of groups. A representative value extraction unit for inputting a plurality of voltage detection values by the voltage detector of the converter cell of the above, and the plurality of said ones according to a random number generated in a fixed cycle or a count value counted up in a fixed cycle. It has a selection switching unit that switches a selection signal for selecting one of them, and the representative value extraction unit is one of the plurality of voltage detection values according to the selection signal from the selection switching unit. The first aspect of claim 1, wherein one voltage detection value is extracted as a representative value, and the voltage evaluation value generation unit outputs the representative value extracted by the representative value extraction unit to the voltage macro control unit as the voltage evaluation value. Power converter. The power converter further includes a current detector arranged for each arm, and in each of the plurality of converter cells, the plurality of switching elements have an AC voltage command value set for each arm. On / off control is performed according to pulse width modulation control based on comparison with a periodic carrier signal, and the voltage evaluation value generation unit includes an evaluation value calculation unit that calculates the voltage evaluation value for each group, and the group includes a plurality of evaluation value calculation units. Corresponding to each of the provided arms, the evaluation value calculation unit performs the pulse width modulation obtained from the arm current detected by the current detector and the AC voltage command value of the arm for each arm. It has a first voltage estimation unit that calculates the voltage estimation value of each storage element by using the time integration value of the multiplication value with the modulation factor command value in control, and the first voltage estimation unit is said. The voltage estimation value is calculated according to the value obtained by dividing the time integration value by the sum of the capacitance values of the power storage elements of the plurality of converter cells included in each of the arms, and the voltage evaluation value generation unit is the first. The power conversion device according to claim 1, wherein the voltage estimation value extracted by the voltage estimation unit of 1 is output to the voltage macro control unit as the voltage evaluation value of the group. The power converter further includes a detector for detecting the input / output power of the power converter, and the voltage evaluation value generator calculates an evaluation value for calculating the voltage evaluation value of all the converter cells. The evaluation value calculation unit includes a second voltage estimation unit that calculates a voltage estimation value of each of the power storage elements of all the converter cells using the time integration value of the input / output power. The second voltage estimation unit divides the time integration value by the total value of the capacitance values of the power storage elements of all the converter cells, and further divides the time integration value by the nominal voltage value of each power storage element. The voltage estimation value is calculated according to the calculation to be performed, and the voltage evaluation value generation unit uses the voltage estimation value extracted by the second voltage estimation unit as the voltage evaluation value of all the converter cells. The power conversion device according to claim 1, which outputs to a macro control unit. The voltage evaluation value generation unit includes a plurality of evaluation value calculation units that calculate the voltage evaluation value by different methods, and an output selection circuit that selects one of the calculation values calculated by the plurality of evaluation value calculation units. The output selection circuit switches the selection of the one calculated value according to the operating condition of the power converter, and the voltage evaluation value generator is the one calculated value selected by the output selection circuit. The power conversion device according to claim 1, wherein the voltage is output to the voltage macro control unit as the voltage evaluation value. The voltage evaluation value generation unit further includes an abnormal value removing unit for inputting the plurality of voltage detection values and removing the abnormal value from the plurality of voltage detection values, and the evaluation value calculation unit includes the above-mentioned evaluation value calculation unit. The power conversion device according to any one of claims 2 to 6, wherein the plurality of voltage detection values processed by the outlier removal unit are input. The voltage evaluation value generation unit further includes a filter for passing the output value of the evaluation value calculation unit, the filter is configured to have a characteristic of averaging the output values, and the voltage evaluation value generation unit is configured. The power conversion device according to any one of claims 2 to 6 and 10, wherein the output value of the filter is output to the voltage macro control unit as the voltage evaluation value. The voltage evaluation value generation unit further includes a filter for passing the output value of the evaluation value calculation unit, and the filter is configured to have a characteristic of extracting a change in the output value, and the voltage evaluation value generation unit is provided. The power conversion device according to claim 7 or 8, wherein the unit outputs the output value of the filter as the voltage evaluation value to the voltage macro control unit. The voltage evaluation value generation unit includes a plurality of evaluation value calculation units that calculate the voltage evaluation value by different methods, a plurality of filters that pass a plurality of output values from each of the plurality of evaluation value calculation units, and a plurality of filters. A gain multiplication unit that outputs a plurality of multiplication values obtained by multiplying each of the plurality of output signals of the plurality of filters by a plurality of predetermined gains, and the plurality of multiplication values output from the gain multiplication unit. The power conversion device according to claim 1, wherein the voltage evaluation value generation unit outputs the output value of the addition unit to the voltage macro control unit as the voltage evaluation value. The power converter further includes a current detector arranged for each arm, and in each of the plurality of converter cells, the plurality of switching elements have an AC voltage command value set for each arm. On / off control is performed according to pulse width modulation control based on comparison with a periodic carrier signal, the group corresponds to each of the plurality of arms provided, and the plurality of evaluation value calculation units are the first and second evaluation value calculation units. The first evaluation value calculation unit includes an evaluation value calculation unit, and the first evaluation value calculation unit calculates a plurality of voltage detection values by the voltage detectors of the plurality of converter cells included in the same group among the plurality of groups. The maximum value extraction unit that is input and extracts the maximum value among the plurality of voltage detection values and the plurality of voltage detection values common to the maximum value extraction unit are input, and the plurality of voltage detection values are input. Average value calculation that calculates the average value of the minimum value extraction unit that extracts the minimum value, the maximum value extracted by the maximum value extraction unit, and the minimum value extracted by the minimum value extraction unit. The first evaluation value calculation unit outputs the average value calculated by the average value calculation unit, and the second evaluation value calculation unit outputs the average value calculated by the average value calculation unit. For each arm, the time-integrated value of the product of the arm current detected by the current detector and the modulation factor command value in the pulse width modulation control obtained from the AC voltage command value of the arm is used. The voltage estimation unit has a voltage estimation unit that calculates a voltage estimation value of each storage element, and the voltage estimation unit converts the time integration value into the capacity of the power storage element of the plurality of converter cells included in each arm. The voltage estimation value is calculated according to the value divided by the sum of the values, the second evaluation value calculation unit outputs the voltage estimation value calculated by the voltage estimation unit, and the plurality of filters use the first evaluation value. The first filter includes a first filter that passes the output value of the evaluation value calculation unit and a second filter that passes the output value of the second evaluation value calculation unit. The second filter is configured to have a characteristic of averaging the output value of the evaluation value calculation unit, and the second filter is configured to have a characteristic of extracting a change in the output value of the second evaluation value calculation unit. The plurality of gains include a first gain that is multiplied by the output value of the first filter and a second gain that is multiplied by the output value of the second filter. The sum of the gains of 2 is 1.0, The power conversion device according to claim 13, wherein the addition unit adds and outputs a first multiplication value related to the first gain and a second multiplication value related to the second gain. | [JA WO2021111502A1]: 電力変換装置 本発明は、電力変換装置に関する。 電力系統に設置される大容量の電力変換装置として、複数の単位変換器(以下、「変換器セル」と称する)がカスケードに接続されるモジュラーマルチレベル変換器(MMC:Modular Multilevel Converter)が知られている。通常、変換器セルは、複数のスイッチング素子と蓄電素子(代表的には、キャパシタ)とを備える。 モジュラーマルチレベル変換器では、所望の制御出力を得るためには、個々の変換器セルの蓄電素子の電圧(キャパシタ電圧)を目標値近辺に維持する必要がある。キャパシタ電圧が当該目標値から外れると、変換器セルの出力電圧が指令通りとならないことで、意図しない循環電流の発生等によって制御特性が悪化することが懸念される。著しい場合には、いずれかの変換器セルにおいて、キャパシタ電圧が過電圧(OV)保護又は低電圧(UV)保護のレベルまで過上昇又は過低下することで、MMCの動作が停止される虞がある。 通常、キャパシタ電圧は、個別の変換器セル毎のキャパシタ電圧制御(以下、「個別制御」とも称する)に加えて、MMC内での変換器セル全体での制御(以下、「全電圧制御」とも称する)、及び、一定のグループ(例えば、アーム、又は、相)の間でのバランス制御によって、多階層で制御されることが一般的である。 例えば、特許第4999930号公報(特許文献1)には、複数のサブモジュール(変換器セル)がカスケード接続された複数の相モジュールを有する電力変換装置において、全サブモジュールのキャパシタ電圧の平均値(全体平均値)、及び、各相モジュール内でのキャパシタ電圧の平均値(相毎平均値)を用いた制御が記載される。具体的には、全体平均値を相数で除算した基準値と、相毎平均値との偏差を縮小するフィードバック制御によって、相間での貯蔵されたエネルギの不均一を抑制する制御が行われる。 特許第4999930号公報 上述した、全電圧制御、及び、グループ間でのバランス制御は、電力変換器全体、及び、一定グループ内でのキャパシタでの蓄積エネルギの過不足を抑制するものである。このため、変換器セルの全体又は一定グループ内の複数の変換器セルに対して共通に、当該過不足の制御値が反映されることになる。 特許文献1では、変換器セルの全体又は一定グループ内の複数の変換器セルの蓄積エネリグの評価値として、複数の変換器セルのキャパシタ電圧の平均値を用いることが記載されている。 しかしながら、単純な平均値に基づく評価値では、当該複数の変換器セル内で充電又は放電の度合いが大きい変換器セルの情報が当該評価値に反映されないことで、OV保護又はUV保護を回避する面からの制御性が不十分となることが懸念される。或いは、キャパシタ電圧の変化は、実際に蓄積エネルギの過不足が生じた結果として生じるので、キャパシタ電圧の検出値のみに依存して評価値を求めると、当該過不足の検出遅れにより、制御性が低下することも懸念される。 本発明はこのような問題点を解決するためになされたものであって、本発明の目的は、複数の変換器セルを単位として蓄積エネルギを制御するための、当該複数の変換器セルのキャパシタ電圧の評価値を適切に算出することによって、電力変換装置の制御性を向上することである。 本発明のある局面では、電力変換装置は、電力変換器と、電力変換器を制御する制御装置とを備える。電力変換器は、互いにカスケード接続された複数の変換器セルを有するアームを少なくとも1つ含む。複数の変換器セルの各々は、一対の入出力端子と、複数のスイッチング素子と、蓄電素子と、蓄電素子の電圧を検出する電圧検出器とを有する。蓄電素子は、数のスイッチング素子を介して入出力端子と電気的に接続される。制御装置は、電圧マクロ制御部と、電圧評価値生成部とを含む。電圧マクロ制御部は、電力変換器を構成する全ての変換器セルによる蓄電素子の蓄積エネルギの過不足、及び、全ての変換器セルを予め区分した複数のグループの各々に含まれる複数個の変換器セルによる蓄電素子の蓄積エネルギの過不足の少なくとも一方を制御する。電圧評価値生成部とを含み、全ての変換器セルについての、それぞれの蓄電素子の電圧検出値の平均値とは異なる各蓄電素子の電圧評価値、及び、グループ毎の複数個の変換器セルについての、それぞれの蓄電素子の電圧検出値の平均値とは異なる各蓄電素子の電圧評価値の少なくとも一方を算出する。特に、電圧マクロ制御部は、蓄積エネルギの過不足を制御するための、少なくとも複数個の変換器セルに対して共通に設定される制御値を、電圧評価値生成部からの電圧評価値に基づいて算出する。 本発明によれば、複数の変換器セルを単位として蓄積エネルギを制御するための、当該複数の変換器セルのキャパシタ電圧の評価値を、単純な平均値と異なる手法で適切に算出することによって、電力変換装置の制御性を向上することができる。 本実施の形態に係る電力変換装置の概略構成図である。 図1に示された電力変換器を構成する変換器セルの構成例を示す回路図である。 図1に示された制御装置の内部構成を説明する機能ブロック図である。 図1に示された制御装置のハードウェア構成例を示すブロック図である。 図3に示された基本制御部の構成例を説明するブロック図である。 図3に示されたアーム制御部の構成例を示すブロック部である。 図6に示された個別セル制御部の構成例を示すブロック図である。 図7に示されたゲート信号生成部によるPWM変調を説明するための概念的な波形図である。 実施の形態1に係る電圧評価部の第1の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第2の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第3の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第4の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第5の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第6の構成例を説明するブロック図である。 実施の形態1に係る電圧評価部の第7の構成例を説明するブロック図である。 実施の形態1の変形例に係る電圧評価部の構成例を説明するブロック図である。 実施の形態2に係る電圧評価部の構成例を説明するブロック図である。 実施の形態3に係る電圧評価部の構成例を説明するブロック図である。 実施の形態4に係る電圧評価部の構成を説明するブロック図である。 実施の形態4に係る電圧評価部の具体例を説明するブロック図である。 個別セル制御部の他の構成例を説明するブロック図である。 キャリア信号変調の第1の例を説明する概念的な波形図である。 キャリア信号変調の第2の例を説明する概念的な波形図である。 電力変換装置の構成の第1の変形例を説明する回路図である。 電力変換装置の構成の第2の変形例を説明する回路図である。 以下に、本発明の実施の形態について、図面を参照して詳細に説明する。なお、以下では、図中の同一又は相当部分には同一符号を付して、その説明は原則的に繰返さないものとする。 実施の形態1. (電力変換装置の全体構成) 図1は、本実施の形態に係る電力変換装置1の概略構成図である。 図1を参照して、電力変換装置1は、互いに直列接続された複数の変換器セルを含むモジュラーマルチレベル変換器によって構成されている。尚、「変換器セル」は、「サブモジュール」、SM、又は「単位変換器」とも呼ばれる。電力変換装置1は、直流回路14と交流回路12との間で電力変換を行なう。電力変換装置1は、電力変換器2と、制御装置3とを含む。 電力変換器2は、正極直流端子(即ち、高電位側直流端子)Npと、負極直流端子(即ち、低電位側直流端子)Nnとの間に互いに並列に接続された複数のレグ回路4u,4v,4w(総称する場合又は任意のものを示す場合、レグ回路4と記載する)を含む。 レグ回路4は、交流を構成する複数相の各々に設けられる。レグ回路4は、交流回路12と直流回路14との間に接続され、両回路間で電力変換を行なう。図1には、交流回路12が3相交流系統の場合が示され、U相、V相、W相にそれぞれ対応して3個のレグ回路4u,4v,4wが設けられている。 レグ回路4u,4v,4wにそれぞれ設けられた交流入力端子Nu,Nv,Nwは、変圧器13を介して交流回路12に接続される。交流回路12は、例えば、交流電源などを含む交流電力系統である。図1では、図解を容易にするために、交流入力端子Nv,Nwと変圧器13との接続は図示していない。 各レグ回路4に共通に接続された高電位側直流端子Np及び低電位側直流端子Nnは、直流回路14に接続される。直流回路14は、例えば、直流送電網などを含む直流電力系統又は他の電力変換装置の直流端子である。後者の場合、2台の電力変換装置を連結することによって定格周波数などが異なる交流電力系統間を接続するためのBTB(Back To Back)システムが構成される。 図1の変圧器13を用いる代わりに、連系リアクトルを介して交流回路12に接続する構成としてもよい。更に、交流入力端子Nu,Nv,Nwに代えてレグ回路4u,4v,4wにそれぞれ一次巻線を設け、この一次巻線と磁気結合する二次巻線を介してレグ回路4u,4v,4wが変圧器13又は連系リアクトルに交流的に接続するようにしてもよい。この場合、一次巻線を下記のリアクトル8A,8Bとしてもよい。即ち、レグ回路4は、交流入力端子Nu,Nv,Nw又は上記の一次巻線など、各レグ回路4u,4v,4wに設けられた接続部を介して電気的に(すなわち直流的又は交流的に)交流回路12と接続される。 レグ回路4uは、高電位側直流端子Npから交流入力端子Nuまでの上アーム5と、低電位側直流端子Nnから交流入力端子Nuまでの下アーム6とを含む。上アーム5及び下アーム6の接続点である交流入力端子Nuは、変圧器13と接続される。高電位側直流端子Np及び低電位側直流端子Nnは、直流回路14に接続される。レグ回路4v,4wについても同様の構成を有するので、以下、レグ回路4uの構成について代表的に説明する。 上アーム5は、カスケード接続された複数の変換器セル7と、リアクトル8Aとを含む。複数の変換器セル7及びリアクトル8Aは、直列に接続されている。同様に、下アーム6は、カスケード接続された複数の変換器セル7と、リアクトル8Bとを含む。複数の変換器セル7及びリアクトル8Bは、直列に接続されている。以下の説明では、上アーム5及び下アーム6の各々に含まれる変換器セル7の数をNcellとする。但し、Ncell≧2とする。 リアクトル8Aが挿入される位置は、レグ回路4uの上アーム5のいずれの位置であってもよく、リアクトル8Bが挿入される位置は、レグ回路4uの下アーム6のいずれの位置であってもよい。リアクトル8A,8Bはそれぞれ複数個設けられてもよい。各リアクトルのインダクタンス値は互いに異なっていてもよい。更に、上アーム5のリアクトル8Aのみ、もしくは、下アーム6のリアクトル8Bのみを設けてもよい。又、変圧器結線を工夫して、直流分電流の磁束を打ち消すとともに、交流分電流に対して変圧器の漏れリアクタンスが作用することでリアクトルの代替としてもよい。リアクトル8A,8Bを設けることにより、交流回路12又は直流回路14等の事故時における事故電流が急激な増大を抑制することができる。 電力変換装置1は、更に、制御に使用される電気量(電流、電圧など)を計測する各検出器として、交流電圧検出器10と、交流電流検出器16と、直流電圧検出器11A,11Bと、各レグ回路4に設けられたアーム電流検出器9A,9Bとを含む。これらの検出器によって検出された信号は、制御装置3に入力される。 尚、図1では図解を容易にするために、各検出器から制御装置3に入力される信号の信号線と、制御装置3及び各変換器セル7間で入出力される信号の信号線とは、一部まとめて記載されているが、実際には検出器ごと及び変換器セル7ごとに設けられている。各変換器セル7と制御装置3との間の信号線は、送信用と受信用とが別個に設けられていてもよい。信号線は、例えば光ファイバによって構成される。 次に、各検出器について具体的に説明する。 交流電圧検出器10は、交流回路12のU相の交流電圧Vacu、V相の交流電圧Vacv、及び、W相の交流電圧Vacwを検出する。以下の説明では、Vacu、Vacv、及び、Vacwを総称してVacとも記載する。 交流電流検出器16は、交流回路12のU相の交流電流Iacu、V相の交流電流Iacv、及び、W相の交流電流Iacwを検出する。以下の説明では、Iacu、Iacv、及びIacwを総称してIacとも記載する。 直流電圧検出器11Aは、直流回路14に接続された高電位側直流端子Npの直流電圧Vdcpを検出する。直流電圧検出器11Bは、直流回路14に接続された低電位側直流端子Nnの直流電圧Vdcnを検出する。直流電圧Vdcpと直流電圧Vdcnとの差を直流電圧Vdcとする。直流電圧検出器17は、高電位側直流端子Np又は低電位側直流端子Nnを流れる直流電流Idcを検出する。 U相用のレグ回路4uに設けられたアーム電流検出器9A及び9Bは、上アーム5に流れる上アーム電流Ipu、及び、下アーム6に流れる下アーム電流Inuをそれぞれ検出する。V相用のレグ回路4vに設けられたアーム電流検出器9A及び9Bは、上アーム電流Ipv及び下アーム電流Invをそれぞれ検出する。W相用のレグ回路4wに設けられたアーム電流検出器9A及び9Bは、上アーム電流Ipw及び下アーム電流Inwをそれぞれ検出する。以下の説明では、上アーム電流Ipu、Ipv、Ipwを総称して上アーム電流Iarmpとも記載し、下アーム電流Inu、Inv、Inwを総称して下アーム電流Iarmnとも記載し、上アーム電流Iarmpと下アーム電流Iarmnとを総称してIarmとも記載する。 (変換器セルの構成例) 図2(a)及び図2(b)は、電力変換器2を構成する変換器セル7の構成例を示す回路図である。 図2(a)に示す変換器セル7は、ハーフブリッジ構成と呼ばれる回路構成を有する。この変換器セル7は、2つのスイッチング素子31p及び31nを直列接続して形成した直列体と、蓄電素子32と、電圧検出器33と、入出力端子P1,P2とを備える。スイッチング素子31p及び31nの直列体と蓄電素子32とは並列接続される。電圧検出器33は、蓄電素子32の両端の電圧Vcを検出する。 スイッチング素子31nの両端子は、入出力端子P1,P2とそれぞれ接続される。変換器セル7は、スイッチング素子31p,31nのスイッチング動作により、蓄電素子32の電圧Vc又は零電圧を、入出力端子P1及びP2の間に出力する。スイッチング素子31pがオン、かつスイッチング素子31nがオフとなったときに、変換器セル7からは、蓄電素子32の電圧Vcが出力される。スイッチング素子31pがオフ、かつスイッチング素子31nがオンとなったときに、変換器セル7は、零電圧を出力する。 図2(b)に示す変換器セル7は、フルブリッジ構成と呼ばれる回路構成を有する。この変換器セル7は、2つのスイッチング素子31p1及び31n1を直列接続して形成された第1の直列体と、2つスイッチング素子31p2及び31n2を直列接続して形成された第2の直列体と、蓄電素子32と、電圧検出器33と、入出力端子P1,P2とを備える。第1の直列体と、第2の直列体と、蓄電素子32とが並列接続される。電圧検出器33は、蓄電素子32の両端の電圧Vcを検出する。 スイッチング素子31p1及びスイッチング素子31n1の中点は、入出力端子P1と接続される。同様に、スイッチング素子31p2及びスイッチング素子31n2の中点は、入出力端子P2と接続される。変換器セル7は、スイッチング素子31p1,31n1,31p2,31n2のスイッチング動作により、蓄電素子32の電圧Vc、-Vc、又は零電圧を、入出力端子P1及びP2の間に出力する。 図2(a)及び図2(b)において、スイッチング素子31p,31n,31p1,31n1,31p2,31n2は、例えば、IGBT(Insulated Gate Bipolar Transistor)、GCT(Gate Commutated Turn-off)サイリスタなどの自己消弧型の半導体スイッチング素子にFWD(Freewheeling Diode)が逆並列に接続されて構成される。 図2(a)及び図2(b)において、蓄電素子32には、フィルムコンデンサなどのキャパシタが主に用いられる。蓄電素子32は、以降の説明では、キャパシタと呼称することもある。以下では、蓄電素子32の電圧Vcをキャパシタ電圧Vcとも称する。 図1に示されるように、変換器セル7はカスケード接続されている。図2(a)及び図2(b)の各々において、上アーム5に配置された変換器セル7では、入出力端子P1は、隣の変換器セル7の入出力端子P2又は高電位側直流端子Npと接続され、入出力端子P2は、隣の変換器セル7の入出力端子P1又は交流入力端子Nuと接続される。同様に、下アーム6に配置された変換器セル7では、入出力端子P1は、隣の変換器セル7の入出力端子P2又は交流入力端子Nuと接続され、入出力端子P2は、隣の変換器セル7の入出力端子P1又は低電位側直流端子Nnと接続される。 以降では、変換器セル7を図2(a)に示すハーフブリッジセルの構成とし、スイッチング素子として半導体スイッチング素子、蓄電素子としてキャパシタを用いた場合を例に説明する。但し、電力変換器2を構成する変換器セル7を図2(b)に示すフルブリッジ構成とすることも可能である。又、上記で例示した構成以外の変換器セル、例えば、クランプトダブルセルと呼ばれる回路構成などを適用した変換器セルを用いてもよく、スイッチング素子及び蓄電素子も上記の例示に限定されるものではない。 (制御装置) 図3は、図1に示された制御装置3の内部構成を説明する機能ブロック図である。 図3を参照して、制御装置3は、各変換器セル7のスイッチング素子31p,31nのオン、オフを制御するためのスイッチング制御部501を備える。 スイッチング制御部501は、U相基本制御部502Uと、U相上アーム制御部503UPと、U相下アーム制御部503UNと、V相基本制御部502Vと、V相上アーム制御部503VPと、V相下アーム制御部503VNと、W相基本制御部502Wと、W相上アーム制御部503WPと、W相下アーム制御部503WNとを含む。 以下の説明では、U相基本制御部502U、V相基本制御部502V、及び、W相基本制御部502Wを総称して基本制御部502とも記載する。同様に、U相上アーム制御部503UP、U相下アーム制御部503UN、V相上アーム制御部503VP、V相下アーム制御部503VN、W相上アーム制御部503WP、及び、W相下アーム制御部503WNを総称してアーム制御部503とも記載する。 図4には、制御装置のハードウェア構成例が示される。図4には、コンピュータによって制御装置3を構成する例が示される。 図4を参照して、制御装置3は、1つ以上の入力変換器70と、1つ以上のサンプルホールド(S/H)回路71と、マルチプレクサ(MUX)72と、A/D変換器73とを含む。更に、制御装置3は、1つ以上のCPU(Central Processing Unit)74と、RAM(Random Access Memory)75と、ROM(Read Only Memory)76とを含む。更に、制御装置3は、1つ以上の入出力インターフェイス77と、補助記憶装置78と、上記の構成要素間を相互に接続するバス79を含む。 入力変換器70は、入力チャンネルごとに補助変成器(図示せず)を有する。各補助変成器は、図1の各電気量検出器による検出信号を、後続する信号処理に適した電圧レベルの信号に変換する。 サンプルホールド回路71は、入力変換器70ごとに設けられる。サンプルホールド回路71は、対応の入力変換器70から受けた電気量を表す信号を規定のサンプリング周波数でサンプリングして保持する。 マルチプレクサ72は、複数のサンプルホールド回路71に保持された信号を順次選択する。A/D変換器73は、マルチプレクサ72によって選択された信号をデジタル値に変換する。なお、複数のA/D変換器73を設けることによって、複数の入力チャンネルの検出信号に対して並列的にA/D変換を実行するようにしてもよい。 CPU74は、制御装置3の全体を制御し、プログラムに従って演算処理を実行する。揮発性メモリとしてのRAM75及び不揮発性メモリとしてのROM76は、CPU74の主記憶として用いられる。ROM76は、プログラム及び信号処理用の設定値などを収納する。補助記憶装置78は、ROM76に比べて大容量の不揮発性メモリであり、プログラム及び電気量検出値のデータなどを格納する。 入出力インターフェイス77は、CPU74及び外部装置の間で通信する際のインターフェイス回路である。 尚、図3の例とは異なり、制御装置3の少なくとも一部をFPGA(Field Programmable Gate Array)及び、ASIC(Application Specific Integrated Circuit)等の回路を用いて構成することも可能である。即ち、図3に記載された各機能ブロックの機能は、図4に例示されたコンピュータをベースに構成することもできるし、その少なくとも一部をFPGA及びASICなどの回路を用いて構成することができる。又、各機能ブロックの機能の少なくとも一部は、アナログ回路によって構成することも可能である。 図5は、図3に示された基本制御部502の構成例を説明するブロック図である。 図5を参照して、基本制御部502は、アーム電圧指令生成部601を含む。更に、制御装置3は、アーム電圧指令生成部601で用いられる電圧評価値Vcgを生成する電圧評価値生成部700をさらに備える。 アーム電圧指令生成部601は、上アームのアーム電圧指令値krefpと、下アームのアーム電圧指令値krefnとを算出する。以下の説明では、krefpとkrefnとを総称してkrefと記載する。 電圧評価値生成部700は、各変換器セル7において電圧検出器33によって検出されたキャパシタ電圧Vcを受ける。電圧評価値生成部700は、各変換器セル7のキャパシタ電圧Vcから、電力変換器2の全ての変換器セル7のキャパシタ32の蓄積エネルギの総和を評価するための全電圧評価値Vcgallと、予め定められたグループ毎での変換器セル7のキャパシタ32の蓄積エネルギの総和を示すグループ毎電圧評価値Vcgrとを生成する。 例えば、グループ毎電圧評価値Vcgrは、レグ回路4u(U相)、4v(V相)、及び、4w(W相)のそれぞれに含まれる複数個(2×Necll個)の変換器セル7の蓄積エネルギの総和を評価するためのU相電圧評価値Vcgu、V相電圧評価値Vcgv、及び、V相電圧評価値Vcgvを含む。或いは、グループ毎電圧評価値Vcgrは、レグ回路4(U相,V相,W相)毎の電圧評価値に代えて、或いはこれに加えて、各レグ回路4について上アーム5及び下アーム6のそれぞれについて、各アームに含まれる複数個(Necll個)の変換器セル7の蓄積エネルギの総和を評価するためのグループ毎電圧評価値Vcgrを含んでもよい。本実施の形態では、電圧評価値生成部700によって生成される全電圧評価値Vcgall及びグループ毎電圧評価値Vcgrを、包括的に電圧評価値Vcgと表記する。 特許文献1では、これらの電圧評価値Vcgは、電力変換器2の全ての変換器セル7のキャパシタ電圧Vcの平均値、或いは、各グループ(各相レグ回路又は各アーム)に属する複数個の変換器セル7のキャパシタ電圧Vcの平均値として求められている。本実施の形態では、平均値とは異なる評価値を算出して、蓄積エネルギが制御される。電圧評価値生成部700の構成例については、後程、詳細に説明する。 アーム電圧指令生成部601は、交流電流制御部603と、循環電流算出部604と、循環電流制御部605と、指令分配部606と、電圧マクロ制御部610とを含む。 交流電流制御部603は、検出された交流電流Iacと設定された交流電流指令値Iacrefとの偏差が0になるように交流制御指令値Vcpを算出する。 循環電流算出部604は、上アームのアーム電流Iarmpと、下アームのアーム電流Iarmpとに基づいて、1つのレグ回路4に流れる循環電流Izを計算する。循環電流は、複数のレグ回路4の間を循環する電流である。例えば、1つのレグ回路4に流れる循環電流Izは、以下の式(1)及び式(2)によって計算できる。 Idc=(Ipu+Ipv+Ipw+Inu+Inv+Inw)/2 ...(1) Iz=(Iarmp+Iarmn)/2-Idc/3 ...(2) 電圧マクロ制御部610は、電圧評価値生成部700によって生成された電圧評価値Vcgに基づいて、電力変換器2の全ての変換器セル7での蓄積エネルギの過不足、及び、グループ間(各相レグ回路間又はアーム間)での蓄積エネルギの不均衡を補償するように、循環電流指令値Izrefを生成する。 例えば、電圧マクロ制御部610は、減算部611,613、全電圧制御部612、グループ間電圧制御部614、及び、加算部615を含む。 減算部611は、電圧評価値生成部700によって生成された全電圧評価値Vcgallを、全電圧指令値Vc*から減算する。全電圧指令値Vc*は、各変換器セル7におけるキャパシタ32での蓄積エネルギの基準値に相当する、キャパシタ電圧Vcの基準値である。全電圧制御部612は、減算部611によって算出された、全電圧指令値Vc*に対する全電圧評価値Vcgallの偏差に対して演算を施すことによって、第1の電流指令値Izref1を生成する。第1の電流指令値Izref1は、各変換器セル7のキャパシタ電圧Vcの全体レベルを、全電圧指令値Vc*に制御することで、電力変換器2の全ての変換器セル7での蓄積エネルギの過不足を解消するための循環電流値に相当する。 同様に、減算部613は、全電圧評価値Vcgallからグループ毎電圧評価値Vcgrを減算する。例えば、基本制御部502がU相基本制御部502である場合には、減算部613には、グループ毎電圧評価値Vcgrとして、U相電圧評価値Vcguが入力される。グループ間電圧制御部614は、減算部613によって算出された、全電圧評価値Vcgallに対するグループ毎電圧評価値Vcgr(U相電圧評価値Vcgu)の偏差に対して演算を施すことによって、第2の電流指令値Izref2を生成する。第2の電流指令値Izref2は、グループ間(ここでは、相毎のレグ回路間)で、変換器セル7のキャパシタ電圧Vcのレベルを均一化して、グループ間での変換器セル7での蓄積エネルギの不均衡を解消するための循環電流値に相当する。 例えば、全電圧制御部612及びグループ間電圧制御部614は、減算部611,613が算出した上記偏差に対して比例演算及び積分演算を行うPI制御器として構成することもできるし、更に微分演算を行うPID制御器として構成することもできる。或いは、一般的にフィードバック制御に用いられる他の制御器の構成を用いて、全電圧制御部612及びグループ間電圧制御部614を構成することも可能である。 加算部615は、全電圧制御部612からの第1の電流指令値Izref1と、グループ間電圧制御部614からの第2の電流指令値Izref2とを加算して、循環電流指令値Izrefを生成する。 循環電流制御部605は、循環電流算出部604によって算出された循環電流Izを、電圧マクロ制御部610によって設定された循環電流指令値Izrefに追従制御するための循環制御指令値Vzpを算出する。循環電流制御部605についても、循環電流指令値Izrefに対する循環電流Izの偏差に対して、PI制御又はPID制御等を実行する制御器によって構成することが可能である。即ち、電圧評価値Vcgを用いる電圧マクロ制御部610は、循環電流を制御するマイナーループを構成することによって、全ての変換器セル7、又は、グループ毎の複数個の変換器セル7での蓄積エネルギの過不足を抑制する。 指令分配部606は、交流制御指令値Vcpと、循環制御指令値Vzpと、直流電圧指令値Vdcrefと、中性点電圧Vsnと、交流電圧Vacとを受ける。電力変換器2の交流側が変圧器13を介して交流回路12に接続されているため、中性点電圧Vsnは、直流回路14の直流電源の電圧により求めることができる。直流電圧指令値Vdcrefは、直流出力制御により与えられても、一定値でもよい。 指令分配部606は、これらの入力に基づいて、上アーム及び下アームがそれぞれ出力分担する電圧を算出する。指令分配部606は、算出した電圧から上アーム又は下アーム内のインダクタンス成分による電圧降下分をそれぞれ差し引くことによって、上アームのアーム電圧指令値krefp、及び、下アームのアーム電圧指令値krefnを決定する。 決定された上アームのアーム電圧指令値krefp、及び下アームのアーム電圧指令値krefnは、交流電流Iacを交流電流指令値Iacrefに追従させ、循環電流Izを循環電流指令値Izrefに追従させ、直流電圧Vdcを直流電圧指令値Vdcrefに追従させるとともに、交流電圧Vacをフィードフォワード制御する出力電圧指令となる。この様に、循環電流Izを循環電流指令値Izrefに追従させるための循環制御指令値Vzpは、アーム電圧指令値krefp,krefnに反映されている。即ち、電圧マクロ制御部610によって算出される循環電流指令値Izref、又は、循環制御指令値Vzpは、同一アームに含まれるNcell個の変換器セル7に対して共通に設定される「制御値」の一実施例に相当する。 基本制御部502は、上アームのアーム電流Iarmpと、下アームのアーム電流Iarmnと、上アームのアーム電圧指令値krefpと、下アームのアーム電圧指令値krefnとを出力する。 図6は、アーム制御部503の構成例を説明するブロック図である。 図6を参照して、アーム制御部503は、Ncell個の個別セル制御部202を含む。 個別セル制御部202は、対応する変換器セル7を個別に制御する。個別セル制御部202は、基本制御部502からアーム電圧指令値kref、アーム電流Iarm、及び、キャパシタ指令電圧値Vcrefを受ける。 個別セル制御部202は、対応する変換器セル7のゲート信号gaを生成して、対応する変換器セル7へ出力する。ゲート信号gaは、図2(a)の変換器セル7では、スイッチング素子31p及び31nのオンオフを制御する信号である(n=2)。尚、変換器セル7が、図2(b)のフルブリッジ構成である場合には、スイッチング素子31p1,31n1,31p2,31n2のそれぞれのゲート信号が生成される(n=4)。一方で、各変換器セル7の電圧検出器33からの検出値(キャパシタ電圧Vc)は、図5に示された電圧評価値生成部700へ送出される。 図7は、図6に示された個別セル制御部202の構成例を示すブロック図である。 図7を参照して、個別セル制御部202は、キャリア発生器203と、個別電圧制御部205と、加算器206と、ゲート信号生成部207とを有する。 キャリア発生器203は、位相シフトPWM(Pulse Width Modulation)制御で用いられる、ある定められた周波数を有するキャリア信号CSを生成する。位相シフトPWM制御とは、同一アーム(上アーム5又は下アーム6)を構成する複数(Ncell個)の変換器セル7のそれぞれに対して出力されるPWM信号のタイミングを相互にずらすものである。 これによって、各変換器セル7の出力電圧の合成電圧に含まれる高調波成分が削減されることが知られている。例えば、キャリア発生器203が、アーム制御部503から受信した共通の基準位相θiに基づいて、上記Ncell個の変換器セル7の間で相互に位相のずれたキャリア信号CSを生成する。 個別電圧制御部205には、電圧指令値Vcell*と、対応する変換器セル7のキャパシタ電圧Vcと、対応する変換器セル7が属するアームのアーム電流とを受ける。電圧指令値Vcell*は、図5の全電圧制御部612の電圧指令値Vc*と共通の値(固定値)に設定することができる。或いは、同一アーム内でのキャパシタ電圧Vcを均一化するために、電圧指令値Vcell*は、同一アームに含まれるNcell個の変換器セル7のキャパシタ電圧の平均値に設定されてもよい。 個別電圧制御部205は、電圧指令値Vcell*に対するキャパシタ電圧Vcの偏差に演算を施して、個別電圧制御のための制御出力dkrefcを算出する。個別電圧制御部205についても、PI制御又はPID制御等を実行する制御器によって構成することが可能である。又、上記制御器による演算値に対して、アーム電流Iarmの極性に応じて、「+1」又は「-1」を乗算することによって、上記偏差を解消する方向にキャパシタ32を充放電するための制御出力dkrefcが算出される。 加算器206は、基本制御部502からのアーム電圧指令値krefと、個別電圧制御部205の制御出力dkrefとを加算することによって、セル電圧指令値krefcを出力する。 ゲート信号生成部207は、キャリア発生器203からのキャリア信号CSによって、セル電圧指令値krefcをPWM変調することでゲート信号gaを生成する。 図8は、図7に示されたゲート信号生成部によるPWM変調制御を説明するための概念的な波形図である。尚、図8に示された信号波形は説明のために誇張したものであり、実際の信号波形をそのまま示したものではない。 図8を参照して、セル電圧指令値krefcは、代表的には三角波で構成されるキャリア信号CSと、電圧比較される。セル電圧指令値krefcの電圧が、キャリア信号CSの電圧よりも高いときには、PWM変調信号Spwmはハイレベル(Hレベル)に設定される。反対に、キャリア信号CSの電圧がセル電圧指令値krefcの電圧よりも高いときには、PWM変調信号Spwmはローレベル(Lレベル)に設定される。 例えば、PWM変調信号SpwmのHレベル期間では、図2(a)の変換器セル7において、スイッチング素子31pをオンする一方で、スイッチング素子31nをオフするようにゲート信号ga(n=2)が生成される。反対に、PWM変調信号SpwmのLレベル期間では、スイッチング素子31nをオンする一方で、スイッチング素子31pをオフするようにゲート信号ga(n=2)が生成される。 ゲート信号gaとして、変換器セル7のスイッチング素子31p、31nのゲートドライバ(図示せず)に送出されることによって、変換器セル7のスイッチング素子31p、31nがオンオフ制御される。 セル電圧指令値krefcは、制御出力dkrefによって修正された、正弦波電圧に相当する。従って、制御装置3では、当該正弦波電圧(アーム電圧指令値kref)の振幅(又は、実効値)と、キャリア信号CSの振幅から、PWM変調での変調率指令値を公知の手法によって算出することが可能である。 (電圧評価値生成部の構成例) このように、本実施の形態に係る電力変換装置では、変換器セル7のキャパシタ電圧Vcは、変換器セル7毎での個別制御(個別電圧制御部205)と、電力変換器2の全体、又は、同じグループ(各相レグ回路又はアーム)内の複数の変換器セル7での蓄積エネルギを制御するためのマクロ制御(電圧マクロ制御部610)との多階層で制御されることが理解される。 本実施の形態の電力変換器の特徴点である、マクロ制御に用いられる電圧評価値Vcgを算出する電圧評価値生成部700(図5)の実施の形態1に係る構成例について、以下に説明を進める。 図9~図15は、実施の形態1に係る電圧評価値生成部の第1~第7の構成例を説明するブロック図である。 図9を参照して、実施の形態1の第1の構成例では、電圧評価値生成部700は、最大値抽出部711によって構成された評価値算出部710を少なくとも1個有する。 最大値抽出部711には、予め定められたグループ、例えば、同一のレグ回路4、又は、同一のアーム(各相での上アーム5或いは下アーム6)に含まれる複数個(2×Ncell個、又は、Ncell個)の変換器セル7から、電圧検出器33によるキャパシタ電圧Vcの検出値が入力される。最大値抽出部711は、入力された複数個のキャパシタ電圧Vcのうちの最大値を抽出し、電圧評価値生成部700は、最大値抽出部711によって抽出された最大値を、電圧評価値Vcgとして出力する。 例えば、電圧評価値生成部700が、電圧評価値Vcgとして、U相電圧評価値Vcgu、V相電圧評価値Vcgv、及び、V相電圧評価値Vcgvを出力する場合には、U相、V相、及び、W相の各々に対応して設けられた最大値抽出部711に対して、レグ回路4u(U相)、4v(V相)、及び、4w(W相)のいずれかに含まれる複数の変換器セル7から(2×Ncell)個のキャパシタ電圧Vcが入力される。これにより、電圧評価値生成部700からは、各相に対応する最大値抽出部711によって抽出された、(2×Ncell)個のキャパシタ電圧Vcの最大値が、U相電圧評価値Vcgu、V相電圧評価値Vcgv、及び、V相電圧評価値Vcgvとして出力される。 又、電圧評価値生成部700が、電圧評価値Vcgとして、各相のアーム(上アーム5又は下アーム6)毎の電圧評価値を生成する場合には、各相の上アーム5及び下アーム6の各々に対応して設けられた最大値抽出部711に対して、当該上アーム5又は下アーム6に含まれる複数の変換器セル7からNcell個のキャパシタ電圧Vcが入力される。この場合には、(3×2)個の最大値抽出部711によって抽出されたNcell個のキャパシタ電圧Vcの最大値が、計6個のアームのそれぞれの電圧評価値として出力される。 或いは、電力変換器2を構成する全ての変換器セル7のキャパシタ電圧Vc(3×2×Ncell個)のうちの最大値を、全電圧評価値Vcgallとして出力することも可能である。 図10を参照して、実施の形態1の第2の構成例では、電圧評価値生成部700は、少なくとも1個の最小値抽出部712によって構成された評価値算出部710を少なくとも1個有する。最小値抽出部712には、図9の最大値抽出部711と同様の複数個のキャパシタ電圧Vcが入力される。最小値抽出部712は、入力された複数個のキャパシタ電圧Vcのうちの最小値を抽出し、電圧評価値生成部700は、最小値抽出部712によって抽出された最小値を、電圧評価値Vcgとして出力する。 第2の構成例によれば、各グループ内のキャパシタ電圧Vcの最小値がグループ間で均衡するように制御する、或いは、全ての変換器セル7内でのキャパシタ電圧Vcの最小値を全電圧指令値Vc*に制御するように、電圧マクロ制御部610が動作することになる。従って、キャパシタ電圧Vcの過低下に対する保護効果を高める制御が実現できる。 図11を参照して、実施の形態1の第3の構成例では、電圧評価値生成部700は、最大値抽出部711と、最小値抽出部712と、平均値演算部713とによって構成された評価値算出部710を少なくとも1個有する。 最大値抽出部711の入出力、及び、最小値抽出部712の入出力は、図9及び図10と同様である。平均値演算部713は、最大値抽出部711から出力されたVcmax及び最小値抽出部712から出力されたVcminとの平均値((Vcmax+Vcmin)/2)を出力する。 電圧評価値生成部700は、平均値演算部713によって算出された、最大値及び最小値の平均値を、電圧評価値Vcgとして出力する。このように算出された電圧評価値Vcgは、単純なキャパシタ電圧Vcの平均値と比較して、最大値及び最小値が高い重み付けで反映されている。又、第1及び第2の構成例と比較すると、最大値及び最小値の平均を取ることによって、キャパシタ電圧Vcのばらつき及び平均に関する情報についても、電圧評価値Vcgに反映することができる。 第3の構成例によれば、電圧マクロ制御部610によって、キャパシタ電圧Vcの平均及びばらつきを制御するとともに、過上昇及び過低下の保護効果を高めることが期待できる。 図12を参照して、実施の形態1の第4の構成例では、電圧評価値生成部700は、少なくとも1個の最頻値抽出部714によって構成された評価値算出部710を少なくとも1個有する。最頻値抽出部714には、図9の最大値抽出部711、及び、図10の最小値抽出部712と同様の複数個のキャパシタ電圧Vcが入力される。最頻値抽出部714は、入力された複数個のキャパシタ電圧Vcの最頻値を抽出する。 例えば、複数個のキャパシタ電圧について、予め定められた複数の電圧領域に区分して、最大個数のキャパシタ電圧Vcが区分された電圧領域の中心値を、上記最頻値として抽出することができる。電圧評価値生成部700は、最頻値抽出部714によって抽出された最頻値を、電圧評価値Vcgとして出力する。 第4の構成例によれば、各グループ内のキャパシタ電圧Vcの最頻値がグループ間で均衡するように制御する、或いは、全での変換器セル7内でのキャパシタ電圧Vcの最頻値を全電圧指令値Vc*に制御するように、電圧マクロ制御部610が動作することになる。従って、キャパシタ電圧Vcの分布を考慮して、蓄積エネルギの平均的なレベルについて、過不足又は不均衡を適切に解消することが期待できる。 図13を参照して、実施の形態1の第5の構成例では、電圧評価値生成部700は、代表値抽出部715と、選択切替部716とによって構成された評価値算出部710を少なくとも1個有する。 代表値抽出部715には、図9の最大値抽出部711、及び、図10の最小値抽出部712と同様の複数個のキャパシタ電圧Vcが入力される。選択切替部716は、代表値抽出部715に入力されるキャパシタ電圧Vcの個数(ここでは、N個とする)のうちの1つを選択するための選択信号SLを生成する。選択切替部716は、一定周波数を有するクロックCLKcnの1周期毎、又は、複数周期毎に選択信号SLを切り替える。 例えば、選択切替部716は、乱数発生器(図示せず)から出力される乱数に基づいて、選択信号SLを生成することができる。或いは、選択切替部716は、クロックCLKnに応じてカウントアップされるカウント値を用いて、Ncell個の変換器セル7を順番に選択するように、選択信号SLを生成することも可能である。 代表値抽出部715は、入力されたNcell個のキャパシタ電圧Vcから、選択切替部716からの選択信号SLに従って1個のキャパシタ電圧Vcを抽出する。電圧評価値生成部700は、代表値抽出部715によって、乱数に従ってランダムに抽出された、或いは、カウント値に応じて順次抽出されたキャパシタ電圧Vcの代表値を、電圧評価値Vcgとして出力する。 第5の構成例によれば、乱数又はカウント値に従って抽出されたキャパシタ電圧Vcを電圧評価値Vcgとするので、電圧評価値Vcgを生成する際の演算負荷が軽減される。又、ランダム抽出又は順次抽出された代表値を電圧評価値Vcgとすることで、キャパシタ電圧Vcの平均及びばらつきを反映した電圧マクロ制御部610による制御が実現できる。 図14を参照して、実施の形態1の第6の構成例では、電圧評価値生成部700は、キャパシタ電圧推定部717によって構成された評価値算出部710を少なくとも1個有する。例えば、キャパシタ電圧推定部717は、各相の上アーム5及び下アーム6の各々に対応して配置される。キャパシタ電圧推定部717は、「第1の電圧推定部」の一実施例に対応する。 ここでは、キャパシタ電圧推定部717は、1アーム分のキャパシタ電圧Vcの推定値を、アーム電流Iarm及び変調率指令値Amに基づいて算出する。上述のように、各相の上アーム5及び下アーム6のアーム電流larm(Iarmp,Iarmn)は、アーム電流検出器9A及び9Bによって検出される。又、上述の様に、各アームでのアーム電圧指令値kref(正弦波電圧)に対して、PWM変調での変調率指令値Amが算出できる。例えば、図2(a)のハーフブリッジ構成の変換器セル7では、変調率指令値Amは、0~1.0の範囲内である。 各アームにおいて、アーム電流Iarm及び変調率指令値Amの乗算値を時間積分すると、Ncell個の変換器セル7に入出力された電荷量を推定することができる。 従って、アーム単位でのキャパシタ電圧Vcを下記の式(3)に従って推定することができる。式(1)中のCsmは、各キャパシタ32の容量(公称値)であり、Carmは、1アーム分の変換器セル7でのキャパシタ32の容量値の総和を意味している。 Vcg=(1/Carm)×∫(Am×Iarm)dt ...(3) 但し、Carm=Csm×Ncell 又、式(1)に従った、上アーム5及び下アーム6のキャパシタ電圧推定値を平均することで、各相(レグ回路4)のキャパシタ電圧Vcの推定値を求めることも可能である。 第6の構成例によれば、アーム毎又は相毎の電圧評価値Vcg(グループ毎電圧評価値Vcgr)について、キャパシタ32の充放電によってキャパシタ電圧Vcの検出値が変化するよりも早く、キャパシタ32の充放電電流の挙動から蓄積エネルギの変化を反映して求めることができる。この結果、当該電圧評価値Vcgに基づく電圧マクロ制御部610の動作により、グループ間(各相レグ回路間又はアーム間)での蓄積エネルギの不均衡を速やかに解消することが可能となる。 図15を参照して、実施の形態1の第7の構成例では、電圧評価値生成部700は、キャパシタ電圧推定部718によって構成された評価値算出部710を有する。キャパシタ電圧推定部718は、電圧評価値Vcgのうち、全電圧評価値Vcgallを算出する。キャパシタ電圧推定部718は、「第2の電圧推定部」の一実施例に対応する。 キャパシタ電圧推定部718は、電力変換器2と外部回路(例えば、図1における交流回路12及び直流回路14)との間で入出力される瞬時電力の総和である、電力変換器2全体でのトータル入出力電力Ptを求める。 交流入力端子Nu,Nv,Nwの各々において、交流電流検出器16による交流電流Iacu,Iacv,Iacwの検出値、及び、交流電圧検出値による交流電圧Vacu,Vacv,Vacwの検出値から、交流回路12との間で入出力される瞬時電力Pacを、各時点で算出することができる。同様に、高電位側直流端子Np及び低電位側直流端子Nnにおいて、直流電圧検出器11A,11BによるVdc=(Vdcp-Vdcn)の検出値と、直流電圧検出器17による直流電流Idcの検出値とから、直流回路14とので入出力される瞬時電力Pdcを、各時点で算出することができる。尚、直流電圧(Vdc)は、上アーム5及び下アーム6に含まれる複数の変換器セル7のキャパシタ電圧Vc(検出値)の総和によっても算出することができる。上述のトータル入出力電力Ptは、瞬時電力Pac及びPdcの和に従って求めることができる。 更に、当該トータル入出力電力Ptの時間積分値によって、電力変換器2全体での変換器セル7(キャパシタ32)の蓄積エネルギの総和の変化を推定することで、1個の変換器セル7でのキャパシタ電圧Vcを下記の式(4)に従って算出することができる。 Vcg=(1/Ct)×(1/Vsm)×∫Ptdt ...(4) 式(4)において、Ctは、電力変換器2全体での変換器セル7でのキャパシタ32の容量値の総和を意味しており、Ct=3×2×Ncell×Csmで与えられる。又、Vsmは、各キャパシタ32の電圧の公称値を意味している。 第7の構成例によれば、電圧評価値Vcgのうちの全電圧評価値Vcgallについて、キャパシタ32の充放電によってキャパシタ電圧Vcの検出値が変化するよりも早く、キャパシタ32の充放電電流の挙動から蓄積エネルギの変化を反映して求めることができる。この結果、当該電圧評価値Vcgに基づく電圧マクロ制御部610の動作により、グループ間(各相レグ回路間又はアーム間)での蓄積エネルギの不均衡を速やかに解消することが可能となる。 又、第6の構成例(図14)及び第7の構成例(図15)では、キャパシタ電圧Vcの検出値を用いることなく、電圧評価値Vcgを求めることが可能である。 実施の形態1の変形例. 図16は、実施の形態1の変形例に係る電圧評価部の構成例を説明するブロック図である。 図16を参照して、実施の形態1の変形例に係る電圧評価値生成部700は、異常値除去部720と、評価値算出部710とを含む。評価値算出部710は、図9~図13に示した第1~第5の構成例のいずれかと同様である。異常値除去部720は、図9~図13において、最大値抽出部711、最小値抽出部712、最頻値抽出部714、及び、代表値抽出部715に入力されるのと同様の複数個のキャパシタ電圧Vcが入力される。 異常値除去部720は、入力された複数個のキャパシタ電圧Vcから、Vc&lt;Vchkminのもの、及び、Vc&gt;Vchkmaxのものを異常値として除去する。 尚、キャパシタ電圧Vcについての過電圧(OV)保護のための判定電圧Vov、及び、低電圧(UV)保護のための判定電圧Vuvと、異常値除去部720での判定電圧Vchkmin,Vchkmaxとの間には、Vuv&lt;Vchk&lt;&lt;Vc*(Vsm)&lt;&lt;Vchkmax&lt;Vovの関係が成立する。 異常値除去部720は、異常値の除去後の残りのキャパシタ電圧Vcを、最大値抽出部711、最小値抽出部712、最頻値抽出部714、及び、代表値抽出部715の少なくともいずれかに入力する。これらのキャパシタ電圧Vcが入力された後の、最大値抽出部711、最小値抽出部712、最頻値抽出部714、及び、代表値抽出部715の動作は、実施の形態1と同様であるので、詳細な説明は繰り返さない。 このように、実施の形態1の変形例によれば、異常値が除去されたキャパシタ電圧Vcに基づいて電圧評価値Vcgが算出されることにより、電圧マクロ制御部610による上述の制御の性能を向上することができる。 実施の形態2. 図17は、実施の形態2に係る電圧評価部の構成例を説明するブロック図である。 図17を参照して、実施の形態2に係る電圧評価値生成部700は、複数の評価値算出部710と、出力選択部725とを含む。 複数の評価値算出部710には、図9~図15に示した評価値算出部710の少なくとも一部が適用される。又、複数の評価値算出部710の入力側には、図16に示した異常値除去部720を更に配置することも可能である。 出力選択部725は、電力変換器2の動作状況に応じて設定される選択信号Sslに従って、複数の評価値算出部710のそれぞれからの複数の出力値のうちの1つの出力値を選択する。電圧評価値生成部700は、出力選択部725によって選択された出力値を、電圧評価値Vcgとして電圧マクロ制御部610へ出力する。 例えば、選択信号Sslは、電圧検出器33による電圧検出状態に応じて変化することができる。一例として、全ての電圧検出器33によってキャパシタ電圧Vcが検出されているときには、図9~図12に示された、最大値及び最小値の少なくとも一方の抽出に従う評価値算出部710の出力値を選択する一方で、いずれかの電圧検出器33による電圧検出に異常が生じた場合には、これに代えて、図13~図15に示された、第4~7の構成例に係る評価値算出部710のいずれかの出力値を選択することができる。 又、電圧検出器33による検出値に異常値が多いとき(例えば、異常値除去部720による除去数が予め定められた値より大きいとき)には、キャパシタ電圧Vcの検出値を用いない、図14及び図15に示した第6及び第7の構成例に係る評価値算出部710のいずれかの出力値を選択することができる。 このように、実施の形態2によれば、電力変換器2の動作状況(例えば、各変換器セル7での電圧検出器33の異常/正常、又は、キャパシタ電圧Vcの分布状況)に基づき、電圧マクロ制御部610で用いられる電圧評価値Vcgを適切に生成することができる。 実施の形態3. 図18は、実施の形態3に係る電圧評価部の第1の構成例を説明するブロック図である。 図18を参照して、実施の形態3に係る電圧評価値生成部700は、評価値算出部710と、フィルタ730とを含む。評価値算出部710は、図9~図15に示した第1~第7の構成例のいずれかと同様である。又、評価値算出部710の入力側には、図16に示した異常値除去部720を適宜配置することも可能である。 フィルタ730は、予め定められた特性を有するように設計される。例えば、フィルタ730は、短時間の変化分を除くために、逐次生成される評価値算出部710の出力値を平均化する特性を有するように構成される。この場合には、一次遅れ系等の低域通過フィルタ、又は、移動平均値或いは積分平均値を算出するフィルタによって、フィルタ730を構成することができる。 或いはこれと反対に、フィルタ730は、短時間の変化分を抽出するために、評価値算出部710から逐次出力された出力値の変化分を抽出する特性を有するように構成されてもよい。この場合には、低域遮断(高域通過)フィルタ、又は、疑似微分フィルタ等によって、フィルタ730を構成することができる。 電圧評価値生成部700は、フィルタ730によって処理後された、評価値算出部710の出力値を、電圧評価値Vcgとして電圧マクロ制御部610へ出力する。 例えば、図9~図13に示された第1~第5の構成例に係る評価値算出部710と、平均化特性を有するフィルタ730との組み合わせにより、キャパシタ電圧Vcのリップル分の影響を除去して電圧評価値Vcgを生成することができる。これにより、電圧マクロ制御部610による制御を安定化することが可能となる。 一方で、図14及び図15に示された第6及び第7の構成例に係る評価値算出部710と、変化分を抽出する特性を有するフィルタ730との組み合わせにより、電流挙動又は電力挙動によるキャパシタ電圧Vcの変化分を速やかに反映して、電圧評価値Vcgを生成することができる。これにより、電圧マクロ制御部610による制御の応答性を高めることができる。 実施の形態4. 図19は、実施の形態4に係る電圧評価部の構成を説明するブロック図である。 図19を参照して、実施の形態4に係る電圧評価値生成部700は、実施の形態3で説明した、評価値算出部710及びフィルタ730の組をM個(M:2以上の自然数)備えるとともに、ゲイン乗算部740と、加算部745とを更に備える。 評価値算出部710の各々は、実施の形態3と同様に、図9~図15に示した第1~第7の構成例のいずれかと同様である。又、評価値算出部710の入力側には、図16に示した異常値除去部720を適宜配置することも可能である。 フィルタ730は、実施の形態3と同様に、予め定められた特性を有しており、評価値算出部710の出力値を通過させる。複数のフィルタ730の各々の特性は、互いに異なっていてもよく、少なくとも一部のフィルタ730で共通であってもよい。 ゲイン乗算部740は、複数(M個)のフィルタ730の出力値のそれぞれに対するゲインki(i=1~M)の乗算値を出力する。ゲインk1~kMの各々は、0以上1.0以下の範囲内に設定される。 加算部745は、ゲイン乗算部740からのM個の出力値を加算する。電圧評価値生成部700は、加算部745の出力値を、電圧評価値Vcgとして電圧マクロ制御部610へ出力する。特に、異なる周波数特性のフィルタ730を通過させることで、ゲインkiによる重み付けの調整によって、電圧評価値Vcgを適切に設定することが期待できる。 図20には、実施の形態4に係る電圧評価部の具体例を説明するブロック図が示される。 図20を参照して、実施の形態4に係る電圧評価値生成部700は、図11に示した評価値算出部710と、図14に示したキャパシタ電圧推定部717と、フィルタ730a,730bと、ゲイン乗算部740a,740bと、加算部745とを備える。 評価値算出部710は、図11で説明したように、同一グループ(相又はアーム)内の(Vcmax+Vcmin)/2を出力する。同様に、キャパシタ電圧推定部717は、同一グループ(相又はアーム)内のアーム電流Iarmから推定されたキャパシタ電圧推定値を出力する。 フィルタ730aは、逐次生成される評価値算出部710の出力値を平均化する特性を有するように構成される。上述のように、フィルタ730aは、一次遅れ系等の低域通過フィルタ、又は、移動平均値或いは積分平均値を算出するフィルタ等で構成することができる。 フィルタ730bは、キャパシタ電圧推定部717から逐次出力されたキャパシタ電圧推定値の変化分を抽出する特性を有するように構成される。上述のように、フィルタ730bは、低域遮断(高域通過)フィルタ、又は、疑似微分フィルタ等によって構成することができる。 ゲイン乗算部740aは、フィルタ730aの出力値に対するゲインkaの乗算値を出力する。ゲイン乗算部740bは、フィルタ730bの出力値に対するゲインkbの乗算値を出力する。ゲインka,kbの各々は、0以上1.0以下の範囲内に設定される。 加算部745は、ゲイン乗算部740a及び740bの出力値を加算する。電圧評価値生成部700は、加算部745の出力値を、電圧評価値Vcgとして電圧マクロ制御部610へ出力する。 図20において、評価値算出部710(図11)は「第1の評価値算出部」の一実施例に対応し、キャパシタ電圧推定部717は「第2の評価値算出部」の一実施例に対応し、フィルタ730aは「第1のフィルタ」の一実施例に対応し、フィルタ730bは「第2のフィルタ」の一実施例に対応する。又、ゲインkaは「第1のゲイン」に対応し、ゲインkbは「第2のゲイン」に対応する。 図20の具体例では、キャパシタ電圧Vcの検出に基づく、評価値算出部710(図11)の算出値に対しては、フィルタ730a(低域通過フィルタ)を通過させてリップル電圧の影響を除去する。一方で、キャパシタ電圧推定部717による、アーム電流Iarmの挙動が反映されるキャパシタ電圧推定値に対して、フィルタ730b(低域遮断フィルタ)の通過によってキャパシタ電圧Vcの変化分を抽出することが可能である。 更に、両者をゲインka,kbによる重み付けの調整を伴って加算することで、リップル変動の影響を抑制し、かつ、アーム電流Iarmによる電圧変化を速やかに反映するように、電圧評価値Vcgを生成することができる。この結果、電圧マクロ制御部610による制御の安定性及び応答性を高めることが可能である。 尚、電圧評価値Vcgを用いた、複数の変換器セル7を単位とした蓄積エネルギの制御について、図5では、電圧マクロ制御部610によって循環電流を制御するマイナーループの制御値(循環電流指令値Izref、又は、循環制御指令値Vzp)を生成する制御を例示したが、電圧評価値Vcgを用いた制御はこのような例に限定されるものではないことを確認的に記載する。即ち、上述した、全ての変換器セル7、又は、グループ毎の複数個の変換器セル7等でのキャパシタ電圧Vcの平均値の制御において、本実施の形態で説明した電圧評価値Vcgを制御対象値とすることが可能である。 例えば、実施の形態1では、図5において、変換器セル7間での蓄積エネルギの過不足を制御するための循環制御指令値Vzpが、指令分配部606において、アーム電圧指令値krefp,krefnに反映される制御を説明した。しかしながら、循環制御指令値Vzpによる制御は、図5の例に限定されるものではない。例えば、各個別セル制御部202でのPWM制御に用いられるキャリア信号の変調によって、変換器セル7間での蓄積エネルギの過不足を制御することも可能である。 図21は、個別セル制御部の他の構成例を説明するブロック図である。 図21を参照して、変形例に係る個別セル制御部202は、図5の構成と比較して、キャリア発生器203に、図5の循環制御指令値Vzpが入力される点で異なる。一方で、図5のアーム電圧指令生成部601では、循環制御指令値Vzpが指令分配部606に入力されなくなり、指令分配部606は、循環制御指令値Vzpを反映することなく、アーム電圧指令値krefp,krefnを生成する。 図5で説明したように、循環制御指令値Vzpは、電圧評価値Vcg(全電圧評価値Vcgall及びグループ毎電圧評価値Vcgr)を用いて生成されており、同一のグループ(各相レグ回路又は各アーム)に属する複数個の変換器セル7の各個別セル制御部202に対して、共通の値が入力される。 図21の構成において、個別電圧制御部205の機能は、図7と同様である。一方で、キャリア発生器203は、図5と同様の、基準位相θiに従う位相シフトPWM制御のためのキャリア信号を、循環制御指令値Vzpに応じて変調することでキャリア信号CSを生成する。ゲート信号生成部207は、図5で説明したのと同様に、キャリア発生器203からのキャリア信号CSと、セル電圧指令値krefcとの比較に従うPMW変調信号Spwmを用いてゲート信号gaを生成する。この際に、キャリア信号CSが循環制御指令値Vzpに応じて変調されることにより、図22及び図23で説明するように、PMW変調信号Spwm(即ち、ゲート信号ga)のパルス幅は、循環制御指令値Vzpに応じて、図5での循環電流Iz及び循環電流指令値Izrefとの差がより小さくなるように制御されることになる。 図22及び図23を用いて、キャリア信号の変調手法の例として、ベースライン変調及び周波数変調について説明する。図22には、キャリア信号変調の第1の例として、ベースライン変調を説明する概念的な波形図が示される。一方で、図23には、キャリア信号変調の第2の例として、周波数変調を説明する概念的な波形図が示される。尚、キャリア信号CSの変調手法は、これらの方法には限定されない。最終的に生成されるPMW変調信号Spwm(即ち、ゲート信号ga)のパルス幅が循環電圧指令値に応じて変化する(例えば、循環制御指令値Vpzが大きいほどPMW変調信号Spwmのパルス幅が広くなる)ように制御可能であれば、任意の変調方法を適用することが可能である。 ベースライン変調が行われない場合には、図8に示されたように、三角波のキャリア信号CSのベースラインBL=0に固定される。図8では、BL=0に固定されたキャリア信号CSと、アーム電圧指令値krefとを比較するPWM変調によって、PMW変調信号Spwm(ゲート信号ga)が生成される。 図22を参照して、ベースライン変調では、図8と同様の三角波のキャリア信号CSの基準電位であるベースラインBLが、循環制御指令値Vpzに応じて変化する。尚、図8及び図22の間で、アーム電圧指令値krefの波形は同一である。図22についても、図8と同様に、信号波形は説明のために誇張したものであり、実際の信号波形をそのまま示したものではない。 図22のPMW変調信号Spwmは、図8と比較すると、ベースラインBLが循環制御指令値Vpzに応じて変化するため、パルス幅がベースラインBLの変化に応じて変化することが理解される。具体的には、ベースラインBLがより低電位になると、PMW変調信号Spwmのパルス幅がより大きくなる一方で、ベースラインBLがより高電位になると、PMW変調信号Spwmのパルス幅がより小さくなる。このように、キャリア信号CSのベースライン変調によっても、循環制御指令値Vpzに応じてPMW変調信号Spwmのパルス幅を変化させることができる。 図23を参照して、周波数変調では、キャリア信号CSの周波数が、循環制御指令値Vpzに応じて変化する。図23では、キャリア信号CSとしてのこぎり波状のパルス波形が用いられる。 図23では、キャリア信号CSを構成する各単一パルスの波形は同一であるが、その生成頻度(すなわち、キャリア信号CSの周波数)が、循環制御指令値Vpzに応じて変化する。具体的には、図23の例では、循環制御指令値Vpzが小さいほどキャリア信号CSの周波数が高くなり、この結果、PMW変調信号Spwm(ゲート信号ga)のパルス幅が小さくなる。逆に、循環制御指令値Vpzが大きいほどキャリア信号CSの周波数が低くなり、この結果、PMW変調信号Spwm(ゲート信号ga)のパルス幅が大きくなる。このように、キャリア信号CSの周波数変調によっても、循環制御指令値Vpzに応じてPMW変調信号Spwmのパルス幅を変化させることができる。 このように、図21~図23で説明したキャリア信号変調によっても、電圧評価値Vcgを用いて生成された循環制御指令値Vzpに従って、変換器セル7間での蓄積エネルギの過不足を制御することができる。通常、アーム電流の大きさに比べて、循環電流はかなり小さいため、図5のように、アーム電圧指令値krefに対して循環制御指令値Vpzを反映する制御では、量子化ビット数の影響で、循環制御指令値Vpzの変化をアーム電圧指令値krefに十分に反映できないことが懸念される。これと比較すると、キャリア信号変調による制御では、循環電流の制御精度の向上が期待できる。 又、図1では、電力変換器2は、いわゆるダブルスター型と呼ばれる構成を有しており、主にHVDC(High Voltage Direct Current)送電用の交直変換器に使われる。しかしながら、上記の実施形態で説明した電力変換器の制御は、他の構成の電力変換器にも適用することが可能である。 例えば、図24に示されるように、シングルデルタ型と呼ばれる構成を有する電力変換器2に対しても、本実施の形態で説明した制御を適用することが可能である。 或いは、図25に示されるように、シングルスター型と呼ばれる構成を有する電力変換器2に対して、本実施の形態で説明した制御を適用することが可能である。図24及び図25に示された電力変換器2の構成は、主に無効電力補償装置に適用されることが知られている。 今回開示された実施の形態はすべての点で例示であって制限的なものではないと考えられるべきである。本発明の範囲は上記した説明ではなくて請求の範囲によって示され、請求の範囲と均等の意味及び範囲内でのすべての変更が含まれることが意図される。 1 電力変換装置、2 電力変換器、3 制御装置、4,4u,4v,4w レグ回路、5 上アーム、6 下アーム、7 変換器セル、8A,8B リアクトル、9A,9B アーム電流検出器、10 交流電圧検出器、11A,11B,17 直流電圧検出器、12 交流回路、13 変圧器、14 直流回路、16 交流電流検出器、31n2,31n1,31n,31p,31p2,31p1 スイッチング素子、32 キャパシタ(蓄電素子)、33 電圧検出器、70 入力変換器、71 サンプルホールド回路、72 マルチプレクサ、73 変換器、75 RAM、76 ROM、77 入出力インターフェイス、78 補助記憶装置、79 バス、202 個別セル制御部、203 キャリア発生器、205 個別電圧制御部、206 加算器、207 ゲート信号生成部、501 スイッチング制御部、502,502U,502V,502W 基本制御部、503,503UN,503UP,503VN,503VP,503WN,503WP アーム制御部、601 アーム電圧指令生成部、603 交流電流制御部、604 循環電流算出部、605 循環電流制御部、606 指令分配部、610 電圧マクロ制御部、611,613 減算部、612 全電圧制御部、614 グループ間電圧制御部、615,745 加算部、700 電圧評価値生成部、710 評価値算出部、711 最大値抽出部、712 最小値抽出部、713 平均値演算部、714 最頻値抽出部、715 代表値抽出部、716 乱数発生器、717,718 キャパシタ電圧推定部、720 異常値除去部、725 出力選択部、730,730a,730b フィルタ、740,740a,740b ゲイン乗算部、Am 変調率指令値、CLKn クロック、CS キャリア信号、Iacref 交流電流指令値、Iacu,Iacv,Iacw 交流電流、Iarm アーム電流、Idc 直流電流、Iz 循環電流、Izref 循環電流指令値、Nn 低電位側直流端子、Np 高電位側直流端子、Nu,Nv,Nw 交流入力端子、P1,P2 入出力端子、Spwm 変調信号、Ssl 選択信号、Vacu,Vacv,Vacw 交流電圧、Vc キャパシタ電圧、Vcg 電圧評価値、Vcgall 全電圧評価値、Vcgr グループ毎電圧評価値、Vdcn,Vdcp 直流電圧、Vdcref 直流電圧指令値、Vsn 中性点電圧、Vzp 循環制御指令値、ga ゲート信号、kref,krefn,krefp アーム電圧指令値、krefc セル電圧指令値。 [EN WO2021111502A1]: Power converter The present invention relates to a power converter. Modular Multilevel Converter (MMC), in which multiple unit converters (hereinafter referred to as "converter cells") are connected in cascade, is known as a large-capacity power converter installed in the power system. Has been done. Usually, a converter cell includes a plurality of switching elements and a power storage element (typically, a capacitor). In a modular multi-level converter, it is necessary to maintain the voltage (capacitor voltage) of the power storage element of each converter cell near the target value in order to obtain a desired control output. If the capacitor voltage deviates from the target value, the output voltage of the converter cell does not follow the command, and there is a concern that the control characteristics may deteriorate due to the unintended generation of circulating current or the like. In significant cases, in any of the transducer cells, the capacitor voltage may over-rise or fall to the level of overvoltage (OV) protection or undervoltage (UV) protection, causing MMC operation to stop. .. Normally, the capacitor voltage is controlled by the entire converter cell in the MMC (hereinafter, also referred to as "total voltage control") in addition to the capacitor voltage control for each individual converter cell (hereinafter, also referred to as "individual control"). It is generally controlled in multiple layers by balance control between a certain group (for example, arm or phase). For example, Japanese Patent No. 4999930 (Patent Document 1) states that in a power conversion device hav
[ZH CN211701885U]: 一种模块化多电平换流器集中控制系统 [EN CN211701885U]: Modular multilevel converter centralized control system | [ZH CN211701885U]: 本实用新型属于电力系统运行与控制技术领域，尤其涉及一种模块化多电平换流器集中控制系统，包括相互连接的：模块化多电平换流器以及集中控制系统，模块化多电平换流器包括三相电路，每相电路均包括相互串联的上、下桥臂，且上、下两桥臂分别与交流母线相连；各相电路并联后分别作为模块化多电平换流器直流侧的正、负极输出端；每个桥臂均包括若干级联的子模块HBSM及电感L。所述集中控制系统包括控制方式选择模块、换流器网侧交流电压检测模块、换流器网侧交流电流检测模块、基准值设定模块、运行参考值设定模块、标幺值变换模块、锁相环模块、派克变换模块、外环控制模块、内环控制模块、标幺值反变换模块、派克反变换模块、控制模块。 [EN CN211701885U]: The utility model belongs to the technical field of power system operation and control. The modular multilevel converter centralized control system comprises a modular multilevel converter and a centralized control system which are connected with each other, the modular multilevel converter comprises three phases of circuits, each phase of circuit comprises an upper bridge arm and a lower bridge arm which are connected in series, and the upper bridge arm and the lower bridge arm are respectively connected with an alternating current bus; all phases of circuits are connected in parallel and then respectively serve as positive and negative output ends of the direct current side of the modular multilevel converter; each bridge arm comprises a plurality of cascaded submodules HBSM and an inductor L0. The centralized control system comprises a control mode selection module. The system comprises a converter network side AC voltage detection module, a converter network side AC current detection module, a reference value setting module, an operation reference value setting module, a per-unit value conversion module, a phase-locked loop module, a Parker conversion module, an outer loop control module, an inner loop control module, a per-unit value inverse conversion module, a Parker inverse conversion module and a control module. | CN211701885U | 2020-10-16 | CN201921357459U | 2019-08-20 | CN201921357459U, 2019-08-20 | CN211701885U: 2020-10-16 | ELECTRIC POWER DISPATCHING CONTROL CT GUANGDONG POWER GRID CO LTD UNIV NORTH CHINA ELECTRIC POWER | CHEN HUICAN LIU HAOYU XU CHUNHUA LIU CHONGRU LIU SIJIE YU JIANYU WANG YU WANG JIECONG SHEN JINYI LI ZHIYU | H02M7/483: I |  |  |  | [ZH CN211701885U]: 1.一种模块化多电平换流器集中控制系统，其特征在于，包括相互连接的：模块化多电 平换流器以及集中控制系统，模块化多电平换流器包括三相电路，每相电路均包括相互串 联的上、下桥臂，且上、下两桥臂分别与交流母线相连;各相电路并联后分别作为模块化多 电平换流器直流侧的正、负极输出端;每个桥臂均包括若干级联的子模块HBSM及电感L0； 所述集中控制系统包括控制方式选择模块、换流器网侧交流电压检测模块、换流器网 侧交流电流检测模块、基准值设定模块、运行参考值设定模块、标幺值变换模块、锁相环模 块、派克变换模块、外环控制模块、内环控制模块、标幺值反变换模块、派克反变换模块、控 制模块； 所述控制方式选择模块用于设置外环控制器有功类控制方式； 所述换流器网侧交流电压检测模块用于对模块化多电平换流器运行过程中的网侧交 流电压进行实时检测，并将换流器网侧电压发送至标幺值变换模块； 所述基准值设定模块用于设置模块化多电平换流器运行过程中的系统容量、交流电压 和直流电压基准值，并将其发送至标幺值变换模块和标幺值反变换模块； 所述运行参考值设定模块用于设置模块化多电平换流器运行状态的参考值，其中包括 有功功率参考值和无功功率参考值，并将其发送至标幺值变换模块； 所述标幺值变换模块用于将换流器网侧电压和电流的有名值以及功率参考值的有名 值变成标幺值，并将换流器网侧电压标幺值发送至锁相环模块，将换流器网侧电压和电流 的标幺值发送至派克变换模块，将功率参考值的标幺值发送至外环控制模块； 所述锁相环模块用于锁出换流器网侧电压的相角，并将其发送至派克变换模块和派克 反变换模块； 所述派克变换模块用于将换流器网侧交流电压和电流从静止的三相坐标系变化到旋 转的d、q轴坐标系，并将换流器网侧交流电压和电流的d、q轴分量发送到外环控制模块和内 环控制模块;所述外环控制模块用于跟踪模块化多电平换流器的功率参考值来生成d、q轴 电流参考值，并将其发送到内环控制模块;所述内环控制模块跟踪外环控制模块生成的d、q 轴电流参考值，产生换流器输出电压的d、q轴参考值，并将其发送到标幺值反变换模块;所 述标幺值反变换模块将接收的换流器输出电压的d、q轴参考值标幺值变换成有名值，并将 其发送至派克反变换模块； 所述派克反变换模块用于换流器输出电压的d、q轴参考值变化到三相静止坐标系下， 并将其发送至控制模块;控制模块用于根据接收的换流器输出电压，产生三相调制波信号， 并发送到下层控制器，从而实现模块化多电平换流器的系统级控制。 [EN CN211701885U]: 1. A modular multilevel converter centralized control system, characterized in that it comprises interconnected: modular multilevel converter and a centralized control system, the modular multilevel converter includes a three-phase circuit Each phase circuit includes the upper and lower bridge arms connected in series, and the upper and lower bridge arms are respectively connected to the AC bus; each phase circuit is connected in parallel as the positive and negative output of the DC side of the modular multilevel converter. Each bridge arm includes several cascaded sub-modules HBSM and inductor L0; The centralized control system includes a control mode selection module, a converter grid-side AC voltage detection module, a converter grid-side AC current detection module, Reference value setting module, operating reference value setting module, standard unit value conversion module, phase-locked loop module, Parker conversion module, outer loop control module, inner loop control module, standard unit value inverse conversion module, Parker inverse conversion module, Control module; the control mode selection module is used to set the active power control mode of the outer loop controller; the inverter grid-side AC voltage detection module is used to communicate on the grid side during the operation of the modular multilevel converter The voltage is detected in real time, and the grid-side voltage of the converter is sent to the standard unit value conversion module; the reference value setting module is used to set the system capacity, AC voltage and DC voltage during the operation of the modular multilevel converter The voltage reference value is sent to the per-unit value conversion module and the per-unit value inverse conversion module; the operating reference value setting module is used to set the reference value of the operating state of the modular multilevel converter, including The active power reference value and the reactive power reference value are sent to the per-unit value conversion module; the per-unit value conversion module is used to convert the famous value of the voltage and current on the grid side of the converter and the famous value of the power reference value Convert the converter grid-side voltage to the phase-locked loop module, and send the converter grid-side voltage and current to the Parker transformation module, and send the power reference value to the unit The value is sent to the outer loop control module; the phase-locked loop module is used to lock the phase angle of the grid-side voltage of the converter, and send it to the Parker conversion module and the Parker inverse conversion module; the Parker conversion module is used to The AC voltage and current on the grid side of the converter change from a static three-phase coordinate system to a rotating d and q axis coordinate system, and the d and q axis components of the AC voltage and current on the grid side of the converter are sent to the outer loop control module And the inner loop control module; the outer loop control module is used to track the power reference value of the modular multilevel converter to generate the d and q axis current reference values, and send it to the inner loop control module; the inner The loop control module tracks the d and q axis current reference values generated by the outer loop control module, generates the d and q axis reference values of the converter output voltage, and sends it to the standard unit value inverse conversion module; the standard unit value is reversed The conversion module converts the received d and q axis reference value per unit value of the converter output voltage into a well-known value, and sends it to the Parker inverse conversion module; the Parker inverse conversion module is used for the d of the converter output voltage , Q-axis reference value changes to the three-phase stationary coordinate system, And send it to the control module; the control module is used to generate a three-phase modulation wave signal according to the received converter output voltage, and send it to the lower-level controller, so as to realize the system-level control of the modular multi-level converter. | [ZH CN211701885U]: 一种模块化多电平换流器集中控制系统 技术领域 [0001]本实用新型属于电力系统运行与控制技术领域，尤其涉及一种模块化多电平换流 器集中控制系统。 背景技术 [0002]模块化多电平换流器是一种新型电压源型换流器拓扑结构。基于子模块级联结构 的模块化多电平换流器具有很多优点，如保持较大桥臂等效开关频率的同时降低开关频率 和开关损耗，没有直接串联开关元件动作一致性问题，输出的交流电压波形质量好。因此， 模块化多电平换流器在高压大容量输送电能和电力驱动应用方面十分有前景。 [0003]最常用的模块化多电平换流器的控制系统为矢量控制系统，该控制系统分为外环 控制器和内环控制器，外环控制器根据系统运行参考值生成d、q轴电流参考值，内环控制器 跟踪外环控制器生成的d、q轴电流参考值生成系统的调制波。 [0004]如图1所示为矢量控制系统的控制框图，该控制系统是一种分布式的控制结构，控 制系统的各个组成部分是由单独的控制元件搭建而成的。在进行电磁暂态仿真时，需要使 用大量控制元件搭建模块化多电平换流器的控制系统，建模效率低下，参数设定繁杂，而且 容易出错。 实用新型内容 [0005]针对上述问题，本实用新型提出了一种模块化多电平换流器集中控制系统，包括 相互连接的:模块化多电平换流器(MMC)以及集中控制系统，模块化多电平换流器包括三相 电路，每相电路均包括相互串联的上、下桥臂，且上、下两桥臂分别与交流母线相连;各相电 路并联后分别作为模块化多电平换流器直流侧的正、负极输出端;每个桥臂均包括若干级 联的子模块HBSM及电感L0。 [0006]所述集中控制系统包括控制方式选择模块、换流器网侧交流电压检测模块、换流 器网侧交流电流检测模块、基准值设定模块、运行参考值设定模块、标幺值变换模块、锁相 环(PLL)模块、派克变换模块、外环控制模块、内环控制模块、标幺值反变换模块、派克反变 换模块、控制模块。 [0007] 所述控制方式选择模块用于设置外环控制器有功类控制方式。 [0008]所述换流器网侧交流电压检测模块用于对模块化多电平换流器运行过程中的网 侧交流电压进行实时检测，并将换流器网侧电压发送至标幺值变换模块。 [0009]所述基准值设定模块用于设置模块化多电平换流器运行过程中的系统容量、交流 电压和直流电压基准值，并将其发送至标幺值变换模块和标幺值反变换模块。 [0010]所述运行参考值设定模块用于设置模块化多电平换流器运行状态的参考值，其中 包括有功功率参考值(直流电压参考值)和无功功率参考值，并将其发送至标幺值变换模 块。 [0011]所述标幺值变换模块用于将换流器网侧电压和电流的有名值以及功率参考值的 有名值变成标幺值，并将换流器网侧电压标幺值发送至锁相环模块，将换流器网侧电压和 电流的标幺值发送至派克变换模块，将功率参考值的标幺值发送至外环控制模块。 [0012]所述锁相环模块用于锁出换流器网侧电压的相角，并将其发送至派克变换模块和 派克反变换模块。 [0013]所述派克变换模块用于将换流器网侧交流电压和电流从静止的三相坐标系变化 到旋转的d、q轴坐标系，并将换流器网侧交流电压和电流的d、q轴分量发送到外环控制模块 和内环控制模块;所述外环控制模块用于跟踪模块化多电平换流器的功率参考值来生成d、 q轴电流参考值，并将其发送到内环控制模块；所述内环控制模块跟踪外环控制模块生成的 d、q轴电流参考值，产生换流器输出电压的d、q轴参考值，并将其发送到标幺值反变换模块; 所述标幺值反变换模块将接收的换流器输出电压的d、q轴参考值标幺值变换成有名值，并 将其发送至派克反变换模块。 [0014]所述派克反变换模块用于换流器输出电压的d、q轴参考值变化到三相静止坐标系 下，并将其发送至控制模块；控制模块用于根据接收的换流器输出电压，产生三相调制波信 号，并发送到下层控制器，从而实现模块化多电平换流器的系统级控制。 [0015] 本实用新型的有益效果： [0016] 1、本实用新型设计了模块化多电平换流器的集中控制系统来实现系统级控制，其 采用的控制逻辑与分布式控制系统完全相同，因此可以取得和分布式控制系统完全相同的 控制效果。 [0017] 2、本实用新型由于采用了集中式的模块化多电平换流器控制系统，相比于分布式 的控制系统，用一个整体的控制器代替了数量众多的控制元件，极大地简化了建模过程，并 且参数可以集中调试，大幅度降低了出错概率。因此本实用新型可以广泛地应用于模块化 多电平换流器的系统级控制。 附图说明 [0018]图1为矢量控制系统控制结构图。 [0019]图2为模块化多电平换流器的拓扑结构图。 [0020]图3为送端换流站仿真结果图。 [0021]图4为受端换流站仿真结果图。 具体实施方式 [0022]下面结合附图和实施例对本实用新型进行详细说明。 [0023]如图2所示，本实用新型提出了一种模块化多电平换流器集中控制系统，包括相互 连接的：模块化多电平换流器(MMC)以及集中控制系统，模块化多电平换流器包括三相电 路，每相电路均包括相互串联的上、下桥臂，且上、下两桥臂分别与交流母线相连;各相电路 并联后分别作为模块化多电平换流器直流侧的正、负极输出端;每个桥臂均包括若干级联 的子模块HBSM及电感L0。 [0024]所述集中控制系统包括控制方式选择模块、换流器网侧交流电压检测模块、换流 器网侧交流电流检测模块、基准值设定模块、运行参考值设定模块、标幺值变换模块、锁相 环(PLL)模块、派克变换模块、外环控制模块、内环控制模块、标幺值反变换模块、派克反变 换模块、控制模块。 [0025] 所述控制方式选择模块用于设置外环控制器有功类控制方式。 [0026]所述换流器网侧交流电压检测模块用于对模块化多电平换流器运行过程中的网 侧交流电压进行实时检测，并将换流器网侧电压发送至标幺值变换模块。 [0027]所述基准值设定模块用于设置模块化多电平换流器运行过程中的系统容量、交流 电压和直流电压基准值，并将其发送至标幺值变换模块和标幺值反变换模块。 [0028]所述运行参考值设定模块用于设置模块化多电平换流器运行状态的参考值，其中 包括有功功率参考值（直流电压参考值）和无功功率参考值，并将其发送至标幺值变换模 块。 [0029]所述标幺值变换模块用于将换流器网侧电压和电流的有名值以及功率参考值的 有名值变成标幺值，并将换流器网侧电压标幺值发送至锁相环模块，将换流器网侧电压和 电流的标幺值发送至派克变换模块，将功率参考值的标幺值发送至外环控制模块。 [0030]所述锁相环模块用于锁出换流器网侧电压的相角，并将其发送至派克变换模块和 派克反变换模块。 [0031]所述派克变换模块用于将换流器网侧交流电压和电流从静止的三相坐标系变化 到旋转的d、q轴坐标系，并将换流器网侧交流电压和电流的d、q轴分量发送到外环控制模块 和内环控制模块;所述外环控制模块用于跟踪模块化多电平换流器的功率参考值来生成d、 q轴电流参考值，并将其发送到内环控制模块；所述内环控制模块跟踪外环控制模块生成的 d、q轴电流参考值，产生换流器输出电压的d、q轴参考值，并将其发送到标幺值反变换模块; 所述标幺值反变换模块将接收的换流器输出电压的d、q轴参考值标幺值变换成有名值，并 将其发送至派克反变换模块。 [0032]所述派克反变换模块用于换流器输出电压的d、q轴参考值变化到三相静止坐标系 下，并将其发送至控制模块；控制模块用于根据接收的换流器输出电压，产生三相调制波信 号，并发送到下层控制器，从而实现模块化多电平换流器的系统级控制。 [0033] 本实例中，在PSCAD/EMTDC中搭建了一个双端的模块化多电平换流器系统，其中受 端换流站参数为:交流电源线电压有效值为110kV，交流线路电阻为0.3142Ω，交流线路电 感为0.001H，桥臂子模块数目为100，桥臂电感L0为0.007H，子模块电容为0.000833F ；送端 换流站参数为:交流电源线电压有效值为110kV，交流电源内电阻为0.01Ω，交流电源内电 感为0.02H，交流线路电阻为0.3142Ω，交流线路电感为0.001H，桥臂子模块数目为100，桥 臂电感L0为0.04H，子模块电容为0.000833F。 [0034] 1）送端的模块化多电平换流器采用定有功功率和定无功功率的控制模式，受端换 流站采用定直流电压和定无功功率的控制模式。 [0035] 2）换流器网侧交流电压检测模块是实时检测模块化多电平换流器网侧交流电压 的瞬时值，并发送至标幺值变换模块。 [0036] 3）换流器网侧交流电流检测模块实时检测模块化多电平换流器网侧交流电流的 瞬时值，并发送至标幺值变换模块。 [0037] 4）基准值设定模块分别输入模块化多电平换流器运行过程中的系统容量、交流电 压和直流电压的基准值，并将其发送到标幺值变换模块和标幺值反变换模块。 [0038] 5）运行参考值设定模块设置模块化多电平换流器运行状态的参考值，并将其发送 至标幺值变换模块。本实施例中送端有功功率参考值Pref=100MW,无功功率参考值Qref = 30MVar；受端直流电压参考值Udcref = 200kV,无功参考值Qref = 30MVar。 [0039] 6）标幺值变换模块将接收的换流器网侧电压和电流的有名值以及功率参考值的 有名值变成标幺值，并将换流器网侧电压标幺值发送至锁相环模块，将换流器网侧电压和 电流的标幺值发送至派克变换模块，将功率参考值的标幺值发送至外环控制模块。 [0040] 7）锁相环模块输入锁相环的参数，从而实现锁出换流器网侧交流电压相角的作 用，并将换流器网侧交流电压的相角发送到派克变换和派克反变换模块。 [0041] 8）派克变换模块根据接收的换流器网侧交流电压和交流电流的标幺值以及锁相 环锁出的交流电压的相角，将基于三相静止坐标系的换流器网测电流和网侧电压变换为基 于d、q轴旋转坐标系的d、q轴分量，为外环和内环控制模块进行d、q轴的解耦控制奠定基础， 换流器网侧电压、电流的d、q轴分量将被送至外环控制模块和内环控制模块。 [0042] 9）外环控制模块输入有功类和无功类控制的参数，根据接收的系统运行状态的参 考值，计算生成d、q轴电流的参考值，并发送到内环控制模块。 [0043] 10）内环控制模块输入框中输入d、q轴的控制参数，根据接收的外环控制模块生成 的d、q轴电流参考值，计算生成换流器输出电压的d、q轴参考值，并将其发送到标幺值反变 换模块。 [0044] 11）标幺值反变换模块将接收的换流器输出电压的d、q轴参考值的标幺值变换成 有名值，并将其发送至派克反变换模块。 [0045] 12）派克反变换模块根据接收的交流电压相角，将换流器输出电压的d、q轴参考值 变换成三相静止坐标系下的三相分量，并发送至控制模块。 [0046] 13）模块化多电平换流器集中控制系统右侧三个输出端子Ma、Mb、Mc为控制模块， 根据接收的换流器三相输出电压，产生三相调制波信号,并发送到下层控制器,从而实现模 块化多电平换流器的系统级控制。 [0047] 分别采用分布式控制系统和集中控制系统对系统进行电磁暂态仿真，如图3和图 4,本实用新型的集中控制系统的仿真结果与分布式控制系统的仿真结果完全相同。 [0048]实施例仅为本实用新型较佳的具体实施方式，但本实用新型的保护范围并不局限 于此，任何熟悉本技术领域的技术人员在本实用新型揭露的技术范围内，可轻易想到的变 化或替换，都应涵盖在本实用新型的保护范围之内。因此，本实用新型的保护范围应该以权 利要求的保护范围为准。 [EN CN211701885U]: The technical field of a modular multilevel converter centralized control system [0001] This utility model belongs to the technical field of power system operation and control, and in particular relates to a modular multilevel converter centralized control system. Background technique [0002] Modular multilevel converter is a new type of voltage source converter topology. The modular multi-level converter based on the sub-module cascade structure has many advantages, such as reducing the switching frequency and switching loss while maintaining the equivalent switching frequency of a larger bridge arm, and there is no direct series switching element operation consistency problem, and the output AC The voltage waveform is of good quality. Therefore, modular multilevel converters are very promising in high-voltage and large-capacity transmission of electric energy and electric drive applications. [0003] The most commonly used modular multilevel converter control system is a vector control system. The control system is divided into an outer loop controller and an inner loop controller. The outer loop controller generates d and q according to the system operation reference value. Axis current reference value, the inner loop controller tracks the d and q axis current reference values generated by the outer loop controller to generate the modulation wave of the system. [0004] Figure 1 shows a control block diagram of a vector control system. The control system is a distributed control structure, and each component of the control system is constructed by separate control elements. In the electromagnetic transient simulation, a large number of control components are needed to build the control system of the modular multi-level converter, the modeling efficiency is low, the parameter setting is complicated, and it is easy to make mistakes. Utility model content [0005] In response to the above problems, the present utility model proposes a modular multilevel converter centralized control system, including interconnected: modular multilevel converter (MMC) and centralized control system, modular multi The level converter includes a three-phase circuit. Each phase circuit includes upper and lower bridge arms connected in series, and the upper and lower bridge arms are respectively connected to the AC bus; each phase circuit is connected in parallel as a modular multilevel converter. The positive and negative output terminals of the DC side of the inverter; each bridge arm includes several cascaded sub-modules HBSM and inductor L0. [0006] The centralized control system includes a control mode selection module, a converter grid-side AC voltage detection module, a converter grid-side AC current detection module, a reference value setting module, an operating reference value setting module, and a standard unit value Conversion module, phase-locked loop (PLL) module, Parker conversion module, outer loop control module, inner loop control module, standard unit inverse conversion module, Parker inverse conversion module, control module. [0007] The control mode selection module is used to set the active control mode of the outer loop controller. [0008] The converter grid-side AC voltage detection module is used for real-time detection of the grid-side AC voltage during the operation of the modular multilevel converter, and sends the converter grid-side voltage to the standard unit value Transformation module. [0009] The reference value setting module is used to set the system capacity, AC voltage and DC voltage reference values during the operation of the modular multilevel converter, and send them to the per-unit value conversion module and per-unit value Inverse transformation module. [0010] The operating reference value setting module is used to set the reference value of the operating state of the modular multi-level converter, including the active power reference value (DC voltage reference value) and the reactive power reference value, and Send to the unit value conversion module. [0011] The standard unit value conversion module is used to convert the well-known values of the grid-side voltage and current and the power reference value of the converter The famous value becomes the standard unit value, and the standard unit value of the converter grid-side voltage is sent to the phase-locked loop module, and the standard unit value of the converter grid-side voltage and current is sent to the Parker transformation module, and the power reference value The unit value is sent to the outer loop control module. [0012] The phase-locked loop module is used to lock the phase angle of the grid-side voltage of the converter and send it to the Parker conversion module and the Parker inverse conversion module. [0013] The Parker transformation module is used to change the grid-side AC voltage and current of the converter from a static three-phase coordinate system to a rotating d, q-axis coordinate system, and convert the grid-side AC voltage and current of the converter d and q axis components are sent to the outer loop control module and the inner loop control module; the outer loop control module is used to track the power reference value of the modular multilevel converter to generate the d and q axis current reference value, and It is sent to the inner loop control module; the inner loop control module tracks the d and q axis current reference values generated by the outer loop control module, generates the d and q axis reference values of the converter output voltage, and sends it to the standard unit Inverse value conversion module; The inverse per-unit value conversion module converts the received d, q-axis reference value per unit value of the inverter output voltage into a well-known value, and sends it to the Parker inverse conversion module. [0014] The Parker inverse transformation module is used to change the d and q axis reference values of the converter output voltage to the three-phase stationary coordinate system and send it to the control module; the control module is used to change the reference value of the converter output voltage according to the received converter Output voltage, generate three-phase modulation wave signal, and send it to the lower controller, so as to realize the system-level control of the modular multi-level converter. [0015] The beneficial effects of the utility model: [0016] 1. The present utility model designs a centralized control system of modular multilevel converters to achieve system-level control. The control logic adopted by the utility model is exactly the same as that of the distributed control system, so it can be completely integrated with the distributed control system. The same control effect. [0017] 2. Because the present utility model adopts a centralized modular multilevel converter control system, compared with a distributed control system, a whole controller replaces a large number of control elements, which greatly The modeling process is simplified, and the parameters can be intensively debugged, which greatly reduces the error probability. Therefore, the utility model can be widely used in system-level control of modular multilevel converters. Description of the drawings [0018] FIG. 1 is a control structure diagram of a vector control system. [0019] FIG. 2 is a topological structure diagram of a modular multilevel converter. [0020] FIG. 3 is a diagram of the simulation results of the sending-end converter station. [0021] Figure 4 is a diagram of the simulation results of the receiving converter station. detailed description [0022] The utility model is described in detail below with reference to the drawings and embodiments. [0023] As shown in Figure 2, the present utility model proposes a modular multilevel converter centralized control system, including interconnected: modular multilevel converter (MMC) and centralized control system, modules The multilevel converter includes a three-phase circuit. Each phase circuit includes upper and lower bridge arms connected in series with each other, and the upper and lower bridge arms are respectively connected to the AC bus; each phase circuit is connected in parallel as a modular multi-circuit The positive and negative output terminals of the DC side of the flat converter; each bridge arm includes several cascaded sub-modules HBSM and inductor L0. [0024] The centralized control system includes a control mode selection module, a converter grid-side AC voltage detection module, a converter grid-side AC current detection module, a reference value setting module, an operating reference value setting module, and a standard unit value Conversion module, phase-locked loop (PLL) module, Parker conversion module, outer loop control module, inner loop control module, standard unit inverse conversion module, Parker inverse conversion Change module, control module. [0025] The control mode selection module is used to set the active power control mode of the outer loop controller. [0026] The converter grid-side AC voltage detection module is used for real-time detection of the grid-side AC voltage during the operation of the modular multilevel converter, and sends the converter grid-side voltage to the standard unit value Transformation module. [0027] The reference value setting module is used to set the system capacity, AC voltage and DC voltage reference values during the operation of the modular multilevel converter, and send them to the per-unit value conversion module and the per-unit value Inverse transformation module. [0028] The operating reference value setting module is used to set the reference value of the operating state of the modular multilevel converter, including the active power reference value (direct current voltage reference value) and the reactive power reference value, and Send to the unit value conversion module. [0029] The standard unit value conversion module is used to convert the famous value of the grid side voltage and current of the converter and the famous value of the power reference value into a standard unit value, and send the standard unit value of the converter grid side voltage to The phase-locked loop module sends the unit value of the voltage and current on the grid side of the converter to the Parker transformation module, and sends the unit value of the power reference value to the outer loop control module. [0030] The phase-locked loop module is used to lock the phase angle of the grid-side voltage of the converter and send it to the Parker conversion module and the Parker inverse conversion module. [0031] The Parker transformation module is used to change the grid-side AC voltage and current of the converter from a static three-phase coordinate system to a rotating d, q-axis coordinate system, and convert the grid-side AC voltage and current of the converter d and q axis components are sent to the outer loop control module and the inner loop control module; the outer loop control module is used to track the power reference value of the modular multilevel converter to generate the d and q axis current reference value, and It is sent to the inner loop control module; the inner loop control module tracks the d and q axis current reference values generated by the outer loop control module, generates the d and q axis reference values of the converter output voltage, and sends it to the standard unit Inverse value conversion module; The inverse per-unit value conversion module converts the received d, q-axis reference value per unit value of the inverter output voltage into a well-known value, and sends it to the Parker inverse conversion module. [0032] The Parker inverse transformation module is used to change the d and q axis reference values of the converter output voltage to the three-phase stationary coordinate system and send it to the control module; the control module is used to change the reference value of the converter output voltage according to the received converter Output voltage, generate three-phase modulation wave signal, and send it to the lower controller, so as to realize the system-level control of the modular multi-level converter. [0033] In this example, a double-ended modular multilevel converter system is built in PSCAD/EMTDC, where the parameters of the receiving end converter station are: the effective value of the AC power line voltage is 110kV, and the AC line resistance is 0.3142 Ω, the AC line inductance is 0.001H, the number of bridge arm sub-modules is 100, the bridge arm inductance L0 is 0.007H, and the sub-module capacitance is 0.000833F; the parameters of the sending-end converter station are: the effective value of the AC power line voltage is 110kV, AC The internal resistance of the power supply is 0.01Ω, the internal inductance of the AC power supply is 0.02H, the AC line resistance is 0.3142Ω, the AC line inductance is 0.001H, the number of bridge arm submodules is 100, the bridge arm inductance L0 is 0.04H, and the submodule capacitance is 0.000833 F. [0034] 1) The modular multilevel converter at the sending end adopts a constant active power and constant reactive power control mode, and the receiving end converter station adopts a constant DC voltage and constant reactive power control mode. [0035] 2) The grid-side AC voltage detection module of the converter detects the instantaneous value of the grid-side AC voltage of the modular multilevel converter in real time, and sends it to the unit value conversion module. [0036] 3) The grid-side AC current detection module of the converter detects the instantaneous value of the grid-side AC current of the modular multilevel converter in real time, and sends it to the unit value conversion module. [0037] 4) The reference value setting module separately inputs the reference values of the system capacity, AC voltage and DC voltage during the operation of the modular multilevel converter, and sends them to the unit value conversion module and unit value Inverse transformation module. [0038] 5) The operating reference value setting module sets the reference value of the operating state of the modular multilevel converter and sends it To the standard unit value conversion module. In this embodiment, the sending end active power reference value Pref=100MW, the reactive power reference value Qref=30MVar; the receiving end DC voltage reference value Udcref=200kV, and the reactive power reference value Qref=30MVar. [0039] 6) The standard unit value conversion module converts the received famous value of the inverter grid-side voltage and current and the famous value of the power reference value into a standard unit value, and sends the standard unit value of the converter grid-side voltage to The phase-locked loop module sends the grid-side voltage and current of the converter to the Parker transformation module, and the power reference value to the outer loop control module. [0040] 7) The phase-locked loop module inputs the parameters of the phase-locked loop, so as to lock out the phase angle of the AC voltage on the grid side of the converter, and send the phase angle of the AC voltage on the grid side of the converter to Parker Transformation and Parker Inverse transformation module. [0041] 8) The Parker transformation module converts the converter network based on the three-phase stationary coordinate system according to the received AC voltage and AC current of the grid side of the converter and the phase angle of the AC voltage locked by the phase-locked loop. The measured current and grid-side voltage are transformed into d and q-axis components based on the d and q-axis rotating coordinate system, which lays the foundation for the decoupling control of the d and q axes of the outer loop and inner loop control module. The converter grid-side voltage, The d and q axis components of the current will be sent to the outer loop control module and the inner loop control module. [0042] 9) The outer loop control module inputs active and reactive power control parameters, and calculates and generates the reference values of the d and q axis currents according to the received reference values of the system operating state, and sends them to the inner loop control module. [0043] 10) Input the control parameters of the d and q axes in the input box of the inner loop control module, and calculate and generate the d and q axes of the converter output voltage according to the received d and q axis current reference values generated by the outer loop control module The reference value, and send it to the standard unit value inverse transformation module. [0044] 11) The per-unit inverse conversion module converts the received per-unit values of the d and q-axis reference values of the inverter output voltage into a well-known value, and sends it to the Parker inverse conversion module. [0045] 12) The Parker inverse transformation module transforms the d and q axis reference values of the converter output voltage into three-phase components in a three-phase stationary coordinate system according to the received AC voltage phase angle, and sends them to the control module. [0046] 13) The three output terminals Ma, Mb, Mc on the right side of the modular multilevel converter centralized control system are control modules, which generate three-phase modulated wave signals according to the received three-phase output voltage of the converter, and Send to the lower-level controller to realize the system-level control of the modular multilevel converter. [0047] The distributed control system and the centralized control system are respectively adopted to perform electromagnetic transient simulation of the system, as shown in FIG. 3 and FIG. 4. The simulation result of the centralized control system of the present invention is exactly the same as the simulation result of the distributed control system. [0048] The embodiments are only preferred specific implementations of the present utility model, but the scope of protection of the present utility model is not limited thereto. Any person skilled in the art can easily within the technical scope disclosed by the present utility model. Any changes or replacements that come to mind should be covered by the protection scope of the present invention. Therefore, the protection scope of the present utility model should be subject to the protection scope of the claims.
[ZH CN112054696A]: 基于最小回流功率的多电平变换器优化控制方法及装置 [EN CN112054696A]: Multilevel converter optimization control method and device based on minimum reflux power | [ZH CN112054696A]: 本发明实施例涉及一种基于最小回流功率的多电平变换器优化控制方法及装置，通过求解得到多电平变换器在最小回流功率下的输入内移相角、输出内移相角和外移相角对多电平变换器进行控制运行，不仅能够改善多电平变换器在移相控制时由于输入输出电压不匹配时造成的较大回流功率和效率低等缺陷，在全功率范围和全变压比范围内均能有效减小变换器的回流功率，提高整个变换器的效率及性能，解决了现有三电平DAB变换器在电压不匹配运行工况下，采用传统移相控制方式会产生较大的回流功率，导致系统损耗增加，效率降低的技术问题。 [EN CN112054696A]: The embodiment of the invention relates to a multilevel converter optimization control method and device based on minimum reflux power, and the method comprises the steps: obtaining an input internalphase shift angle, an output internal phase shift angle and an output external phase shift angle of a multilevel converter under the minimum reflux power through solving, and carrying out the controloperation of the multilevel converter; the defects of large reflux power, low efficiency and the like caused by mismatching of input and output voltages during phase shift control of the multilevel converter can be overcome, the reflux power of the converter can be effectively reduced in a full power range and a full transformation ratio range, and the efficiency and the performance of the whole converter are improved; the technical problems that the system loss is increased and the efficiency is reduced due to the fact that an existing three-level DAB converter generates large reflux power byadopting a traditional phase shift control mode under the voltage mismatching operation working condition are solved. | CN112054696A | 2020-12-08 | CN202010974495A | 2020-09-16 | CN202010974495A, 2020-09-16 | CN112054696A: 2020-12-08 | ELECTRIC POWER RES INST GUANGDONG POWER GRID CORP | JIN LI MA MING LIANG XIAOBING LEI ERTAO DU WANLIN WANG LING TANG TING XU BAIYU | H02M3/335: I | H02M3/33523: I H02M3/33584: I H02M1/0058: A Y02B70/10: A | CN106981992A CN107911028A |  | [ZH CN112054696A]: L 一种基于最小回流功率的多电平变换器优化控制方法，其特征在于，包括以下步骤： SL获取多电平变换器的变压比； S2.根据所述多电平变换器的输入电压、输出电压、输出电流、谐振电感、变换器匝数 比、开关频率计算得到所述多电平变换器标幺化的传输功率； S3.在所述多电平变换器处于最小回流功率状态下，根据所述变压比、所述变换器匝数 比和所述传输功率计算得到所述多电平变换器的输入内移相角和输出内移相角；以及采用 PI控制器调节所述多电平变换器的所述输出电压稳定输出，得到所述多电平变换器的外移 相角； S4.将所述输入内移相角、所述输出内移相角和所述外移相角输入驱动生成模块控制 所述多电平变换器中开关器件的通断； 其中，在步骤S3中，计算所述多电平变换器的输入内移相角和输出内移相角的公式为： M=o 式中，α为输入内移相角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数 比。 2.根据权利要求1所述的基于最小回流功率的多电平变换器优化控制方法，其特征在 于，计算所述多电平变换器的输入内移相角和输出内移相角具体步骤包括： S31.获取所述多电平变换器标幺值的传输功率基波分量和回流功率基波分量； S32.采用拉格朗日乘数法建立基于所述传输功率基波分量和所述回流功率基波分量 的拉格朗日方程，并对所述拉格朗日方程中的三个移相角进行求偏导数，得到三个移相角 的导数式； S33.根据限制条件对所述导数式进行求解,得到所述多电平变换器的输入内移相角和 输出内移相角的公式； 其中，所述拉格朗日方程为： 三个移相角的所述导数式为： « - 2 ο 二 s ο c p h s u £. 2 222 1 S h ο s c a j 2 a - 2 s s o o c c -- (cos Λ sin φ)=ϋ •(sin / +丸cose) = 0 所述限制条件为: 片 ”(α，a*)= Pq 式中，。为多电平变换器输入端与输出端电压中点之间的移相角,α为输入内移相角,8 为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数比，牙（巴丛㈤为传输功率基波 分量，0：（&amp;，孔8）为回流功率基波分量，尸#,%）为拉格朗日函数,人为拉格朗日系数。 3.根据权利要求1所述的基于最小回流功率的多电平变换器优化控制方法，其特征在 于,在步骤S3中，采用ΡΙ控制器调节所述多电平变换器的所述输出电压稳定输出具体包括: 将所述输出电压与所述多电平变换器指令电压之间的差值经过所述ΡΙ控制器按照所述外 移相角调节控制，使得所述输出电压等于所述指令电压。 4.根据权利要求1所述的基于最小回流功率的多电平变换器优化控制方法，其特征在 于，所述驱动生成模块采用2SP0320x2Ax型号的控制芯片控制所述多电平变换器中开关器 件的通断。 5.一种基于最小回流功率的多电平变换器优化控制装置,包括变压比计算模块和传输 功率计算模块，其特征在于,还包括优化移相角计算模块和控制模块； 所述变压比计算模块，用于根据多电平变换器的输入电压、输出电压和变换器匝数比 计算所述多电平变换器的变压比； 所述传输功率计算模块，用于根据所述多电平变换器的输入电压、输出电压、输出电 流、谐振电感、变换器匝数比、开关频率计算得到所述多电平变换器标幺化的传输功率； 所述优化移相角计算模块，用于在所述多电平变换器处于最小回流功率状态下，根据 所述变压比、所述变换器匝数比和所述传输功率计算得到所述多电平变换器的输入内移相 角和输出内移相角；以及采用PI控制器调节所述多电平变换器的所述输出电压稳定输出， 得到所述多电平变换器的外移相角； 所述控制模块，用于根据所述输入内移相角、所述输出内移相角和所述外移相角控制 所述多电平变换器中开关器件的通断； 其中，计算所述多电平变换器的输入内移相角和输出内移相角的公式为： 式中，α为输入内移相角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数 比。 6.根据权利要求5所述的基于最小回流功率的多电平变换器优化控制装置，其特征在 于，所述优化移相角计算模块包括获取功率基波分量子模块、求导计算子模块和移相角计 算子模块； 所述获取功率基波分量子模块，用于获取所述多电平变换器标幺值的传输功率基波分 量和回流功率基波分量 所述求导计算子模块，用于采用拉格朗日乘数法建立基于所述传输功率基波分量和所 述回流功率基波分量的拉格朗日方程，并对所述拉格朗日方程中的三个移相角进行求偏导 数,得到三个移相角的导数式； 所述移相角计算子模块，用于根据限制条件对所述导数式进行求解，得到所述多电平 变换器的输入内移相角和输出内移相角的公式； 其中，所述拉格朗日方程为： 上@万例兀）=力㈤—兑耳*也力㈤—死］ 三个移相角的所述导数式为： .a =sin —— —cos —+ —!—cos --(Asin ω-cos= 0 k 2 2N 2 ' _ =cos y - sin y (cos ζρ - Λ sin 8)=0 -cosy .cos—(sin ¢&gt; + zcos^)- 0 所述限制条件为： 片” (a,广#)=&lt; cost I jcosi * Isin (0)=p0 式中为多电平变换器输入端与输出端电压中点之间的移相角,α为输入内移相角,8 为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数比，＜*（©民㈤为传输功率基波 分量，0：（a*向为回流功率基波分量，民他灯为拉格朗日函数，人为拉格朗日系数。 7 .根据权利要求5所述的基于最小回流功率的多电平变换器优化控制装置，其特征在 于，所述控制模块还用于将所述输出电压与所述多电平变换器指令电压之间的差值经过所 述ΡΙ控制器按照所述外移相角调节控制，使得所述输出电压等于所述指令电压。 8 .根据权利要求5所述的基于最小回流功率的多电平变换器优化控制装置，其特征在 于，所述控制模块采用2SP0320x2Ax型号的控制芯片形成的驱动生成模块控制所述多电平 变换器中开关器件的通断。 9 .一种计算机可读存储介质，其特征在于,所述计算机存储介质用于存储计算机指令, 当其在计算机上运行时,使得计算机执行如权利要求卜4任意一项所述的基于最小回流功 率的多电平变换器优化控制方法。 10 . 一种终端设备,其特征在于，包括处理器以及存储器； 所述存储器,用于存储程序代码,并将所述程序代码传输给所述处理器； 所述处理器，用于根据所述程序代码中的指令执行如权利要求「4任意一项所述的基 于最小回流功率的多电平变换器优化控制方法。 [EN CN112054696A]: L A multi-level converter optimized control method based on minimum return power, which is characterized in that it includes the following steps: SL obtains the transformation ratio of the multilevel converter; S2. Calculate the standardized transmission power of the multi-level converter according to the input voltage, output voltage, output current, resonant inductance, converter turns ratio, and switching frequency of the multi-level converter; S3. When the multi-level converter is in the minimum return power state, the input phase shift of the multi-level converter is calculated according to the transformation ratio, the turns ratio of the converter, and the transmission power Angle and output internal phase shift angle; and using a PI controller to adjust the stable output of the output voltage of the multi-level converter to obtain the external phase shift angle of the multi-level converter; S4. The input inner phase shift angle, the output inner phase shift angle, and the outer phase shift angle input drive generation module to control the on-off of the switching device in the multilevel converter; wherein, in step S3 , The formula for calculating the input internal phase shift angle and the output internal phase shift angle of the multilevel converter is: M=o where α is the input internal phase shift angle, 8 is the output internal phase shift angle, k is the transformation ratio, ρο is the transmission power, and Ν is the converter turns ratio. 2. The optimized control method for a multilevel converter based on the minimum return power of claim 1, wherein the specific steps of calculating the input internal phase shift angle and the output internal phase shift angle of the multilevel converter include : S31. Obtain the fundamental wave component of the transmission power and the fundamental wave component of the return power of the multilevel converter per unit value; S32. Establish a Lagrangian equation based on the fundamental wave component of the transmission power and the fundamental wave component of the return power by using the Lagrangian multiplier method, and compare the three phase shift angles in the Lagrangian equation Calculate the partial derivative to obtain the derivative formula of the three phase shift angles; S33. Solve the derivative formula according to the restriction conditions to obtain the formulas of the input internal phase shift angle and the output internal phase shift angle of the multilevel converter; wherein, the Lagrangian equation is: three shifts The derivative formula of the phase angle is: «-2 ο Two s ο cp hsu £. 2 222 1 S h ο scaj 2 a-2 ssoocc - (cos Λ sin φ)=ϋ (sin / +pill cose) = 0 The restriction conditions are: Slice" (α, a*)= In the formula Pq,. Is the phase shift angle between the input of the multilevel converter and the midpoint of the output voltage, α is the input phase shift angle, 8 Is the internal phase shift angle of the output, k is the transformation ratio, ρο is the transmission power, Ν is the transformer turns ratio, and (Ba Cong (V) is the fundamental component of the transmission power, 0: (&amp;, hole 8) is the return power base The wave component, (#,%) is the Lagrangian function, and the Lagrangian coefficient is artificial. 3. The optimized control method of a multi-level converter based on minimum return power according to claim 1, wherein in step S3, a PI controller is used to adjust the output voltage of the multi-level converter to stabilize the output voltage of the multi-level converter. The output specifically includes: adjusting and controlling the difference between the output voltage and the command voltage of the multilevel converter through the PI controller according to the outer phase shift angle, so that the output voltage is equal to the command voltage . 4. The optimized control method for a multi-level converter based on minimum return power according to claim 1, wherein the drive generation module uses a 2SP0320x2Ax control chip to control the switching devices in the multi-level converter. On and off. 5. A multi-level converter optimization control device based on minimum return power, comprising a transformation ratio calculation module and a transmission power calculation module, characterized in that it also includes an optimized phase shift angle calculation module and a control module; The ratio calculation module is used to calculate the transformation ratio of the multi-level converter according to the input voltage, the output voltage and the turns ratio of the converter; the transmission power calculation module is used to calculate the transformation ratio of the multi-level converter according to the multiple The input voltage, output voltage, output current, resonance inductance, converter turns ratio, and switching frequency of the level converter are calculated to obtain the standardized transmission power of the multilevel converter; the optimized phase shift angle calculation module, It is used to calculate the input internal phase shift of the multi-level converter according to the transformation ratio, the turn ratio of the converter and the transmission power when the multi-level converter is in the minimum return power state And the output internal phase shift angle; and the PI controller is used to adjust the stable output of the output voltage of the multilevel converter to obtain the external phase shift angle of the multilevel converter; the control module is configured to According to the input internal phase shift angle, the output internal phase shift angle, and the external phase shift angle, the switching devices in the multi-level converter are controlled to be turned on and off; wherein, the input of the multi-level converter is calculated The formulas for the internal phase shift angle and the output internal phase shift angle are: In the formula, α is the input internal phase shift angle, 8 is the output internal phase shift angle, k is the transformation ratio, ρο is the transmission power, and N is the converter turns ratio. 6. The multi-level converter optimization control device based on the minimum return power according to claim 5, wherein the optimized phase shift angle calculation module includes a power fundamental wave component acquisition sub-module, a derivative calculation sub-module, and A phase shift angle calculation sub-module; the power fundamental wave component acquisition sub-module is used to obtain the transmission power fundamental wave component and the return power fundamental wave component of the multi-level converter per unit, the derivative calculation sub-module, It is used to establish the Lagrangian equation based on the fundamental wave component of the transmission power and the fundamental wave component of the return power by using the Lagrangian multiplier method, and adjust the three phase shift angles in the Lagrangian equation The partial derivative is calculated to obtain the derivative formulae of the three phase shift angles; the phase shift angle calculation sub-module is used to solve the derivative formula according to the restriction conditions to obtain the input internal phase shift of the multilevel converter Angle and the formula of the phase shift angle within the output; Among them, the Lagrangian equation is: on@Wan Jiwu)=Force (v)Duier*Yelidead] The derivative formula of the three phase shift angles is: .a =sin cos -+ -!-cos --(Asin ω-cos = 0 k 2 2N 2 '_ =cos y-sin y (cos ζρ-Λ sin 8)=0 -cosy .cos-(sin ¢&gt; + zcos^)- 0 The restriction is: sheet" (a,wide#)=&lt; cost I jcosi * Isin (0)=p0 Where is the phase shift angle between the input of the multilevel converter and the midpoint of the output voltage, α is the input phase shift angle, 8 is the output phase shift angle, k is the transformation ratio, and ρο is the transmission power, Ν is the turns ratio of the converter, &lt;*(©People is the fundamental wave component of the transmission power, 0: (a* direction is the fundamental wave component of the return power, the mint lamp is the Lagrangian function, and the artificial Lagrangian coefficient . 7 The multi-level converter optimization control device based on the minimum return power according to claim 5, wherein the control module is further configured to adjust the output voltage to the command voltage of the multi-level converter. The difference value of is adjusted and controlled by the PI controller according to the outer phase shift angle, so that the output voltage is equal to the command voltage. 8 The multi-level converter optimization control device based on the minimum return power of claim 5, wherein the control module adopts a drive generation module formed by a 2SP0320x2Ax control chip to control the multi-level converter Switching device on and off. 9 A computer-readable storage medium, characterized in that the computer storage medium is used to store computer instructions, which when running on a computer, cause the computer to execute the minimum reflux power based on any one of claims 1-4 Optimized control method of multilevel converter. 10 A terminal device, characterized by comprising a processor and a memory; the memory is used for storing program code and transmitting the program code to the processor; the processor is used for according to the program The instructions in the code execute the optimized control method of the multi-level converter based on the minimum reflux power according to any one of claim "4." | [ZH CN112054696A]: 基于最小回流功率的多电平变换器优化控制方法及装置 技术领域 [0001]本发明涉及变换器技术领域，尤其涉及一种基于最小回流功率的多电平变换器优 化控制方法及装置。 背景技术 [0002]随着直流输电技术的快速发展，作为高压输电和低压直流配电网的中间环节，中 压直流配网受到越来越多的关注。在中压直流配电网中，需要采用高频隔离双向直流变换 器作为互联装置，用于实现电气隔离、电压变换以及功率的双向流动。 [0003] DAB变换器具有高功率密度、能实现功率的双向传输，易于实现软开关和模块化等 特点，被广泛应用于双向隔离变换领域。近年来，关于DAB变换器的性能优化，不管是对DAB 变换器中的软开关范围的扩展，还对DAB变换器中的电流应力的减小以及回流功率的减小 进行优化，在优化过程中主要是基于DAB变换器的线性建立分段时域模型，这个分段时域模 型能够准确的界定各个工作模态的边界条件，求解各个工作模式下的系统传输功率、回流 功率。当DAB变换器的控制策略或者控制自由度发生变化时，变换器的分段时域模型也将随 之变化，而针对特定控制策略建立的分段时域模型将不再适用，并且随着DAB变换器可控自 由度数量的增加，分段时域模型在不同分段的时域分析过程将更复杂。因此现有对求解DAB 变换器在工作模式下的回流功率、传输功率优化方式存在系统复杂且适用性差。 发明内容 [0004]本发明实施例提供了一种基于最小回流功率的多电平变换器优化控制方法及装 置，用于解决现有三电平DAB变换器在电压不匹配运行工况下，采用传统移相控制方式会产 生较大的回流功率，导致系统损耗增加，效率降低的技术问题。 [0005]为了实现上述目的，本发明实施例提供如下技术方案： [0006] 一种基于最小回流功率的多电平变换器优化控制方法，包括以下步骤： [0007] S1.获取多电平变换器的变压比； [0008] S2.根据所述多电平变换器的输入电压、输出电压、输出电流、谐振电感、变换器匝 数比、开关频率计算得到所述多电平变换器标幺化的传输功率； [0009] S3.在所述多电平变换器处于最小回流功率状态下，根据所述变压比、所述变换器 匝数比和所述传输功率计算得到所述多电平变换器的输入内移相角和输出内移相角；以及 采用PI控制器调节所述多电平变换器的所述输出电压稳定输出，得到所述多电平变换器的 外移相角； [0010] S4.将所述输入内移相角、所述输出内移相角和所述外移相角输入驱动生成模块 控制所述多电平变换器中开关器件的通断； [0011]其中，在步骤S3中，计算所述多电平变换器的输入内移相角和输出内移相角的公 式为： [0012] a = 2arccos [0013] 匝数比。 [0014] [0015] [0016] 因=0 式中，α为输入内移相角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器 优选地，计算所述多电平变换器的输入内移相角和输出内移相角具体步骤包括： S31.获取所述多电平变换器标幺值的传输功率基波分量和回流功率基波分量； S32.采用拉格朗日乘数法建立基于所述传输功率基波分量和所述回流功率基波 分量的拉格朗日方程，并对所述拉格朗日方程中的三个移相角进行求偏导数，得到三个移 相角的导数式； [0017] S33.根据限制条件对所述导数式进行求解，得到所述多电平变换器的输入内移相 角和输出内移相角的公式； [0018] 其中，所述拉格朗日方程为： 上@力,色兀)=Q： (α,力㈤—尤/f (α,力㈤—死] 三个移相角的所述导数式为： [0019] [0020] U 02 ο a- 2 s -— cos——I--cos --(Asin ^-cosw) = 0 k 2 2N 2 ' ' = cosy sin y (cos^-Asin(p] = 0 =cos--cos—(sin ¢? + zcos^) = 0 [0022] 所述限制条件为： [0023] /f (虞,β, φ} = cos]?¦ cos(g) sin (¢)= Ρο [0024] 式中，夕为多电平变换器输入端与输出端电压中点之间的移相角,α为输入内移相 角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数比，耳*(4民为传输功率 基波分量，。：但*用)为回流功率基波分量，d力血；1)为拉格朗日函数，人为拉格朗日系 数。 [0025] 优选地，在步骤S3中，采用ΡΙ控制器调节所述多电平变换器的所述输出电压稳定 输出具体包括:将所述输出电压与所述多电平变换器指令电压之间的差值经过所述ΡΙ控制 器按照所述外移相角调节控制，使得所述输出电压等于所述指令电压。 [0026] 优选地，所述驱动生成模块采用2SP0320x2Ax型号的控制芯片控制所述多电平变 换器中开关器件的通断。 [0027]本发明还提供一种基于最小回流功率的多电平变换器优化控制装置，包括变压比 计算模块和传输功率计算模块,还包括优化移相角计算模块和控制模块； [0028] 所述变压比计算模块，用于根据多电平变换器的输入电压、输出电压和变换器匝 数比计算所述多电平变换器的变压比； [0029]所述传输功率计算模块，用于根据所述多电平变换器的输入电压、输出电压、输出 电流、谐振电感、变换器匝数比、开关频率计算得到所述多电平变换器标幺化的传输功率； [0030]所述优化移相角计算模块，用于在所述多电平变换器处于最小回流功率状态下, 根据所述变压比、所述变换器匝数比和所述传输功率计算得到所述多电平变换器的输入内 移相角和输出内移相角；以及采用PI控制器调节所述多电平变换器的所述输出电压稳定输 出，得到所述多电平变换器的外移相角； [0031]所述控制模块，用于根据所述输入内移相角、所述输出内移相角和所述外移相角 控制所述多电平变换器中开关器件的通断； [0032] 其中，计算所述多电平变换器的输入内移相角和输出内移相角的公式为: [0033] a = 2arccos 笈见 , 因=0 式中，α为输入内移相角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器 优选地，所述优化移相角计算模块包括获取功率基波分量子模块、求导计算子模 [0034] 匝数比。 [0035] 块和移相角计算子模块； [0036]所述获取功率基波分量子模块，用于获取所述多电平变换器标幺值的传输功率基 波分量和回流功率基波分量 [0037]所述求导计算子模块，用于采用拉格朗日乘数法建立基于所述传输功率基波分量 和所述回流功率基波分量的拉格朗日方程,并对所述拉格朗日方程中的三个移相角进行求 偏导数,得到三个移相角的导数式； [0038]所述移相角计算子模块，用于根据限制条件对所述导数式进行求解，得到所述多 电平变换器的输入内移相角和输出内移相角的公式； [0039] [0040] [0041] 其中，所述拉格朗日方程为： £(&amp;,月,0,力=0*(&amp;,万向一犯*(%万向—%] 三个移相角的所述导数式为： 2] 0 ο 江流生微az¥ .a—sin ——2 Ί— cos k —I--cos — (Asin &lt;p — cos(p\2 2N 2 ' _ a= cos—2 .β sin — 2 (cos@一片sin φ) = 0 a= cos— 2 βcos—2 ・($in ¢? + zcos^) = 0 =0 [0043] [0044] [0045] 所述限制条件为: 片.(度浮向二壬cos f c* sinS)=p。 式中，户为多电平变换器输入端与输出端电压中点之间的移相角,α为输入内移相 角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数比，尸,冉为传输功率 基波分量，0：(α/Μ)为回流功率基波分量，为拉格朗日函数，人为拉格朗日系 数。 [0046] 优选地，所述控制模块还用于将所述输出电压与所述多电平变换器指令电压之间 的差值经过所述ΡΙ控制器按照所述外移相角调节控制，使得所述输出电压等于所述指令电 压。 [0047] 优选地，所述控制模块采用2SP0320x2Ax型号的控制芯片形成的驱动生成模块控 制所述多电平变换器中开关器件的通断。 [0048]本发明还提供一种计算机可读存储介质，所述计算机存储介质用于存储计算机指 令，当其在计算机上运行时，使得计算机执行上述所述的基于最小回流功率的多电平变换 器优化控制方法。 [0049] 本发明还提供一种终端设备，包括处理器以及存储器； [0050] 所述存储器,用于存储程序代码,并将所述程序代码传输给所述处理器； [0051]所述处理器，用于根据所述程序代码中的指令执行上述所述的基于最小回流功率 的多电平变换器优化控制方法。 [0052]从以上技术方案可以看出，本发明实施例具有以下优点：该基于最小回流功率的 多电平变换器优化控制方法及装置通过求解得到多电平变换器在最小回流功率下的输入 内移相角、输出内移相角和外移相角对多电平变换器进行控制运行,不仅能够改善多电平 变换器在移相控制时由于输入输出电压不匹配时造成的较大回流功率和效率低等缺陷，在 全功率范围和全变压比范围内均能有效减小变换器的回流功率，提高整个变换器的效率及 性能，解决了现有三电平DAB变换器在电压不匹配运行工况下,采用传统移相控制方式会产 生较大的回流功率，导致系统损耗增加，效率降低的技术问题。 [0053]基于最小回流功率的多电平变换器优化控制方法根据采样多电平变换器的电压 电流计算得到最优移相角，实现回流功率减小，提高多电平变换器的性能，与常规的回流功 率控制算法，该方法无需复杂的模态分析及分区间范围判断，降低了控制芯片的计算量以 及运算复杂度。 附图说明 [0054]为了更清楚地说明本发明实施例或现有技术中的技术方案,下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本 发明的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可 以根据这些附图获得其它的附图。 [0055]图1为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法中三 电平DAB变换器的电路原理图。 [0056]图2为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法中三 电平DAB变换器的电压电流波形图。 [0057]图3为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法的步 骤流程图。 [0058]图4为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法的框 架图。 [0059]图5为在相同功率条件不同移相控制方式时的稳态仿真结果图。 [0060]图6为本发明实施例所述基于最小回流功率的多电平变换器优化控制方法在不同 功率和变压比时的仿真结果图。 [0061]图7为本发明实施例所述基于最小回流功率的多电平变换器优化控制方法在不同 控制方式的电流有效值仿真结果图。 具体实施方式 [0062]为使得本发明的发明目的、特征、优点能够更加的明显和易懂，下面将结合本发明 实施例中的附图，对本发明实施例中的技术方案进行清楚、完整地描述，显然，下面所描述 的实施例仅仅是本发明一部分实施例，而非全部的实施例。基于本发明中的实施例,本领域 普通技术人员在没有做出创造性劳动前提下所获得的所有其它实施例，都属于本发明保护 的范围。 [0063]目前为了降低应用于中高压场合电力电子变压器中的双有源全桥(Dual Active Bridge,DAB)变换器中开关器件的电压应力,将三电平拓扑引入到DAB变换器中构成的三电 平DAB变换器，该三电平DAB变换器同时具有多电平变换器和DAB变换器的优势，控制更灵 活,具有广阔的研究前景。但是多电平DAB变换器增加了控制自由度数量，相同的控制策略 下,较传统DAB变换器具有更高的控制灵活性。多电平DAB变换器在相同电压和功率等级下， 可使用性能更优的低电压开关器件，提高系统效率，在如城市轨道交通、高速化电气铁路以 及舰船等中大功率直流配电系统中将具有不可估量的发展前景。 [0064]由此，本申请实施例提供了一种基于最小回流功率的多电平变换器优化控制方法 及装置能够实现三电平DAB变换器在各个工作状态时的回流功率最小，并能提高系统效率, 用于解决了现有三电平DAB变换器在电压不匹配运行工况下，采用传统移相控制方式会产 生较大的回流功率，导致系统损耗增加，效率降低的技术问题。在本实施例中，多电平变换 器是以三电平DAB变换器作为案例进行说明。 [0065]图1为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法中三 电平DAB变换器的电路原理图，图2为本发明实施例所述的基于最小回流功率的多电平变换 器优化控制方法中三电平DAB变换器的电压电流波形图。 [0066]如图1所示,三电平DAB变换器包括由两个带箝位二极管和飞跨电容的三电平全桥 单元、谐振电感L、隔直电容Cbi、Cb2和高频变压器T组成。其中，开关器件S11-S18,箝位二极 管Dc『Dc4,飞跨电容Css『Css2以及均压电容C11-C12构成变压器原边的三电平全桥;开关 器件S21-S28,箝位二极管Dc5-Dc8,飞跨电容Css3-Css4以及均压电容C21-C22构成变压器 副边的三电平全桥。高频变压器原副边的匝数比为Ν： 1,即是变换器匝数比，VI和V2分别为 输入电压和输出电压,A、B为原边桥臂中点，C、D为副边桥臂中点,01、02为输入端和输出端 分压电容的中点。移相控制三电平DAB变换器的通用电压电流波形如图2所示，其中vab和vcd 分别为变压器原副边的桥臂电压,iLr为流过谐振电感Lr的电流，设α为原边三电平全桥的内 移相角,8为副边三电平全桥的内移相角，尹为原副边对应开关器件之间的移相角，同时还 定义VAB和VCD电压中点之间的移相角为0。 [0067]需要说明的是，开关器件可以为三极管，也可以为MOS管、IGBT器件等具有开关功 能的其他电子开关管。 [0068] 实施例一： [0069]图3为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法的步 骤流程图，图4为本发明实施例所述的基于最小回流功率的多电平变换器优化控制方法的 框架图。 [0070]如图3和图4所示,本发明实施例提供了一种基于最小回流功率的多电平变换器优 化控制方法，包括以下步骤： [0071] S1.获取多电平变换器的变压比； [0072] S2.根据多电平变换器的输入电压、输出电压、输出电流、谐振电感、变换器匝数 比、开关频率计算得到多电平变换器标幺化的传输功率； [0073] S3.在多电平变换器处于最小回流功率状态下，根据变压比、变换器匝数比和传输 功率计算得到多电平变换器的输入内移相角和输出内移相角；以及采用PI控制器调节多电 平变换器的输出电压稳定输出，得到多电平变换器的外移相角； [0074] S4.将输入内移相角、输出内移相角和外移相角输入驱动生成模块控制多电平变 换器中开关器件的通断； [0075]其中，在步骤S3中，计算多电平变换器的输入内移相角和输出内移相角的公式为： [0076] I 32 ) / = 0 [0077] 式中，α为输入内移相角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器 匝数比。 [0078] 在本发明实施例的步骤S1中，主要求多电平变换器的变压比，根据实时采集多电 平变换器的输入电压V1、输出电压V2,变压器原副边匝数比Ν,变压比k计算如下： [0079] [0080]在本发明实施例的步骤S2中，主要是求多电平变换器标幺化的传输功率标幺值 POo [0081]需要说明的是，在多电平变换器的稳态工况下，可实时采样获得变换器的输入电 压V1、输出电压V2、输出电流12,结合已知的多电平变换器谐振电感L、开关频率fs,因此，计 算多电平变换器标幺化的传输功率的计算公式如下： Γ Ί [0082] Pq=京 j。 [0083] 在本发明实施例的步骤S3中，主要是根据步骤S1和步骤S2计算得到的变压比k和 传输功率P0,求解多电平变换器回流功率最小时对应的最优输出电压V1侧的输入内移相角α 和最优输出电压V2侧的输出内移相角仇以及通过PI控制器控制输出电压V2稳定在参考指令 电压Vref实现对外移相角8的调节，从而得到V2 = Vref情况下的外移相角9。 [0084]需要说明的是，采用PI控制器调节多电平变换器的输出电压稳定输出具体包括： 将输出电压与多电平变换器指令电压之间的差值经过所述PI控制器按照外移相角调节控 制，使得输出电压等于指令电压。具体地，将输出电压V2与指令电压Vref的差值经过PI控制 器控制，实现输出电压等于指令电压使得多电平变换器无静差的稳态输出电压。而PI控制 器最终通过调节原副边对应开关器件之间的移相角e实现电压的稳定输出，根据PI控制器 调节V2 = Vref可以得到外移相角尹的数值。 [0085]在本发明实施例中，多电平变换器在实际控制中，若固定传输功率,在此该基于最 小回流功率的多电平变换器优化控制方法控制方式下,移相角也相当于为固定值了。但是 当多电平变换器的输入输出电压比值发生变化,在相同的传输功率下，仍可以用上述求解 的移相角实现最小回流功率传输，为了同时保证输出电压的恒定，所以该基于最小回流功 率的多电平变换器优化控制方法直接利用PI控制器控制移相角W的输出，使得多电平变换 器维持输出电压无静差的前提下，同时实现多电平变换器的回流功率最小。 [0086] 在本发明实施例的步骤S4中，主要是根据步骤S3计算得到的内外移相角a、B、e对 多电平变换器的所有开关器件进行驱动控制。根据计算得到的内外移相角对多电平变换器 的开关器件的控制能够改善多电平变换器在移相控制时由于输入输出电压不匹配时造成 的较大回流功率和效率低等缺陷,在全功率范围和全变压比范围内均能有效减小变换器的 回流功率，提高整个变换器的效率及性能。 [0087]需要说明的是，该基于最小回流功率的多电平变换器优化控制方法根据采样多电 平变换器的电压电流计算得到最优移相角，实现回流功率减小，提高多电平变换器的性能, 与常规的回流功率控制算法，该方法无需复杂的模态分析及分区间范围判断，降低了控制 芯片的计算量以及运算复杂度。在本实施例中，内外移相角a、B、e送入驱动生成模块 2SP0320x2Ax型号的控制芯片中，实现对多电平变换器开关器件驱动信号的控制输出，并最 终实现多电平变换器的优化控制。 [0088]本发明提供的一种基于最小回流功率的多电平变换器优化控制方法通过求解得 到多电平变换器在最小回流功率下的输入内移相角、输出内移相角和外移相角对多电平变 换器进行控制运行,不仅能够改善多电平变换器在移相控制时由于输入输出电压不匹配时 造成的较大回流功率和效率低等缺陷，在全功率范围和全变压比范围内均能有效减小变换 器的回流功率，提高整个变换器的效率及性能,解决了现有三电平DAB变换器在电压不匹配 运行工况下,采用传统移相控制方式会产生较大的回流功率,导致系统损耗增加，效率降低 的技术问题。 [0089]在本发明的一个实施例中，计算所述多电平变换器的输入内移相角和输出内移相 角具体步骤包括： [0090] S31.获取所述多电平变换器标幺值的传输功率基波分量和回流功率基波分量； [0091] S32.采用拉格朗日乘数法建立基于所述传输功率基波分量和所述回流功率基波 分量的拉格朗日方程，并对所述拉格朗日方程中的三个移相角进行求偏导数，得到三个移 相角的导数式； [0092] S33.根据限制条件对所述导数式进行求解，得到所述多电平变换器的输入内移相 角和输出内移相角的公式； [0093]其中，所述拉格朗日方程为： [0094] L(a, β,φ, Λ)= 力㈤—}\ρ*(α,β, 0) — p(J [0095]三个移相角的所述导数式为： 0 ο [0097] [0098] [0099] 江流la£wlaz[¥ .a —sin —— —cos —+ —!—cos --(Asin ©-cosco) = 0 k 2 2N 2 ' ' =cos y - sin y (cos ζρ - Λ sin 8) = 0 -cosy .cos—(sin ¢&gt; + zcos^)- 0 所述限制条件为: /f (虞,β, φ}=鼻 cosf¦jcosi¦jsin (¢)= p0 式中，0为多电平变换器输入端与输出端电压中点之间的移相角,α为输入内移相 角，B为输出内移相角,k为变压比,po为传输功率,N为变换器匝数比，6*(&amp;, Β* φ)为传输功率 基波分量，0：(ά*#)为回流功率基波分量，“生民Ο”)为拉格朗日函数，人为拉格朗日系 数。 [0100]以三电平DAB变换器作为多电平变换器进行说明，在本发明实施例的步骤S31中, 主要获取三电平DAB变换器传输功率和回流功率标幺值的基波分量，因基波分量属于传输 功率和回流功率标幺值的一部分,而传输功率和回流功率标幺值的表达式分别为： [0102] c * _ 32 (nd 二 L· 3 3Λ/ι/ cos -y η π NV2 12 匕cos fl Σ (刖=1,3,5 ” J 1,3,5,,.) [0104]式中，P为一个周期内的传输功率,Pbase为功率基准值,N为变压器的匝数比(即是 变换器匝数比)，α为输入内移相角,8为输出内移相角，e为VAB和VCD电压中点之间的移相角, m和η分别代表求解功率时电压和电流高频谐波表达式的阶次,Q为回流功率,Qm=n*为电压和 电流阶次一致时产生的回流功率标幺值,Qm/n*为电压和电流阶次不一致时产生的回流功率 标幺值,m为电压的阶次,η为电流的阶次,V1、V2分别为输入电压和输出电压,A和B为计算中 间量。 [0105]图5为在相同功率条件不同移相控制方式时的稳态仿真结果图，图6为本发明实施 例所述基于最小回流功率的多电平变换器优化控制方法在不同功率和变压比时的仿真结 果图，图7为本发明实施例所述基于最小回流功率的多电平变换器优化控制方法在不同控 制方式的电流有效值仿真结果图。 [0106] 在本发明实施例中，在MATLAB/SIMULINK中搭建了三电平DAB变换器的控制模型， 变换器的主电路参数如表1所示，仿真中模拟中压大容量的变换场合，输入电压V1设置为 800V,闭环控制输出电压V2为600V,负载功率72kW。同时，为了说明该基于最小回流功率的 多电平变换器优化控制方法的有效性，进行了几组移相控制方法的控制效果对比，具体的 控制方法及控制参数如表2所示,采用该基于最小回流功率的多电平变换器优化控制方法 得到三电平DAB变换器稳态波形图，如图5至图7所示。 [0107] 表1为变换器的主电路参数 [0108] 主电路参数 符号 数值 分压电容 C11、C12、C21、C22 2.9mF 飞跨电容 Cssl&gt;Css2&gt;Css3&gt;Css4 4uF 谐振电感 Lr 65uH 隔直电容 Cbl、Cb2 150uF 变压器匝数比 N 1:1 开关频率 fs 10kHz [0109] 表2为采用控制方法的控制参数 [0110] 控制策略 Vi侧内移相角α V2侧内移相角0 单移相控制(SPS) 0 0 扩展移相控制l(EPS-l) 0.1 π 0 扩展移相控制2(EPS-2) 0 0.1 π 双重移相控制(DPS) 0.1 π 0.1 π 三重移相控制(TPS) 0.2 π 0.1 π [0111] 本发明提出的控制(OPS) α β [0112]由图5可知，每幅图中从上到下依次为原边桥臂电压VAB、副边桥臂电压VCD、传输电 感电流必以及瞬时输入功率Pin。由于每种移相控制方式下内移相角比例的不同，原副边的 桥臂电压也存在一定的差异，进一步影响电感电流的变化趋势，并最终体现在瞬时输入功 率的变化上。瞬时输入功率曲线小于零的部分与横轴围成的面积体现了变换器回流功率的 大小。以图5 (a)的SPS控制和图5 (b)的EPS-1控制为例分析,EPS-1控制的原边内移相角比 SPS控制时大，而副边的内移相角两种控制方式一致。首先,EPST控制原边桥臂电压有一段 时间为零电平,对应时间瞬时输入功率为零，而相应SPS控制该时间段瞬时功率小于零,此 时变换器有回流功率,故EPS-1控制时的回流功率相对较小；同样地，图5 (c) EPS-2控制和图 4 (d) DPS控制方式下，因为DPS控制时的α更大,所以回流功率(DPS)〈回流功率(EPS-2)。那么 随着α的进一步增大，如图5(e)的TPS控制(α = 0.2”)，相同负载条件下，回流功率的变化规 律为回流功率(TPS)〈回流功率(DPS)〈回流功率(EPS-2)。本发明所提基于最小回流功率的 多电平变换器优化控制方法下的稳态波形如图5 (f)所示，明显地，与图5(a)〜图5 (e)五种 移相控制方案相比，所提控制方法下变换器具有最小的回流功率。 [0113]由图6可知，左侧图6 (al)〜图6 (cl)为相同变压比k (=3/4)时不同负载条件下的 稳态波形图，从上到下负载依次为R = 5Q (P = 72kW)、R=16/3Q (P = 67.5kW)、R = 6Q (P = 60kW)。当P = 72kW时，图6(a1)中瞬时功率曲线小于零的部分，随着P的减小，当P = 60kW时， 图6(c1)中变换器的回流功率近似为零。说明，随着负载功率的减小，所提基于最小回流功 率的多电平变换器优化控制方法下的原边内移相角逐渐增加，变换器的回流功率逐渐减 小，即输出功率越小，变换器的回流功率越小。同理，可分析不同变压比时优化控制策略下 变换器的回流功率变化。图6 (a2)〜图6 (c2)所示为相同传输功率po(=P/Pbase)时变压比依 次为k = 3/4 (Vo = 600V)、k= 1/2 (Vo = 400V)和k= 1/4 (Vo = 200V)的稳态波形。当变压器输 入和输出电压越不匹配时，即变压比k越小时，加载在传输电感两端的电压更大，根据基尔 霍夫电压定律，此时流过传输电感的电流绝对值也更大，因此相同的输入电压，电压越不匹 配，变换器的回流功率越大。所以，图6 (a2)所示工况下，回流功率最小，图6 (c2)所示工况下 回流功率最大。 [0114] 由图7可知，输入电压Vin = 800V,输出电压Vo = 200V,功率P = 24kW,图7(a)〜图7 (d)分别对应SPS控制、EPS-1控制且原边内移相角a = 0.1n、EPS-1控制且原边内移相角α = 0.2π、以及本发明所提基于最小回流功率的多电平变换器优化控制方法控制。首先，在四种 控制方式下，随着原边内移相角的增加,3L-DAB变换器系统的回流功率逐渐减小，SPS控制 时最大，本发明所提基于最小回流功率的多电平变换器优化控制方法控制时最小。同时，电 感电流最大值随着原边内移相角的增加而减小，SPS控制时最大，本发明所提基于最小回流 功率的多电平变换器优化控制方法控制时最小。根据记录的数据，图7(a)所示SPS控制时电 流有效值lLr_rms=155.6A,图7(b)所示EPS-1控制时电流有效值lLr_rms=149.9A,图7(c)所示 EPS-1控制时电流有效值lLr_rms=143.6A,图7(d)所示本发明所提控制时电流有效值lLr_rms = 128.4A,可见，本发明所提基于最小回流功率的多电平变换器优化控制方法控制在给定 工况下，减小回流功率的同时也减小了变换器的电流应力。 [0115] 实施例二： [0116]本发明实施例还提供一种基于最小回流功率的多电平变换器优化控制装置，包括 变压比计算模块、传输功率计算模块、优化移相角计算模块和控制模块； [0117]变压比计算模块，用于根据多电平变换器的输入电压、输出电压和变换器匝数比 计算多电平变换器的变压比； [0118]传输功率计算模块，用于根据多电平变换器的输入电压、输出电压、输出电流、谐 振电感、变换器匝数比、开关频率计算得到多电平变换器标幺化的传输功率； [0119]优化移相角计算模块，用于在多电平变换器处于最小回流功率状态下，根据变压 比、变换器匝数比和传输功率计算得到多电平变换器的输入内移相角和输出内移相角；以 及采用PI控制器调节多电平变换器的输出电压稳定输出，得到多电平变换器的外移相角； [0120]控制模块，用于根据输入内移相角、输出内移相角和外移相角控制多电平变换器 中开关器件的通断； [0121]其中，计算多电平变换器的输入内移相角和输出内移相角的公式为： [0122] a = 2arccos [0123]式中，α为输入内移相角,8为输出内移相角,k为变压比，po为传输功率,N为变换器 匝数比。 [0124]在本发明实施例中，优化移相角计算模块包括获取功率基波分量子模块、求导计 算子模块和移相角计算子模块； [0125]获取功率基波分量子模块，用于获取多电平变换器标幺值的传输功率基波分量和 回流功率基波分量 [0126]求导计算子模块，用于采用拉格朗日乘数法建立基于传输功率基波分量和回流功 率基波分量的拉格朗日方程，并对拉格朗日方程中的三个移相角进行求偏导数，得到三个 移相角的导数式； [0127]移相角计算子模块，用于根据限制条件对导数式进行求解,得到多电平变换器的 输入内移相角和输出内移相角的公式； [0128]其中，拉格朗日方程为： [0129] L(a, β,φ, Λ)- φ}-φ}-ρ0] [0130]三个移相角的导数式为： 比仪吐尸吐夕 δ 3 -d 3 -d 3 &lt; .a =sin —— —cos —+ —!—cos --(Asin ©-cosco) = 0 k 2 2N 2 ' ' =cos-sin y-(cos^-Asin w) = 0 a = cos— 2 -cos --(sin 2、 [0132]限制条件为: [0133] 券ί}*，以亦区 [0134] 式中，W为多电平变换器输入端与输出端电压中点之间的移相角,a为输入内移相 角,8为输出内移相角,k为变压比,ρο为传输功率,Ν为变换器匝数比，牙(©民㈤为传输功率 基波分量为回流功率基波分量，齐伊力为拉格朗日函数，人为拉格朗日系 数。 [0135]在本发明的实施例中，控制模块还用于将输出电压与多电平变换器指令电压之间 的差值经过PI控制器按照外移相角调节控制，使得输出电压等于指令电压。 [0136] 在本发明的实施例中，控制模块采用2SP0320x2Ax型号的控制芯片形成的驱动生 成模块控制多电平变换器中开关器件的通断。 [0137]需要说明的是，实施例二装置中的模块对应于实施例一方法中的步骤，实施例一 方法的步骤已在实施例一中详细阐述了，在此实施例二中不再对装置的模块内容进行详细 阐述。 [0138] 实施例三： [0139]本发明实施例提供了一种计算机可读存储介质，计算机存储介质用于存储计算机 指令，当其在计算机上运行时，使得计算机执行上述的基于最小回流功率的多电平变换器 优化控制方法。 [0140] 实施例四： [0141]本发明实施例提供了一种终端设备，包括处理器以及存储器； [0142] 存储器，用于存储程序代码，并将程序代码传输给处理器； [0143]处理器，用于根据程序代码中的指令执行上述的基于最小回流功率的多电平变换 器优化控制方法。 [0144]需要说明的是，处理器用于根据所程序代码中的指令执行上述的一种基于最小回 流功率的多电平变换器优化控制方法实施例中的步骤。或者，处理器执行计算机程序时实 现上述各系统/装置实施例中各模块/单元的功能。 [0145]示例性的，计算机程序可以被分割成一个或多个模块/单元，一个或者多个模块/ 单元被存储在存储器中，并由处理器执行，以完成本申请。一个或多个模块/单元可以是能 够完成特定功能的一系列计算机程序指令段，该指令段用于描述计算机程序在终端设备中 的执行过程。 [0146] 终端设备可以是桌上型计算机、笔记本、掌上电脑及云端服务器等计算设备。终端 设备可包括，但不仅限于，处理器、存储器。本领域技术人员可以理解，并不构成对终端设备 的限定，可以包括比图示更多或更少的部件，或者组合某些部件，或者不同的部件，例如终 端设备还可以包括输入输出设备、网络接入设备、总线等。 [0147] 所称处理器可以是中央处理单元(Central Processing Unit，CPU)，还可以是其 他通用处理器、数字信号处理器(Digital Signal Processor，DSP)、专用集成电路 (Application Specific Integrated Circuit，ASIC)、现成可编程门阵列(FieldProgrammable Gate Array，FPGA)或者其他可编程逻辑器件、分立门或者晶体管逻辑器件、 分立硬件组件等。通用处理器可以是微处理器或者该处理器也可以是任何常规的处理器 等。 [0148] 存储器可以是终端设备的内部存储单元，例如终端设备的硬盘或内存。存储器也 可以是终端设备的外部存储设备，例如终端设备上配备的插接式硬盘，智能存储卡(Smart Media Card，SMC)，安全数字(Secure Digital，SD)卡，闪存卡(Flash Card)等。进一步地， 存储器还可以既包括终端设备的内部存储单元也包括外部存储设备。存储器用于存储计算 机程序以及终端设备所需的其他程序和数据。存储器还可以用于暂时地存储已经输出或者 将要输出的数据。 [0149]所属领域的技术人员可以清楚地了解到，为描述的方便和简洁，上述描述的系统， 装置和单元的具体工作过程，可以参考前述方法实施例中的对应过程，在此不再赘述。 [0150]在本申请所提供的几个实施例中，应该理解到，所揭露的系统，装置和方法，可以 通过其它的方式实现。例如，以上所描述的装置实施例仅仅是示意性的，例如，所述单元的 划分，仅仅为一种逻辑功能划分，实际实现时可以有另外的划分方式，例如多个单元或组件 可以结合或者可以集成到另一个系统，或一些特征可以忽略，或不执行。另一点，所显示或 讨论的相互之间的耦合或直接耦合或通信连接可以是通过一些接口，装置或单元的间接耦 合或通信连接，可以是电性，机械或其它的形式。 [0151]所述作为分离部件说明的单元可以是或者也可以不是物理上分开的，作为单元显 示的部件可以是或者也可以不是物理单元，即可以位于一个地方，或者也可以分布到多个 网络单元上。可以根据实际的需要选择其中的部分或者全部单元来实现本实施例方案的目 的。 [0152]另外，在本发明各个实施例中的各功能单元可以集成在一个处理单元中，也可以 是各个单元单独物理存在，也可以两个或两个以上单元集成在一个单元中。上述集成的单 元既可以采用硬件的形式实现，也可以采用软件功能单元的形式实现。 [0153]所述集成的单元如果以软件功能单元的形式实现并作为独立的产品销售或使用 时，可以存储在一个计算机可读取存储介质中。基于这样的理解，本发明的技术方案本质上 或者说对现有技术做出贡献的部分或者该技术方案的全部或部分可以以软件产品的形式 体现出来，该计算机软件产品存储在一个存储介质中，包括若干指令用以使得一台计算机 设备(可以是个人计算机，服务器，或者网络设备等)执行本发明各个实施例所述方法的全 部或部分步骤。而前述的存储介质包括：U盘、移动硬盘、只读存储器(ROM，Read - Only Memory)、随机存取存储器(RAM，Random Access Memory)、磁碟或者光盘等各种可以存储程 序代码的介质。 [0154]以上所述，以上实施例仅用以说明本发明的技术方案，而非对其限制;尽管参照前 述实施例对本发明进行了详细的说明，本领域的普通技术人员应当理解:其依然可以对前 述各实施例所记载的技术方案进行修改，或者对其中部分技术特征进行等同替换;而这些 修改或者替换，并不使相应技术方案的本质脱离本发明各实施例技术方案的精神和范围。 [EN CN112054696A]: Multi-level converter optimized control method and device based on minimum return power Technical field [0001] The present invention relates to the technical field of converters, and in particular to an optimized control method and device for multilevel converters based on minimum return power. Background technique [0002] With the rapid development of DC power transmission technology, as an intermediate link between high-voltage power transmission and low-voltage DC distribution networks, medium-voltage DC distribution networks have received more and more attention. In the medium-voltage DC distribution network, high-frequency isolation bidirectional DC converters are required as interconnection devices to achieve electrical isolation, voltage conversion, and bidirectional power flow. [0003] DAB converters have high power density, can realize two-way transmission of power, are easy to realize soft switching and modularization, etc., and are widely used in the field of two-way isolation conversion. In recent years, regarding the performance optimization of the DAB converter, whether it is the expansion of the soft switching range in the DAB converter, the reduction of the current stress and the reduction of the return power in the DAB converter are also optimized. During the optimization process The segmented time domain model is mainly established based on the linearity of the DAB converter. This segmented time domain model can accurately define the boundary conditions of each operating mode and solve the system transmission power and return power in each operating mode. When the control strategy or control degree of freedom of the DAB converter changes, the segmented time domain model of the converter will also change, and the segmented time domain model established for a specific control strategy will no longer be applicable, and with the DAB As the number of controllable degrees of freedom of the converter increases, the time-domain analysis process of the segmented time-domain model in different segments will be more complicated. Therefore, the existing optimization methods for solving the return power and transmission power of the DAB converter in the working mode have complex systems and poor applicability. Summary of the invention [0004] The embodiments of the present invention provide a multi-level converter optimization control method and device based on minimum return power, which are used to solve the problem of using traditional phase shifting in the existing three-level DAB converter under voltage mismatch operating conditions. The control method will produce a large return power, which leads to technical problems such as increased system loss and reduced efficiency. [0005] In order to achieve the foregoing objectives, the embodiments of the present invention provide the following technical solutions: [0006] An optimized control method for a multilevel converter based on minimum return power includes the following steps: [0007] S1. Obtain the transformation ratio of the multilevel converter; [0008] S2. According to the input voltage, output voltage, output current, resonant inductance, converter turns ratio, and switching frequency of the multilevel converter, the standard unitized transmission power of the multilevel converter is calculated; [0009] S3. When the multi-level converter is in the minimum return power state, the input of the multi-level converter is calculated according to the transformation ratio, the turns ratio of the converter, and the transmission power An inner phase shift angle and an output inner phase shift angle; and a PI controller is used to adjust the stable output of the output voltage of the multilevel converter to obtain the outer phase shift angle of the multilevel converter; [0010] S4. The input inner phase shift angle, the output inner phase shift angle and the outer phase shift angle input drive generation module to control the on-off of the switching device in the multilevel converter; [0011] Wherein, in step S3, the formula for calculating the input internal phase shift angle and the output internal phase shift angle of the multilevel converter is: [0012] a = 2arccos [0013] Turns ratio. [0014] [0015] [0016] Because = 0 where α is the input internal phase shift angle, 8 is the output internal phase shift angle, k is the transformation ratio, ρο is the transmission power, and N is the converter. Preferably, calculate The specific steps of the input internal phase shift angle and the output internal phase shift angle of the multilevel converter include: S31. Obtain the transmission power fundamental wave component and the return power fundamental wave component of the multilevel converter per unit value; S32 Use the Lagrangian multiplier method to establish a Lagrangian equation based on the fundamental wave component of the transmission power and the fundamental wave component of the return power, and perform the three phase shift angles in the Lagrangian equation Find the partial derivative and get the derivative formula of the three phase shift angles; [0017] S33. Solve the derivative formula according to the restriction conditions to obtain the formula of the input phase shift angle and the output phase shift angle of the multilevel converter; [0018] Wherein, the Lagrangian equation is: upper@force,Color)=Q: (α, Force (v)you/f (α, Force (v)dead) the derivative of the three phase shift angles The formula is: [0019] [0020] U 02 ο a-2 s -- cosI--cos --(Asin ^-cosw) = 0 k 2 2N 2 '' = cosy sin y (cos^-Asin(p) = 0 =cos--cos--(sin ¢? + zcos^) = 0 [0022] The restriction conditions are: [0023] /f (Yu,β, φ} = cos]?¦ cos(g) sin (¢)= Ρο [0024] In the formula, Xi is the phase shift angle between the input terminal and the output terminal voltage midpoint of the multilevel converter, α is the input internal phase shift angle, 8 is the output internal phase shift angle, and k is the transformation ratio, ρο is the transmission power, Ν is the turns ratio of the converter, ear* (4min is the fundamental component of the transmission power, .: but *used) is the fundamental component of the return power, d is the force; 1) is the Lagrangian function , Artificial Lagrangian coefficient. [0025] Preferably, in step S3, using a PI controller to adjust the stable output of the output voltage of the multi-level converter specifically includes: adjusting the output voltage to the command voltage of the multi-level converter. The difference value of is adjusted and controlled by the PI controller according to the outer phase shift angle, so that the output voltage is equal to the command voltage. [0026] Preferably, the drive generation module uses a 2SP0320x2Ax control chip to control the on-off of the switching device in the multilevel converter. [0027] The present invention also provides a multi-level converter optimization control device based on the minimum return power, including a transformation ratio calculation module and a transmission power calculation module, and an optimized phase shift angle calculation module and a control module; [0028] The transformation ratio calculation module is used to calculate the input voltage, output voltage, and converter turn of the multi-level converter. Calculating the transformation ratio of the multi-level converter by number ratio; [0029] The transmission power calculation module is configured to calculate the multi-level converter according to the input voltage, output voltage, output current, resonance inductance, converter turns ratio, and switching frequency of the multi-level converter Standardized transmission power; [0030] The optimized phase shift angle calculation module is used for the multi-level converter in the minimum return power state, according to the transformation ratio, the converter turns ratio And the transmission power to calculate the input internal phase shift angle and the output internal phase shift angle of the multi-level converter; and use a PI controller to adjust the output voltage of the multi-level converter to stabilize the output to obtain State the external phase shift angle of the multilevel converter; [0031] The control module is configured to control the on-off of switching devices in the multilevel converter according to the input internal phase shift angle, the output internal phase shift angle, and the external phase shift angle; [0032] Wherein, the formula for calculating the input internal phase shift angle and the output internal phase shift angle of the multilevel converter is: [0033] a = 2arccos See you, Because = 0, where α is the input phase shift angle, 8 is the output phase shift angle, k is the transformation ratio, ρο is the transmission power, and N is the converter. Preferably, the optimized phase shift angle calculation module includes obtaining Power fundamental component sub-module, derivative calculation sub-module [0034] Turns ratio. [0035] Block and phase shift angle calculation sub-module; [0036] The acquiring power fundamental component sub-module is used to acquire the transmission power fundamental component and the return power fundamental component of the multilevel converter per unit value [0037] The derivation calculation sub-module is used to establish a Lagrangian equation based on the fundamental wave component of the transmission power and the fundamental wave component of the return power by using the Lagrangian multiplier method, and to calculate the The three phase shift angles in the Grange equation are used to find the partial derivative, and the derivative formula of the three phase shift angles is obtained; [0038] The phase shift angle calculation sub-module is used to solve the derivative formula according to the restriction conditions to obtain the formula of the input internal phase shift angle and the output internal phase shift angle of the multilevel converter; [0039] [0040] [0041] Wherein, the Lagrangian equation is: £(&amp;, month, 0, force=0*(&amp;, universal one offense*(%universal-%] the derivative of the three phase shift angles The formula is: 2] 0 ο Jiangliushengwei az¥ .a-sin 2 Ί- cos k -I--cos - (Asin &lt;p - cos(p\2 2N 2 '_ a= cos-2 .β sin - 2 (cos@sheetsin φ) = 0 a= cos- 2 βcos-2 .($in ¢? + zcos^) = 0 =0 [0043] [0044] [0045] The restriction conditions are: Piece. (degree floating to two cos fc* sinS)=p. In the formula, household is the phase shift angle between the input terminal and the output terminal voltage midpoint of the multilevel converter, and α is the phase shift within the input Angle, 8 is the internal phase shift angle of the output, k is the transformation ratio, ρο is the transmission power, Ν is the converter turns ratio, and R is the fundamental component of the transmission power, 0: (α/Μ) is the return power base The wave component is the Lagrangian function and the artificial Lagrangian coefficient. [0046] Preferably, the control module is further configured to adjust and control the difference between the output voltage and the command voltage of the multilevel converter through the PI controller according to the outer phase shift angle, so that The output voltage is equal to the command voltage. [0047] Preferably, the control module adopts a drive generation module formed by a 2SP0320x2Ax control chip to control the on-off of the switching device in the multilevel converter. [0048] The present invention also provides a computer-readable storage medium for storing computer instructions, which when running on a computer, cause the computer to execute the above-mentioned multi-level conversion based on the minimum return power Optimized control method. [0049] The present invention also provides a terminal device, including a processor and a memory; [0050] The memory is used to store program code and transmit the program code to the processor; [0051] The processor is configured to execute the above-mentioned method for optimizing control of the multi-level converter based on the minimum reflux power according to the instructions in the program code. [0052] It can be seen from the above technical solutions that the embodiments of the present invention have the following advantages: the multi-level converter optimized control method and device based on the minimum return power can obtain the input of the multi-level converter under the minimum return power through solving. The inner phase shift angle, the output inner phase shift angle and the outer phase shift angle control the operation of the multilevel converter, which can not only improve the large backflow caused by the mismatch of input and output voltages during the phase shift control of the multilevel converter. The shortcomings of low power and efficiency, etc., can effectively reduce the return power of the converter in the full power range and the full transformation ratio range, improve the efficiency and performance of the entire converter, and solve the problem of the existing three-level DAB converter in voltage failure. Under matching operating conditions, the use of traditional phase-shifting control methods will produce a larger return power, leading to technical problems such as increased system losses and reduced efficiency. [0053] The multi-level converter optimization control method based on the minimum return power calculates the optimal phase shift angle according to the voltage and current of the sampled multi-level converter, so as to reduce the return power and improve the performance of the multi-level converter, and Conventional return power control algorithm, this method does not require complicated modal analysis and range judgment between partitions, and reduces the amount of calculation and computational complexity of the control chip. Description of the drawings [0054] In order to more clearly describe the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the accompanying drawings that need to be used in the description of the embodiments or the prior art. Obviously, in the following description The drawings are merely some embodiments of the present invention. For those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative labor. [0055] FIG. 1 is a circuit schematic diagram of a three-level DAB converter in an optimized control method for a multi-level converter based on a minimum reflux power according to an embodiment of the present invention. [0056] FIG. 2 is a voltage and current waveform diagram of a three-level DAB converter in an optimized control method for a multi-level converter based on a minimum reflux power according to an embodiment of the present invention. [0057] FIG. 3 is a flow chart of the steps of an optimized control method for a multilevel converter based on a minimum reflux power according to an embodiment of the present invention. [0058] FIG. 4 is a framework diagram of an optimized control method for a multilevel converter based on a minimum return power according to an embodiment of the present invention. [0059] FIG. 5 is a graph of steady-state simulation results under the same power condition and different phase-shifting control modes. [0060] FIG. 6 is a simulation result diagram of the multi-level converter optimized control method based on the minimum return power according to the embodiment of the present invention at different powers and transformation ratios. [0061] FIG. 7 is a diagram of the simulation results of the current effective value of the multi-level converter optimized control method based on the minimum reflux power in different control modes according to the embodiment of the present invention. Detailed ways [0062] In order to make the objectives, features, and advantages of the present invention more obvious and understandable, the technical solutions in the embo
[ZH CN113437891A]: 一种交直流多端口六边形模块化多电平变换器及控制方法 [EN CN113437891A]: AC-DC multi-port hexagonal modularized multi-level converter and control method | [ZH CN113437891A]: 本发明涉及电力变换器技术，具体涉及一种交直流多端口六边形模块化多电平变换器及控制方法，该变换器由六个桥臂A‑F首尾相连形成六边形环状结构，该环形结构六组顶点按顺时针方向依次为R、W、S、U、T、V，六个桥臂分别与两个三相交流端口相连，其中RST组成第一端口，与交流电网相连，UVW组成第二端口，与风电场相连；各桥臂H桥子模块直流侧的电容采用双向有源桥，接入分布式光伏，作为直流端口。该变换器分别对前后级变换器设计控制实现多个端口之间功率的统一管理，确保该变换器的稳定运行。具有高度集成度的特点，无需高压直流母线，从而降低建设与维护成本，减少能量损耗。 [EN CN113437891A]: The invention relates to power converter technology, in particular to an AC-DC multi-port hexagonal modularized multi-level converter and a control method thereof. The converter is connected end to end by six bridge arms A-F to form a hexagonal ring structure , The six groups of vertices of the ring structure are R, W, S, U, T, V in clockwise direction, and the six bridge arms are respectively connected to two three-phase AC ports, of which RST constitutes the first port and is connected to the AC power grid , UVW forms the second port, which is connected to the wind farm; the capacitors on the DC side of each bridge arm H-bridge sub-module adopt a bidirectional active bridge, which is connected to distributed photovoltaics as a DC port. The converter respectively designs and controls the front and rear converters to realize the unified management of power among multiple ports, and to ensure the stable operation of the converter. It has the characteristics of a high degree of integration and does not require a high-voltage DC bus, thereby reducing construction and maintenance costs and reducing energy loss. | CN113437891A | 2021-09-24 | CN202110742304A | 2021-07-01 | CN202110742304A, 2021-07-01 | CN113437891A: 2021-09-24 | 武汉大学 |  | H02M7/483: I H02M1/088: I |  |  |  | [ZH CN113437891A]: 1 .一种交直流多端口六边形模块化多电平变换器，其特征在于：该变换器由六个桥臂 A-F首尾相连形成六边形环状结构，各桥臂皆由n个H桥子模块与1个电感串联构成，每个子 模块直流侧并联一个电容器，每个子模块输出三种电平+Vdc、0、-Vdc，每个桥臂电压输出2n+ 1电平，n为正整数；该环形结构六组顶点按顺时针方向依次为R、W、S、U、T、V，六个桥臂分别 与两个三相交流端口相连，其中RST组成第一端口，与交流电网相连，UVW组成第二端口，与 风电场相连;各桥臂H桥子模块直流侧的电容采用双向有源桥，接入分布式光伏，作为直流 端口。 2.根据权利要求1所述交直流多端口六边形模块化多电平变换器的控制方法，其特征 在于:变换器的前级变换器为双向有源桥，采用定电流控制，给定值与输入电流采集值作差 通过PI控制生成副边较原边的相位差信号，调节双向有源桥的输出功率;变换器的后级变 换器为输出侧级联的H桥变换器，实现端口间功率平衡控制、桥臂间与桥臂内的均压控制； 该控制方法包括以下步骤： 步骤1、设定直流端口的输入电流给定值，通过后级变换器的均压作用，得到各桥臂前 级变换器的输入功率；保持直流端口、第一端口与第二端口的有功功率平衡，得到第一端口 的有功功率;增加前端总体直压PI控制，各H桥模块直压平均值跟踪电容电压设定值，作为 第一端口有功功率的控制信号； 步骤2、根据第一端口对应的有功功率，计算端口电流幅值;根据坐标变换，生成输入电 流采集值，控制信号与输入电流采集值作差，通过比例谐振控制器QPR，跟踪端口电流频率， 生成第一端口电压控制信号； 步骤3、将桥臂分为两组，桥臂ACE与桥臂BDF；采集并计算桥臂的电容电压平均值，采用 PI控制实现无静差调节，实现桥臂间均压，生成中性点偏移电压vN*信号； 步骤4、第一端口电压控制信号与中性点偏移电压信号的叠加生成桥臂电压控制信号； 采集子模块电容电压，根据子模块所在桥臂电容电压平均值大小，与桥臂电流的大小与方 向，采用比例控制器生成桥臂电压调节值，实现当电容电压低于设定值，由交流侧给电容充 电；当电容电压高于设定值，子模块电容放电； 步骤5、桥臂电压控制信号与桥臂电压调节值叠加生成单个模块的调制信号，采用PSPWM，实现桥臂内各子模块调制信号的移相。 [EN CN113437891A]: 1 . An AC-DC multi-port hexagonal modular multilevel converter, characterized in that: the converter is connected end to end by six bridge arms AF to form a hexagonal ring structure, and each bridge arm is composed of n H bridges. The sub-module is connected in series with an inductor, and each sub-module is connected in parallel with a capacitor on the DC side, and each sub-module outputs three levels +Vdc, 0, -Vdc, The voltage output of each bridge arm is 2n + 1 level, n is a positive integer; the six groups of vertices of the ring structure are R, W, S, U, T, V in a clockwise direction, and the six bridge arms are connected with two three Phase AC ports are connected, of which RST constitutes the first port, which is connected to the AC grid, and UVW constitutes the second port, which is connected to the wind farm; the DC side capacitors of the H-bridge sub-modules of each bridge arm adopt a bidirectional active bridge to connect to distributed photovoltaics , As a DC port. 2. The control method of the AC-DC multi-port hexagonal modular multi-level converter according to claim 1, characterized in that: the front-stage converter of the converter is a bidirectional active bridge, which adopts constant current control, given The difference between the input current and the collected value of the input current is controlled by PI to generate a phase difference signal on the secondary side compared to the primary side to adjust the output power of the bidirectional active bridge; Power balance control between ports, and voltage equalization control between bridge arms and within bridge arms; The control method includes the following steps: Step 1. Set the input current value of the DC port, and obtain the voltage equalization function of the downstream converter. The input power of the pre-converter of each bridge arm; maintain the balance of the active power of the DC port, the first port and the second port to obtain the active power of the first port; increase the overall direct voltage PI control of the front end, and the direct voltage of each H-bridge module is average The value tracking capacitor voltage setting value is used as the control signal of the active power of the first port; Step 2. Calculate the port current amplitude according to the active power corresponding to the first port; According to the coordinate transformation, generate the input current collection value, control signal and input The current acquisition value is changed, and the port current frequency is tracked through the proportional resonant controller QPR to generate the first port voltage control signal; Step 3. Divide the bridge arms into two groups, the bridge arm ACE and the bridge arm BDF; collect and calculate the bridge arm The average value of the capacitor voltage is controlled by PI to achieve no static difference adjustment, realize the voltage equalization between the bridge arms, and generate the neutral point offset voltage vN*Signal; Step 4. The superposition of the first port voltage control signal and the neutral point offset voltage signal generates the bridge arm voltage control signal; collect the sub-module capacitor voltage, and according to the average value of the bridge arm capacitor voltage where the sub-module is located, and the bridge arm For the magnitude and direction of the current, a proportional controller is used to generate the bridge arm voltage adjustment value, so that when the capacitor voltage is lower than the set value, the AC side charges the capacitor; when the capacitor voltage is higher than the set value, the sub-module capacitor discharges; Step 5 , The bridge arm voltage control signal and the bridge arm voltage adjustment value are superimposed to generate the modulation signal of a single module, and PSPWM is used to realize the phase shift of the modulation signal of each sub-module in the bridge arm. | [ZH CN113437891A]: 一种交直流多端口六边形模块化多电平变换器及控制方法 技术领域 [0001]本发明属于电力变换器技术领域，特别涉及一种交直流多端口六边形模块化多电 平变换器及控制方法。 背景技术 [0002]近年来，为缓解能源危机，新能源发电成为优先的发展目标。 [0003]随着大量分布式能源、储能设备等的接入，传统变换器已无法满足新能源出力与 负荷变化的调节、功率多向流动等需求。且多级变换器往往会增加装置的成本与体积，降低 装置的效率，而交直流多端口变换器的是应对这一挑战的重要手段。 [0004]三端口六边形模块化多电平变换器拓扑，实现了三个交流端口间的功率交互。桥 臂复用的特点使装置紧密性高，但引入第三个交流端口，需要增加移相变压器，增加了装置 的体积，且该拓扑的应用场景受限。 发明内容 [0005]针对背景技术存在的问题，本发明提供一种高频化磁耦合的多端口六边形模块化 多电平变换器及控制方法。 [0006]为解决上述技术问题，本发明采用如下技术方案:一种交直流多端口六边形模块 化多电平变换器，该变换器由六个桥臂A-F首尾相连形成六边形环状结构，各桥臂皆由n个H 桥子模块与1个电感串联构成，每个子模块直流侧并联一个电容器，每个子模块输出三种电 平+Vdc、°、-Vdc，每个桥臂电压输出2n+1电平，n为正整数；该环形结构六组顶点按顺时针方 向依次为R、W、S、U、T、V，六个桥臂分别与两个三相交流端口相连，其中RST组成第一端口，与 交流电网相连，UVW组成第二端口，与风电场相连;各桥臂H桥子模块直流侧的电容采用双向 有源桥，接入分布式光伏，作为直流端口。 [0007] 一种交直流多端口六边形模块化多电平变换器的控制方法，变换器的前级变换器 为双向有源桥，采用定电流控制，给定值与输入电流采集值作差通过PI控制生成副边较原 边的相位差信号，调节双向有源桥的输出功率;变换器的后级变换器为输出侧级联的H桥变 换器，实现端口间功率平衡控制、桥臂间与桥臂内的均压控制;该控制方法包括以下步骤： [0008]步骤1、设定直流端口的输入电流给定值，通过后级变换器的均压作用，得到各桥 臂前级变换器的输入功率；保持直流端口、第一端口与第二端口的有功功率平衡，得到第一 端口的有功功率;增加前端总体直压PI控制，各H桥模块直压平均值跟踪电容电压设定值， 作为第一端口有功功率的控制信号； [0009]步骤2、根据第一端口对应的有功功率，计算端口电流幅值；根据坐标变换，生成输 入电流采集值，控制信号与输入电流采集值作差，通过比例谐振控制器QPR，跟踪端口电流 频率，生成第一端口电压控制信号； [0010]步骤3、将桥臂分为两组，桥臂ACE与桥臂BDF；采集并计算桥臂的电容电压平均值， 采用PI控制实现无静差调节，实现桥臂间均压，生成中性点偏移电压vN*信号； [0011]步骤4、第一端口电压控制信号与中性点偏移电压信号的叠加生成桥臂电压控制 信号;采集子模块电容电压，根据子模块所在桥臂电容电压平均值大小，与桥臂电流的大小 与方向，采用比例控制器生成桥臂电压调节值，实现当电容电压低于设定值，由交流侧给电 容充电；当电容电压高于设定值，子模块电容放电； [0012]步骤5、桥臂电压控制信号与桥臂电压调节值叠加生成单个模块的调制信号，采用 PS-PWM，实现桥臂内各子模块调制信号的移相。 [0013]与现有技术相比，本发明的控制部分，可对直流端口与交流端口的能量进行统一 管理，实现直流端口与交流端口的功率平衡。可根据场景需求，改变交流端口的功率的大小 与方向。 附图说明 [0014]图1为本发明一个实施例一种交直流多端口六边形模块化多电平变换器拓扑； [0015]图2为本发明一个实施例一种交直流多端口六边形模块化多电平变换器拓扑的数 学模型； [0016]图3为本发明一个实施例前级变换器双向有源桥的控制框图； [0017]图4为本发明一个实施例后级变换器H桥逆变器的控制框图。 具体实施方式 [0018]下面将结合本发明实施例对本发明实施例中的技术方案进行清楚、完整地描述， 显然，所描述的实施例仅仅是本发明一部分实施例，而不是全部的实施例。基于本发明中的 实施例，本领域普通技术人员在没有作出创造性劳动的前提下所获得的所有其他实施例， 都属于本发明保护的范围。 [0019]需要说明的是，在不冲突的情况下，本发明中的实施例及实施例中的特征可以相 互组合。 [0020]下面结合具体实施例对本发明作进一步说明，但不作为本发明的限定。 [0021] 一种交直流多端口六边形模块化多电平变换器，该变换器拓扑结构为由六个桥臂 首尾相连形成六边形环形结构，该拓扑结构六组顶点按顺时针方向依次命名为R、W、S、U、T、 V。其中RST组成第一端口，与交流电网相连;UVW组成为第二端口，与风电场相连。各桥臂H桥 子模块直流侧采用双向有源桥实现分布式光伏接入，作为直流端口。 [0022] 一种交直流多端口六边形模块化多电平变换器的控制方法，变换器的前级变换器 为双向有源桥，采用定电流控制，给定值与输入电流采集值的作差通过PI控制生成副边较 原边的相位差信号，调节双向有源桥的输出功率。变换器的后级变换器为输出侧级联的H桥 变换器，并由后级变换器实现端口间功率平衡控制、桥臂间与桥臂内的均压控制。该控制方 法具体包括如下步骤： [0023] S1：设定直流端口的输入电流给定值，由于后级变换器起到均压作用，得到各桥臂 前级变换器的输入功率；保证直流端口、第一端口与第二端口的有功功率平衡，可得到第一 端口的有功功率;增加前端总体直压PI控制，各H桥模块直压平均值跟踪电容电压设定值， 防止电容直压泵升，作为第一端口有功功率的控制信号。 [0024] S2:根据交流端口对应的有功功率，计算端口电流幅值；根据坐标变换，生成端口 交流电流信号。控制信号与端口电流采集值作差，通过QPR（比例谐振控制器），跟踪端口电 流频率，生成端口电压控制信号。 [0025] S3:六个桥臂分别与两个三相交流端口相连，与同一端口相连的桥臂具有功率相 似性，可将桥臂分为两组一一桥臂ACE与桥臂BDF。采集并计算桥臂的电容电压平均值，采用 PI控制实现无静差调节，达到桥臂间均压的目的，生成中性点偏移电压vN*信号。 [0026] S4：端口控制信号与中性点偏移电压信号的叠加生成桥臂电压控制信号。采集子 模块电容电压，根据子模块所在桥臂电容电压平均值大小，与桥臂电流的大小与方向，采用 比例控制器生成桥臂电压调节值，实现当电容电压低于设定值，由交流侧给电容充电；当电 容电压高于设定值，子模块电容放电。 [0027] S5：桥臂电压控制信号与调节值的叠加生成单个模块的调制信号，采用PS-PWM，实 现桥臂内各子模块调制信号的移相，可保证良好的输出特性。 [0028]具体实施时，如图1所示，为一种交直流多端口六边形模块化多电平变换器。 [0029]该拓扑结构由六个桥臂A-F，首尾相连形成六边形环状结构，各桥臂皆由n个H桥子 模块与1个电感串联构成。每个子模块直流侧并联一个电容器。每个子模块输出三种电平，+ Vdc、°、7dc，即每个桥臂电压输出2n+1电平，n为正整数。 [0030] 该拓扑结构六个顶点依次R、W、S、U、T、V，分别与两组三相交流端口相连:RST为第 一端口，与交流电网相连；UVW为第二端口，与海上风电场相连。 [0031]各H桥子模块直流侧的电容，采用双向有源桥变换器实现分布式光伏的接入，且各 有源输入独立，作为直流端口。根据分布式光伏规模,设计变压器变比与电感参数。 [0032]交直流端口的功率通过六个桥臂进行交互。由分布式光伏与海上风电场发电并 网，传输给交流电网。 [0033]如图2所示，为本实施例一种交直流多端口六边形模块化多电平变换器的数学模 型。 [0034]各桥臂等效为一个电压源与电感的串联,六个桥臂的电压依次命名为va,vb,vc, vd,ve和vf，六个桥臂的电流依次命名为ia,ib,ic,id,ie和if。端口1的三相电压依次为vr,vs和 vt，端口1的三相电流依次为ir,is和it；端口2的三相电压依次为vu,vv和vw，端口1的三相电 流依次为iu,iv和iw。端口1的中性点设为叫，端口2的中性点设为N2,以端口2为参考点，端口1 较端口2的中性点偏移电压为vN。 [0035]如图3所示，为双向有源桥（前级变换器）的控制框图，采用定电流控制，参考值 iin ref与输入电流采集值iin的作差通过PI控制生成副边较原边的相位差信号，调节双向有 源桥的输出功率。 [0036]如图4所示，为H桥逆变器（后级变换器）的控制框图，以实现端口间功率平衡控制、 桥臂间与桥臂内的均压控制。交直流多端口六边形模块化多电平变换器控制方法具体包括 如下步骤： [0037] ⑴设定直流端口的输入电流给定值，由于后级变换器起到均压作用，得到各桥臂 前级变换器的输入功率ppv；保证直流端口 ppv、第一端口 pp1与第二端口 pp2的有功功率平衡， 可得到第一端口的有功功率;增加前端总体直压PI控制，各H桥模块直压平均值跟踪电容电 压设定值，防止电容直压泵升，作为第一端口有功功率的控制信号。 [0038] ⑵根据交流端口对应的有功功率，计算端口电流d轴分量i*1d ；根据坐标变换，生 成端口交流电流信号控制信号ij和iu「与端口电流采集值Lt和八作差，通过QPR (比例谐振控制器)，跟踪端口电流频率，生成端口电压控制信号V®*和Vu;。 [0039] (3)六个桥臂分别与两个三相交流端口相连，与同一端口相连的桥臂具有功率相 似性，可将桥臂分为两组，桥臂ACE与桥臂BDF。采集并计算桥臂的电容电压平均值丫公3与 vdc bdf，采用PI控制实现无静差调节，达到桥臂间均压的目的，生成中性点偏移电压V；信号。 [0040] ⑷端口控制信号7；和Vs*与中性点偏移电压信号vj的叠加生成桥臂电压控制 信号Vbij。采集子模块电容电压Vdc bii，根据模块所在桥臂电容电压平均值大小r，与桥臂 J UC 01J — 电流的大小与方向，采用比例控制器生成桥臂电压调节值Α ν山.,实现当电容电压低于设定 值，由交流侧给电容充电；当电容电压高于设定值，子模块电容放电。 [0041] ⑸桥臂电压控制信号ν山.与调节值Α ν皿.的叠加生成单个模块的调制信号，采用 PS-PWM,实现桥臂内各子模块调制信号的移相，可保证良好的输出特性。 [0042]本实施例一种交直流多端口六边形模块化多电平变换器可实现分布式光伏与海 上风电并网，该变换器由六个桥臂首尾相连构成，可引出两个三相交流端口，分别连接交流 电网与海上风电场;各桥臂Η桥子模块直流侧引入独立的有源输入，采用双向有源桥变换器 实现分布式光伏的接入。为确保该变换器的稳定运行,分别对前后级变换器设计控制实现 多个端口之间功率的统一管理。具有高度集成度的特点，无需高压直流母线，从而降低建设 与维护成本，减少能量损耗。 [0043]以上仅为本发明较佳的实施例，并非因此限制本发明的实施方式及保护范围，对 于本领域技术人员而言，应当能够意识到凡运用本发明内容所作出的等同替换和显 而易见的变化所得到的方案，均应当包含在本发明的保护范围内。 [EN CN113437891A]: Technical field of AC-DC multi-port hexagonal modularized multi-level converter and control method [0001] The present invention belongs to the technical field of power converters, and particularly relates to an AC-DC multi-port hexagonal modular multi-level converter and a control method. Background technique [0002] In recent years, in order to alleviate the energy crisis, new energy power generation has become a priority development goal. [0003] With the access of a large number of distributed energy sources, energy storage equipment, etc., traditional converters have been unable to meet the needs of new energy output and load change adjustment, and power multi-directional flow. In addition, multi-level converters tend to increase the cost and volume of the device and reduce the efficiency of the device. AC-DC multi-port converters are an important means to deal with this challenge. [0004] The three-port hexagonal modular multilevel converter topology realizes the power interaction between the three AC ports. The characteristics of bridge arm multiplexing make the device compact, but the introduction of the third AC port requires the addition of a phase-shifting transformer, which increases the size of the device, and the application scenarios of this topology are limited. Summary of the invention [0005] In view of the problems existing in the background art, the present invention provides a high-frequency magnetic coupling multi-port hexagonal modular multi-level converter and a control method. [0006] In order to solve the above technical problems, the present invention adopts the following technical solutions: an AC-DC multi-port hexagonal modular multilevel converter, the converter is formed by six bridge arms AF end to end to form a hexagonal ring Structure, each bridge arm is composed of n H bridge sub-modules and 1 inductor in series, each sub-module is connected in parallel with a capacitor on the DC side, and each sub-module outputs three levels +Vdc, °, -Vdc, The voltage output of each bridge arm is 2n+1 level, n is a positive integer; the six groups of vertices of the ring structure are R, W, S, U, T, V in a clockwise direction, and the six bridge arms are connected with two Three-phase AC ports are connected, of which RST constitutes the first port, which is connected to the AC grid, and UVW constitutes the second port, which is connected to the wind farm; the DC side capacitors of the H-bridge sub-modules of each bridge arm adopt a bidirectional active bridge, which is connected to the distributed Photovoltaic, as a DC port. [0007] A control method of an AC-DC multi-port hexagonal modular multi-level converter, the front-stage converter of the converter is a bidirectional active bridge, which adopts constant current control, and the given value and the input current acquisition value are used as The difference is controlled by PI to generate the phase difference signal of the secondary side compared to the primary side to adjust the output power of the bidirectional active bridge; The voltage equalization control between the arms and the bridge arms; the control method includes the following steps: [0008] Step 1. Set a given value of the input current of the DC port, and obtain the front of each bridge arm through the voltage equalization effect of the downstream converter The input power of one-stage converter; maintain the balance of the active power of the DC port, the first port and the second port to obtain the active power of the first port; increase the front-end overall direct voltage PI control, and the direct voltage average value of each H-bridge module tracks the capacitor voltage The set value is used as a control signal for the active power of the first port; [0009] Step 2. Calculate the port current amplitude according to the active power corresponding to the first port; generate the input current acquisition value according to the coordinate transformation, and make the difference between the control signal and the input current acquisition value, and track the port through the proportional resonance controller QPR Current frequency, generating the first port voltage control signal; [0010] Step 3. Divide the bridge arms into two groups, the bridge arm ACE and the bridge arm BDF; collect and calculate the average value of the capacitor voltage of the bridge arm, adopt PI control to achieve no static difference adjustment, realize the voltage equalization between the bridge arms, and generate Neutral point offset voltage vN*Signal; [0011] Step 4. The superposition of the first port voltage control signal and the neutral point offset voltage signal generates the bridge arm voltage control signal; collect the sub-module capacitor voltage, and according to the average value of the bridge arm capacitor voltage where the sub-module is located, and the bridge arm For the magnitude and direction of the current, a proportional controller is used to generate the bridge arm voltage adjustment value, so that when the capacitor voltage is lower than the set value, the AC side charges the capacitor; when the capacitor voltage is higher than the set value, the sub-module capacitor discharges; [0012] Step 5, the bridge arm voltage control signal and the bridge arm voltage adjustment value are superimposed to generate a modulation signal of a single module, and PS-PWM is used to realize the phase shift of the modulation signal of each sub-module in the bridge arm. [0013] Compared with the prior art, the control part of the present invention can uniformly manage the energy of the DC port and the AC port, and realize the power balance between the DC port and the AC port. The size and direction of the power of the AC port can be changed according to the needs of the scene. Description of the drawings [0014] FIG. 1 is an AC-DC multi-port hexagonal modular multi-level converter topology according to an embodiment of the present invention; [0015] FIG. 2 is a mathematical model of an AC-DC multi-port hexagonal modular multi-level converter topology according to an embodiment of the present invention; [0016] FIG. 3 is a control block diagram of a bidirectional active bridge of the pre-converter according to an embodiment of the present invention; [0017] FIG. 4 is a control block diagram of the H-bridge inverter of the post-converter according to an embodiment of the present invention. Detailed ways [0018] The technical solutions in the embodiments of the present invention will be clearly and completely described below in conjunction with the embodiments of the present invention. Obviously, the described embodiments are only a part of the embodiments of the present invention, rather than all the embodiments. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0019] It should be noted that the embodiments of the present invention and the features in the embodiments can be combined with each other if there is no conflict. [0020] The present invention will be further described below in conjunction with specific embodiments, but not as a limitation of the present invention. [0021] An AC-DC multi-port hexagonal modular multilevel converter. The converter topology is formed by connecting six bridge arms end to end to form a hexagonal ring structure. The six sets of vertices of the topology structure are clockwise. They are named R, W, S, U, T, V in turn. The RST constitutes the first port, which is connected to the AC power grid; the UVW constitutes the second port, which is connected to the wind farm. The DC side of the H-bridge sub-modules of each bridge arm adopts a bidirectional active bridge to realize distributed photovoltaic access as a DC port. [0022] A control method of an AC-DC multi-port hexagonal modular multi-level converter, the front-stage converter of the converter is a bidirectional active bridge, which adopts constant current control, and the set value is compared with the input current collection value. The difference is controlled by PI to generate a phase difference signal between the secondary side and the primary side to adjust the output power of the bidirectional active bridge. The downstream converter of the converter is a cascaded H-bridge converter on the output side, and the latter converter implements power balance control between ports and voltage equalization control between the bridge arms and the bridge arms. The control method specifically includes the following steps: [0023] S1: Set the given value of the input current of the DC port, because the downstream converter plays the role of voltage equalization, the input power of the front converter of each bridge arm is obtained; the DC port, the first port and the second port are guaranteed The active power of the first port can be balanced, and the active power of the first port can be obtained; the front-end overall direct voltage PI control is added, and the direct voltage average value of each H-bridge module tracks the capacitor voltage setting value to prevent the capacitor direct voltage pump from rising, as the first port active power Control signal. [0024] S2: Calculate the port current amplitude according to the active power corresponding to the AC port; generate the port according to the coordinate transformation AC current signal. The difference between the control signal and the port current collection value, through the QPR (Proportional Resonant Controller), tracks the port current frequency, and generates the port voltage control signal. [0025] S3: The six bridge arms are respectively connected to two three-phase AC ports, and the bridge arms connected to the same port have power similarity. The bridge arms can be divided into two groups, one bridge arm ACE and bridge arm BDF. Collect and calculate the average value of the capacitor voltage of the bridge arm, adopt PI control to achieve no static difference adjustment, achieve the purpose of voltage equalization between the bridge arms, and generate the neutral point offset voltage vN*Signal. [0026] S4: The superposition of the port control signal and the neutral point offset voltage signal generates a bridge arm voltage control signal. Collect the capacitor voltage of the sub-module. According to the average value of the capacitor voltage of the bridge arm where the sub-module is located, and the size and direction of the bridge arm current, a proportional controller is used to generate the bridge arm voltage adjustment value, so that when the capacitor voltage is lower than the set value, the AC Charge the capacitor on the side; when the capacitor voltage is higher than the set value, the sub-module capacitor discharges. [0027] S5: The superposition of the bridge arm voltage control signal and the adjustment value generates the modulation signal of a single module, and PS-PWM is used to realize the phase shift of the modulation signal of each sub-module in the bridge arm, which can ensure good output characteristics. [0028] In specific implementation, as shown in FIG. 1, it is an AC-DC multi-port hexagonal modular multi-level converter. [0029] The topological structure is composed of six bridge arms AF, which are connected end to end to form a hexagonal ring structure, and each bridge arm is composed of n H bridge sub-modules and an inductor in series. A capacitor is connected in parallel on the DC side of each sub-module. Each sub-module outputs three levels, + Vdc、°、7dc, That is, each bridge arm voltage output 2n+1 level, n is a positive integer. [0030] The six vertices of the topological structure are sequentially R, W, S, U, T, V, respectively connected to two groups of three-phase AC ports: RST is the first port, which is connected to the AC power grid; UVW is the second port, and The offshore wind farm is connected. [0031] The capacitor on the DC side of each H-bridge sub-module adopts a bidirectional active bridge converter to implement distributed photovoltaic access, and each active input is independent as a DC port. According to the scale of distributed photovoltaic, design transformer transformation ratio and inductance parameters. [0032] The power of the AC and DC ports interacts through six bridge arms. Distributed photovoltaics and offshore wind farms are connected to the grid and transmitted to the AC grid. [0033] As shown in FIG. 2, this embodiment is a mathematical model of an AC-DC multi-port hexagonal modular multi-level converter. [0034] Each bridge arm is equivalent to a series connection of a voltage source and an inductor, and the voltages of the six bridge arms are named v in turna,vb,vc, vd,veAnd vf, The currents of the six bridge arms are named i in turna,ib,ic,id,ieAnd if. The three-phase voltage of port 1 is v in turnr,vsAnd vt, The three-phase current of port 1 is ir,isAnd it; The three-phase voltage of port 2 is v in turnu,vvAnd vw, The three-phase current of port 1 is iu,ivAnd iw. The neutral point of port 1 is set to be called, the neutral point of port 2 is set to N2, Taking port 2 as the reference point, the offset voltage of port 1 from the neutral point of port 2 is vN。 [0035] As shown in Fig. 3, it is a control block diagram of a bidirectional active bridge (pre-converter), which adopts constant current control, and the reference value iin refAnd input current acquisition value iinThe difference is controlled by PI to generate a phase difference signal between the secondary side and the primary side to adjust the output power of the bidirectional active bridge. [0036] As shown in FIG. 4, it is a control block diagram of an H-bridge inverter (post-converter) to achieve power balance control between ports, and voltage equalization control between bridge arms and within bridge arms. The control method of the AC-DC multi-port hexagonal modular multi-level converter specifically includes the following steps: [0037] Set the given value of the input current of the DC port, since the downstream converter plays the role of voltage equalization, the input power p of the front-stage converter of each bridge arm is obtainedpv; Ensure that the DC port ppv, The first port pp1With the second port pp2Active power balance of the first port can be obtained; the front-end overall direct voltage PI control is added, and the average direct voltage of each H-bridge module tracks the capacitor voltage setting value to prevent the capacitor direct pressure pump from rising as the first port active power Control signal. [0038] According to the active power corresponding to the AC port, calculate the d-axis component of the port current i*1d ;According to the coordinate transformation, The port AC current signal control signals ij and iu" are differentiated from the port current acquisition values Lt and B, and the port current frequency is tracked through QPR (Proportional Resonance Controller) to generate port voltage control signals V®* and Vu;. [0039] (3) The six bridge arms are respectively connected to two three-phase AC ports, and the bridge arms connected to the same port have power similarity. The bridge arms can be divided into two groups, the bridge arm ACE and the bridge arm BDF. Collect and calculate the average value of the capacitor voltage of the bridge arm, Yagong 3 and vdc bdf, using PI control to achieve no static difference adjustment, achieve the purpose of voltage equalization between the bridge arms, and generate the neutral point offset voltage V; signal. [0040] (4) The port control signal 7; and the superposition of Vs* and the neutral point offset voltage signal vj to generate the bridge arm voltage control signal Vbij. Collect the capacitor voltage Vdc bii of the sub-module. According to the average value r of the capacitor voltage of the bridge arm where the module is located, J UC 01J - The magnitude and direction of the current, the proportional controller is used to generate the bridge arm voltage adjustment value Ανshan. When the capacitor voltage is lower than the set value, the AC side charges the capacitor; when the capacitor voltage is higher than the set value , The sub-module capacitor is discharged. [0041] The bridge arm voltage control signal ν mountain and the adjustment value Α ν dish superimposed to generate the modulation signal of a single module, using PS-PWM realizes the phase shift of the modulation signal of each sub-module in the bridge arm, which can ensure good output characteristics. [0042] The AC-DC multi-port hexagonal modular multi-level converter of this embodiment can realize the grid connection of distributed photovoltaic and offshore wind power. The converter consists of six bridge arms connected end to end, which can lead to two three Phase AC ports are respectively connected to the AC power grid and offshore wind farms; the DC side of each bridge arm H-bridge sub-module introduces independent active inputs, and uses bidirectional active bridge converters to achieve distributed photovoltaic access. In order to ensure the stable operation of the converter, the front and rear converters are designed and controlled to realize the unified management of power among multiple ports. It has the characteristics of a high degree of integration and does not require a high-voltage DC bus, thereby reducing construction and maintenance costs and reducing energy loss. [0043] The above are only preferred embodiments of the present invention, and do not therefore limit the implementation and protection scope of the present invention. For those skilled in the art, it should be possible to realize that equivalent replacements and obvious alternatives made by using the content of the present invention All the solutions obtained by the changes should be included in the protection scope of the present invention.
[ZH CN113271029A]: 一种低电压应力宽输出范围DAB型单级双向AC/DC变换器 [EN CN113271029A]: A DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range | [ZH CN113271029A]: 一种低电压应力宽输出范围DAB(双有源桥)型单级双向AC/DC变换器，是由交流滤波器、周波变换器、n个原边串联的高频变压器、n个全桥电路、直流滤波器、变结构开关组依序级联构成；其中，每个变压器副边经漏感分别与一个全桥电路连接，n个全桥电路输出端由变结构开关组实现串联或并联，周波变换器、n个高频变压器和n个全桥电路组成n组双有源桥结构；变换器采用电流外环功率内环控制策略，可工作在整流和逆变模式，实现双向AC/DC变换和交流侧功率因数控制；该变换器采用DAB结构降低了周波变换器的开关电压应力，属于单级功率变换，没有直流环节，提高了变换器的可靠性；n组双有源桥结构和变结构开关组提高了变换器的容量，适用于大功率场合。 [EN CN113271029A]: A DAB (Dual Active Bridge) single-stage bidirectional AC/DC converter with low voltage stress and wide output range. It consists of an AC filter, a cycloconverter, a high-frequency transformer connected in series with n primary sides, and n full-bridge circuits. , DC filter, and variable structure switch groups are sequentially cascaded; among them, each transformer secondary side is connected to a full bridge circuit via leakage inductance, and n full bridge circuit output terminals are connected in series or parallel by the variable structure switch group. Cyclic converter, n high-frequency transformers and n full-bridge circuits form n groups of dual active bridge structures; the converter adopts current outer loop power inner loop control strategy, and can work in rectification and inverter modes to achieve bidirectional AC/DC Conversion and AC-side power factor control; the converter adopts DAB structure to reduce the switching voltage stress of the cycloconverter. It belongs to single-stage power conversion and has no DC link, which improves the reliability of the converter; n groups of dual active bridge structures and The variable structure switch group increases the capacity of the converter and is suitable for high-power applications. | CN113271029A | 2021-08-17 | CN202110591932A | 2021-05-28 | CN202110591932A, 2021-05-28 | CN113271029A: 2021-08-17 | 青岛大学 |  | H02M7/797: I B60L55/00: I H02J3/32: I H02J7/06: I H02M5/293: I |  |  |  | [ZH CN113271029A]: 1 .一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，其特征在于：该变换器是 由交流滤波器、周波变换器、n个原边串联的高频变压器、n个全桥电路、直流滤波器、变结构 开关组依序级联构成;其中，每个变压器副边经漏感分别与一个全桥电路连接，n个全桥电 路输出端由变结构开关组实现串联或并联，周波变换器、n个高频变压器和n个全桥电路组 成n组双有源桥结构；所述交流滤波器由m相LC滤波器构成(m=1,3,5,6,……)；所述周波变 换器为m相m桥臂周波变换器,特别地,当m=1时所述周波变换器为单相两桥臂周波变换器； 所述周波变换器的每个桥臂由两个反向串联的功率开关构成;所述n个高频变压器原边绕 组串联，副边分别连接到一个全桥电路;所述每个全桥电路由四个功率开关组成,n个全桥 电路输出端经直流滤波器连接到变结构开关组，所述直流滤波器由电容C滤波器构成;变结 构开关组由3n-3个功率开关构成，包括n-1个串联选择开关和2n-2个并联选择开关，变结构 开关组输出连接到直流侧电源。 2 .根据权利要求1所述的一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，其 特征在于:所述变换器的交流滤波器连接m相交流电源和m相周波变换器;所述交流电源为 单相、三相、六相等多相电源;特别地，当变换器连接到单相工频电网时，电网经单相LC滤波 器连接到单相周波变换器第1、2桥臂的中点；当变换器连接到三相工频电网时，电网的A、B、 C相分别经三相LC滤波器连接到三相周波变换器第1、2、3桥臂的中点；上桥臂的公共端连接 至节点P,下桥臂的公共端连接至节点N；所述n个高频变压器原边绕组依次串联在P、N节点 之间;所述n个全桥电路分别与n个高频变压器的副边绕组连接;所述n个高频双向全桥整流 器输出端经直流滤波器连接到变结构开关组;变结构开关组输出并联到直流侧电源两端。 3 .根据权利要求1所述的一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，其 特征在于:所述变换器采用双有源桥结构，周波变换器的开关电压应力为交流侧线电压。 4 .根据权利要求1所述的一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，其 特征在于:所述变换器的输入串联的n组双有源桥结构可以工作在同步模式，也可以工作在 非同步模式；当工作在同步模式时,n组双有源桥结构输出均衡功率；当工作在非同步模式 时，变换器可以实现n组双有源桥结构的功率分配，也可以关闭其中一个或多个双有源桥结 构以调整输出功率等级。 5 .根据权利要求1所述的一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，其 特征在于:所述变结构开关组是由3n-3个开关构成，包括n-1个串联选择开关和2n-2个并联 选择开关;所述n-1个串联选择开关闭合、2n-2个并联选择开关断开时,n个高频双向全桥整 流器输出端串联;所述n-1个串联选择开关断开、2n-2个并联选择开关闭合时,n个高频双向 全桥整流器输出端并联;所述变换器通过变结构开关组改变各高频双向全桥整流器的串、 并联结构，既能实现输出电压的宽范围调节，又能实现分压和分流，减小系统设计容量。 [EN CN113271029A]: 1 A DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range, characterized in that: the converter is composed of an AC filter, a cycloconverter, n primary-side high-frequency transformers in series, and n full The bridge circuit, the DC filter, and the variable structure switch group are sequentially cascaded; among them, the secondary side of each transformer is connected to a full bridge circuit via leakage inductance, and the output terminals of the n full bridge circuits are connected in series or by the variable structure switch group. In parallel, the cycloconverter, n high-frequency transformers and n full-bridge circuits form n groups of dual active bridge structures; the AC filter is composed of m-phase LC filters (m=1,3,5,6,... ...); The cycloconverter is an m-phase m-arm cycloconverter, in particular, when m=1, the cycloconverter is a single-phase two-arm cycloconverter; each bridge of the cycloconverter The arm is composed of two power switches connected in reverse series; the primary windings of the n high-frequency transformers are connected in series, and the secondary sides are respectively connected to a full bridge circuit; each full bridge circuit is composed of four power switches, n The output terminal of the full-bridge circuit is connected to the variable structure switch group via a DC filter, the DC filter is composed of a capacitor C filter; the variable structure switch group is composed of 3n-3 power switches, including n-1 series selection switches and 2n-2 parallel selection switches, the output of the variable structure switch group is connected to the DC side power supply. 2 The DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range according to claim 1, characterized in that: the AC filter of the converter is connected to an m-phase AC power supply and an m-phase cycloconverter The AC power supply is a single-phase, three-phase, six-phase multi-phase power supply; in particular, when the converter is connected to a single-phase power frequency grid, the grid is connected to the single-phase cycloconverter 1st through a single-phase LC filter 2 The midpoint of the bridge arm; when the converter is connected to a three-phase power frequency grid, the A, B, and C phases of the grid are respectively connected to the first, second, and third bridge arms of the three-phase cycloconverter through a three-phase LC filter. Midpoint; the common end of the upper bridge arm is connected to node P, and the common end of the lower bridge arm is connected to node N; the n primary windings of the high-frequency transformer are connected in series between the nodes P and N; the n total The bridge circuit is respectively connected to the secondary windings of n high-frequency transformers; the output ends of the n high-frequency bidirectional full-bridge rectifiers are connected to the variable structure switch group via a DC filter; the output of the variable structure switch group is connected in parallel to both ends of the DC side power supply . 3 The DAB single-stage bidirectional AC/DC converter with low voltage stress and wide output range according to claim 1, characterized in that: the converter adopts a dual active bridge structure, and the switching voltage stress of the cyclic converter is AC side line voltage. 4 The DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range according to claim 1, characterized in that: the input of the converter is connected in series with n groups of dual active bridge structures that can work in synchronization Mode, it can also work in non-synchronous mode; when working in synchronous mode, n groups of dual active bridge structure output balanced power; when working in non-synchronous mode, the converter can realize the power distribution of n groups of dual active bridge structure , You can also turn off one or more of the dual active bridge structures to adjust the output power level. 5 The DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range according to claim 1, characterized in that: the variable structure switch group is composed of 3n-3 switches, including n-1 Two series selection switches and 2n-2 parallel selection switches; when the n-1 series selection switches are closed and the 2n-2 parallel selection switches are open, the output terminals of the n high-frequency bidirectional full-bridge rectifiers are connected in series; the n When -1 series selection switches are opened and 2n-2 parallel selection switches are closed, the output terminals of n high-frequency bidirectional full-bridge rectifiers are connected in parallel; the converter changes the series of each high-frequency bidirectional full-bridge rectifier through a variable structure switch group. , Parallel structure, not only can realize wide-range adjustment of output voltage, but also realize voltage division and current distribution, reducing system design capacity. | [ZH CN113271029A]: 一种低电压应力宽输出范围DAB型单级双向人。/[）。变换器 技术领域： [0001]本发明所涉及的一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，属于电 能变换领域。 背景技术： [0002]随着经济的飞速发展和生活水平的提高，汽车已成为必不可少的代步工具，使用 新能源逐步代替传统化石燃料来驱动汽车，是未来汽车工业发展的必然趋势。在新基建背 景支持下，充电设备的建设也随着电动汽车数量的增长而得到了快速的发展，并且拥有广 阔的发展空间。 [0003]大量电动汽车接入电网，也使合理利用汽车和电网的互动、实现最优充电成为研 究热点。如果使这些汽车在用电低谷时段从电网吸收能量，对电动汽车进行充电;在用电高 峰时段，将电动汽车蓄电池的能量回馈给电网，就能有效减小电网日用电负荷峰谷差，对电 网起到削峰填谷的作用，实现双向逆变式充电技术，也称电动汽车与电网双向互动 （vehicle to grid，V2G），使电动汽车兼具负荷管理和系统调峰的作用，以便实现能源的合 理分配并达成电网与用户双赢，长期来看V2G技术将成为能源互联的重要一环。 [0004]双向AC/DC变换器作为连接电动汽车与电网的重要环节，现有研究主要集中于两 级式结构，这类结构存在两级功率变换、功率密度低、变换效率不够理想、直流母线电解电 容寿命低等问题。因此，寻求一种具有单级功率变换、电路拓扑简洁、电气隔离、高效、高功 率密度、宽输出范围的双向AC/DC变换器具有重要理论和实践价值。 发明内容： [0005]本发明的目的是要提供一种具有单级功率变换、电路拓扑简洁、电气隔离、高效、 高功率密度、宽输出范围等特点的单级高频环节组合双向AC/DC变换器。 [0006]为了实现上述技术目的，本发明的技术方案在于： [0007] 一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，是由交流滤波器、周波 变换器、n个原边串联的高频变压器、n个全桥电路、直流滤波器、变结构开关组依序级联构 成；其中，每个变压器副边经漏感分别与一个全桥电路连接，n个全桥电路输出端由变结构 开关组实现串联或并联，周波变换器、n个高频变压器和n个全桥电路组成n组双有源桥结 构;输入串联n组双有源桥结构和变结构开关组在双向功率变换中实现高频双向全桥整流 器串、并联灵活切换，提高变换器的输出范围，减小系统的设计容量。 [0008] 所述变换器采用电流外环功率内环控制策略，直流侧电流外环用以实现稳定、优 质直流电流的输出（或输入），交流侧功率内环实现交流侧功率因数的控制;直流侧电流外 环输出交流侧功率内环的参考量，特别地，当m = 3时，内环功率控制在两相同步速dq坐标系 中进行,通过对瞬时有功功率和瞬时无功功率的控制,达到功率因数校正的目的。 [0009] 所述变换器可工作在整流模式和逆变模式，实现双向AC/DC变换，以及直流侧电流 和交流侧功率因数控制;直流电流给定参考量大于0时，变换器工作在整流模式，直流电流 给定参考量小于0时，变换器工作在逆变模式;在整流模式下，所述变换器实现交流侧的单 位功率因数控制;在逆变模式下，所述变换器可实现单位功率因数并网逆变或者参与电网 无功调节。 [0010] 本发明能够实现单级AC/DC变换，实现电网向电动汽车充电、电动汽车向电网发 电、参与电网无功调节等功能，具有单级功率变换、电路拓扑简洁、电气隔离、高效、高功率 密度、直流端口适应工作电压范围宽的特点。 附图说明 [0011]图1为所述变换器的结构图。 [0012]图2为所述变换器的单相多变压器电路拓扑实例。 [0013]图3为所述变换器的三相多变压器电路拓扑实例。 [0014]图4为所述变换器的六相多变压器电路拓扑实例。 [0015]图5为所述变换器的三相双变压器电路电路拓扑。 [0016]图6为所述变换器变结构开关组的两种等效电路。 [0017]图7为开关驱动波形、变压器电感电流和关键节点电压波形。 [0018]图8为所述变换器工作过程中的高频开关过程等效电路图。 具体实施方式： [0019]下面通过具体实例结合附图对本发明的技术方案做进一步详细的描述。 [0020] 一种低电压应力宽输出范围DAB型单级双向AC/DC变换器，是由m相交流滤波器、m 相周波变换器、n个原边串联的高频变压器、n个全桥电路、直流滤波器、变结构开关组依序 级联构成;其中，每个变压器副边经漏感分别与一个全桥电路连接，n个全桥电路输出端并 联，周波变换器、n个高频变压器和n个全桥电路组成n组双有源桥结构。所述变换器采用电 流外环功率内环控制策略，可工作在整流和逆变模式，实现双向AC/DC变换，以及直流侧电 流和交流侧功率因数控制。图2-图5分别为所述变换器的单相多变压器电路拓扑实例、三相 多变压器电路拓扑实例、六相多变压器电路拓扑实例、单相双变压器电路拓扑实例。以单相 双变压器电路拓扑为例，v是单相电压源，Lac Cac是单相LC滤波器，$1-$4、工’64'是单相周波 变换器的功率开关，Q「Q8是全桥电路的功率开关，TrT2是高频变压器，lrl2分别是「、12的 漏感，Co是直流滤波电容，VDC是直流电源。 [0021]所述变换器通过变结构开关组改变各高频双向全桥整流器的串、并联结构，既能 实现输出电压的宽范围调节，又能实现分压和分流，减小系统设计容量。串联选择开关飞]闭 合、并联选择开关SS1n和SS2P断开时，2个高频双向全桥整流器输出端串联，等效电路如图6 (a)所示；串联选择开关SS1断开、并联选择开关SS1n和SS2P闭合时，2个高频双向全桥整流器输 出端并联，等效电路如图6 (b)所示。 [0022]以整流模式、DAB直流侧并联为例，采用双移相控制，交流侧桥臂中点电压超前于 直流侧桥臂中点电压，从而实现能量由交流侧向直流侧的传输。图7是开关驱动波形、变压 器电感电流和关键节点电压波形。 [0023]变换器在一个高频开关周期内包括6个工作模态，等效电路如图8 (a) - (f)所示。 [0024] 模态1 (0&lt;t&lt;t]):交流侧电流以S2、S2'、T1、T2、S3、S3'为通路，变压器副边经Q2、Q3、 Q6«7向直流侧传送能量，作用时间为D · Ts，电感电流增量为： [0025] iLk i = T一- *D*TS - L1 [0026] 模态2 : t = J时，S]、S]'、S‘、S,'闭合，S?、S?'、S3、S3'关断，VpN反向，k、 由负变正。作用时间为(0.5-2D) · Ts，电感电流增量为： [0027] iLk_2 = + *(°-5 - 2D) * 3 [0028] 模态3 (t2&lt;t&lt;t3): t = t?时，Q3«7关断，、4«8导通。直流侧电流通过、2«4“6«8以及 变压器副边绕组形成回路。作用时间为D · Ts，电感电流增量为： kVDC — vc [0029] kk_3=T一 [0030] 模态4(t3〈t〈t/ ：t = t3时，Q2、Q6关断，SrS5开通。直流侧电流流经副边绕组及Qr Q4、Q5、Q8向负载传输电能。作用时间为D · Ts，电感电流增量为： kVDC + vc [0031] iLk4 =-- »D^T3 [0032] 模态 5(t4〈t〈t5): t = t,时，$2、$2'、$3、$3'闭合，$1、$1'、$4、$4'关断，丫「1^反向，£1、£2 由正变负。交流侧电流与模态1 一致。作用时间为(0.5-2D) · Ts，电感电流增量为： [0033] iLk_s = * *(05 - 2D) * 3 [0034] 模态6 (t5&lt;t&lt;t6) :t = t§时，Q4和Qg关断，Q3和Q7导通。直流侧电流通过5«3«5«7以 及变压器副边形成续流回路，作用时间为D · Ts，电感电流增量为： [0035] μ=苫--3 Ts [0036] [0037] t = t6时,Q]和Q5关断，Q2和Q6开通，之后电路回到模态1，进入下一开关周期。 根据电感的伏秒平衡： [0038] 4D [0039] - 4D kVDC 即得 [0040] [0041] kVDC D=--— 4(1+舟 KVDC 电路处于输入工频电压负半波时的工作模态与正半波类似，仅需调换SrSi'、S4、 SJ与$2、$2'、$3、$3'开关相位即可实现变换器的逆变模式。 [0042]以上所述实施例只为本发明之较佳实施例，本发明及其实施例不应仅限于此，故 凡依本发明之形状、原理所作的变化,均应涵盖在本发明的保护范围内。 [EN CN113271029A]: A DAB single-stage two-way human with low voltage stress and wide output range. /[). Converter technology field: [0001] The present invention relates to a DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range, which belongs to the field of electric energy conversion. Background technology: [0002] With the rapid economic development and the improvement of living standards, automobiles have become an indispensable means of transportation. The use of new energy sources to gradually replace traditional fossil fuels to drive automobiles is an inevitable trend in the future development of the automobile industry. With the support of the new infrastructure, the construction of charging equipment has also been rapidly developed with the increase in the number of electric vehicles, and has a broad space for development. [0003] A large number of electric vehicles are connected to the power grid, which also makes the rational use of the interaction between the vehicle and the power grid and the realization of optimal charging become a research hotspot. If these cars are made to absorb energy from the grid during the trough period of electricity consumption and charge electric vehicles; during the peak period of electricity consumption, the energy of the electric vehicle battery is fed back to the grid, which can effectively reduce the peak-valley difference of the daily power load of the grid. It plays the role of peak-shaving and valley-filling for the grid, and realizes the two-way inverter charging technology, also known as the two-way interaction between electric vehicles and the grid (vehicle to grid, V2G), so that electric vehicles have the functions of load management and system peak regulation. To realize the rational distribution of energy and achieve a win-win situation for the power grid and users, V2G technology will become an important part of energy interconnection in the long run. [0004] The bidirectional AC/DC converter is an important link between the electric vehicle and the power grid. Existing research mainly focuses on the two-stage structure. This type of structure has two-stage power conversion, low power density, unsatisfactory conversion efficiency, and DC bus. Problems such as low life of electrolytic capacitors. Therefore, seeking a bidirectional AC/DC converter with single-stage power conversion, simple circuit topology, electrical isolation, high efficiency, high power density, and wide output range has important theoretical and practical value. Summary of the invention: [0005] The purpose of the present invention is to provide a single-stage high-frequency link combined bidirectional AC/DC converter with the characteristics of single-stage power conversion, simple circuit topology, electrical isolation, high efficiency, high power density, and wide output range. [0006] In order to achieve the above technical objectives, the technical solution of the present invention is: [0007] A DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range is composed of an AC filter, a cycloconverter, a high frequency transformer connected in series with n primary sides, n full bridge circuits, and a DC filter. The transformer and variable structure switch groups are formed in sequence in cascade; among them, the secondary side of each transformer is connected to a full bridge circuit via leakage inductance, and the output terminals of n full bridge circuits are connected in series or parallel by the variable structure switch group, and the cycle converter , N high-frequency transformers and n full-bridge circuits form n groups of dual active bridge structures; input series n groups of dual active bridge structures and variable structure switch groups to realize high-frequency bidirectional full-bridge rectifiers in series and parallel in bidirectional power conversion Flexible switching, increase the output range of the converter, and reduce the design capacity of the system. [0008] The converter adopts a current outer loop power inner loop control strategy, the DC side current outer loop is used to achieve a stable and high-quality DC current output (or input), and the AC side power inner loop realizes the control of the AC side power factor; The DC side current outer loop outputs the reference value of the AC side power inner loop. In particular, when m = 3, the inner loop power control is carried out in the two-phase synchronous speed dq coordinate system, by comparing the instantaneous active power and instantaneous reactive power Control to achieve the purpose of power factor correction. [0009] The converter can work in rectification mode and inverter mode to realize bidirectional AC/DC conversion, as well as DC side current and AC side power factor control; when the reference value of DC current is greater than 0, the converter works in rectification Mode, DC current When the given reference value is less than 0, the converter works in the inverter mode; in the rectifier mode, the converter realizes unit power factor control on the AC side; in the inverter mode, the converter can realize unit power factor parallel Grid inversion or participation in grid reactive power regulation. [0010] The present invention can realize single-stage AC/DC conversion, realize the functions of charging electric vehicles from the grid, generating electric vehicles to the grid, and participating in grid reactive power regulation. It has single-stage power conversion, simple circuit topology, electrical isolation, high efficiency, High power density, DC port adapts to the characteristics of wide operating voltage range. Description of the drawings [0011] FIG. 1 is a structural diagram of the converter. [0012] FIG. 2 is an example of a single-phase multi-transformer circuit topology of the converter. [0013] FIG. 3 is an example of a three-phase multi-transformer circuit topology of the converter. [0014] FIG. 4 is an example of the six-phase multi-transformer circuit topology of the converter. [0015] FIG. 5 is the circuit topology of the three-phase dual-transformer circuit of the converter. [0016] FIG. 6 shows two equivalent circuits of the variable structure switch group of the converter. [0017] FIG. 7 shows the switch drive waveforms, transformer inductor current, and key node voltage waveforms. [0018] FIG. 8 is an equivalent circuit diagram of the high-frequency switching process in the working process of the converter. Specific implementation mode: [0019] The technical solutions of the present invention will be further described in detail below through specific examples in conjunction with the accompanying drawings. [0020] A DAB type single-stage bidirectional AC/DC converter with low voltage stress and wide output range is composed of an m-phase AC filter, an m-phase cycloconverter, a high-frequency transformer connected in series with n primary sides, and n full bridges. The circuit, DC filter, and variable structure switch group are sequentially cascaded; among them, the secondary side of each transformer is connected to a full-bridge circuit via leakage inductance, n full-bridge circuit output terminals are connected in parallel, and cycle converters, n high Frequency transformer and n full bridge circuits form n groups of dual active bridge structures. The converter adopts a current outer loop power inner loop control strategy, and can work in rectification and inverter modes to realize bidirectional AC/DC conversion, as well as DC side current and AC side power factor control. Figures 2 to 5 are respectively a single-phase multi-transformer circuit topology example, a three-phase multi-transformer circuit topology example, a six-phase multi-transformer circuit topology example, and a single-phase dual-transformer circuit topology example of the converter. Take the single-phase dual-transformer circuit topology as an example, v is a single-phase voltage source, Lac CacIs a single-phase LC filter, $1-$4, Gong'64'Is the power switch of the single-phase cycloconverter, Q "Q8It is the power switch of the full bridge circuit, TrT2Is a high frequency transformer, lrl2They are ", 12Leakage inductance, Co is the DC filter capacitor, VDCIt is a DC power supply. [0021] The converter changes the series and parallel structure of each high-frequency bidirectional full-bridge rectifier through a variable structure switch group, which can not only realize a wide range of output voltage adjustment, but also realize voltage division and shunting, and reduce system design capacity. Series selector switch fly] closed, parallel selector switch SS1nAnd SS2PWhen disconnected, the output terminals of the two high-frequency bidirectional full-bridge rectifiers are connected in series, the equivalent circuit is shown in Figure 6 (a); the series selection switch SS1Disconnect, parallel selector switch SS1nAnd SS2PWhen closed, the output terminals of the two high-frequency bidirectional full-bridge rectifiers are connected in parallel, and the equivalent circuit is shown in Figure 6 (b). [0022] Taking the rectification mode and the parallel connection of the DAB DC side as an example, using dual phase shift control, the AC side bridge arm midpoint voltage is ahead of the DC side bridge arm midpoint voltage, so as to realize energy transmission from the AC side to the DC side. Figure 7 shows the switch drive waveforms, transformer inductor current and key node voltage waveforms. [0023] The converter includes 6 working modes in one high-frequency switching cycle, and the equivalent circuit is shown in Figure 8 (a)-(f). [0024] Mode 1 (0&lt;t&lt;t]): AC side current is expressed as S2, S2', T1, T2, S3, S3'Is the path, the secondary side of the transformer passes through Q2, Q3、 Q6«7 transfers energy to the DC side, the action time is D · Ts, and the inductance current increment is: [0025] iLk i = T-*D*TS - L1 [0026] Mode 2: When t=J, S], S]', S', S,' are closed, S?, S?', S3, S3' are off, VpN is reversed, k, changes from negative Positive. The action time is (0.5-2D) · Ts, the inductance current increment is: [0027] iLk_2 = + *(°-5 -2D) * 3 [0028] Mode 3 (t2&lt;t&lt;t3): When t = t?, Q3«7 is off, and 4«8 is on. The DC side current passes through, 2«4"6«8 and the transformer secondary winding to form a loop. The acting time is D · Ts, and the inductance current increment is: kVDC - Vc [0029] kk_3=TOne [0030] Mode 4 (t3&lt;t&lt;t/: when t=t3, Q2 and Q6 are turned off, and SrS5 is turned on. The DC side current flows through the secondary winding and Qr Q4, Q5, and Q8 transmit electric energy to the load. The acting time is D · Ts, and the inductance current increment is: kVDC + vc [0031] iLk4 =-- »D^T3 [0032] Mode 5 (t4&lt;t&lt;t5): t = t, when $2, $2', $3, and $3' are closed, $1, $1', $4, and $4' are off, ah"1^In reverse, £1 and £2 change from positive to negative. The AC side current is consistent with mode 1. The action time is (0.5-2D) · Ts, the inductance current increment is: [0033] iLk_s = * *(05-2D) * 3 [0034] Mode 6 (t5&lt;t&lt;t6): When t = t§, Q4 and Qg are off, and Q3 and Q7 are on. The DC side current passes through 5«3«5«7 and the secondary side of the transformer to form a freewheeling loop. The acting time is D · Ts, and the inductance current increment is: [0035] μ = thatch-3 Ts [0036] [0037] When t=t6, Q] and Q5 are turned off, Q2 and Q6 are turned on, and then the circuit returns to mode 1 and enters the next switching cycle. According to the volt-second balance of the inductance: [0038] 4D [0039] -4D kVDC Get it [0040] [0041] kVDC D=--- 4(1+boat KVWhen the DC circuit is in the negative half-wave of the input power frequency voltage, the working mode is similar to the positive half-wave. It only needs to exchange SrSi', S4, SJ and $2, $2', $3, $3' switch phase can realize the inverter mode of the converter. [0042] The above-mentioned embodiments are only preferred embodiments of the present invention, and the present invention and its embodiments should not be limited thereto. Therefore, all changes made in accordance with the shape and principle of the present invention should be covered by the present invention. Within the scope of protection.
[EN WO2021159219A1]: THREE-PHASE MULTILEVEL ELECTRIC POWER CONVERTER [FR WO2021159219A1]: CONVERTISSEUR D'ÉNERGIE ÉLECTRIQUE MULTI-NIVEAU TRIPHASÉ | [EN WO2021159219A1]: A power converter for transforming electrical power between direct current (DC) power and alternating current (AC) power is provided, as well as a controller therefor and associated methods and systems. The power converter comprises: a first set of packed U-cell converters connectable between a first common connection point and a first terminal of an external circuit, the first common connection point connecting to a first terminal of a DC circuit element; a second set of packed U-cell converters connectable between a second common connection point and a second, opposite terminal of the external circuit, the second common connection point connecting to a second, opposite terminal of the DC circuit element; and a controller configured for controlling the operation of the first and second sets of packed U-cell converters. [FR WO2021159219A1]: L'invention concerne un convertisseur d'énergie permettant de transformer une énergie électrique entre une alimentation en courant continu (CC) et une alimentation en courant alternatif (CA), ainsi que son dispositif de commande et des systèmes et procédés associés. Le convertisseur d'énergie comprend : un premier ensemble de convertisseurs de cellules en U conditionnés pouvant être connectés entre un premier point de connexion commun et une première borne d'un circuit externe, le premier point de connexion commun se connectant à une première borne d'un élément de circuit CC ; un second ensemble de convertisseurs de cellules en U conditionnés pouvant être connectés entre un second point de connexion commun et une seconde borne opposée du circuit externe, le second point de connexion commun se connectant à une seconde borne opposée de l'élément de circuit CC ; et un dispositif de commande configuré pour commander le fonctionnement des premier et second ensembles de convertisseurs de cellules en U conditionnés. | WO2021159219A1 | 2021-08-19 | CA2021050161W | 2021-02-15 | US202062976952P, 2020-02-14 | WO2021159219A1: 2021-08-19 | ECOLE TECHNOLOGIE SUPERIEURE | ARAZM SAEED AL-HADDAD KAMAL | H02M7/44: I | H02M7/483: I H02M7/4833: I H02M7/4835: I | WO2019204935A1 WO2017152181A1 |  | [EN WO2021159219A1]: CLAIMS: 1. A power converter for transforming electrical power between direct current (DC) power and alternating current (AC) power, comprising: a first set of packed U-cell converters connectable between a first common connection point and a first terminal of an external circuit, the first common connection point connecting to a first terminal of a DC circuit element; a second set of packed U-cell converters connectable between a second common connection point and a second, opposite terminal of the external circuit, the second common connection point connecting to a second, opposite terminal of the DC circuit element; and a controller configured for controlling operation of the first and second sets of packed U-cell converters. 2. The power converter of claim 1, wherein the first and second sets of packed U-cell converters each comprise three packed U-cell converters, and wherein, when the external circuit is a three-phase load and the DC circuit element is a DC source, the controller is configured for controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three-phase load. 3. The power converter of claim 2, wherein the controller controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three-phase load comprises causing the first and second sets of packed U-cell converters to operate with at least one redundant state to produce the AC power, wherein the AC power has 2n + 1 phase voltage levels, where n is the number of capacitors in each packed U-cell converter. 4. The power converter of claim 2, wherein the controller controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three-phase load comprises causing the first and second sets of packed U-cell converters to operate in a plurality of non-redundant states to produce the AC power, wherein the AC power has 2(n+1) - 1 phase voltage levels where n is the number of capacitors in each packed U-cell converter. 5. The power converter of claim 1, wherein the first and second sets of packed U-cell converters each comprise three packed U-cell converters, and wherein, when the external circuit is a three-phase AC source and the DC circuit element is a load, the controller is configured for controlling the operation of the first and second sets of packed U-cell converters to transform AC power produced by the three-phase AC source into DC power delivered to the load. 6. The power converter of any one of claims 1 to 5, wherein each packed U- cell converter of the first and second set of packed U-cell converters comprises: a half-bridge connecting to a first terminal of the packed U-cell converter, the half-bridge comprising a first pair of switches and a first capacitor coupled therebetween; and a switching cell coupled to the half-bridge and connecting to a second terminal of the packed U-cell converter, the switching cell comprising first and second branches comprising respective first and second groups of switches, and at least one flying capacitor connecting the first and second branches. 7. The power converter of claim 6, wherein the switching cell is extendible to including a plurality of flying capacitors connecting the first and second branches, each flying capacitor coupled to the first and second branches between respective pairs of switches of the first and second groups of switches. 8. The power converter of any one of claims 1 to 7, wherein the controller comprises: a pulse-width modulator configured for obtaining a modulation index and at least one carrier signal and for producing a plurality of voltage levels; and a voltage balancer coupled to the pulse-width modulator and configured for receiving the plurality of voltage levels and for controlling the operation of the first and second sets of packed U-cell converters based thereon. 9. The power converter of claim 8, wherein the voltage balancer is further configured for controlling the operation of the first and second sets of packed U-cell converters to produce positive-polarity current across the first and second terminals of the external circuit. 10. The power converter of claim 1, wherein the first set of packed U-cell converters comprises a first collection of submodules and wherein the second set of packed U-cell converters comprises a second collection of submodules, each submodule of the first and second collections comprising a packed U-cell converter, and wherein the controller being configured for controlling the operation of the first and second sets of packed U-cell converters comprises the controller being configured for controlling operation of the first and second collections of submodules. 11. The power converter of claim 10, wherein the first and second collection of submodules each comprise a plurality of parallel branches each comprising at least one submodule arranged in series. 12. The power converter of claim 10 or 11, wherein the controller being configured for controlling the first and second collections of submodules comprises determining an amount of energy stored in capacitors of the submodules of the first and second collections of submodules and controlling the operation of the first and second collections of submodules based on the amount of energy. 13. The power converter of claim 12, wherein the controller is further configured for determining a direction of current flow through at least one of the first and the second collections of submodules, wherein controlling the operation of the first and second collections of submodules is further based on the direction of current flow. 14. The power converter of claim 13, wherein determining a direction of current flow through at least one of the first and the second collections of submodules comprises sorting the capacitors of the submodules based on a stored energy value for the capacitors. 15. A controller for an electrical power converter for transforming electrical power between direct current (DC) power and alternating current (AC) power, comprising: a pulse-width modulator configured for obtaining a modulation index and at least one carrier signal; and producing a plurality of voltage levels based on the modulation index and the at least one carrier signal; and a voltage balancer coupled to the pulse-width modulator and configured for: obtaining the plurality of voltage levels from the pulse-width modulator; and controlling charging states of capacitors of first and second sets of packed U-cell converters of the electrical power converter based on the plurality of voltage level to operate the electrical power converter. 16. The controller of claim 15, wherein the voltage balancer is further configured for controlling operation of the first and second sets of packed U-cell converters to cause the electrical power converter to produce positive-polarity current. 17. The controller of claim 15 or 16, wherein the voltage balancer being configured for controlling the charging states of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter comprises controlling the capacitors to operate with at least one redundant state. 18. The controller of claim 15 or 16, wherein the voltage balancer being configured for controlling the charging states of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter comprises controlling the capacitors to operate in a plurality of non-redundant states. 19. The controller of any one of claims 15 to 18, further comprising a plurality of sensors for measuring actual voltage levels of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter. 20. The controller of any one of claims 15 to 19, wherein the pulse-width modulator is a phase-shift pulse-width modulator. | [EN WO2021159219A1]: THREE-PHASE MULTILEVEL ELECTRIC POWER CONVERTER TECHNICAL FIELD [0001] The present disclosure relates generally to the field of power electronic converters, and more particularly to multilevel power converters. BACKGROUND [0002] Voltage source inverters (VSIs) have become a dominant power electronics converter in various industrial applications. VSIs are used in a number of applications, including multilevel converters, which can offer improved power quality and voltage stress reduction. In particular, modular multilevel converters (MMCs) have been used in industry due to ease of repair and maintenance, since damaged modules can easily be fixed or replaced. [0003] A traditional MMC design is composed of multiple sub-modules, which typically rely on two-level converters of various types. However, many existing MMC designs are limited in their applicability, require components having high tolerances, or produce outputs which are of limited fidelity. In some cases, achieving higher quality output waveforms requires the number of submodules in the design to be increased. This in turn can result in higher power losses, lower reliability, higher complexity in voltage balancing, increased sensors and component complexity. [0004] As a result, improvements are needed. SUMMARY [0005] In accordance with a broad aspect, there is provided a power converter for transforming electrical power between direct current (DC) power and alternating current (AC) power. The power converter comprises: a first set of packed U-cell converters connectable between a first common connection point and a first terminal of an external circuit, the first common connection point connecting to a first terminal of a DC circuit element; a second set of packed U-cell converters connectable between a second common connection point and a second, opposite terminal of the external circuit, the second common connection point connecting to a second, opposite terminal of the DC circuit element; and a controller configured for controlling the operation of the first and second sets of packed U-cell converters. [0006] In at least some embodiments according to any one or more of the previous embodiments, the first and second sets of packed U-cell converters each comprise three packed U-cell converters, and wherein, when the external circuit is a three-phase load and the DC circuit element is a DC source, the controller is configured for controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three- phase load. [0007] In at least some embodiments according to any one or more of the previous embodiments, the controller controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three-phase load comprises causing the first and second sets of packed U-cell converters to operate with at least one redundant state to produce the AC power, wherein the AC power has 2n + 1 phase voltage levels, where n is the number of flying capacitors in each packed U-cell converter. [0008] In at least some embodiments according to any one or more of the previous embodiments, the controller controlling the operation of the first and second sets of packed U-cell converters to transform DC power produced by the DC source into AC power delivered to the three-phase load comprises causing the first and second sets of packed U-cell converters to operate in a plurality of non-redundant states to produce the AC power, wherein the AC power has 2(n+1) - 1 phase voltage levels, where n is the number flying capacitors in each packed U-cell [0009] In at least some embodiments according to any one or more of the previous embodiments, the first and second sets of packed U-cell converters each comprise three packed U-cell converters, and wherein, when the external circuit is a three-phase AC source and the DC circuit element is a load, the controller is configured for controlling the operation of the first and second sets of packed U-cell converters to transform AC power produced by the three-phase AC source into DC power delivered to the load. [0010] In at least some embodiments according to any one or more of the previous embodiments, each packed U-cell converter of the first and second set of packed U-cell converters comprises: a half-bridge connecting to a first terminal of the packed U-cell converter, the half-bridge comprising a first pair of switches and a first capacitor coupled therebetween; and a switching cell coupled to the half-bridge and connecting to a second terminal of the packed U-cell converter, the switching cell comprising first and second branches comprising respective first and second groups of switches, and at least one flying capacitor connecting the first and second branches. [0011] In at least some embodiments according to any one or more of the previous embodiments, the switching cell is extendible to including a plurality of flying capacitors connecting the first and second branches, each flying capacitor coupled to the first and second branches between respective pairs of switches of the first and second groups of switches. [0012] In at least some embodiments according to any one or more of the previous embodiments, the controller comprises: a pulse-width modulator configured for obtaining a modulation index and at least one carrier signal and for producing a plurality of voltage levels; and a voltage balancer coupled to the pulse-width modulator and configured for receiving the plurality of voltage levels and for controlling the operation of the first and second sets of packed U-cell converters based thereon [0013] In at least some embodiments according to any one or more of the previous embodiments, the voltage balancer is further configured for controlling the operation of the first and second sets of packed U-cell converters to produce positive-polarity current across the first and second terminals of the external circuit. [0014] In at least some embodiments according to any one or more of the previous embodiments, the first set of packed U-cell converters comprises a first collection of submodules and wherein the second set of packed U-cell converters comprises a second collection of submodules, each submodule of the first and second collections comprising a packed U-cell converter, and wherein the controller being configured for controlling the operation of the first and second sets of packed U-cell converters comprises the controller being configured for controlling operation of the first and second collections of submodules. [0015] In at least some embodiments according to any one or more of the previous embodiments, the first and second collection of submodules each comprise a plurality of parallel branches each comprising at least one submodule arranged in series. [0016] In at least some embodiments according to any one or more of the previous embodiments, the controller being configured for controlling the first and second collections of submodules comprises determining an amount of energy stored in capacitors of the submodules of the first and second collections of submodules and controlling the operation of the first and second collections of submodules based on the amount of energy. [0017] In at least some embodiments according to any one or more of the previous embodiments, the controller is further configured for determining a direction of current flow through at least one of the first and the second collections of submodules, wherein controlling the operation of the first and second collections of submodules is further based on the direction of current flow. [0018] In at least some embodiments according to any one or more of the previous embodiments, determining a direction of current flow through at least one of the first and the second collections of submodules comprises sorting the capacitors of the submodules based on a stored energy value for the capacitors. [0019] In accordance with another broad aspect, there is provided a controller for an electrical power converter for transforming electrical power between direct current (DC) power and alternating current (AC) power. The controller comprises a pulse-width modulator and a voltage balancer coupled to the pulse-width modulator. The pulse- width modulator is configured for: obtaining a modulation index and at least one carrier signal; and producing a plurality of voltage levels based on the modulation index and the at least one carrier signal. The voltage balancer is configured for: obtaining the plurality of voltage levels from the pulse-width modulator; and controlling charging states of capacitors of first and second sets of packed U-cell converters of the electrical power converter based on the plurality of voltage level to operate the electrical power converter. [0020] In at least some embodiments according to any one or more of the previous embodiments, the voltage balancer is further configured for controlling operation of the first and second sets of packed U-cell converters to cause the electrical power converter to produce positive-polarity current. [0021] In at least some embodiments according to any one or more of the previous embodiments, the voltage balancer being configured for controlling the charging states of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter comprises controlling the capacitors to operate with at least one redundant state. [0022] In at least some embodiments according to any one or more of the previous embodiments, the voltage balancer being configured for controlling the charging states of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter comprises controlling the capacitors to operate in a plurality of non- redundant states. [0023] In at least some embodiments according to any one or more of the previous embodiments, the controller further comprises a plurality of sensors for measuring actual voltage levels of the capacitors of the first and second sets of packed U-cell converters of the electrical power converter. [0024] In at least some embodiments according to any one or more of the previous embodiments, the pulse-width modulator is a phase-shift pulse-width modulator. [0025] Features of the systems, devices, and methods described herein may be used in various combinations, in accordance with the embodiments described herein. BRIEF DESCRIPTION OF THE DRAWINGS [0026] Further features and advantages of the present invention will become apparent from the following detailed description, taken in combination with the appended drawings, in which: [0027] FIGs. 1A-B illustrate example packed U-cell converter topologies; [0028] FIG. 2 illustrates an example three-phase converter topology connected to a three-phase load; [0029] FIG. 3 illustrates an example grid-connected three-phase converter topology; [0030] FIG. 4A illustrates a block diagram of an example control system for the three- phase converter topology of FIGs. 2 and/or 3; [0031] FIG. 4B illustrates example carrier signals and reference voltage values for use by the control system of FIG. 4A; [0032] FIGs. 5 and 6 are flowcharts for example methods of controlling the three-phase converter topology of FIGs. 2 and/or 3; [0033] FIG. 7 illustrates an example modular three-phase converter topology; [0034] FIG. 8 is a flowchart of an example method of controlling the modular three- phase of FIG. 7; [0035] FIG. 9A-C illustrate example simulation results for outputs of the converter topologies of FIGs. 2, 3, and 7. [0036] It will be noted that throughout the appended drawings, like features are identified by like reference numerals. DETAILED DESCRIPTION [0037] With reference to FIG. 1A, there is illustrated a voltage source inverter (VSI), termed a packed U-cell converter (PUC) 100. The PUC 100 is connectable to other circuit elements via an input terminal 102 and an output terminal 104. It should be noted that, although the terms “input terminal” and “output terminal” are used for terminals 102, 104, the PUC 100 can be configured to permit the flow of current in any suitable fashion between terminals 102, 104. As will be described in greater detail hereinbelow, the PUC 100 can be used both as a rectifier and as an inverter, and has applications in a number of power converter configurations and systems. For example, the PUC 100 can be provided with a source of direct current (DC), and be used to produce an alternating current (AC). In another example, the PUC 100 is provided with an AC source, and produces a DC output. [0038] It should be noted that the embodiment of the PUC 100 is a variant different from what may be considered a “standard” PUC; in particular, a standard PUC may operate with one (or more) voltage sources. However, the PUC 100 illustrated in FIG. 1A is instead provided with a capacitor to replace the voltage source. In the foregoing discussion, it is considered that the various PUCs used may be similarly modified, that is to say, to replace the voltage source that may be present in a standard PUC with a capacitor. Cases where the PUCs are not varied are also considered. [0039] The PUC 100 is composed of a half-bridge 110 and a switching cell 120. The half-bridge 110 is connected to the input terminal 102, and is composed of a pair of switches S1 and S2 and a capacitor C1 coupled between the switches S1, S2. The input terminal 102 connects at a point intermediate the switches S1, S2. The switching cell 130 is composed of a pair of branches 122, 124 which both connect to the output terminal 104. The branch 122 is composed of switches S3, S5, and branch 124 is composed of switches S4, S6. A capacitor C2 is connected between the branches 122, 124. The output terminal 104 connects at a point intermediate the switches S5, S6, i.e. where the branches 122, 124 connect again. [0040] Various modes of operation for the PUC 100 are considered. In some embodiments, the PUC 100 generates 5 different voltage levels with redundant switching states. When a load is placed across the terminals 102, 104, the 5 different voltage levels can be used to produce a 9-level waveform. In some other embodiments, the PUC 100 generates 7 different voltage levels using a more complex control approach, without redundant states. [0041] In some embodiments, switches S1, S2 which compose the half-bridge inverter 110 have a switching frequency less than a switching frequency of switches S3 to S6 of the switching cell 120. For example, the switches S1, S2 operate at the fundamental frequency of the alternating current to be produced by or provided to the PUC 100 (e.g., 50 Hz, 60 Hz), and the switches S3 to S6 operate at a frequency several orders of magnitude above the fundamental frequency (e.g., 1 kHz or more). In some embodiments, a rated voltage value for switches S3 to S6 of the switching cell 130 is lower than a rated voltage value for switches S1, S2 which compose the half-bridge inverter 110. Other embodiments are also considered. [0042] It should also be noted that the switching cell 120 is extensible. With additional reference to FIG. 1B, an alternative embodiment of the PUC 100 is illustrated at 105. The PUC 105 is provided with a switching cell 130 having branches 132, 134. The branches 132, 134 include additional switches S7, Se, and the switching cell 130 includes an additional capacitor C3. The additional switches S7, Se and capacitor C3 form an additional switching unit 136 composing the switching cell 130, and enable the PUC 105 to generate additional voltage levels. For example, the PUC 105 can generate 9 different voltage levels with redundant switching states, or 15 voltage levels with no redundancy. If a further additional switching unit 136 is added to the PUC 105, 17 different voltage levels can be generated with redundant switching states, and 31 voltage levels with no redundancy. PUCs having any suitable number of switching units 136 are considered. In general, a PUC (such as the PUCs 100 and 150) can be used to produce 2n + 1 phase voltage levels when operated with redundant states, and to produce 2n+1 - 1 phase voltage levels when operated without redundant states, where n is the number of capacitors in each PUC. [0043] With reference to FIG. 2, a three-phase converter topology 200 (referred to herein as a “double-star topology”) is illustrated as being connected to an external circuit, for instance a three-phase load 220. The double-star topology 200 is composed of two sets of converters 204 and 206. The converters 204 and 206 can each be embodied as one of the PUCs 100, one of the PUCs 105, or as a generic PUC 150, which can have any number of switching units within a switching cell 152. Disposed between the two sets of converters is a DC circuit element, in this case a DC source 202. [0044] The converters 204 and 206 each have two connection ports, corresponding to the ports 102, 104. The converters 204 are arranged such that one port for each of the converters 204 is coupled to a common coupling point 203 with the DC source 202, and the other port for each of the converters 204 couples to respective coupling points with one of the converters 206, and with one phase of the three-phase load 220. The converters 206 are similarly arranged, with one port for each of the converters being coupled to a common coupling point 205 with the DC source 202, and the other port for each of the converters 206 being coupled to the respective one of the converters 204 via the aforementioned coupling points. [0045] It should be noted that the nomenclature “double-star topology” is used to describe the converter topology 200 in FIG. 2 because the arrangement of the converters 204 and 206, and their connections to the three-phase load 220, somewhat resembles a three-pointed star. This nomenclature does not imply, and should not be interpreted as implying, however, that the particular physical connections linking the converters 204 and 206 to the three-phase load 202 needs necessarily be star-shaped. Rather, any suitably-shaped connection between the converters 204 and 206 and the three-phase load 202 are considered, so long as the connections couple the aforementioned components as illustrated in FIG. 2. [0046] With reference to FIG. 3, the double-star topology 200 can also be used for connection to different types of external circuits, for instance a grid 230, which as illustrated in FIG. 3 is a three-phase grid, and which can be used to provide DC power to a DC circuit element (illustrated at 302). The connections between the converters 204 and 206 with the three-phase load 220 of FIG. 2 are substituted for connections to the grid 230. It should be noted that the configurations presented in FIGs. 2 and 3 are example configurations, and that others are also considered. [0047] The converters 204, indicated as M1a, M1b, M1c, and the converters 206, indicated as M2a, M2b and M2c, form three-phase arms in two parallel branches. The converters 204 and 206 can be operated as PUC5, PUC7, PUC9, PUC15, or any other suitable PUC level, depending on the required voltage levels for each application. In some embodiments, the PUCs 100, 105, and/or 150 are modified to replace a DC source found therein with a flying capacitor. [0048] With continued reference to FIG. 1A, Table 1 hereinbelow presents switching states for the PUC 100, Table 2 hereinbelow presents charging states for the capacitors C1 and C2, and Table 3 hereinbelow presents how selection of different capacitor charging states is performed. [0049] In Table 1, if VC1=2VC2, the PUC 100 shown of FIG. 1 will generate five voltage levels. If VC1= 3VC2, the PUC 100 produces seven voltage levels. When the PUC 100 is generating seven voltage levels, the PUC 100 does not provide any redundant states, which can complicate the control scheme for the PUC 100. The use of PUC 100 in a mode generating five voltage levels — or the use of the PUC 105 in a mode generating nine voltage levels — can reduce the need for dedicated control systems. [0050] Table II shows the relation between the current flow and charge and discharge of the flying capacitors C1 and C2 of the PUC 100. IL is illustrated in FIG. 1A as the current leaving the output terminal 104 . For instance, it is observed from the FIG. 1A that when II is positive, the capacitor C1 is charged, and C2 is excluded from the current flow. [0051] Table 3 is based on Table 2, in which suitable states in redundant states are selected in terms of current direction and conditions of charging and discharging of the flying capacitors C1 and C2. In states 1 and 8 that generate voltage +2E and -2E, there is no redundancy and consequently selections of them are inevitable. In states 4 and 5, the capacitors are excluded from the current flow, and thus no selection is required. Flence, states 2 and 3, as well as states 6 and 7, are used to generate the voltages E and -E, and thus the states to balance the voltages in C1 and C2. As illustrated in Table 2, for situations where IL&gt;0, C1 is charged and C2 is discharged during state 2; during state 3, C2 is charged and the charge state of C1 does not change.. [0052] With continued reference to FIG. 1B, the additional switching unit 136 enables the PUC 105 to provide nine voltage levels with redundancy or fifteen (15) voltage levels without redundancy. Table 4 hereinbelow presents switching states for the PUC 150 in the nine-level configuration, in which the capacitors C1, C2, and C3 are tuned such that VC1 = 2 · VC2 = 4 · VC3 = 4 · E. [0053] The difference between each module of PUC shown in Fig. 1, 2 that is used in proposed topology and conventional one is that the capacitor C1 is replaced by DC source. [0054] Table 5 hereinbelow presents charging states for the capacitors C1, C2, and C3 of the PUC 105, and Table 6 hereinbelow presents how selection of different capacitor charging states is performed. [0055] A voltage balancing approach for the PUC 105 of FIG. 1B, having two capacitors and a DC source, is explained in detail in “Nine-Level Packed U-Cell (PUC9) Inverter Topology with Single-DC-Source and Effective Voltage Balancing of Auxiliary Capacitors” by S. Arazm, H. Vahedi, and K. Al-Haddad, published in 2019 IEEE 28th International Symposium on Industrial Electronics (ISIE), 2019, pp. 944-949, the contents of which is hereby incorporated by reference. [0056] Put briefly, the voltages of the capacitors C1, C2, and C3 must be normalized based on E to be equal for suitable comparison. Thus, the following equations are considered: [0057] In equations (1) to (3), it is considered that the reference voltage for the PUCs is equal to 4 E, and that the values for and are measured via sensors in the capacitors C1, C2, and C3. Referring again to Table 6, the selection of states is based on the direction of current flow within the PUC 105, and on a comparison among the normalized voltages of the capacitors C1, C2, and C3. As indicated in Table 5, States 1 and 16 do not effect charging or discharging of the capacitors C1, C2, and C3. Additionally, States 8 and 9, which produce a voltage level of -4E and +4E, respectively, are not redundant states. The conditions for voltage balancing in the remaining 12 states is shown in Table 6. Based on Table 6, an approach for simplifying the voltage balancing for the PUC 150, for instance for use with the double-star topology 200, can be devised. As mentioned hereinabove, the approach is described in more detail in in “Nine-Level Packed U-Cell (PUC9) Inverter Topology with Single-DC-Source and Effective Voltage Balancing of Auxiliary Capacitors”. [0058] With reference to FIG. 4, a control system 400 for the double-star topology 200 is illustrated. The control system 400 is composed of a pulse-width modulator (PWM) 410 and a voltage balancer 420. In some embodiments, the PWM 410 can be a phase-shift pulse-width modulator (PS-PWM). The PWM 410 receives a modulation index and carrier signals and generates a plurality of voltage levels indicative of the voltages to be produced by the PUCs 150 of the double-star topology 200. The voltage balancer 420 then uses the voltage levels provided by the PWM 410 and implements an algorithm, detailed in Table 6, to control the operation of the PUCs 150. It should be noted that in some other embodiments, the PS-PWM 410 can be replaced by a space-vector modulator, or by a level-shift PWM (LS-PWM). [0059] In order to account for the three-phase nature of the double-star topology 200, additional modifications to the control system for voltage balancing of the PUCs 150 can be made. For instance, because the PUCs 150 will experience bipolar circulating current, the habitual voltage balancing approach may not allow the capacitors C1, C2, and C3 to charge and discharge in the usual fashion. In some embodiments, the voltage balancing approach can be modified to restrict the use of the states presented in Table 6 to those states which generate positive-polarity current, from the perspective of the terminals 102, 104. Although this modified approach can result in a reduced number of voltage levels producible by each of the PUCs 150, it can also eliminate the need for a DC fault circuit breaker to account for those states which generate negative-polarity current. [0060] With continued reference to FIG. 4, the PUCs 150 can be illustrated via a single- line diagram, as shown in FIG. 4. It should be understood that the configuration illustrated at element 150 in FIG. 4 represents the same PUC configuration as the PUC 150 in FIGs. 2 and 3, but with simplified circuit elements to facilitate the explanation. The current provided to a load 154 comes from left and right branches of the PUC 150, and can be expressed as: where ix is the current to the load 154, iL is the current from the left branch of the PUC 150, and iR is the current from the right branch of the PUC 150. The voltage provided to the load 154, termed here Vdiff, can be determined by Vdiff = VL - VR - 2Vdc (5) where VL is the voltage across the left branch of the PUC 150, VR is the voltage across the right branch of the PUC 150, and the voltage provided by the source is 2Vdc. [0061] From equation (5), it can be deduced that, to reduce the current circulating in each states subtraction of voltages in left and right side should be equal or close to the DC link voltage. If high levels of current are permitted to circulate through the left and right branches of the PUC 150, unstable operation of the PUC 150 can occur. A switching methodology for controlling the PUC 150 in the double-star configuration 200 is shown below in Table 7. [0062] Table 7 shows the all output voltages produced by the PUC 150 with one module in two sides for one phase of the double-star topology 200. Of note, Vdiff is zero in a number of states, which results in a minimum amount of current circulating through the PUC 150. With additional reference to Table 1 , states 100, 101 , 110, 111 , 000 generate voltage +2E, +E, 0. Accordingly, it can be seen from Table 7 that Vdiff is zero on states 6, 9, 10, 11 , 12 and 19 where both left and right modules has been set on positive mentioned polarity. As a result, this modified voltage balancing approach uses those states with positive-polarity current; states with negative-polarity current are used for disconnecting the converter in DC fault short circuit current. In some embodiments, these considerations are also applied to modular PUCs. [0063] In one example, and with reference to FIG. 4B, to generate five phase-voltage levels and nine line-voltage levels at the output of a multilevel embodiment of the PUC 150 with one DC source, three reference voltages, illustrated by sinusoidal curves 452, and four carrier signals, illustrated by zigzag lines 454, are produced to initiate the switching devices. As illustrated in FIG. 4B, the carriers CrL1 and CrL2 are related to the left side module and CrR1 , CrR2 are the carriers for right side module. Reference voltages Vref-a, Vref-b and Vref-c are the modulating signals. The values presented in Tables 8, 9, and 10 indicate the switching methodology used for the PUCs 150 within the double-star topology 200, both in three-phase and when used as part of a modular converter, when the PUCs 150 correspond to the PUCs 100 of FIG. 1A. In particular, Table 8 indicates the switching states for the PUCs 100, Table 9 indicates the charging or discharging state for the capacitors, and Table 10 indicates the state selection methodology. [0064] With reference to FIG. 5, methods 500 and 550 for controlling and balancing the voltage of the PUCs 150 are illustrated via flowcharts. The method 500 is used for voltage balancing for the right branch of the PUCs 150, and the method 550 is used for voltage balancing for the left branch. The methods 500 and 550 apply when the PUCs 150 correspond to PUCs 100 of FIG. 1A. [0065] Considering first the method 500, the method starts at 502. At 510, an evaluation is made regarding whether the reference voltage is greater than the carrier voltages. If yes, the switches of state 1 (from Table 9) are activated, as per step 512. If no, the method 500 proceeds to step 520. [0066] At step 520, an evaluation is made regarding whether the reference voltage is greater than the carrier voltage CrR1 and less than the carrier voltage CrR2, or whether the reference voltage is less than the carrier voltage CrR1 and greater than the carrier voltage CrR2. If yes, the switches of state 2 or 3 are activated, in accordance with Table 10, as per step 522. If no, the method 500 proceeds to step 530. [0067] At step 530, an evaluation is made regarding whether the reference voltage is less than the carrier voltages. If yes, the switches of state 4 (from Table 9) are activated, as per step 532. The method then ends at step 504. [0068] In the method 550, the method starts at 552. At 560, an evaluation is made regarding whether the reference voltage is greater than the carrier voltages. If yes, the switches of state 4 (from Table 9) are activated, as per step 562. If no, the method 550 proceeds to step 570. [0069] At step 570, an evaluation is made regarding whether the reference voltage is greater than the carrier voltage CrL1 and less than the carrier voltage CrR2, or whether the reference voltage is less than the carrier voltage CrL1 and greater than the carrier voltage CrL2. If yes, the switches of state 2 or 3 are activated, in accordance with Table 10, as per step 572. If no, the method 500 proceeds to step 580. [0070] At step 580, an evaluation is made regarding whether the reference voltage is less than the carrier voltages. If yes, the switches of state 1 (from Table 9) are activated, as per step 582. The method then ends at step 554. [0071] Although, according to Table 8, each of the PUCs 150 generates three voltage levels, the control algorithm proposed in FIG. 5 produces five voltage levels at the output of each phase, and consequently nine voltage levels at the line voltage. The methods 500, 550 are based on phase shift modulation techniques. [0072] With additional reference to FIG. 6, similar methods 600 and 650 can be used for PUCs 150 which correspond to the PUCs 105 of FIG. 1B. The values presented in Tables 11, 12, and 13 indicate the switching methodology used for the PUCs 150 within the double-star topology 200, both in three-phase and when used as part of a modular converter, when the PUCs 150 correspond to the PUCs 105 of FIG. 1B. In particular, Table 11 indicates the switching states for the PUCs 105, Table 12 indicates the charging or discharging state for the capacitors, and Table 13 indicates the state selection methodology. [0073] Considering first the method 600, the method starts at 602. At step 610, an evaluation is made regarding whether the reference voltage is greater than the four carrier voltages. If yes, the switches of state 1 (from Table 12) are activated, as per step 612. If no, the method 600 proceeds to step 616. [0074] At step 616, an evaluation is made regarding whether the reference voltage i
[JA JP2020156163A]: マルチレベル電力変換装置 [EN JP2020156163A]: MULTI-LEVEL POWER CONVERSION DEVICE | [JA JP2020156163A]: 【課題】フライングキャパシタを含んだ回路を有しているマルチレベル電力変換装置において、配線インダクタンスに起因してスイッチングデバイスのターンオフ時に発生するサージ電圧を抑制することにより、スイッチングデバイスの破損を抑制し、装置の信頼性を向上させる。【解決手段】第１半導体スイッチＳａには、第１スナバコンデンサＣ１，第１スナバダイオードＤｓ１，第１抵抗Ｒ１を有したスナバ回路を設ける。第２半導体スイッチＳｂには、第２スナバコンデンサＣ２，第２スナバダイオードＤｓ２，第２抵抗Ｒ２を有したスナバ回路を設ける。第３半導体スイッチＳａには、第３スナバコンデンサＣ３，第３スナバダイオードＤｓ３，第３抵抗Ｒ３を有したスナバ回路を設ける。第４半導体スイッチＳｄには、第４スナバコンデンサＣ４，第４スナバダイオードＤｓ４，第４抵抗Ｒ４を有したスナバ回路を設ける。【選択図】図１ [EN JP2020156163A]: To suppress damage of a switching device and improve reliability of the device by suppressing a surge voltage generated at a switching device turn-off due to wiring inductance in a multi-level power conversion device having a circuit including a flying capacitor.SOLUTION: A first semiconductor switch Sa is provided with a snubber circuit having a first snubber capacitor C1, a first snubber diode Ds1, and a first resistor R1. A second semiconductor switch Sb is provided with a snubber circuit having a second snubber capacitor C2, a second snubber diode Ds2, and a second resistor R2. A third semiconductor switch Sa is provided with a snubber circuit having a third snubber capacitor C3, a third snubber diode Ds3, and a third resistor R3. A fourth semiconductor switch Sd is provided with a snubber circuit having a fourth snubber capacitor C4, a fourth snubber diode Ds4, and a fourth resistor R4.SELECTED DRAWING: Figure 1 | JP2020156163A | 2020-09-24 | JP2019050594A | 2019-03-19 | JP2019050594A, 2019-03-19 | JP2020156163A: 2020-09-24 | MEIDENSHA ELECTRIC MFG CO LTD | HASEGAWA ISAMU | H02M7/483: I H02M7/48: I |  |  |  | [JA JP2020156163A]: 直列接続された第1,第2直流リンクキャパシタと、 第1~第4半導体スイッチが当該第1~第4の順に直列接続された半導体直列回路と、 第1~第4スナバコンデンサが当該第1~第4の順に直列接続されたコンデンサ直列回路と、 第1,第2スナバコンデンサの両者間に挿入接続された第1スナバダイオードと、 第2,第3スナバコンデンサの両者間に挿入接続された第2,第3スナバダイオードの直列回路と、 第3,第4スナバコンデンサの両者間に挿入接続された第4スナバダイオードと、を備え、 半導体直列回路の一端側に位置する第1半導体スイッチの一端が、第1直流リンクキャパシタの正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチの一端が、第2直流リンクキャパシタの負極端に接続され、 コンデンサ直列回路の一端側に位置する第1スナバコンデンサの一端が、第1直流リンクキャパシタの正極端と第1半導体スイッチとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサの一端が、第2直流リンクキャパシタの負極端と第4半導体スイッチとの共通接続点に接続され、 第1スナバダイオードは、アノードが第1スナバコンデンサに接続され、カソードが第1,第2半導体スイッチの共通接続点に接続され、 第2スナバダイオードは、アノードが第2スナバコンデンサに接続され、カソードが第2,第3半導体スイッチの共通接続点に接続され、 第3スナバダイオードは、アノードが第2,第3半導体スイッチの共通接続点に接続され、カソードが、第3スナバコンデンサに接続され、 第4スナバダイオードは、アノードが第3,第4半導体スイッチの共通接続点に接続され、カソードが第4スナバコンデンサに接続され、 フライングキャパシタの正極端が、第2スナバコンデンサと第1スナバダイオードとの共通接続点に接続され、当該フライングキャパシタの負極端が、第3スナバコンデンサと第4スナバダイオードとの共通接続点に接続され、 第1スナバコンデンサと第1スナバダイオードとの共通接続点に、第1抵抗の一端が接続され、当該第1抵抗の他端が、第1,第2直流リンクキャパシタの共通接続点に接続され、 第2スナバコンデンサと第2スナバダイオードとの共通接続点に、第2抵抗の一端が接続され、当該第2抵抗の他端が、フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に接続され、 第3スナバコンデンサと第3スナバダイオードとの共通接続点に、第3抵抗の一端が接続され、当該第3抵抗R3の他端が、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、 第4スナバコンデンサと第4スナバダイオードとの共通接続点に、第4抵抗の一端が接続され、当該第4抵抗の他端が、第1,第2直流リンクキャパシタの共通接続点に接続されている、 ことを特徴とするマルチレベル電力変換装置。 直流リンクキャパシタと、 第1~第4半導体スイッチが当該第1~第4の順に直列接続された半導体直列回路と、 第1~第4スナバコンデンサが当該第1~第4の順に直列接続されたコンデンサ直列回路と、 第1,第2スナバコンデンサの両者間に挿入接続された第1スナバダイオードと、 第2,第3スナバコンデンサの両者間に挿入接続された第2,第3スナバダイオードの直列回路と、 第3,第4スナバコンデンサの両者間に挿入接続された第4スナバダイオードと、を備え、 半導体直列回路の一端側に位置する第1半導体スイッチの一端が、直流リンクキャパシタの正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチの一端が、直流リンクキャパシタの負極端に接続され、 コンデンサ直列回路の一端側に位置する第1スナバコンデンサの一端が、直流リンクキャパシタの正極端と第1半導体スイッチとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサの一端が、直流リンクキャパシタの負極端と第4半導体スイッチとの共通接続点に接続され、 第1スナバダイオードは、アノードが第1スナバコンデンサに接続され、カソードが第1,第2半導体スイッチの共通接続点に接続され、 第2スナバダイオードは、アノードが第2スナバコンデンサに接続され、カソードが第2,第3半導体スイッチの共通接続点に接続され、 第3スナバダイオードは、アノードが第2,第3半導体スイッチの共通接続点に接続され、カソードが第3スナバコンデンサに接続され、 第4スナバダイオードは、アノードが第3,第4半導体スイッチの共通接続点に接続され、カソードが第4スナバコンデンサに接続され、 フライングキャパシタの正極端が、第2スナバコンデンサと第1スナバダイオードとの共通接続点に接続され、フライングキャパシタの負極端が、第3スナバコンデンサと第4スナバダイオードとの共通接続点に接続され、 第1スナバコンデンサと第1スナバダイオードとの共通接続点に、第1抵抗の一端が接続され、当該第1抵抗の他端が、直流リンクキャパシタの負極端と第4スナバコンデンサとの共通接続点に接続され、 第2スナバコンデンサと第2スナバダイオードとの共通接続点に、第2抵抗の一端が接続され、当該第2抵抗の他端が、フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に接続され、 第3スナバコンデンサと第3スナバダイオードとの共通接続点に、第3抵抗の一端が接続され、当該第3抵抗の他端が、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、 第4スナバコンデンサと第4スナバダイオードとの共通接続点に、第4抵抗の一端が接続され、当該第1抵抗の他端が、直流リンクキャパシタの正極端と第1スナバコンデンサとの共通接続点に接続されている、 ことを特徴とするマルチレベル電力変換装置。 第1スナバコンデンサ,第1スナバダイオード,第1抵抗の共通接続点に、第1アバランシェ素子のアノードが接続され、当該第1アバランシェ素子のカソードが、直流リンクキャパシタの正極端と第1スナバコンデンサとの共通接続点に接続され、 第2スナバコンデンサ,第2スナバダイオード,第2抵抗の共通接続点に、第2アバランシェ素子のアノードが接続され、当該第2アバランシェ素子のカソードが、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、 フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に、第3アバランシェ素子のアノードが接続され、当該第3アバランシェ素子のカソードが、第3スナバコンデンサ,第3スナバダイオード,第3抵抗の共通接続点に接続され、 直流リンクキャパシタの負極端と第4スナバコンデンサとの共通接続点に、第4アバランシェ素子のアノードが接続され、当該第4アバランシェ素子のカソードが、第4スナバコンデンサ,第4スナバダイオード,第4抵抗の共通接続点に接続されている、 ことを特徴とする請求項2記載のマルチレベル電力変換装置。 [EN JP2020156163A]: the [ the 1st and 2nd direct-current link capacitor by which series connection was carried out, and ] -- the 1~4th solid state switch -- the [ concerned ] -- a semiconductor series circuit by which series connection was carried out to the 4th order of 1~, the -- the 1~4th snubber capacitor -- the [ concerned ] -- a capacitor series circuit by which series connection was carried out to the 4th order of 1~, The 1st snubber diode by which insertion connection was made among both of the 1st and 2nd snubber capacitor, A series circuit of the 2nd and 3rd snubber diode by which insertion connection was made among both of the 2nd and 3rd snubber capacitor, The 4th snubber diode by which insertion connection was made among both of the 3rd and 4th snubber capacitor, An end of the 1st solid state switch located in the one end side of a preparation and a semiconductor series circuit, It is connected to an anode end of the 1st direct-current link capacitor, and an end of the 4th solid state switch located in the other end side of the semiconductor series circuit concerned, It is connected to a cathode end of the 2nd direct-current link capacitor, and an end of the 1st snubber capacitor located in the one end side of a capacitor series circuit, It is connected to a point of a right extreme of the 1st direct-current link capacitor, and the 1st solid state switch connecting [ common ], An end of the 4th snubber capacitor located in the other end side of the capacitor series circuit concerned is connected to a point of a cathode end of the 2nd direct-current link capacitor, and the 4th solid state switch connecting [ common ], and it is the 1st snubber diode, an anode is connected to the 1st snubber capacitor and a cathode is connected to a point of the 1st and 2nd solid state switch connecting [ common ] -- the 2nd snubber diode, An anode is connected to the 2nd snubber capacitor, a cathode is connected to a point of the 2nd and 3rd solid state switch connecting [ common ], and it is the 3rd snubber diode, an anode is connected to a point of the 2nd and 3rd solid state switch connecting [ common ], and a cathode is connected to the 3rd snubber capacitor -- the 4th snubber diode, An anode is connected to a point of the 3rd and 4th solid state switch connecting [ common ], and a cathode is connected to the 4th snubber capacitor, An anode end of a premature start capacitor is connected to a point of the 2nd snubber capacitor and the 1st snubber diode connecting [ common ], A cathode end of the premature start capacitor concerned is connected to a point of the 3rd snubber capacitor and the 4th snubber diode connecting [ common ], An end of the 1st resistance is connected to a point of the 1st snubber capacitor and the 1st snubber diode connecting [ common ], The other end of the 1st resistance concerned is connected to a point of the 1st and 2nd direct-current link capacitor connecting [ common ], one end of the 2nd resistance is connected to a point of the 2nd snubber capacitor and the 2nd snubber diode connecting [ common ], and the other end of the 2nd resistance concerned, It is connected to a point of a cathode end of a premature start capacitor, the 3rd snubber capacitor, and the 4th snubber diode connecting [ common ], An end of the 3rd resistance is connected to a point of the 3rd snubber capacitor and the 3rd snubber diode connecting [ common ], The other end of the 3rd resistance R3 concerned is connected to a point of a right extreme of a premature start capacitor, the 2nd snubber capacitor, and the 1st snubber diode connecting [ common ], one end of the 4th resistance is connected to a point of the 4th snubber capacitor and the 4th snubber diode connecting [ common ], and the other end of the 4th resistance concerned is connected to it at a point of the 1st and 2nd direct-current link capacitor connecting [ common ] -- a multilevel power converter characterized by things. the [ a direct-current link capacitor and ] -- the 1~4th solid state switch -- the [ concerned ] -- a semiconductor series circuit by which series connection was carried out to the 4th order of 1~, the -- the 1~4th snubber capacitor -- the [ concerned ] -- a capacitor series circuit by which series connection was carried out to the 4th order of 1~, The 1st snubber diode by which insertion connection was made among both of the 1st and 2nd snubber capacitor, A series circuit of the 2nd and 3rd snubber diode by which insertion connection was made among both of the 2nd and 3rd snubber capacitor, The 4th snubber diode by which insertion connection was made among both of the 3rd and 4th snubber capacitor, An end of the 1st solid state switch located in the one end side of a preparation and a semiconductor series circuit, It is connected to an anode end of a direct-current link capacitor, and an end of the 4th solid state switch located in the other end side of the semiconductor series circuit concerned, it is connected to a cathode end of a direct-current link capacitor -- an end of the 1st snubber capacitor located in the one end side of a capacitor series circuit, It is connected to a point of a right extreme of a direct-current link capacitor, and the 1st solid state switch connecting [ common ], and an end of the 4th snubber capacitor located in the other end side of the capacitor series circuit concerned is connected to a point of a cathode end of a direct-current link capacitor, and the 4th solid state switch connecting [ common ], as for the 1st snubber diode, an anode is connected to the 1st snubber capacitor and a cathode is connected to a point of the 1st and 2nd solid state switch connecting [ common ] -- the 2nd snubber diode, An anode is connected to the 2nd snubber capacitor, a cathode is connected to a point of the 2nd and 3rd solid state switch connecting [ common ], and it is the 3rd snubber diode, an anode is connected to a point of the 2nd and 3rd solid state switch connecting [ common ], and a cathode is connected to the 3rd snubber capacitor -- the 4th snubber diode, An anode is connected to a point of the 3rd and 4th solid state switch connecting [ common ], and a cathode is connected to the 4th snubber capacitor, An anode end of a premature start capacitor is connected to a point of the 2nd snubber capacitor and the 1st snubber diode connecting [ common ], A cathode end of a premature start capacitor is connected to a point of the 3rd snubber capacitor and the 4th snubber diode connecting [ common ], An end of the 1st resistance is connected to a point of the 1st snubber capacitor and the 1st snubber diode connecting [ common ], The other end of the 1st resistance concerned is connected to a point of a cathode end of a direct-current link capacitor, and the 4th snubber capacitor connecting [ common ], one end of the 2nd resistance is connected to a point of the 2nd snubber capacitor and the 2nd snubber diode connecting [ common ], and the other end of the 2nd resistance concerned, It is connected to a point of a cathode end of a premature start capacitor, the 3rd snubber capacitor, and the 4th snubber diode connecting [ common ], An end of the 3rd resistance is connected to a point of the 3rd snubber capacitor and the 3rd snubber diode connecting [ common ], The other end of the 3rd resistance concerned is connected to a point of a right extreme of a premature start capacitor, the 2nd snubber capacitor, and the 1st snubber diode connecting [ common ], one end of the 4th resistance is connected to a point of the 4th snubber capacitor and the 4th snubber diode connecting [ common ], and the other end of the 1st resistance concerned is connected to it at a point of a right extreme of a direct-current link capacitor, and the 1st snubber capacitor connecting [ common ] -- a multilevel power converter characterized by things. At the 1st snubber capacitor, the 1st snubber diode, and a point of the 1st resistance connecting [ common ], An anode of the 1st avalanche element is connected and a cathode of the 1st avalanche element concerned, It is connected to a point of a right extreme of a direct-current link capacitor, and the 1st snubber capacitor connecting [ common ], At the 2nd snubber capacitor, the 2nd snubber diode, and a point of the 2nd resistance connecting [ common ], An anode of the 2nd avalanche element is connected and a cathode of the 2nd avalanche element concerned, It is connected to a point of a right extreme of a premature start capacitor, the 2nd snubber capacitor, and the 1st snubber diode connecting [ common ], At a point of a cathode end of a premature start capacitor, the 3rd snubber capacitor, and the 4th snubber diode connecting [ common ], An anode of the 3rd avalanche element is connected and a cathode of the 3rd avalanche element concerned, It is connected to the 3rd snubber capacitor, the 3rd snubber diode, and a point of the 3rd resistance connecting [ common ], An anode of the 4th avalanche element is connected to a point of a cathode end of a direct-current link capacitor, and the 4th snubber capacitor connecting [ common ], and a cathode of the 4th avalanche element concerned is connected to it at the 4th snubber capacitor, the 4th snubber diode, and a point of the 4th resistance connecting [ common ], The multilevel power converter according to claim 2 characterized by things. | [JA JP2020156163A]: 本発明は、 多相のマルチレベル電力変換装置に係り、特に、マルチレベル電力変換装置に備えられたスナバ回路に関する。 種々の分野で適用されている電力変換装置において、例えば、使用する半導体スイッチング素子等の耐圧を高耐圧化せずに回路自体の高圧化を図った構成としては、半導体スイッチング素子を多数直列に接続したマルチレベル電力変換装置が検討されている。 従来のマルチレベル電力変換装置としては、例えば図4に示すように、複数の相モジュール2と1つの共通モジュール1より構成された5レベル電力変換装置が挙げられる。図4の共通モジュール1は、直列接続された2つの基本セルCell1,Cell2を有し、各基本セルCell1,Cell2は4つの半導体スイッチ(IGBT)とフライングキャパシタにより構成されている。 図4の5レベル電力変換装置が3相の場合は、3台の相モジュール2が共通モジュール1の出力に並列接続される。この構成は、特許文献1に開示されている。なお、図4の第1,第2ダイオードD1,D2は第9,第10スイッチングデバイスS9,S10(IGBT)に置き換えてもよい。この場合、第9スイッチングデバイスS9のコレクタ端子を第3スイッチングデバイスS3と第4スイッチングデバイスS4との共通接続点に接続し、第10スイッチングデバイスS10のエミッタ端子を第5スイッチングデバイスS5と第6スイッチングデバイスS6との共通接続点に接続する。さらに、図4内の各半導体スイッチ,スイッチングデバイス(またはダイオード)は、複数の半導体スイッチ,スイッチングデバイス(またはダイオード)を直列接続または並列接続する構成としてもよい。 基本セルCell1,Cell2は、図5に示すような二種類のスイッチングパターン(MODE1,MODE2)を有する。電流経路に応じて2種類のスイッチングパターン(MODE1,MODE2)を選択することで第1,第2フライングキャパシタFC1,FC2の充電または放電を選択し、第1,第2フライングキャパシタFC1,FC2の電圧を制御することができる。ここで、図5中(および後述の各図中)の丸印は、導通中の半導体スイッチ,スイッチングデバイスを示す。 IGBTにはオン状態からオフ状態に移行するまでに時間がかかることから基本セルCell1,Cell2の2つのMODE(スイッチングパターン)の移行時には一度すべての半導体スイッチをオフしてからもう一つのスイッチングパターンに移行する必要がある。このすべての半導体スイッチがオフの状態(図5(a))をデッドタイムと呼ぶ。デッドタイムはフライングキャパシタの直流短絡を防ぐために設ける。 基本セルCell1,Cell2が相モジュール2を介して交流出力端子に電流を流していると、デッドタイム中に半導体スイッチ,スイッチングデバイスに並列接続されているダイオードが導通して電流が流れる現象が起きる。これを転流と定義する。この転流現象により、図6(b)のような過電圧(2E)が第1スイッチングデバイスS1に印加される問題が発生する。 第1,第2直流リンクキャパシタCDC1,CDC2を2Eの電圧に制御し、第1,第2フライングキャパシタFC1,FC2をEの電圧に制御すると、転流現象が起きていないときには共通モジュール1と相モジュール2を接続する接点の電位は、図6(a)に示すように常に2E,E,0,-E,-2Eに保たれる(電位の基準点はNP端子(第1,第2直流リンクキャパシタCDC1,CDC2の共通接続点)とする)。 ここで、図6(b)に示すように、第2半導体スイッチSf2と第4半導体スイッチSf4のダイオードに電流が流れる転流現象が発生すると、第2半導体スイッチSf2→第4半導体スイッチSf4→第2スイッチングデバイスS2→第3スイッチングデバイスS3→第4スイッチングデバイスS4→交流出力端子を介して電流が流れる。その結果、共通モジュール1の出力電位が2E,0,0,-E,-2Eとなり、第1スイッチングデバイスS1に2Eが印加されてしまう。 同様に上下対称の回路構成であることから、図7に示すように第8スイッチングデバイスS8に2Eが印加される現象も起きる。第1,第8スイッチングデバイスS1,S8に2Eが印加されることにより、以下の(1),(2)の問題が生じる。 (1)第1,第8スイッチングデバイスS1,S8に過電圧が印加されるため、第1,第8スイッチングデバイスS1,S8が過電圧損傷等を引き起こすおそれがある。これにより、5レベル電力変換装置の信頼性が低下する可能性がある。 (2)交流出力端子の電位が+Eまたは-Eのときに上記の基本セルCell1,Cell2のスイッチングパターンが移行する場合、交流出力端子の電位が不変(+Eまたは-E)であることが望ましい。しかし、図6(b)に示す転流期間中、交流出力端子の電位は0となる。これにより、電力変換装置の出力電圧の精度が劣化する可能性がある。 そこで、上記(1),(2)の問題点を解消するために、マルチレベル電力変換装置にスナバ回路を設けた構成が検討されている。図8にスナバ回路を設けた5レベル電力変換装置の構成例を示す。図8中の破線は電流経路を表す。 図8に示すようにスナバ回路として第3,第4半導体スイッチSf3,Sf4の共通接続点と第2半導体スイッチSf2の一端(つまりNP端子)との間、および、第5半導体スイッチSf5の一端(つまりNP端子)と第7,第8半導体スイッチSf7,Sf8の共通接続点の間に、第1,第2スナバコンデンサCf1、Cf2を接続する。 これにより、共通モジュール1のデッドタイム時においても電流は第1,第2スナバコンデンサCf1、Cf2を通るようになる。これは第1スナバコンデンサCf1が充電されている場合、第1スナバコンデンサCf1の上側の端子の電位はNP端子の電位よりも高くなるので、第2半導体スイッチSf2と第4半導体スイッチSf4のダイオードが導通しなくなるためである。したがって、図6、図7のような過電圧現象を抑制することができる。 また、第1,第2スナバコンデンサCf1、Cf2の電圧は第1,第2フライングキャパシタFC1,FC2と接続することで一定に保つことができる。 図9に第1スナバコンデンサCf1の電圧の充電・放電方法を示す。第2,第3半導体スイッチSf2,Sf3をオンし、第1スナバコンデンサCf1を第1フライングキャパシタFC1と接続することで、第1フライングキャパシタFC1と同じ電圧に制御可能である。第2スナバコンデンサCf2の充電・放電方法も同様である。 基本セルCell,Cell2の2種類のスイッチングパターン(MODE1,MODE2)のいずれにおいても、第1スナバコンデンサCf1の上側の端子の電位は+E,第2スナバコンデンサCf2の下側の端子の電位は-Eに保たれている。5レベル電力変換装置の運転中、基本セルCell1,Cell2はデッドタイム期間を除く大半の期間において上記2種類のスイッチングパターン(MODE1,MODE2)のいずれかを選択しているため、第1,第2スナバコンデンサCf1,Cf2の静電容量を第1,第2フライングキャパシタFC1,FC2よりも十分小さくすることで、第1,第2スナバコンデンサCf1、Cf2の電圧を+Eまたは-Eに制御することが可能である。 特開2015-47056号公報 図8に示したような回路構成(以下、単に従来構成と適宜称する)では共通モジュール1の転流時に生じる過電圧を防ぐことはできるが、特定経路(例えば第1直流リンクキャパシタCDC1の正極側、および、第2直流リンクキャパシタCDC2の負極側の経路)上の配線インダクタンスに起因するサージ電圧を防ぐことはできない。 また、従来構成のスナバ回路は、主に相モジュール2を想定(例えば第1スイッチングデバイスS1等が電流iをターンオフした際に発生し得るサージ電圧L*di/dtを想定)したものとなっている。 そこで、フライングキャパシタを含んだ回路(例えば、共通モジュール1の各Cell1,Cell2)においても、スナバ回路を適用して、配線インダクタンスに起因してスイッチングデバイスのターンオフ時に発生するサージ電圧を抑制することが考えられるが、具体的な構成については出現していない。 以上示したようなことから、マルチレベル電力変換装置において、配線インダクタンスに起因してスイッチングデバイスのターンオフ時に発生し得るサージ電圧を抑制することにより、スイッチングデバイスの破損を抑制し、装置の信頼性を向上させることが課題となる。 本発明は、前記従来の問題に鑑み、案出されたもので、その一態様は、直列接続された第1,第2直流リンクキャパシタと、第1~第4半導体スイッチが当該第1~第4の順に直列接続された半導体直列回路と、第1~第4スナバコンデンサが当該第1~第4の順に直列接続されたコンデンサ直列回路と、第1,第2スナバコンデンサの両者間に挿入接続された第1スナバダイオードと、第2,第3スナバコンデンサの両者間に挿入接続された第2,第3スナバダイオードの直列回路と、第3,第4スナバコンデンサの両者間に挿入接続された第4スナバダイオードと、を備えたマルチレベル電力変換装置である。 当該一態様によるマルチレベル電力変換装置では、半導体直列回路の一端側に位置する第1半導体スイッチの一端が、第1直流リンクキャパシタの正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチの一端が、第2直流リンクキャパシタの負極端に接続されている また、コンデンサ直列回路の一端側に位置する第1スナバコンデンサの一端が、第1直流リンクキャパシタの正極端と第1半導体スイッチとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサの一端が、第2直流リンクキャパシタの負極端と第4半導体スイッチとの共通接続点に接続されている。 また、第1スナバダイオードは、アノードが第1スナバコンデンサに接続され、カソードが第1,第2半導体スイッチの共通接続点に接続され、第2スナバダイオードは、アノードが第2スナバコンデンサに接続され、カソードが第2,第3半導体スイッチの共通接続点に接続され、第3スナバダイオードは、アノードが第2,第3半導体スイッチの共通接続点に接続され、カソードが第3スナバコンデンサに接続され、第4スナバダイオードは、アノードが第3,第4半導体スイッチの共通接続点に接続され、カソードが第4スナバコンデンサに接続されている。 また、フライングキャパシタの正極端が、第2スナバコンデンサと第1スナバダイオードとの共通接続点に接続され、当該フライングキャパシタの負極端が、第3スナバコンデンサと第4スナバダイオードとの共通接続点に接続されている。 そして、第1スナバコンデンサと第1スナバダイオードとの共通接続点に、第1抵抗の一端が接続され、当該第1抵抗の他端が、第1,第2直流リンクキャパシタの共通接続点に接続され、第2スナバコンデンサと第2スナバダイオードとの共通接続点に、第2抵抗の一端が接続され、当該第2抵抗の他端が、フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に接続され、第3スナバコンデンサと第3スナバダイオードとの共通接続点に、第3抵抗の一端が接続され、当該第3抵抗R3の他端が、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、第4スナバコンデンサと第4スナバダイオードとの共通接続点に、第4抵抗の一端が接続され、当該第4抵抗の他端が、第1,第2直流リンクキャパシタの共通接続点に接続されている、ことを特徴とするものである。 他の態様においては、直流リンクキャパシタと、第1~第4半導体スイッチが当該第1~第4の順に直列接続された半導体直列回路と、第1~第4スナバコンデンサが当該第1~第4の順に直列接続されたコンデンサ直列回路と、第1,第2スナバコンデンサの両者間に挿入接続された第1スナバダイオードと、第2,第3スナバコンデンサの両者間に挿入接続された第2,第3スナバダイオードの直列回路と、第3,第4スナバコンデンサの両者間に挿入接続された第4スナバダイオードと、を備えたマルチレベル電力変換装置である。 当該他の態様によるマルチレベル電力変換装置では、半導体直列回路の一端側に位置する第1半導体スイッチの一端が、直流リンクキャパシタの正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチの一端が、直流リンクキャパシタの負極端に接続されている。 また、コンデンサ直列回路の一端側に位置する第1スナバコンデンサの一端が、直流リンクキャパシタの正極端と第1半導体スイッチとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサの一端が、直流リンクキャパシタの負極端と第4半導体スイッチとの共通接続点に接続されている。 また、第1スナバダイオードは、アノードが第1スナバコンデンサに接続され、カソードが第1,第2半導体スイッチの共通接続点に接続され、第2スナバダイオードは、アノードが第2スナバコンデンサに接続され、カソードが第2,第3半導体スイッチの共通接続点に接続され、第3スナバダイオードは、アノードが第2,第3半導体スイッチの共通接続点に接続され、カソードが第3スナバコンデンサに接続され、第4スナバダイオードは、アノードが第3,第4半導体スイッチの共通接続点に接続され、カソードが第4スナバコンデンサに接続されている。 また、フライングキャパシタの正極端が、第2スナバコンデンサと第1スナバダイオードとの共通接続点に接続され、フライングキャパシタの負極端が、第3スナバコンデンサと第4スナバダイオードとの共通接続点に接続されている。 そして、第1スナバコンデンサと第1スナバダイオードとの共通接続点に、第1抵抗の一端が接続され、当該第1抵抗の他端が、直流リンクキャパシタの負極端と第4スナバコンデンサとの共通接続点に接続され、第2スナバコンデンサと第2スナバダイオードとの共通接続点に、第2抵抗の一端が接続され、当該第2抵抗の他端が、フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に接続され、第3スナバコンデンサと第3スナバダイオードとの共通接続点に、第3抵抗の一端が接続され、当該第3抵抗の他端が、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、第4スナバコンデンサと第4スナバダイオードとの共通接続点に、第4抵抗の一端が接続され、当該第1抵抗の他端が、直流リンクキャパシタの正極端と第1スナバコンデンサとの共通接続点に接続されている、ことを特徴とするものである。 他の態様においては、第1スナバコンデンサ,第1スナバダイオード,第1抵抗の共通接続点に、第1アバランシェ素子のアノードが接続され、当該第1アバランシェ素子のカソードが、直流リンクキャパシタの正極端と第1スナバコンデンサとの共通接続点に接続され、第2スナバコンデンサ,第2スナバダイオード,第2抵抗の共通接続点に、第2アバランシェ素子のアノードが接続され、当該第2アバランシェ素子のカソードが、フライングキャパシタの正極端,第2スナバコンデンサ,第1スナバダイオードの共通接続点に接続され、フライングキャパシタの負極端,第3スナバコンデンサ,第4スナバダイオードの共通接続点に、第3アバランシェ素子のアノードが接続され、当該第3アバランシェ素子のカソードが、第3スナバコンデンサ,第3スナバダイオード,第3抵抗の共通接続点に接続され、直流リンクキャパシタの負極端と第4スナバコンデンサとの共通接続点に、第4アバランシェ素子のアノードが接続され、当該第4アバランシェ素子のカソードが、第4スナバコンデンサ,第4スナバダイオード,第4抵抗の共通接続点に接続されている、ことを特徴しても良い。 本発明によれば、マルチレベル電力変換装置において、配線インダクタンスに起因してスイッチングデバイスのターンオフ時に発生し得るサージ電圧を抑制することにより、スイッチングデバイスの破損を抑制し、装置の信頼性の向上に貢献可能となる。 実施例1によるマルチレベル電力変換装置を示す回路構成図。 実施例2によるマルチレベル電力変換装置を示す回路構成図。 実施例3によるマルチレベル電力変換装置を示す回路構成図。 従来のマルチレベル電力変換装置の一例を示す回路構成図。 基本セルのスイッチングパターンを示す図。 出力Eの時の転流現象を示す図。 出力-Eの時の転流現象を示す図。 出力Eの時の転流現象を示す図。 スナバコンデンサの電圧制御例を示す図。 配線インダクタンスに起因するサージ電圧発生を示す図。 参考例1によるマルチレベル電力変換装置を示す回路構成図。 参考例1によるマルチレベル電力変換装置の動作例(放電時)を示す図。 参考例1によるマルチレベル電力変換装置の動作例を示す図。 参考例2によるマルチレベル電力変換装置を示す回路構成図。 参考例2によるマルチレベル電力変換装置のスイッチングパターンを示す図。 参考例2によるマルチレベル電力変換装置の配線インダクタンスに起因するサージ電圧発生を示す図。 本発明の実施形態によるマルチレベル電力変換装置は、フライングキャパシタを含んだ回路を有したものであって、単に従来構成に示すようなスナバ回路を適用するものとは、全く異なるものである。 すなわち、本実施形態によるマルチレベル電力変換装置では、フライングキャパシタを含んだ回路に構成されている各半導体スイッチに対し、スナバコンデンサ,スナバダイオード,抵抗を有したスナバ回路を、それぞれ設けた構成である。 このような構成のスナバ回路を、フライングキャパシタを含んだ回路に適用することにより、単に従来構成のスナバ回路を適用した場合と比較して、配線インダクタンスによる影響を小さくすることができる。 これにより、配線インダクタンスに起因してスイッチングデバイスのターンオフ時に発生し得るサージ電圧を抑制することにより、スイッチングデバイスの破損を抑制し、装置の信頼性の向上に貢献可能となる。 本実施形態のマルチレベル電力変換装置は、前述のようにスナバコンデンサ,スナバダイオード,抵抗を有したスナバ回路を、フライングキャパシタを含んだ回路に適用した構成であれば良く、種々の分野(例えばマルチレベル電力変換装置技術,スナバ回路技術,フライングキャパシタ技術等の分野)の技術常識を適宜適用して設計することが可能であり、その一例として後述の実施例1~3が挙げられる。 なお、図4~図10に示すものと同様のものには同一符号を付する等により、その詳細な説明を適宜省略する。 ≪参考例1≫ まず、図8に示した従来構成に着目すると、以下に示すことが言える。図8の従来構成の場合、共通モジュール1の転流時に生じる過電圧を防ぐことはできるが、特定経路(第1直流リンクキャパシタCDC1の正極側、および、第2直流リンクキャパシタCDC2の負極側の経路)上の配線インダクタンスに起因するサージ電圧を防ぐことはできない。 図10にその例を示す。図10中の破線の丸で囲んだ半導体スイッチ,スイッチングデバイスは導通している。また、図10の電流経路に配線インダクタンスLが存在する。よって、相モジュール2の第1スイッチングデバイスS1が電流iをターンオフした際に配線インダクタンスLのインダクタンス値Lに比例したサージ電圧L*di/dtが第1スイッチングデバイスS1に発生する。 このとき、第1スイッチングデバイスS1に印加される電圧は、第1,第2直流リンクキャパシタCDC1,CDC2の電圧合計値が2E,第1,第2フライングキャパシタFC1,FC2の電圧合計値がEとすると、E+Ldi/dtとなる。インダクタンス値Lが大きい場合、第1スイッチングデバイスS1の印加電圧が大きくなるため第1スイッチングデバイスS1の過電圧破損につながる可能性があった。 そこで、例えば図11に示すようにマルチレベル電力変換装置を構成することが考えられる。図11では、各相共通の共通モジュール1と、1相以上の相モジュール2と、各相共通のスナバ回路3と、を備え、直流-交流変換、または、交流-直流変換を行えるように構成されている。なお、図1では、簡略化して相モジュール2を1相分のみ示している。 共通モジュール1は、直列接続された第1,第2直流リンクキャパシタCDC1,CDC2を有している。第1直流リンクキャパシタCDC1の正極端には、第1半導体スイッチSf1の一端が接続されている。第1直流リンクキャパシタCDC1の負極端には、第2半導体スイッチSf2の一端が接続されている。第1半導体スイッチSf1の他端と第2半導体スイッチSf2の他端との間には、第1フライングキャパシタFC1が接続されている。 第1半導体スイッチSf1と第1フライングキャパシタFC1の共通接続点と第2半導体スイッチSf2と第1フライングキャパシタFC1の共通接続点との間には、第3,第4半導体スイッチSf3,Sf4が直列接続されている。 第2直流リンクキャパシタCDC2の正極端には、第5半導体スイッチSf5の一端が接続されている。第2直流リンクキャパシタCDC2の負極端には、第6半導体スイッチSf6の一端が接続されている。第5半導体スイッチSf5の他端と第6半導体スイッチSf6の他端との間には、第2フライングキャパシタFC2が接続されている。 第5半導体スイッチSf5と第2フライングキャパシタFC2の共通接続点と第6半導体スイッチSf6と第2フライングキャパシタFC2の共通接続点との間には、第7,第8半導体スイッチSf7,Sf8が直列接続されている。 相モジュール2は、第1半導体スイッチSf1の一端と第3,第4半導体スイッチSf3,Sf4の共通接続点との間には、第1,第2スイッチングデバイスS1,S2が直列接続されている。 第7,第8半導体スイッチSf7,Sf8の共通接続点と第6半導体スイッチSf6の一端との間には、第7,第8スイッチングデバイスS7,S8が直列接続されている。第1,第2スイッチングデバイスS1,S2の共通接続点と、第7,第8スイッチングデバイスS7,S8の共通接続点との間には、第3,第4,第5,第6スイッチングデバイスS3,S4,S5,S6が直列接続されている。 前記第3,第4スイッチングデバイスS3,S4の共通接続点と第5,第6スイッチングデバイスS5,S6の共通接続点との間には、第1,第2ダイオードD1,D2が直列接続されている。なお、この第1,第2ダイオードD1,D2は、第9,第10スイッチングデバイス(IGBT等)に置き換えても良い。 スナバ回路3は、第1半導体スイッチSf1の一端と第3,第4半導体スイッチSf3,Sf4の共通接続点との間には、第1スナバコンデンサCf1が接続されている。第3,第4半導体スイッチSf3,Sf4の共通接続点と第2半導体スイッチSf2の一端との間には、第2スナバコンデンサCf2が接続されている。 第5半導体スイッチSf5の一端と第7,第8半導体スイッチSf7,Sf8の共通接続点との間には、第3スナバコンデンサCf3が接続されている。第7,第8半導体スイッチSf7,Sf8の共通接続点と第6半導体スイッチSf6の一端との間には、第4スナバコンデンサCf4が接続されている。 また、前記第1~第4スナバコンデンサCf1~Cf4には、第1~第4スナバダイオードDf1~Df4がそれぞれ直列接続されている。 図11の場合、第1スナバダイオードDf1は、アノードが第1スナバコンデンサCf1に接続され、カソードが第3,第4半導体スイッチSf3,Sf4の共通接続点に接続されている。第2スナバダイオードDf2は、アノードが第3,第4半導体スイッチSf3,Sf4の共通接続点に接続され、カソードが第2スナバコンデンサCf2に接続されている。 第3スナバダイオードDf3は、アノードが第3スナバコンデンサCf3に接続され、カソードが第7,第8半導体スイッチSf7,Sf8の共通接続点に接続されている。第4スナバダイオードDf4は、アノードが第7,第8半導体スイッチSf7,Sf8の共通接続点に接続され、カソードが第4スナバコンデンサCf4に接続されている。 前記のように第1~第4スナバコンデンサCf1~Cf4それぞれに第1~第4スナバダイオードDf1~Df4を直列接続したことにより、第1,第2ダイオードDf1,Df2の直列回路、および、第3,第4ダイオードDf3,Df4の直列回路が構成され、当該各直列回路には、第5,第6抵抗Rf5,Rf6がそれぞれ並列接続されている。 図11に示した電力変換装置のスナバ回路3の放電経路は、図12に示すとおりとなる。まず、第1,第2直流リンクキャパシタCDC1,CDC2の電圧合計値2Eよりも第1,第2スナバコンデンサCf1,Cf2の電圧合計値が高くなると、第1,第2スナバコンデンサCf1,Cf2の電圧は第5抵抗Rf5を介して放電される。第3,第4スナバコンデンサCf3,Cf4も同様にして第6抵抗R6で放電される。そして、第1,第2スナバコンデンサCf1,Cf2の電圧合計値が2Eまで低下すると放電動作が終了することとなる。 図13は、第1スイッチングデバイスS1をターンオフした場合の動作例を示すものである。第1スナバコンデンサCf1と第1ダイオードD1,第4スナバコンデンサCf4と第4ダイオードD4を第1,第8スイッチングデバイスS1,S8の一端にも接続することで相モジュール2の第1,第8スイッチングデバイスS1,S8に印加されるサージ電圧Ldi/dtを吸収することができる。 配線インダクタンスLに流れていた電流は、第1スイッチングデバイスS1のターンオフ直後に第1スナバコンデンサCf1→第1スナバダイオードDf1→第3半導体スイッチSf3→第1半導体スイッチSf1を通って流れ続ける。よって、配線インダクタンスLによるサージ電圧Ldi/dt分のエネルギーをスナバコンデンサCf1が吸収するため、第1スイッチングデバイスS1に印加されるサージ電圧を低減することが可能となる。第8スイッチングデバイスS8をターンオフした場合での動作も同様である。 ゆえに、図11に示したような電力変換装置によれば、従来装置と比較して、以下に示すことが言える。すなわち、配線インダクタンスに起因して、スイッチングデバイスのターンオフ時に発生し得るサージ電圧を抑制することができる。これにより、スイッチングデバイスの過電圧破損を低減できるため、電力変換装置の信頼性の向上に貢献可能となる。 ≪参考例2≫ 参考例1に示した電力変換装置において、フライングキャパシタを有した回路部に着目すると、図14に示すような3レベル電力変換装置の構成が挙げられる。 図14の電力変換装置では、一個のフライングキャパシタFCと4つの半導体スイッチSa~Sd(IGBTなど)により1アームが構成されており、直流リンクキャパシタCdcの電圧をVdc,フライングキャパシタFCの電圧をVdc/2に制御して動作する構成となっている。 図14において、第1~第4半導体スイッチSa~Sdは直列接続されており、当該直列一端側に位置する第1半導体スイッチSaの一端が、直流リンクキャパシタCdcの正極端に接続され,当該直列他端側に位置する第4半導体スイッチSdの一端が、直流リンクキャパシタCdcの負極端に接続されている。 第1,第2半導体スイッチSa,Sbの共通接続点と、第3,第4半導体スイッチSc,Sdの共通接続点と、の間にはフライングキャパシタFCが接続されている。第2,第3半導体スイッチSb,Scの共通接続点は、交流出力端子となる。 図14の電力変換装置の場合、第1~第4半導体スイッチSa~Sdを適宜導通させることにより、図15に示すような4種類のスイッチングパターンを適宜選択し、3レベルの電圧を出力することができる。したがって、流れる相電流I1の方向に応じてスイッチングパターンを選択することにより、フライングキャパシタFCの充電または放電を選択し、当該フライングキャパシタFCの電圧を制御することができる。ここで、図15中の「ON」は、導通中の半導体スイッチを示す。 図14の電力変換装置において、参考例1に示したスナバ回路3を単に適用すると、例えば図16に示したような構成となる。 図16の電力変換装置の場合、2つの半導体スイッチに対して1つのスナバ回路が接続されているに等しい構成となっている。すなわち、半導体スイッチSa~Sdごとにはスナバ回路が接続されていないため、例えば2素子分の配線インダクタンス(例えば図16中のL)によるサージ電圧が発生し得る。 例えば図14の経路k1に配線インダクタンスがある場合、第1,第2半導体スイッチSa,Sbのサージ電圧が大きくなり、経路k2に配線インダクタンスがある場合には、第3,第4半導体スイッチSc,Sdのサージ電圧が大きくなり得る。これにより、各半導体スイッチSa~Sdにおいては、素子の耐圧を超えて破損等に至る可能性がある。 ≪実施例1≫ 図1は、実施例1による電力変換装置を示すものであり、参考例1,2等に基づいて見出されたものである。なお、参考例1,2等と同様のものには同一符号を付する等により、その詳細な説明を適宜省略する。 図1の電力変換装置では、半導体スイッチSa~Sdに対し、スナバコンデンサ(C1~C4),スナバダイオード(Ds1~Ds4),抵抗(R1~R4)を有したスナバ回路が、それぞれ設けられた構成となっている。 図1の電力変換装置においては、直列接続された第1,第2直流リンクキャパシタCdc1,Cdc2を有している。また、第1~第4半導体スイッチSa~Sdが当該第1~第4の順に直列接続された直列回路(以下、単に半導体直列回路と適宜称する)を有し、当該半導体直列回路の一端側に位置する第1半導体スイッチSaの一端が、第1直流リンクキャパシタCdc1の正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチSdの一端が、第2直流リンクキャパシタCdc2の負極端に接続されている。 また、第1~第4スナバコンデンサC1~C4が当該第1~第4の順に直列接続された直列回路(以下、単にコンデンサ直列回路と適宜称する)を有しており、当該コンデンサ直列回路の一端側に位置する第1スナバコンデンサC1の一端が、第1直流リンクキャパシタCdc1の正極端と第1半導体スイッチSaとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサC4の一端が、第2直流リンクキャパシタCdc2の負極端と第4半導体スイッチSdとの共通接続点に接続されている。 第1~第4スナバコンデンサC1~C4には、第1~第4スナバダイオードDs1~Ds4がそれぞれ直列接続されている。 具体的には、第1,第2スナバコンデンサC1,C2の両者間に第1スナバダイオードDs1が挿入接続され、第2,第3スナバコンデンサC2,C3の両者間に第2,第3スナバダイオードDs2,Ds3の直列回路が挿入接続され、第3,第4スナバコンデンサC3,C4の両者間に第4スナバダイオードDs4が挿入接続されている。 第1スナバダイオードDs1は、アノードが第1スナバコンデンサC1に接続され、カソードが第1,第2半導体スイッチSa,Sbの共通接続点に接続されている。第2スナバダイオードDs2は、アノードが第2スナバコンデンサC2に接続され、カソードが第2,第3半導体スイッチSb,Scの共通接続点に接続されている。 第3スナバダイオードDs3は、アノードが第2,第3半導体スイッチSb,Scの共通接続点に接続され、カソードが第3スナバコンデンサC3に接続されている。第4スナバダイオードDs4は、アノードが第3,第4半導体スイッチSc,Sdの共通接続点に接続され、カソードが第4スナバコンデンサC4に接続されている。 フライングキャパシタFCの正極端は、第2スナバコンデンサC2と第1スナバダイオードDs1との共通接続点に接続され、フライングキャパシタFCの負極端は、第3スナバコンデンサC3と第4スナバダイオードDs4との共通接続点に接続されている。 第1スナバコンデンサC1と第1スナバダイオードDs1との共通接続点には、第1抵抗R1の一端が接続され、当該第1抵抗R1の他端が、第1,第2直流リンクキャパシタCdc1,Cdc2の共通接続点に接続されている。 第2スナバコンデンサC2と第2スナバダイオードDs2との共通接続点には、第2抵抗R2の一端が接続され、当該第2抵抗R2の他端が、フライングキャパシタFCの負極端,第3スナバコンデンサC3,第4スナバダイオードDs4の共通接続点に接続されている。 第3スナバコンデンサC3と第3スナバダイオードDs3との共通接続点には、第3抵抗R3の一端が接続され、当該第3抵抗R3の他端が、フライングキャパシタFCの正極端,第2スナバコンデンサC2,第1スナバダイオードDs1の共通接続点に接続されている。 第4スナバコンデンサC4と第4スナバダイオードDs4との共通接続点には、第4抵抗R4の一端が接続され、当該第4抵抗R4の他端が、第1,第2直流リンクキャパシタCdc1,Cdc2の共通接続点に接続されている。 図1の電力変換装置において、第1~第4スナバコンデンサC1~C4は、第1,第2直流リンクキャパシタCdc1,Cdc2による電圧Vdcの半分の電圧、またはフライングキャパシタFCの電圧であるVdc/2に充電されることとなる。 そして、第1半導体スイッチSaに印加される電圧がVdc/2の値を超えた場合には、第1スナバダイオードDs1が導通し、第1スナバコンデンサC1に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第1半導体スイッチSaに印加され得るサージ電圧を抑制できる。第1スナバコンデンサC1の電圧は、第1抵抗R1を通して第1直流リンクキャパシタCdc1に放電され、Vdc/2に戻る。 第2半導体スイッチSbに印加される電圧がVdc/2の値を超えた場合には、第2スナバダイオードDs2が導通し、第2スナバコンデンサC2に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第2半導体スイッチSbに印加され得るサージ電圧を抑制できる。第2スナバコンデンサC2の電圧は、第2抵抗R2を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第3半導体スイッチScに印加される電圧がVdc/2の値を超えた場合には、第3スナバダイオードDs3が導通し、第3スナバコンデンサC3に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第3半導体スイッチScに印加され得るサージ電圧を抑制できる。第3スナバコンデンサC3の電圧は、第3抵抗R3を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第4半導体スイッチSdに印加される電圧がVdc/2の値を超えた場合には、第4スナバダイオードDs4が導通し、第4スナバコンデンサC4に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第4半導体スイッチSdに印加され得るサージ電圧を抑制できる。第4スナバコンデンサC4の電圧は、第4抵抗R4を通して第2直流リンクキャパシタCdc2に放電され、Vdc/2に戻る。 以上示したように実施例1によれば、半導体スイッチSa,Sb,Sc,Sdに対してスナバ回路がそれぞれ設けられた構成となっているため、例えば単に従来構成のスナバ回路を適用した場合と比較して、配線インダクタンスによる影響を小さくできることが判る。 ≪実施例2≫ 実施例1の場合、第1~第4スナバコンデンサC1~C4の電圧がVdc/2と低いため、サージ電圧に対して吸収すべきエネルギーが大きくなる。このため、スイッチング周波数が高い場合には、例えば第1,第4抵抗R1,R4で消費する電力が大きくなってしまうおそれがある。これにより、スイッチング損失の増加や抵抗の大型化を招くおそれがある。 そこで、実施例2では、図2に示すように電力変換装置を構成して、第1~第4スナバコンデンサC1~C4の電圧が高くなるようにし、サージ電圧に対して吸収すべきエネルギーを抑制できるようにした。なお、図1に示すものと同様のものには同一符号を付する等により、その詳細な説明を適宜省略する。 図2の電力変換装置においては、第1,第2直流リンクキャパシタCdc1,Cdc2の替わりに直流リンクキャパシタCdcを有し、第1~第4半導体スイッチSa~Sdの半導体直列回路の一端側に位置する第1半導体スイッチSaの一端が、直流リンクキャパシタCdcの正極端に接続され、当該半導体直列回路の他端側に位置する第4半導体スイッチSdの一端が、直流リンクキャパシタCdcの負極端に接続されている。 また、第1~第4スナバコンデンサC1~C4のコンデンサ直列回路の一端側に位置する第1スナバコンデンサC1の一端が、直流リンクキャパシタCdcの正極端と第1半導体スイッチSaとの共通接続点に接続され、当該コンデンサ直列回路の他端側に位置する第4スナバコンデンサC4の一端が、直流リンクキャパシタCdcの負極端と第4半導体スイッチSdとの共通接続点に接続されている。 第1抵抗R1においては、当該第1抵抗R1の一端が、第1スナバコンデンサC1と第1スナバダイオードDs1との共通接続点に接続され、当該第1抵抗R1の他端が、直流リンクキャパシタCdcの負極端と第4スナバコンデンサC4との共通接続点に接続されている。 第4抵抗R4においては、当該第4抵抗R4の一端が、第4スナバコンデンサC4と第4スナバダイオードDs4との共通接続点に接続され、当該第4抵抗R4の他端が、直流リンクキャパシタCdcの正極端と第1スナバコンデンサC1との共通接続点に接続されている。 図2の電力変換装置において、第1,第4スナバコンデンサC1,C4は、直流リンクキャパシタCdcの電圧であるVdcに充電されることとなる。また、第2,第3スナバコンデンサC2,C3は、フライングキャパシタFCの電圧であるVdc/2に充電されることとなる。 そして、第1半導体スイッチSaに印加される電圧がVdcの値を超えた場合には、第1スナバダイオードDs1が導通し、第1スナバコンデンサC1に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第1半導体スイッチSaに印加され得るサージ電圧を抑制できる。第1スナバコンデンサC1の電圧は、第1抵抗R1を通して直流リンクキャパシタCdcに放電され、Vdcに戻る。 第2半導体スイッチSbに印加される電圧がVdc/2の値を超えた場合には、第2スナバダイオードDs2が導通し、第2スナバコンデンサC2に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第2半導体スイッチSbに印加され得るサージ電圧を抑制できる。第2スナバコンデンサC2の電圧は、第2抵抗R2を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第3半導体スイッチScに印加される電圧がVdc/2の値を超えた場合には、第3スナバダイオードDs3が導通し、第3スナバコンデンサC3に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第3半導体スイッチScに印加され得るサージ電圧を抑制できる。第3スナバコンデンサC3の電圧は、第3抵抗R3を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第4半導体スイッチSdに印加される電圧がVdcの値を超えた場合には、第4スナバダイオードDs4が導通し、第4スナバコンデンサC4に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第4半導体スイッチSdに印加され得るサージ電圧を抑制できる。第4スナバコンデンサC4の電圧は、第4抵抗R4を通して直流リンクキャパシタCdcに放電され、Vdcに戻る。 以上示したように実施例2によれば、実施例1と同様の作用効果を奏する他に、以下のことが言える。すなわち、スイッチング損失の低減や、第1,第4抵抗R1,R4の小型化に貢献することが可能となる。 ≪実施例3≫ 実施例2の場合、配線インダクタンスによるサージエネルギーを、第1~第4スナバコンデンサC1~C4で吸収することになる。このため、第1~第4スナバコンデンサにおいて大型化してしまうおそれがある。 そこで、実施例3では、図3に示す電力変換装置のように、第1~第4スナバコンデンサC1~C4に対し、アバランシェ特性を持つ第1~第4アバランシェ素子Z1~Z4をそれぞれ並列接続した構成とすることで、第1~第4スナバコンデンサC1~C4が吸収しきれないエネルギーを、当該第1~第4アバランシェ素子Z1~Z4にバイパスできるようにした。なお、図2に示すものと同様のものには同一符号を付する等により、その詳細な説明を適宜省略する。 図3の電力変換装置においては、第1スナバコンデンサC1,第1スナバダイオードDs1,第1抵抗R1の共通接続点に、第1アバランシェ素子Z1のアノードが接続され、当該第1アバランシェ素子Z1のカソードが、直流リンクキャパシタCdcの正極端と第1スナバコンデンサC1との共通接続点に接続されている。 第2スナバコンデンサC2,第2スナバダイオードDs2,第2抵抗R2の共通接続点には、第2アバランシェ素子Z2のアノードが接続され、当該第2アバランシェ素子Z2のカソードが、フライングキャパシタFCの正極端,第2スナバコンデンサC2,第1スナバダイオードDs1の共通接続点に接続されている。 フライングキャパシタFCの負極端,第3スナバコンデンサC3,第4スナバダイオードDs4の共通接続点には、第3アバランシェ素子Z3のアノードが接続され、当該第3アバランシェ素子Z3のカソードが、第3スナバコンデンサC3,第3スナバダイオードDs3,第3抵抗R3の共通接続点に接続されている。 直流リンクキャパシタCdcの負極端と第4スナバコンデンサC4との共通接続点には、第4アバランシェ素子Z4のアノードが接続され、当該第4アバランシェ素子Z4のカソードが、第4スナバコンデンサC4,第4スナバダイオードDs4,第4抵抗R4の共通接続点に接続されている。 第1~第4アバランシェ素子Z1~Z4の動作開始電圧においては、それぞれ第1~第4半導体スイッチSa~Sdの各耐圧に合わせて設定することが可能である。 図3の電力変換装置において、第1,第4スナバコンデンサC1,C4は、直流リンクキャパシタCdcの電圧であるVdcに充電されることとなる。また、第2,第3スナバコンデンサC2,C3は、フライングキャパシタFCの電圧であるVdc/2に充電されることとなる。 そして、第1半導体スイッチSaに印加される電圧がVdcの値を超えた場合には、第1スナバダイオードDs1が導通し、第1スナバコンデンサC1に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第1半導体スイッチSaに印加され得るサージ電圧を抑制できる。 また、第1スナバコンデンサC1に印加される電圧が第1アバランシェ素子Z1の動作開始電圧を超過した場合には、第1アバランシェ素子Z1が動作し、当該印加される電圧が当該動作開始電圧を超過して上昇しないように、バイパスする。第1スナバコンデンサC1の電圧は、第1抵抗R1を通して直流リンクキャパシタCdcに放電され、Vdcに戻る。 第2半導体スイッチSbに印加される電圧がVdc/2の値を超えた場合には、第2スナバダイオードDs2が導通し、第2スナバコンデンサC2に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第2半導体スイッチSbに印加され得るサージ電圧を抑制できる。 また、第2スナバコンデンサC2に印加される電圧が第2アバランシェ素子Z2の動作開始電圧を超過した場合には、第2アバランシェ素子Z2が動作し、当該印加される電圧が当該動作開始電圧を超過して上昇しないように、バイパスする。第2スナバコンデンサC2の電圧は、第2抵抗R2を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第3半導体スイッチScに印加される電圧がVdc/2の値を超えた場合には、第3スナバダイオードDs3が導通し、第3スナバコンデンサC3に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第3半導体スイッチScに印加され得るサージ電圧を抑制できる。 また、第3スナバコンデンサC3に印加される電圧が第3アバランシェ素子Z3の動作開始電圧を超過した場合には、第3アバランシェ素子Z3が動作し、当該印加される電圧が当該動作開始電圧を超過して上昇しないように、バイパスする。第3スナバコンデンサC3の電圧は、第3抵抗R3を通してフライングキャパシタFCに放電され、Vdc/2に戻る。 第4半導体スイッチSdに印加される電圧がVdcの値を超えた場合には、第4スナバダイオードDs4が導通し、第4スナバコンデンサC4に電流が流れることになり、発生し得るサージ電圧をバイパスできることとなる。これにより、第4半導体スイッチSdに印加され得るサージ電圧を抑制できる。 また、第4スナバコンデンサC4に印加される電圧が第4アバランシェ素子Z4の動作開始電圧を超過した場合には、第4アバランシェ素子Z4が動作し、当該印加される電圧が当該動作開始電圧を超過して上昇しないように、バイパスする。第4スナバコンデンサC4の電圧は、第4抵抗R4を通して直流リンクキャパシタCdcに放電され、Vdcに戻る。 以上示したように実施例3によれば、実施例2と同様の作用効果を奏する他に、以下のことが言える。すなわち、第1~第4スナバコンデンサC1~C4が吸収しきれないエネルギーを、第1~第4アバランシェ素子Z1~Z4を介してバイパスでき、スナバ回路の小型化に貢献することが可能となる。 以上、本発明において、記載された具体例に対してのみ詳細に説明したが、本発明の技術思想の範囲で多彩な変形および修正が可能であることは、当業者にとって明白なことであり、このような変形および修正が特許請求の範囲に属することは当然のことである。 Cdc...直流リンクキャパシタ Cdc1,Cdc2...第1,第2直流リンクキャパシタ FC...フライングキャパシタ Sa~Sd...第1~第4半導体スイッチ C1~C4...第1~第4スナバコンデンサ Ds1~Ds4...第1~第4スナバダイオード R1~R4...第1~第4抵抗 Z1~Z4...第1~第4アバランシェ素子 [EN JP2020156163A]: Present invention A multilevel power converter of many phases is started and it is related with a snubber circuit with which a multilevel power converter was equipped especially. In a power converter applied in various fields, a multilevel power converter which connected many solid-state-switching elements to series is examined as composition which attained high-pressure-ization of the circuit itself without high-breakdown-izing resisting pressure, such as a solid-state-switching element to be used. As a conventional multilevel power converter, as shown, for example in Drawing 4, 5 level power converter which comprised a plurality of phase modules 2 and one common modules 1 is mentioned. Common modules 1 of Drawing 4 have two primitive cell Cell1 by which series connection was carried out, and Cell2, and each primitive cell Cell1 and Cell2 are constituted by four solid state switches (IGBT) and premature start capacitors. When 5 level power converters of Drawing 4 are 3 phases, multiple connection of three sets of the phase modules 2 is carried out to an output of common modules 1. This composition is indicated by patent documents 1. The 1st and 2nd diode D1 and D2 of Drawing 4 may be transposed to the 9th and 10th switching devices S9 and S10 (IGBT). In this case, a collector terminal of the 9th switching device S9 is connected to a point of the 3rd switching device S3 and the 4th switching device S4 connecting [ common ], An emitter terminal of the 10th switching device S10 is connected to a point of the 5th switching device S5 and the 6th switching device S6 connecting [ common ]. Each solid state switch in Drawing 4 and a switching device (or diode) are good also considering a plurality of solid state switches and a switching device (or diode) as series connection or composition which carries out multiple connection. Primitive cell Cell1 and Cell2 have two kinds of switching patterns (MODE1, MODE2) as shown in Drawing 5. Charge or electric discharge of 1st and 2nd premature start capacitor FC1 and FC2 can be chosen by choosing two kinds of switching patterns (MODE1, MODE2) according to a current course, and voltage of 1st and 2nd premature start capacitor FC1 and FC2 can be controlled. Here, a round mark in Drawing 5 (and inside of each below-mentioned figure) shows a solid state switch in an electrical connection, and a switching device. Since time will be taken before shifting to an OFF state from an ON state at IGBT, after turning off a solid state switch of all once at the time of shift of two MODE(s) (switching pattern), primitive cell Cell1 and Cell2, it is necessary to shift to another switching pattern. All these solid state switches call a state (Drawing 5 (a)) of OFF the dead time. The dead time is provided in order to prevent a direct-current short circuit of a premature start capacitor. If primitive cell Cell1 and Cell2 are sending current through an exchange output terminal via phase module 2, a phenomenon in which a diode by which multiple connection is carried out to a solid state switch and a switching device flows, and current flows into the dead time will occur. This is defined as a Roll style. According to this Roll style phenomenon, a problem by which excess voltage (2E) as shown in Drawing 6 (b) is impressed to the 1st switching device S1 occurs. The 1st and 2nd direct-current link capacitor CDC1,CDC2If it controls on voltage of 2E and 1st and 2nd premature start capacitor FC1 and FC2 are controlled on voltage of E, Potential of a point of contact which connects common modules 1 and phase module 2 when a Roll style phenomenon has not occurred is always maintained at 2E, E, 0, -E, and -2E, as shown in Drawing 6 (a) (a reference point of potential is NP terminal (the 1st and 2nd direct-current link capacitor C)).DC1,CDC2It is considered as a point connecting [ of common ]. If a Roll style phenomenon in which current flows into a diode of 2nd solid state switch Sf2 and 4th solid state switch Sf4 occurs here as shown in Drawing 6 (b), the 2nd solid state switch Sf2 -&gt; 4th solid state switch Sf4 -&gt; 2nd switching device -- current flows via an S2 -&gt; 3rd switching device S3 -&gt; 4th switching device S4 -&gt; exchange output terminal. As a result, output potential of common modules 1 will be set to 2E, 0, 0, -E, and -2E, and 2E will be impressed to the 1st switching device S1. Since it is circuit composition symmetrical with the upper and lower sides similarly, a phenomenon in which 2E is impressed to the 8th switching device S8 as shown in Drawing 7 also occurs. A problem of following (1) and (2) arises by impressing 2E to the 1st and 8th switching devices S1 and S8. (1) Since excess voltage is impressed to the 1st and 8th switching devices S1 and S8, there is a possibility that the 1st and 8th switching devices S1 and S8 may cause excess voltage damage etc. Thereby, the reliability of 5 level power converter may fall. (2) When potential of an exchange output terminal is +E or -E and a switching pattern of above primitive cell Cell1 and Cell2 shifts, it is desirable for potential of an exchange output terminal to be eternal (+E or -E). However, potential of an exchange output terminal is set to 0 during [ which is shown in Drawing 6 (b) ] the Roll style. Thereby, accuracy of output voltage of a power converter may deteriorate. Then, in order to cancel a problem of the above (1) and (2), composition which provided a snubber circuit in a multilevel power converter is considered. An example of composition of 5 level power converter which provided a snubber circuit in Drawing 8 is shown. A dashed line in Drawing 8 expresses a current course. As shown in Drawing 8, it is as a snubber circuit between a point of 3rd and 4th solid state switch Sf3 and Sf4 connecting [ common ], and an end (that is, NP terminal) of 2nd solid state switch Sf2, And 1st and 2nd snubber capacitor Cf1 and Cf2 are connected with an end (that is, NP terminal) of 5th solid state switch Sf5 between points of 7th and 8th solid state switch Sf7 and Sf8 connecting [ common ]. Thereby, current comes to pass along 1st and 2nd snubber capacitor Cf1 and Cf2 at the time of the dead time of common modules 1. Since potential of a terminal above 1st snubber capacitor Cf1 becomes higher than potential of NP terminal when 1st snubber capacitor Cf1 is charged, this is for a diode of 2nd solid state switch Sf2 and 4th solid state switch Sf4 not to flow. Therefore, an excess voltage phenomenon as shown in Drawing 6 and Drawing 7 can be controlled. Voltage of 1st and 2nd snubber capacitor Cf1 and Cf2 can be kept constant by connecting with 1st and 2nd premature start capacitor FC1 and FC2. Charge and a discharging method of voltage of 1st snubber capacitor Cf1 are shown in Drawing 9. 2nd and 3rd solid state switch Sf2 and Sf3 can be turned on, and 1st snubber capacitor Cf1 can be controlled by connecting with 1st premature start capacitor FC1 on the same voltage as 1st premature start capacitor FC1. Charge and a discharging method of 2nd snubber capacitor Cf2 are also the same. As for potential of a terminal above 1st snubber capacitor Cf1, also in any of two kinds of switching patterns (MODE1, MODE2) of primitive cell Cell and Cell2, potential of a terminal below +E and 2nd snubber capacitor Cf2 is maintained at -E. Since primitive cell Cell1 and Cell2 have chosen either of the two above-mentioned kinds of switching patterns (MODE1, MODE2) in a period of most except a dead time period during operation of 5 level power converter, It is possible to control voltage of 1st and 2nd snubber capacitor Cf1 and Cf2 by making electric capacity of 1st and 2nd snubber capacitor Cf1 and Cf2 smaller enough than 1st and 2nd premature start capacitor FC1 and FC2 to +E or -E. JP,2015-47056,A Although excess voltage which arises at the time of a Roll style of common modules 1 can be prevented with circuit composition (composition is only called suitably conventionally hereafter) as shown in Drawing 8, it is a specific course (for example, the 1st direct-current link capacitor C).DC1The The positive electrode side and the 2nd direct-current link capacitor CDC2Surge voltage resulting from wiring inductance on a course by the side of Negative electrode cannot be prevented. A snubber circuit of composition is what mainly assumed phase module 2 (surge voltage L*di/dt which may occur when for example, a 1st switching device S1 grade carries out turn-off of the current i is assumed) conventionally. Then, it is although it is possible to control surge voltage which applies a snubber circuit, originates in wiring inductance also in a circuit (for example, every Cell1 of common modules 1, Cell2) containing a premature start capacitor, and occurs at the time of turn-off of a switching device, It has not appeared about concrete composition. Since it seems that it was shown above, in a multilevel power converter, by controlling surge voltage which originates in wiring inductance and may occur at the time of turn-off of a switching device, breakage of a switching device is controlled and it becomes a subject to raise the reliability of a device. In view of the conventional problem, it was thought out and the present invention is the one mode, the [ the 1st and 2nd direct-current link capacitor by which series connection was carried out, and ] -- the 1~4th solid state switch -- the [ concerned ] -- a semiconductor series circuit by which series connection was carried out to the 4th order of 1~, the -- the 1~4th snubber capacitor -- the [ concerned ] -- a capacitor series circuit by which series connection was carried out to the 4th order of 1~, The 1st snubber diode by which insertion connection was made among both of the 1st and 2nd snubber capacitor, It is the multilevel power converter provided with the 4th snubber diode by which insertion connection was made between a series circuit of the 2nd and 3rd snubber diode by which insertion connection was made among both of the 2nd and 3rd snubber capacitor, and both of the 3rd and 4th snubber capacitor. With a multilevel power converter by the one mode concerned, An end of the 1st solid state switch located in the one end side of a semiconductor series circuit is connected to an anode end of the 1st direct-current link capacitor, An end of the 4th solid state switch located in the other end side of the semiconductor series circuit concerned, It is connected to a cathode end of the 2nd direct-current link capacitor. An end of the 1st snubber capacitor located in the one end side of a capacitor series circuit again, It is connected to a point of a right extreme of the 1st direct-current link capacitor, and the 1st solid state switch connecting [ common ], and an end of the 4th snubber capacitor located in the other end side of the capacitor series circuit concerned is connected to a point of a cathode end of the 2nd direct-current link capacitor, and the 4th solid state switch connecting [ common ]. An anode is connected to the 1st snubber capacitor, a cathode is connected to a point of the 1st and 2nd solid state switch connecting [ common ], and the
[ZH CN113364333A]: 组合式换流器、直流变压器及控制方法 [EN CN113364333A]: Combined converter, DC transformer and control method | [ZH CN113364333A]: 本申请提供组合式换流器、直流变压器及控制方法。所述组合式换流器包括至少一个组合模块，组合模块包括直流端口和交流端口，组合模块包括第一组合模块、第二组合模块和第三组合模块的至少一种；第一组合模块包括第一换流链或/和第二换流链或/和第三换流链，第一换流链并联于直流端口之间，第一换流链中任一节点引出连第二换流链后与交流端口的一端连接，第一换流链中另一节点直连或通过第三换流链连接交流端口的另一端；第二组合模块包括两或三个桥臂，桥臂中点引出连接交流端口，同极桥臂端点连接后连直流端口；第三组合模块包括两或三个桥臂，桥臂中点引出连交流端口，桥臂端点同极连接后再连直流端口；各组合模块的直流端口并联或串联连接。 [EN CN113364333A]: This application provides a combined converter, a DC transformer, and a control method. The combined converter includes at least one combined module, the combined module includes a DC port and an AC port, the combined module includes at least one of a first combined module, a second combined module, and a third combined module; the first combined module includes a first combined module. One converter chain or/and the second converter chain or/and the third converter chain, the first converter chain is connected in parallel between the DC ports, and any node in the first converter chain is connected to the second converter chain Connected to one end of the AC port, the other node in the first converter chain is directly connected or the other end of the AC port is connected through the third converter chain; the second combination module includes two or three bridge arms, the middle point of the bridge arm leads to the connection AC port, the end of the same pole bridge arm is connected to the DC port; the third combination module includes two or three bridge arms, the middle point of the bridge arm is led out to connect to the AC port, and the end of the bridge arm is connected to the DC port after the same pole; each combination module The DC ports are connected in parallel or series. | CN113364333A | 2021-09-07 | CN202110442046A | 2021-04-23 | CN202110442046A, 2021-04-23 | CN113364333A: 2021-09-07 | 南京南瑞继保电气有限公司 南京南瑞继保工程技术有限公司 |  | H02M7/81: I H02M3/335: I H02M7/487: I |  |  |  | [ZH CN113364333A]: 1 .一种组合式换流器，包括： 至少N个组合模块,所述组合模块包括直流端口和交流端D,N为22的正整数;其中，所 述组合模块包括第一组合模块、第二组合模块和第三组合模块的至少一种;其中 所述第一组合模块包括第一换流链或/和第二换流链或/和第三换流链，所述第一换流 链并联于所述直流端口之间，包括串联连接的M个第一子模块，所述第二换流链、第三换流 链分别包括串联连接的P、Q个第二子模块，所述第一换流链中任意一个节点引出连接所述 第二换流链后与所述交流端口的一端连接，第一换流链中另一个节点直接连接或通过所述 第三换流链连接所述交流端口的另一端,M为22的整数，P+Q = K,K为20的整数,P和Q为20 的整数； 所述第二组合模块包括两个或三个桥臂，所述桥臂包括四组或六组全控型功率半导体 器件，所述桥臂的中点引出连接所述交流端口，相同极性的桥臂端点连接后连接所述直流 端口 ； 所述第三组合模块包括两个或三个桥臂，所述桥臂包括四组或六组不控型功率半导体 器件，所述桥臂的中点引出连接所述交流端口，桥臂端点相同极性连接后再连接所述直流 端口 ； 所述各个组合模块的直流端口通过并联或串联的方式连接。 2 .如权利要求1所述的组合式换流器，其中，所述组合式换流器包括三个第一组合模 块，所述三个第一组合模块的交流端口分别引出作为所述组合式换流器的交流A、B、C三相， 且P = K,Q = 0；所述三个第一组合模块的直流端口级联后构成组合式换流器的直流端口。 3 .如权利要求1所述的组合式换流器，其中，所述第一组合模块中第一换流链的两个节 点选取第一换流链的首端和末端。 4 .如权利要求1所述的组合式换流器，其中，所述组合式换流器包括T个组合模块,所述 组合模块包括至少一个第二组合模块与至少一个第三组合模块，第二组合模块与第三组合 模块的直流端口并联或串联连接,构成所述组合模块的直流端口力为21的整数。 5 .如权利要求1所述的组合式换流器，其中，所述第一子模块和所述第二子模块包括单 相全控半桥电路或单相全控全桥电路。 6 .如权利要求1所述的组合式换流器，其中，所述第二组合模块的桥臂包括单相全控半 桥电路，或单相全控全桥电路，或三相全控半桥电路，所述第二组合模块的全控型功率半导 体器件包括IGBT或MOSFET,或IGBT或MOSFET的串联连接的至少一种。 7 .如权利要求1所述的组合式换流器，其中，所述第三组合模块的桥臂包括单相不控全 桥电路，或三相不控半桥电路，所述不控全桥电路包括二极管或二极管的串联连接的至少 一种。 8 .如权利要求1所述的组合式换流器，其中，所述组合模块包括第一组合模块时，还包 括： 至少一个启动支路； 当N21时，所述启动支路并联于所述组合模块的第一交流端口和第二交流端口之间； 或并联于所述组合模块的第一交流端口和直流端口之间；或并联于所述组合模块的两个直 流端口之间；或以上连接方式的组合； 当N22时，所述启动支路还可以并联在不同第一组合模块的第一交流端口之间或第二 交流端口之间或第一交流端口与第二交流端口之间； 所述启动支路包括串联连接的启动开关或/和充电电阻。 9 .如权利要求1所述的组合式换流器，其中，所述第一组合模块还包括： 至少一个电抗器，与所述第一换流链串联连接。 10 .如权利要求1所述的组合式换流器，其中，所述第二换流链还包括： 至少一组电容器组，与所述第二子模块串联连接，所述电容器组包括串联/并联连接的 至少一个电容器。 11 .如权利要求1所述的组合式换流器，其中，所述第二换流链中第二子模块个数K的数 目根据所述组合模块的位置确定； 当组合式换流器直流正负极电压对称时，靠近组合式换流器正负极端口处的所述组合 模块的第二换流链中第二子模块个数2靠近正负极端口中点处的所述组合模块的第二换 流链中第二子模块个数； 当组合式换流器直流正负极电压有一端接地时，靠近非接地端口处的所述组合模块的 第二子模块个数2靠近接地端口处的所述组合模块的第二子模块个数。 12 .如权利要求11所述的组合式换流器，其中，所述第二换流链、第三换流链的一端的 电压始终高于另一端的电压。 13 .如权利要求1至12之任一项所述的组合式换流器，还包括： 第一隔离变压器，所述第一隔离变压器包括至少一个副边绕组，副边绕组数量与所述 组合模块个数相同； 当组合模块个数为1时，所述副边绕组的一端连接所述组合模块的交流端口的一端，所 述副边绕组的另一端连接所述组合模块的直流端口或交流端口的另一端； 当组合模块个数大于1时，所述副边绕组的一端连接所述组合模块的交流端口的一端， 所述副边绕组的另一端互相短接或连接所述组合模块的直流端口或交流端口的另一端。 14 .一种直流变压器，包括： 如权利要求13所述的组合式换流器，所述组合式换流器的直流端口，构成所述直流变 压器的第一直流端口； 第二换流器，包括直流端口和交流端口 ,所述第二换流器的交流端口，根据相别设置连 接所述组合式换流器的第一隔离变压器的原边;所述第二换流器的直流端口 ,构成所述直 流变压器的第二直流端口； 所述第二换流器与所述组合式换流器的结构相同，或者为模块化多电平变换器、单相 全控半桥电路、单相全控全桥电路、三相全控半桥电路的至少一种。 15 .一种控制方法，应用于如权利要求1至13之任一项所述的组合式换流器或如权利要 求14所述的直流变换器，所述控制方法包括直流预充电控制模式、组合式换流器直流端口 至交流端口的逆变运行控制模式、组合式换流器交流端口至直流端口的整流运行控制模 式。 16 .如权利要求15所述的控制方法，其中，所述直流预充电控制模式包括： 完成第一组合模块的第一换流链的所有第一子模块从直流侧充电； 闭合所述组合式换流器的启动支路的启动开关； 依次或按一定逻辑解锁第一换流链中与所述启动支路并联的部分，使第二换流链上的 电压逐渐上升，完成所有第二子模块的充电； 断开所述启动支路的启动开关。 17 .如权利要求15所述的控制方法，其中，所述逆变运行控制模式包括： 在直流预充电控制步骤完成后，解锁所述组合式换流器中第一换流链的所有第一子模 块和第二换流链的所有第二子模块； 采集并控制所述组合式换流器的交流端口电压或功率； 若存在第二换流器，则解锁所述第二换流器，同时，通过所述第二换流器，采集并控制 所述第二换流器的直流端口电压或功率。 18 .如权利要求15所述的控制方法，其中，所述整流运行控制模式包括： 若存在第二换流器，则解锁所述第二换流器，同时，通过所述第二换流器，采集并控制 所述第二换流器的交流端口电压或功率； 完成第一换流链上所有第一子模块和第二换流链所有第二子模块的充电； 解锁所述第一组合模块的第一子模块和第二子模块； 采集并控制所述组合式换流器的直流端口电压或功率。 [EN CN113364333A]: 1 A combined converter, comprising: at least N combined modules, the combined module includes a DC port and an AC terminal D, N is a positive integer of 22; wherein, the combined module includes a first combined module, a second At least one of a combination module and a third combination module; wherein the first combination module includes a first converter chain or/and a second converter chain or/and a third converter chain, and the first converter chain is connected in parallel Between the DC ports, M first sub-modules connected in series are included. The second converter chain and the third converter chain respectively include P and Q second sub-modules connected in series. Any node in the converter chain is connected to the second converter chain and then connected to one end of the AC port. The other node in the first converter chain is directly connected or connected to the AC through the third converter chain. At the other end of the port, M is an integer of 22, P+Q=K, K is an integer of 20, and P and Q are integers of 20; the second combination module includes two or three bridge arms, the bridge arms It includes four or six groups of fully-controlled power semiconductor devices, the midpoint of the bridge arm is led out to connect to the AC port, and the end of the bridge arm of the same polarity is connected to the DC port; the third combination module includes two One or three bridge arms, the bridge arms include four or six groups of uncontrolled power semiconductor devices, the midpoint of the bridge arms is led out to connect to the AC port, and the ends of the bridge arms are connected with the same polarity before connecting the DC port; The DC ports of the various combination modules are connected in parallel or in series. 2 The combined converter according to claim 1, wherein the combined converter comprises three first combined modules, and the AC ports of the three first combined modules are respectively led out as the combined converter The AC three-phase A, B, and C of the converter, and P=K, Q=0; the DC ports of the three first combination modules are cascaded to form the DC ports of the combined converter. 3 The combined converter of claim 1, wherein the two nodes of the first converter chain in the first combined module select the head end and the end of the first converter chain. 4 The combined converter of claim 1, wherein the combined converter includes T combined modules, the combined module includes at least one second combined module and at least one third combined module, the second The combined module is connected in parallel or in series with the DC port of the third combined module, and the DC port force constituting the combined module is an integer of 21. 5 The combined converter of claim 1, wherein the first sub-module and the second sub-module comprise a single-phase full-control half-bridge circuit or a single-phase full-control full-bridge circuit. 6 The combined converter of claim 1, wherein the bridge arm of the second combined module comprises a single-phase fully-controlled half-bridge circuit, or a single-phase fully-controlled full-bridge circuit, or a three-phase fully-controlled half-bridge In the circuit, the fully-controlled power semiconductor device of the second combination module includes at least one of IGBT or MOSFET, or a series connection of IGBT or MOSFET. 7 The combined converter of claim 1, wherein the bridge arm of the third combined module comprises a single-phase uncontrolled full bridge circuit or a three-phase uncontrolled half bridge circuit, the uncontrolled full bridge circuit At least one of a diode or a series connection of diodes is included. 8 The combined converter of claim 1, wherein when the combined module includes the first combined module, it further comprises: at least one starting branch; when N21, the starting branch is connected in parallel to the combination Between the first AC port and the second AC port of the module; or in parallel between the first AC port and the DC port of the combination module; or in parallel between the two DC ports of the combination module; or the above connection When N22, the start branch can also be connected in parallel between the first AC ports or the second AC ports of different first combination modules Between the AC ports or between the first AC port and the second AC port; the starting branch includes a starting switch or/and a charging resistor connected in series. 9 The combined converter of claim 1, wherein the first combined module further comprises: at least one reactor connected in series with the first converter chain. 10 The combined converter of claim 1, wherein the second converter chain further comprises: at least one set of capacitor banks connected in series with the second sub-module, the capacitor banks including series/parallel At least one capacitor connected. 11 The combined converter of claim 1, wherein the number K of the second sub-modules in the second converter chain is determined according to the position of the combined module; when the combined converter is DC positive When the negative pole voltage is symmetrical, the number of second sub-modules in the second converter chain of the combination module close to the positive and negative ports of the combined converter 2 is close to the second sub-module of the combination module at the midpoint of the positive and negative ports 2. The number of the second sub-modules in the converter chain; when one end of the DC positive and negative voltages of the combined converter is grounded, the number of the second sub-modules of the combined module near the non-grounded port 2 is near the grounded port The number of second sub-modules of the combined module. 12 The combined converter of claim 11, wherein the voltage at one end of the second converter chain and the third converter chain is always higher than the voltage at the other end. 13 The combined converter according to any one of claims 1 to 12, further comprising: a first isolation transformer, the first isolation transformer includes at least one secondary winding, and the number of secondary windings is the same as that of the combined module The number is the same; when the number of combined modules is 1, one end of the secondary winding is connected to one end of the AC port of the combined module, and the other end of the secondary winding is connected to the DC port or the AC port of the combined module When the number of combined modules is greater than 1, one end of the secondary winding is connected to one end of the AC port of the combined module, and the other end of the secondary winding is shorted to each other or connected to the DC of the combined module The other end of the port or AC port. 14 A DC transformer, comprising: the combined converter according to claim 13, wherein the DC port of the combined converter constitutes the first DC port of the DC transformer; and the second converter, It includes a DC port and an AC port. The AC port of the second converter is connected to the primary side of the first isolation transformer of the combined converter according to the phase setting; the DC port of the second converter, Constitute the second DC port of the DC transformer; the second converter has the same structure as the combined converter, or is a modular multi-level converter, a single-phase fully controlled half-bridge circuit, or a single-phase At least one of a fully-controlled full-bridge circuit and a three-phase fully-controlled half-bridge circuit. 15 A control method, applied to the combined converter according to any one of claims 1 to 13 or the DC converter according to claim 14, said control method including DC precharge control mode, combination The inverter operation control mode from the DC port to the AC port of the integrated converter, and the rectification operation control mode from the AC port to the DC port of the combined converter. 16 The control method according to claim 15, wherein the DC pre-charging control mode comprises: completing all the first sub-modules of the first converter chain of the first combined module to be charged from the DC side; closing the combined converter The start switch of the start branch of the converter; unlock the part of the first converter chain that is parallel to the start branch in sequence or according to a certain logic, so that the The voltage gradually rises to complete the charging of all the second sub-modules; and the start switch of the start branch is turned off. 17 The control method according to claim 15, wherein the inverter operation control mode comprises: after the DC precharge control step is completed, unlocking all the first components of the first converter chain in the combined converter Module and all the second sub-modules of the second converter chain; collect and control the AC port voltage or power of the combined converter; if there is a second converter, unlock the second converter, and at the same time , Collecting and controlling the DC port voltage or power of the second converter through the second converter. 18 The control method of claim 15, wherein the rectification operation control mode comprises: if there is a second inverter, unlock the second inverter, and at the same time, pass the second inverter, Collect and control the AC port voltage or power of the second converter; complete the charging of all the first sub-modules on the first converter chain and all the second sub-modules of the second converter chain; unlock the first combination module The first sub-module and the second sub-module of the; collecting and controlling the DC port voltage or power of the combined converter. | [ZH CN113364333A]: 组合式换流器、直流变压器及控制方法 技术领域 [0001]本申请涉及电力电子应用技术领域，具体涉及组合式换流器、直流变压器及控制 方法。 背景技术 [0002] 交直换流器作为现有柔性输电电网中，实现电压变换的重要组成设备，一直是柔 性输电领域学者们关注的重点。随着直流输电应用的不断普及，换流器还能通过背靠背连 接实现直流变压器功能。 [0003] 然而，在直流变压器应用中，现有技术存在以下一些问题。 [0004]第一，现有直流变压器的结构使其传输功率时，分为双向传递功率和单向传递功 率两种。单向传递功率时，直流变压器可以大量使用不控型开关器件降低成本，但无法完成 反向功率传递功能。双向传递功率时，现有的拓扑在设计上往往是两个方向的功率设计容 量也完全相同，然而，在一些特殊应用场合，直流变压器模块双向运行情况下，并非需要两 个方向的运行功率完全相同，因此现有的方案在设计上存在一定的优化空间。 [0005]第二，通过MMC背靠背方案实现直流变压器功能时，通常需要六个桥臂，系统的模 块数众多，成本较高。在节省成本方面，有不少文献提出了非隔离方式，但非隔离方式对于 故障隔离，以及系统的安全性存在隐患。所以需要提出一种能够降低成本，且具有隔离功能 的直流变压器。 [0006]第三，随着电压等级的提高，直流变压器模块高压侧的额定电压不断升高，给其辅 助电源电路的设计也带来的挑战，辅助电源电路在满足一定隔离电压和绝缘电压的同时， 还应具备高效、高可靠性要求。 发明内容 [0007]本申请实施例提供一种组合式换流器，包括至少N个组合模块，所述组合模块包括 直流端口和交流端D,N为22的正整数;其中，所述组合模块包括第一组合模块、第二组合 模块和第三组合模块的至少一种;其中，所述第一组合模块包括第一换流链或/和第二换流 链或/和第三换流链，所述第一换流链并联于所述直流端口之间，包括串联连接的M个第一 子模块，所述第二换流链、第三换流链分别包括串联连接的P、Q个第二子模块，所述第一换 流链中任意一个节点引出连接所述第二换流链后与所述交流端口的一端连接，第一换流链 中另一个节点直接连接或通过所述第三换流链连接所述交流端口的另一端,M为22的整 数，P+Q = K,K为20的整数,P和Q为20的整数;所述第二组合模块包括两个或三个桥臂，所 述桥臂包括四组或六组全控型功率半导体器件,所述桥臂的中点引出连接所述交流端口， 相同极性的桥臂端点连接后连接所述直流端口；所述第三组合模块包括两个或三个桥臂， 所述桥臂包括四组或六组不控型功率半导体器件，所述桥臂的中点引出连接所述交流端 口 ,桥臂端点相同极性连接后再连接所述直流端口 ；所述各个组合模块的直流端口通过并 联或串联的方式连接。 [0008] 根据一些实施例，所述组合式换流器包括三个第一组合模块,所述三个第一组合 模块的交流端口分别引出作为所述组合式换流器的交流A、B、C三相，且P = K,Q = 0；所述三 个第一组合模块的直流端口级联后构成组合式换流器的直流端口。 [0009]根据一些实施例，所述第一组合模块中第一换流链的两个节点选取第一换流链的 首端和末端。 [0010]根据一些实施例，所述组合式换流器包括T个组合模块，所述组合模块包括至少一 个第二组合模块与至少一个第三组合模块，第二组合模块与第三组合模块的直流端口并联 或串联连接,构成所述组合模块的直流端口力为21的整数。 [0011]根据一些实施例，所述第一子模块和所述第二子模块包括单相全控半桥电路或单 相全控全桥电路。 [0012]根据一些实施例，所述第二组合模块的桥臂包括单相全控半桥电路，或单相全控 全桥电路，或三相全控半桥电路，所述第二组合模块的全控型功率半导体器件包括IGBT或 MOSFET,或IGBT或MOSFET的串联连接的至少一种。 [0013]根据一些实施例，所述第三组合模块的桥臂包括单相不控全桥电路，或三相不控 半桥电路，所述不控全桥电路包括二极管或二极管的串联连接的至少一种。 [0014]根据一些实施例，所述组合模块包括第一组合模块时，还包括至少一个启动支路; 当N21时，所述启动支路并联于所述组合模块的第一交流端口和第二交流端口之间;或并 联于所述组合模块的第一交流端口和直流端口之间；或并联于所述组合模块的两个直流端 口之间；或以上连接方式的组合；当N22时，所述启动支路还可以并联在不同第一组合模块 的第一交流端口之间或第二交流端口之间或第一交流端口与第二交流端口之间;所述启动 支路包括串联连接的启动开关或/和充电电阻。 [0015] 根据一些实施例，所述第一组合模块还包括至少一个电抗器，所述电抗器与所述 第一换流链串联连接。 [0016] 根据一些实施例，所述第二换流链还包括至少一组电容器组，所述电容器组与所 述第二子模块串联连接，所述电容器组包括串联/并联连接的至少一个电容器。 [0017]根据一些实施例，所述第二换流链中第二子模块个数K的数目根据所述组合模块 的位置确定；当组合式换流器直流正负极电压对称时，靠近组合式换流器正负极端口处的 所述组合模块的第二换流链中第二子模块个数2靠近正负极端口中点处的所述组合模块 的第二换流链中第二子模块个数；当组合式换流器直流正负极电压有一端接地时，靠近非 接地端口处的所述组合模块的第二子模块个数2靠近接地端口处的所述组合模块的第二 子模块个数。 [0018]根据一些实施例，所述第二换流链、第三换流链的一端的电压始终高于另一端的 电压。 [0019] 根据一些实施例，所述的组合式换流器还包括第一隔离变压器，所述第一隔离变 压器包括至少一个副边绕组，副边绕组数量与所述组合模块个数相同；当组合模块个数为1 时，所述副边绕组的一端连接所述组合模块的交流端口的一端，所述副边绕组的另一端连 接所述组合模块的直流端口或交流端口的另一端；当组合模块个数大于1时,所述副边绕组 的一端连接所述组合模块的交流端口的一端，所述副边绕组的另一端互相短接或连接所述 组合模块的直流端口或交流端口的另一端。 [0020] 本申请实施例还提供一种直流变压器，包括如上所述的组合式换流器和第二换流 器，所述组合式换流器的直流端口，构成所述直流变压器的第一直流端口；所述第二换流器 包括直流端口和交流端口，所述第二换流器的交流端口，根据相别设置连接所述组合式换 流器的第一隔离变压器的原边;所述第二换流器的直流端口，构成所述直流变压器的第二 直流端口；所述第二换流器与所述组合式换流器的结构相同，或者为模块化多电平变换器、 单相全控半桥电路、单相全控全桥电路、三相全控半桥电路的至少一种。 [0021] 本申请实施例还提供一种控制方法，应用于如上所述的组合式换流器或所述的直 流变换器，所述控制方法包括直流预充电控制模式、组合式换流器直流端口至交流端口的 逆变运行控制模式、组合式换流器交流端口至直流端口的整流运行控制模式。 [0022]根据一些实施例，所述直流预充电控制模式包括:完成第一组合模块的第一换流 链的所有第一子模块从直流侧充电；闭合所述组合式换流器的启动支路的启动开关;依次 或按一定逻辑解锁第一换流链中与所述启动支路并联的部分，使第二换流链上的电压逐渐 上升，完成所有第二子模块的充电；断开所述启动支路的启动开关。 [0023] 根据一些实施例，所述逆变运行控制模式包括:在直流预充电控制步骤完成后，解 锁所述组合式换流器中第一换流链的所有第一子模块和第二换流链的所有第二子模块;采 集并控制所述组合式换流器的交流端口电压或功率；若存在第二换流器，则解锁所述第二 换流器，同时，通过所述第二换流器，采集并控制所述第二换流器的直流端口电压或功率。 [0024]根据一些实施例，所述整流运行控制模式包括:若存在第二换流器，则解锁所述第 二换流器，同时，通过所述第二换流器，采集并控制所述第二换流器的交流端口电压或功 率;完成第一换流链上所有第一子模块和第二换流链所有第二子模块的充电；解锁所述第 一组合模块的第一子模块和第二子模块;采集并控制所述组合式换流器的直流端口电压或 功率。 [0025]本申请实施例提供的技术方案，在双向功率传递应用场合，通过设计基于全控型 开关器件和不控型开关器件全桥电路的设计容量或电压等级的不同，能够有效解决双向运 行功率存在差异的场合，降低整体设备成本。同时，依据不对称结构，可以设置一个低压全 桥电路，用于辅助电源设计，降低了辅助电源的设计需求。此外，在高压应用中，本申请实施 例提供的技术方案，仅通过增加第二串换流链配合第一串换流链，相比传统MMC方案，在实 现电压等级相同的情况下，能够减少模块数目，降低系统成本。 附图说明 [0026]为了更清楚地说明本申请实施例中的技术方案，下面将对实施例描述中所需要使 用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本申请的一些实施例，对于 本领域普通技术人员来讲，在不付出创造性劳动的前提下，还可以根据这些附图获得其他 的附图。 [0027]图1是本申请提供的一种包含第一组合模块的组合式换流器示意图（N=3）。 [0028]图2是本申请提供的一种第一组合模块的示意图。 [0029]图3是本申请提供的一种包含第二组合模块以及第三组合模块的组合式换流器示 意图。 [0030]图4是本申请提供的一种包含第一组合模块、第一隔离变压器和启动支路的组合 式换流器示意图(N=3)。 [0031]图5是本申请提供的一种包含第二组合模块、第三组合模块和第一隔离变压器组 成的组合式换流器示意图。 [0032]图6是本申请提供的一种单相全控半桥电路示意图。 [0033]图7是本申请提供的一种单相全控全桥电路示意图。 [0034]图8是本申请提供的一种单相全控全桥电路示意图。 [0035]图9是本申请提供的一种三相全控半桥电路示意图。 [0036]图10是本申请提供的一种单相不控全桥电路示意图。 [0037]图11是本申请提供的一种三相不控半桥电路示意图。 [0038]图12是本申请提供的由第二组合模块、第三组合模块和单相全控全桥电路组成的 直流变压器示意图一。 [0039]图13是本申请提供的由第二组合模块、第三组合模块和单相全控全桥电路组成的 直流变压器示意图二。 [0040]图14是本申请提供的由第二组合模块、第三组合模块和单相全控全桥电路组成的 直流变压器示意图三。 [0041]图15是本申请提供的由第一组合模块和单相全控全桥电路组成的直流变压器示 意图(N=2)。 [0042]图16是本申请提供的由第一组合模块和单相全控全桥电路组成的直流变压器示 意图一 (N=3)。 [0043]图17是本申请提供的由第一组合模块和单相全控全桥电路组成的直流变压器示 意图二(N=3)。 [0044]图18是本申请提供的一种组合式换流器的直流预充电控制模式流程图。 [0045]图19是本申请提供的一种组合式换流器的逆变运行控制模式流程图。 [0046]图20是本申请提供的一种组合式换流器的整流运行控制模式流程图。 具体实施方式 [0047]下面将结合本申请实施例中的附图，对本申请实施例中的技术方案进行清楚、完 整地描述，显然，所描述的实施例是本申请一部分实施例，而不是全部的实施例。基于本申 请中的实施例，本领域技术人员在没有做出创造性劳动前提下所获得的所有其他实施例， 都属于本申请保护的范围。 [0048]应当理解，本申请的和权利要求书中使用的术语“包括”和“包含”指示所描 述特征、整体、步骤、操作、元素和/或组件的存在，但并不排除一个或多个其它特征、整体、 步骤、操作、元素、组件和/或其集合的存在或添加。 [0049]图1是本申请提供的一种包含第一组合模块的组合式换流器示意图(N=3)。 [0050] 组合式换流器包括至少N个组合模块。组合模块包括直流端口和交流端口，N为22 的正整数。其中，组合模块包括第一组合模块、第二组合模块和第三组合模块的至少一种。 各个组合模块的直流端口通过并联或串联的方式连接。 [0051]第一组合模块包括第一换流链或/和第二换流链或/和第三换流链。第一换流链并 联于直流端口之间，包括串联连接的M个第一子模块。第二换流链、第三换流链分别包括串 联连接的P、Q个第二子模块。第一换流链中任意一个节点引出连接第二换流链后与交流端 口的一端连接，第一换流链中另一个节点直接连接或通过第三换流链连接交流端口的另一 端,M为22的整数，P+Q = K,K为20的整数,P和Q为20的整数。 [0052]其中，第二换流链中第二子模块个数K的数目根据所述组合模块的位置确定。第二 换流链、第三换流链的一端的电压始终高于另一端的电压。 [0053] 当组合式换流器直流正负极电压对称时，靠近组合式换流器正负极端口处的组合 模块的第二换流链中第二子模块个数2靠近正负极端口中点处的组合模块的第二换流链 中第二子模块个数。 [0054]当组合式换流器直流正负极电压有一端接地时，靠近非接地端口处的组合模块的 第二子模块个数2靠近接地端口处的组合模块的第二子模块个数。 [0055]可选地，第二换流链还包括至少一组电容器组，电容器组与第二子模块串联连接， 电容器组包括串联/并联连接的至少一个电容器。 [0056]根据一些实施例，第一子模块和第二子模块包括单相全控半桥电路或单相全控全 桥电路。 [0057] 一种单相全控半桥电路如图6所示，包括两个串联连接的全控型开关器件或者全 控型开关器件组。一种单相全控全桥电路如图7所示，包括四个两两串联连接的全控型开关 器件或者全控型开关器件组。另一种单相全控全桥电路如图8所示，包括两个串联连接的全 控型开关器件或者全控型开关器件组和两个串联连接的电容器或电容器组。 [0058] 第二组合模块包括两个或三个桥臂，桥臂包括四组或六组全控型功率半导体器 件。桥臂的中点引出连接交流端口，相同极性的桥臂端点连接后连接直流端口。 [0059]根据一些实施例，第二组合模块的桥臂包括单相全控半桥电路，或单相全控全桥 电路，或三相全控半桥电路，所述第二组合模块的全控型功率半导体器件包括IGBT或 MOSFET,或IGBT或MOSFET的串联连接的至少一种。 [0060] 一种三相全控半桥电路如图9所示，包括六个两两串联连接的全控型开关器件或 者全控型开关器件组。 [0061] 第三组合模块包括两个或三个桥臂，桥臂包括四组或六组不控型功率半导体器 件。桥臂的中点引出连接交流端口，桥臂端点相同极性连接后再连接直流端口。 [0062]第三组合模块的桥臂包括单相不控全桥电路，或三相不控半桥电路，不控全桥电 路包括二极管或二极管的串联连接的至少一种。 [0063] 一种单相不控全桥电路如图10所示，包括两个串联连接的二极管或者二极管器件 组。一种三相不控半桥电路如图11所示，包括六个两两串联连接的二极管或者二极管器件 组。 [0064] 可选地，组合式换流器还包括第一隔离变压器，第一隔离变压器包括至少一个副 边绕组，副边绕组数量与组合模块个数相同。 [0065]当组合模块个数为1时，第一隔离变压器的副边绕组的一端连接组合模块的交流 端口的一端,第一隔离变压器的副边绕组的另一端连接组合模块的直流端口或交流端口的 另一端。 [0066]当组合模块个数大于1时，第一隔离变压器的副边绕组的一端连接组合模块的交 流端口的一端，第一隔离变压器的副边绕组的另一端互相短接或连接组合模块的直流端口 或交流端口的另一端。 [0067] 根据一些实施例，组合式换流器包括三个第一组合模块501、502、503,如图1所示。 [0068]三个第一组合模块的第一交流端口分别引出作为组合式换流器的交流A、B、C三 相。 [0069]第一组合模块示意图参见图2,组件101〜10M表示第一子模块，串联连接形成第一 换流链。组件201〜20P以及组件301〜30Q表示第二子模块，串联连接形成第二换流链和第 三换流链。10a和10b为直流端口的两端,10c和10d为交流端口的两端。 [0070] 如图1所示，P = K,Q = 0。三个第一组合模块501、502、503的直流端口级联后构成组 合式换流器的直流端口。第一组合模块中第一换流链的两个节点选取第一换流链的首端和 末端。 [0071]可选地，组合模块包括第一组合模块时，还包括至少一个启动支路。启动支路包括 串联连接的启动开关或/和充电电阻。 [0072]当N2 1时，启动支路并联于组合模块的第一交流端口和第二交流端口之间；或并 联于组合模块的第一交流端口和直流端口之间；或并联于组合模块的两个直流端口之间； 或以上连接方式的组合。 [0073]当N22时，启动支路还可以并联在不同第一组合模块的第一交流端口之间或第二 交流端口之间或第一交流端口与第二交流端口之间。 [0074] 可选地，如图1所示，第一组合模块还包括至少一个电抗器40，电抗器40与第一换 流链串联连接。 [0075]本实施例提供的技术方案，在双向功率传递应用场合,通过设计基于全控型开关 器件和不控型开关器件全桥电路的设计容量或电压等级的不同，能够有效解决双向运行功 率存在差异的场合，降低整体设备成本。此外，在高压应用中，本实施例提供的技术方案，仅 通过增加第二串换流链配合第一串换流链，相比传统MMC方案，在实现电压等级相同的情况 下，能够减少模块数目，降低系统成本。 [0076]图3是本申请提供的一种包含第二组合模块以及第三组合模块的组合式换流器示 意图。 [0077] 组合式换流器包括至少N个组合模块。组合模块包括直流端口和交流端口，N为22 的正整数。其中，组合模块包括第一组合模块、第二组合模块和第三组合模块的至少一种。 各个组合模块的直流端口通过并联或串联的方式连接。 [0078]第一组合模块包括第一换流链、第二换流链或/和第三换流链。第一换流链并联于 直流端口之间，包括串联连接的M个第一子模块。第二换流链、第三换流链分别包括串联连 接的P、Q个第二子模块。第一换流链中任意一个节点引出连接第二换流链后与交流端口的 一端连接，第一换流链中另一个节点直接连接或通过第三换流链连接交流端口的另一端,M 为22的整数，P+Q=K,K为20的整数,P和Q为20的整数。 [0079] 第二组合模块包括两个或三个桥臂，桥臂包括四组或六组全控型功率半导体器 件。桥臂的中点引出连接交流端口，相同极性的桥臂端点连接后连接直流端口。 [0080] 第三组合模块包括两个或三个桥臂，桥臂包括四组或六组不控型功率半导体器 件。桥臂的中点引出连接交流端口，桥臂端点相同极性连接后再连接直流端口。 [0081] 可选地，组合式换流器还包括第一隔离变压器，第一隔离变压器包括至少一个副 边绕组，副边绕组数量与组合模块个数相同。 [0082]当组合模块个数为1时，第一隔离变压器的副边绕组的一端连接组合模块的交流 端口的一端，第一隔离变压器的副边绕组的另一端连接组合模块的直流端口或交流端口的 另一端。 [0083]当组合模块个数大于1时，第一隔离变压器的副边绕组的一端连接组合模块的交 流端口的一端，第一隔离变压器的副边绕组的另一端互相短接或连接组合模块的直流端口 或交流端口的另一端。根据一些实施例，组合式换流器包括第二组合模块以及第三组合模 块，如图3所示。 [0084] 参见图3,组合式换流器包括至少一个第二组合模块与至少一个第三组合模块,N =T。第二组合模块与第三组合模块的直流端口并联或串联，构成组合式换流器的直流端 口 ,T为大于等于1的整数。组件601〜60T表示T个第二组合模块或第三组合模块。 [0085]本实施例提供的技术方案，在双向功率传递应用场合，通过设计基于全控型开关 器件和不控型开关器件全桥电路的设计容量或电压等级的不同，能够有效解决双向运行功 率存在差异的场合，降低整体设备成本。 [0086]图4是本申请提供的一种包含第一组合模块、第一隔离变压器和启动支路的组合 式换流器示意图(N=3)。 [0087] 根据一些实施例，组合式换流器包括第一组合模块和第一隔离变压器,为非对称 组合式换流器，如图4所示(N=3)。启动支路20a包括启动开关20a 1和启动电阻20a2。 [0088] 参加图4,组合式换流器包括三个第一组合模块，第一隔离变压器70包括三个副边 绕组，副边绕组数量与组合模块个数相同。 [0089]第一隔离变压器70的三个副边绕组的一端分别连接组合模块的交流端口的一端， 第一隔离变压器70的三个副边绕组的另一端互相短接。 [0090] 第二换流链还包括至少一组电容器组，电容器组20b与第二子模块串联连接，电容 器组包括串联/并联连接的至少一个电容器。 [0091]本实施例提供的技术方案，依据不对称结构，可以设置一个低压全桥电路，用于辅 助电源设计，降低了辅助电源的设计需求。 [0092]图5是本申请提供的一种包含第二组合模块、第三组合模块和第一隔离变压器组 成的组合式换流器示意图。 [0093] 根据一些实施例，组合式换流器包括至少一个第二组合模块、至少一个第三组合 模块和第一隔离变压器，为非对称组合式换流器，如图5所示。 [0094]参加图5,组合式换流器包括一个第二组合模块和一个第三组合模块，第一隔离变 压器80包括两个个副边绕组，副边绕组数量与组合模块个数相同。 [0095]第一隔离变压器80的两个副边绕组的一端分别连接组合模块的交流端口的一端， 第一隔离变压器80的两个副边绕组的另一端连接组合模块的直流端口或交流端口的另一 端。 [0096] 本实施例提供的技术方案,依据不对称结构,可以设置一个低压全桥电路,用于辅 助电源设计，降低了辅助电源的设计需求。 [0097]图12是本申请实施例提供的一种直流变压器示意图。 [0098] 直流变压器包括组合式换流器和第二换流器。组合式换流器的直流端口，构成直 流变压器的第一直流端口。第二换流器包括直流端口和交流端口，第二换流器的交流端口 根据相别设置连接组合式换流器的第一隔离变压器的原边,第二换流器的直流端口构成直 流变压器的第二直流端口。第二换流器与组合式换流器的结构相同，或者为模块化多电平 变换器、单相全控半桥电路、单相全控全桥电路、三相全控半桥电路的至少一种。 [0099]如图12所示，组合式换流器包括一个第二组合模块和一个第三组合模块。第二组 合模块包括两个桥臂，桥臂包括单相全控全桥电路。桥臂的中点引出连接交流端口，交流端 口连接第一隔离变压器的一个副边绕组，相同极性的桥臂端点连接后连接直流端口。 [0100]第三组合模块包括两个或三个桥臂，桥臂包括单相不控全桥电路。桥臂的中点引 出连接交流端口，交流端口连接第一隔离变压器的另一个副边绕组，桥臂端点相同极性连 接后再连接直流端口。 [0101]第二换流器包括单相全控全桥电路。第二换流器的交流端口连接组合式换流器的 第一隔离变压器的原边。 [0102] 根据一些实施例，另一种直流变压器如图13所示，组合式换流器包括两个第三组 合模块。两个第三组合模块都包括两个桥臂，其中一个第三组合模块的桥臂包括单个二极 管。另一个第三组合模块的桥臂包括串联连接的两个二极管。桥臂的中点引出连接交流端 口，交流端口连接第一隔离变压器的一个副边绕组，桥臂端点相同极性连接后再连接直流 端口。 [0103]第二换流器包括单相全控全桥电路。第二换流器的交流端口连接组合式换流器的 第一隔离变压器的原边。 [0104] 根据一些实施例，又一种直流变压器如图14所示，直流变压器包括组合式换流器 和第二换流器。组合式换流器包括两个第二组合模块。第二换流器包括单相全控全桥电路。 两个第二组合模块一个是单相全桥电路，另一个是三相半桥电路。 [0105] 根据一些实施例，再一种直流变压器如图15所示，直流变压器包括组合式换流器 和第二换流器。组合式换流器包括两个第一组合模块,N=2。第二换流器包括单相全控全桥 电路。 [0106] 根据一些实施例，又另一种直流变压器如图16所示,直流变压器包括组合式换流 器和第二换流器。组合式换流器包括三个第一组合模块,N=3。电容器组1301可以根据电路 等效原则，由跟第二串联链串联，变换为角型连接方式。第二换流器90为模块化多电平电 路。 [0107] 根据一些实施例，又再一种直流变压器如图17所示,直流变压器包括组合式换流 器和第二换流器。组合式换流器包括三个第一组合模块,N=3。电容器组1301包括两个电容 器。第二换流器90为模块化多电平电路。 [0108] 在图17中，当组合式换流器直流正负极电压对称时，靠近组合式换流器正负极端 口处的组合模块的第二换流链中第二子模块个数2靠近正负极端口中点处的组合模块的 第二换流链中第二子模块个数。图17中第二个第一组合模块的第二串联链P = Q = 0,而第一 个和第三个组合模块的第二串联链P&gt;0。 [0109] 本申请还提供一种控制方法，应用于所述的组合式换流器或所述的直流变换器， 所述控制方法包括直流预充电控制模式、组合式换流器直流端口至交流端口的逆变运行控 制模式、组合式换流器交流端口至直流端口的整流运行控制模式。 [0110]其中，直流预充电控制模式如图18所示，包括以下流程。 [0111]在S110中，完成第一组合模块的第一换流链的所有第一子模块从直流侧充电。 [0112]在S120中，闭合组合式换流器的启动支路的启动开关。 [0113]在S130中，依次或按一定逻辑解锁第一换流链中与启动支路并联的部分，使第二 换流链上的电压逐渐上升，完成所有第二子模块的充电。 [0114]在S140中，断开所述启动支路的启动开关。 [0115] 逆变运行控制模式如图19所示，包括以下流程。 [0116]在S210中，在直流预充电控制步骤完成后，解锁组合式换流器中第一换流链的所 有第一子模块和第二换流链的所有第二子模块。 [0117]在S220中，采集并控制组合式换流器的交流端口电压或功率。 [0118] 在S230中，若存在第二换流器，则解锁第二换流器，同时，通过第二换流器，采集并 控制第二换流器的直流端口电压或功率。 [0119] 整流运行控制模式如图20所示，包括以下流程。 [0120] 在S310中，若存在第二换流器，则解锁第二换流器，同时，通过第二换流器，采集并 控制第二换流器的交流端口电压或功率。 [0121]在S320中，完成第一换流链上所有第一子模块和第二换流链所有第二子模块的充 电。 [0122]在S330中，解锁第一组合模块的第一子模块和第二子模块。 [0123] 在S340中，采集并控制所述组合式换流器的直流端口电压或功率。 [0124]以上实施例仅为说明本申请的技术思想，不能以此限定本申请的保护范围，凡是 按照本申请提出的技术思想，在技术方案基础上所做的任何改动，均落入本申请保护范围 之内。 [EN CN113364333A]: Technical field of combined converter, DC transformer and control method [0001] This application relates to the field of power electronics application technology, and specifically relates to a combined converter, a DC transformer, and a control method. Background technique [0002] As an important component device for voltage conversion in the existing flexible power transmission grid, AC-DC converters have always been the focus of attention of scholars in the field of flexible power transmission. With the continuous popularization of DC transmission applications, converters can also achieve DC transformer functions through back-to-back connections. [0003] However, in the application of DC transformers, the prior art has the following problems. [0004] First, the structure of the existing DC transformer is divided into two-way power transmission and one-way power transmission when it transmits power. When transmitting power in one direction, the DC transformer can use a large number of uncontrolled switching devices to reduce the cost, but it cannot complete the reverse power transmission function. When transmitting power in two directions, the existing topology is often designed with the same power design capacity in both directions. However, in some special applications, the DC transformer module does not require complete operation power in both directions under the bidirectional operation. The same, so the existing scheme has a certain optimization space in the design. [0005] Second, when implementing the DC transformer function through the MMC back-to-back solution, six bridge arms are usually required, and the system has a large number of modules and high cost. In terms of cost savings, many documents have proposed non-isolated methods, but non-isolated methods have hidden dangers to fault isolation and system security. Therefore, it is necessary to provide a DC transformer that can reduce the cost and has an isolation function. [0006] Third, as the voltage level increases, the rated voltage of the high-voltage side of the DC transformer module continues to rise, which also brings challenges to the design of its auxiliary power circuit. The auxiliary power circuit is meeting certain isolation voltage and insulation voltage requirements. At the same time, it should also have high efficiency and high reliability requirements. Summary of the invention [0007] The embodiment of the present application provides a combined converter, including at least N combined modules, the combined module includes a DC port and an AC terminal D, N is a positive integer of 22; wherein, the combined module includes the first At least one of a combination module, a second combination module and a third combination module; wherein the first combination module includes a first converter chain or/and a second converter chain or/and a third converter chain, so The first converter chain is connected in parallel between the DC ports and includes M first sub-modules connected in series. The second converter chain and the third converter chain respectively include P and Q second converter chains connected in series. Sub-module, any node in the first converter chain is connected to one end of the AC port after connecting to the second converter chain, and another node in the first converter chain is directly connected or through the third converter chain. The converter chain is connected to the other end of the AC port, M is an integer of 22, P+Q = K, K is an integer of 20, and P and Q are integers of 20; the second combination module includes two or three A bridge arm, the bridge arm includes four or six groups of fully-controlled power semiconductor devices, the midpoint of the bridge arm is led out to connect to the AC port, and the ends of the bridge arms of the same polarity are connected to the DC port; The third combined module includes two or three bridge arms, the bridge arms include four or six groups of uncontrolled power semiconductor devices, the midpoint of the bridge arms is led out to connect to the AC port, and the end points of the bridge arms are the same. After the sexual connection, connect the DC port; the DC port of each combination module passes through the parallel Connected or connected in series. [0008] According to some embodiments, the combined converter includes three first combined modules, and the AC ports of the three first combined modules respectively lead to ACs A, B, and B as the combined converter. C is three-phase, and P=K, Q=0; the DC ports of the three first combined modules are cascaded to form the DC ports of the combined converter. [0009] According to some embodiments, the two nodes of the first converter chain in the first combination module select the head end and the end of the first converter chain. [0010] According to some embodiments, the combined converter includes T combined modules, the combined module includes at least one second combined module and at least one third combined module, the second combined module and the third combined module The DC ports are connected in parallel or in series, and the DC port force constituting the combined module is an integer of 21. [0011] According to some embodiments, the first sub-module and the second sub-module include a single-phase full-control half-bridge circuit or a single-phase full-control full-bridge circuit. [0012] According to some embodiments, the bridge arm of the second combined module includes a single-phase fully-controlled half-bridge circuit, or a single-phase fully-controlled full-bridge circuit, or a three-phase fully-controlled half-bridge circuit, the second combined module The fully-controlled power semiconductor device includes at least one of IGBT or MOSFET, or a series connection of IGBT or MOSFET. [0013] According to some embodiments, the bridge arm of the third combination module includes a single-phase uncontrolled full-bridge circuit, or a three-phase uncontrolled half-bridge circuit, and the uncontrolled full-bridge circuit includes a diode or a series connection of diodes. At least one. [0014] According to some embodiments, when the combination module includes a first combination module, it also includes at least one starting branch; when N21, the starting branch is connected in parallel to the first AC port and the second AC port of the combination module. Between the AC ports; or in parallel between the first AC port and the DC port of the combination module; or in parallel between the two DC ports of the combination module; or a combination of the above connection modes; when N22, all The starting branch can also be connected in parallel between the first AC ports or between the second AC ports or between the first AC port and the second AC port of different first combination modules; the starting branch includes a series-connected starting switch or / And charging resistance. [0015] According to some embodiments, the first combined module further includes at least one reactor, which is connected in series with the first converter chain. [0016] According to some embodiments, the second converter chain further includes at least one capacitor bank connected in series with the second sub-module, and the capacitor bank includes at least one capacitor connected in series/parallel . [0017] According to some embodiments, the number K of the second sub-modules in the second converter chain is determined according to the position of the combined module; when the DC positive and negative voltages of the combined converter are symmetrical, it is close to the combined The number of second sub-modules in the second converter chain of the combined module at the positive and negative ports of the type converter 2 The second sub-module in the second converter chain of the combined module near the midpoint of the positive and negative ports Number of modules; when one end of the DC positive and negative voltages of the combined converter is grounded, the number of the second sub-modules of the combined module near the non-grounded port 2 is the second of the combined module near the grounded port The number of submodules. [0018] According to some embodiments, the voltage at one end of the second and third converter chains is always higher than the voltage at the other end. [0019] According to some embodiments, the combined converter further includes a first isolation transformer, the first isolation transformer includes at least one secondary winding, and the number of secondary windings is the same as the number of the combined modules; When the number of combination modules is 1, one end of the secondary winding is connected to one end of the AC port of the combination module, and the other end of the secondary winding is connected to the DC port or the other end of the AC port of the combination module; when When the number of combined modules is greater than 1, one end of the secondary winding is connected to one end of the AC port of the combined module, and the other end of the secondary winding is shorted to each other or connected to the DC port or the AC port of the combined module another side. [0020] An embodiment of the present application also provides a DC transformer, including the combined converter and the second converter as described above, and the DC port of the combined converter forms the first part of the DC transformer. DC port; the second converter includes a DC port and an AC port, the AC port of the second converter is connected to the primary side of the first isolation transformer of the combined converter according to the phase setting; The DC port of the second converter constitutes the second DC port of the DC transformer; the second converter has the same structure as the combined converter, or is a modular multilevel converter , At least one of a single-phase fully-controlled half-bridge circuit, a single-phase fully-controlled full-bridge circuit, and a three-phase fully-controlled half-bridge circuit. [0021] The embodiments of the present application also provide a control method, which is applied to the combined converter or the DC converter as described above, and the control method includes a DC precharge control mode and a combined converter DC Port to AC port inverter operation control mode, combined converter AC port to DC port rectifier operation control mode. [0022] According to some embodiments, the DC pre-charging control mode includes: completing all first sub-modules of the first converter chain of the first combined module to be charged from the DC side; closing the startup branch of the combined converter The start switch of the circuit; unlock the part of the first converter chain that is in parallel with the start branch in sequence or according to a certain logic, so that the voltage on the second converter chain gradually rises to complete the charging of all the second sub-modules; disconnect The start switch of the start branch. [0023] According to some embodiments, the inverter operation control mode includes: after the DC precharge control step is completed, unlocking all the first sub-modules and the second converter of the first converter chain in the combined converter All the second sub-modules of the flow chain; collect and control the AC port voltage or power of the combined converter; if there is a second converter, unlock the second converter, and at the same time, pass the first The second converter collects and controls the DC port voltage or power of the second converter. [0024] According to some embodiments, the rectification operation control mode includes: if there is a second inverter, unlock the second inverter, and at the same time, collect and control the second inverter through the second inverter. AC port voltage or power of the second converter; complete charging of all first sub-modules on the first converter chain and all second sub-modules of the second converter chain; unlock the first sub-module of the first combination module And a second sub-module; collecting and controlling the DC port voltage or power of the combined converter. [0025] The technical solutions provided by the embodiments of the present application can effectively solve the two-way operation by designing the difference between the design capacity or voltage level of the full-bridge circuit based on the full-control switching device and the uncontrolled switching device in the two-way power transmission application. Where there is a difference in power, the overall equipment cost is reduced. At the same time, based on the asymmetric structure, a low-voltage full-bridge circuit can be set for auxiliary power supply design, which reduces the design requirements for auxiliary power supply. In addition, in high-voltage applications, the technical solutions provided by the embodiments of this application only add the second series of converter chains to cooperate with the first series of converter chains. Compared with the traditional MMC solution, the number of modules can be reduced under the same voltage level. , Reduce system cost. Description of the drawings [0026] In order to more clearly describe the technical solutions in the embodiments of the present application, the following will briefly introduce the drawings that need to be used in the description of the embodiments. Obviously, the drawings in the following description are only some of the present application. Embodiments, for those of ordinary skill in the art, without creative work, other drawings can be obtained based on these drawings. [0027] FIG. 1 is a schematic diagram (N=3) of a combined converter including a first combined module provided by the present application. [0028] FIG. 2 is a schematic diagram of a first combination module provided by the present application. [0029] FIG. 3 is a schematic diagram of a combined converter including a second combined module and a third combined module provided by the present application. [0030] FIG. 4 is a combination of a first combination module, a first isolation transformer and a starting branch provided by the present application Schematic diagram of a type converter (N=3). [0031] FIG. 5 is a schematic diagram of a combined converter comprising a second combined module, a third combined module and a first isolation transformer provided by the present application. [0032] FIG. 6 is a schematic diagram of a single-phase fully controlled half-bridge circuit provided by the present application. [0033] FIG. 7 is a schematic diagram of a single-phase full-control full-bridge circuit provided by the present application. [0034] FIG. 8 is a schematic diagram of a single-phase full-control full-bridge circuit provided by the present application. [0035] FIG. 9 is a schematic diagram of a three-phase fully controlled half-bridge circuit provided by the present application. [0036] FIG. 10 is a schematic diagram of a single-phase uncontrolled full-bridge circuit provided by the present application. [0037] FIG. 11 is a schematic diagram of a three-phase uncontrolled half-bridge circuit provided by the present application. [0038] FIG. 12 is a schematic diagram of a DC transformer composed of a second combination module, a third combination module and a single-phase full-control full-bridge circuit provided by the present application. [0039] FIG. 13 is a second schematic diagram of a DC transformer composed of a second combination module, a third combination module and a single-phase full-control full-bridge circuit provided by the present application. [0040] FIG. 14 is a third schematic diagram of a DC transformer composed of a second combination module, a third combination module and a single-phase full-control full-bridge circuit provided by the present application. [0041] FIG. 15 is a schematic diagram of a DC transformer (N=2) composed of a first combined module and a single-phase full-control full-bridge circuit provided by the present application. [0042] FIG. 16 is a schematic diagram (N=3) of a DC transformer composed of a first combined module and a single-phase full-control full-bridge circuit provided by the present application. [0043] FIG. 17 is a second schematic diagram (N=3) of a DC transformer composed of a first combined module and a single-phase full-control full-bridge circuit provided by the present application. [0044] FIG. 18 is a flow chart of a DC precharge control mode of a combined converter provided by the present application. [0045] FIG. 19 is a flow chart of the inverter operation control mode of a combined converter provided by the present application. [0046] FIG. 20 is a flow chart of a rectification operation control mode of a combined converter provided by the present application. Detailed ways [0047] The following will clearly and completely describe the technical solutions in the embodiments of the present application in conjunction with the drawings in the embodiments of the present application. Obviously, the described embodiments are part of the embodiments of the present application, not all of the embodiments. . Based on the embodiments in this application, all other embodiments obtained by those skilled in the art without creative work shall fall within the protection scope of this application. [0048] It should be understood that the terms "comprising" and "comprising" used in this application and in the claims indicate the existence of the described features, wholes, steps, operations, elements and/or components, but do not exclude one or more The existence or addition of other features, wholes, steps, operations, elements, components, and/or collections thereof. [0049] FIG. 1 is a schematic diagram (N=3) of a combined inverter including a first combined module provided by the present application. [0050] The combined converter includes at least N combined modules. The combination module includes a DC port and an AC port, and N is a positive integer of 22. Wherein, the combination module includes at least one of a first combination module, a second combination module, and a third combination module. The DC ports of each combination module are connected in parallel or in series. [0051] The first combined module includes a first converter chain or/and a second converter chain or/and a third converter chain. The first converter chain is connected in parallel between the DC ports and includes M first sub-modules connected in series. The second converter chain and the third converter chain include string P and Q second sub-modules connected together. Any node in the first converter chain is connected to the second converter chain and then connected to one end of the AC port. The other node in the first converter chain is directly connected or connected to the other end of the AC port through the third converter chain, M Is an integer of 22, P+Q = K, K is an integer of 20, and P and Q are integers of 20. [0052] Wherein, the number of the number K of the second sub-modules in the second converter chain is determined according to the position of the combined module. The voltage at one end of the second and third converter chains is always higher than the voltage at the other end. [0053] When the DC positive and negative voltages of the combined converter are symmetrical, the number of second sub-modules in the second converter chain of the combined module near the positive and negative ports of the combined converter 2 is close to the positive and negative ports The number of the second sub-module in the second converter chain of the combined module at the point. [0054] When one end of the DC positive and negative voltages of the combined converter is grounded, the number of second submodules of the combined module near the non-grounded port 2 is the number of second submodules of the combined module near the grounded port. [0055] Optionally, the second converter chain further includes at least one group of capacitor banks, the capacitor bank is connected in series with the second sub-module, and the capacitor bank includes at least one capacitor connected in series/parallel. [0056] According to some embodiments, the first sub-module and the second sub-module include a single-phase fully-controlled half-bridge circuit or a single-phase fully-controlled full-bridge circuit. [0057] A single-phase full-control half-bridge circuit as shown in FIG. 6 includes two full-control switching devices or a full-control switching device group connected in series. A single-phase full-control full-bridge circuit is shown in Fig. 7, and includes four full-control switching devices or groups of full-control switching devices connected in series. Another single-phase full-control full-bridge circuit is shown in Fig. 8 and includes two full-control switching devices or full
[ZH CN113190993A]: 高压大功率储能变流器电磁暂态快速仿真建模方法及系统 [EN CN113190993A]: Electromagnetic transient fast simulation modeling method and system for high-voltage high-power energy storage converter | [ZH CN113190993A]: 本发明属于变流器仿真建模领域，具体涉及了一种高压大功率储能变流器电磁暂态快速仿真建模方法及系统，旨在解决现有技术无法快速、准确地实现高压大功率储能变流器的电磁暂态仿真建模的问题。本发明包括：基于拓扑分析，进行所述高压大功率储能变流器的解耦拆分和矩阵降维，分别建立高压大功率储能变流器的储能单元、AD/DC变换器、级联H桥变流器的等效电路；分别根据各等效电路中各元件值，进行储能单元、AD/DC变换器以及级联H桥变流器的数字电磁暂态计算；基于各数字电磁暂态计算结果，获得高压大功率储能变流器的电磁暂态快速仿真模型。本发明实现了高压大功率储能变流器快速、准确的仿真建模。 [EN CN113190993A]: The invention belongs to the field of converter simulation modeling, and specifically relates to a high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method and system, and aims to solve the problem that the prior art cannot quickly and accurately realize high-voltage and high-power The problem of electromagnetic transient simulation modeling of energy storage converter. The present invention includes: based on topology analysis, decoupling and splitting and matrix dimension reduction of the high-voltage high-power energy storage converter are performed, and the energy storage unit, AD/DC converter, and AD/DC converter of the high-voltage high-power energy storage converter are respectively established The equivalent circuit of the cascaded H-bridge converter; the digital electromagnetic transient calculations of the energy storage unit, AD/DC converter and the cascaded H-bridge converter are carried out according to the value of each component in each equivalent circuit; The digital electromagnetic transient calculation results are used to obtain the electromagnetic transient fast simulation model of the high-voltage and high-power energy storage converter. The invention realizes fast and accurate simulation modeling of the high-voltage high-power energy storage converter. | CN113190993A | 2021-07-30 | CN202110459845A | 2021-04-27 | CN202110459845A, 2021-04-27 | CN113190993A: 2021-07-30 | 中国科学院电工研究所 |  | G06F30/20: I G06F30/3323: I |  |  |  | [ZH CN113190993A]: 1 .一种高压大功率储能变流器电磁暂态快速仿真建模方法，其特征在于，该方法包括： 步骤S10,基于拓扑分析，进行所述高压大功率储能变流器的解耦拆分和矩阵降维，分 别建立高压大功率储能变流器的储能单元、AD/DC变换器、级联H桥变流器的等效电路； 步骤S20，根据所述储能单元的等效电路中受控电流源^的电流值I『超级电容”的电 容值Cr电压值Ur输入电流值I3、等效内阻凡的电阻值R，限流电抗刀的电抗值^，以及薄膜 电容C2的电容值C2、电压值U2、输入电流值I2,进行所述储能单元的数字电磁暂态计算； 步骤S30，根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受控电压源 Ue2的电压值Ue2以及二极管D/口二极管D2的通断，进行所述AD/DC变换器的数字电磁暂态计 算； 步骤S40，根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值Ua1、受控 电压源Ua2的电压值Ua2，B桥臂受控电压源”曾勺电压值Ub1、受控电压源Ub2的电压值Ub2，C桥臂 受控电压源〃曾勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二极管Da2的 通断,B桥臂二极管Db1、二极管Db2的通断，C桥臂二极管Dc1、二极管Dc2的通断，进行所述级联H 桥变流器的数字电磁暂态计算； 步骤S50,基于所述储能单元、所述AD/DC变换器以及所述级联H桥变流器的数字电磁暂 态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模型。 2 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，所述储能单元，其等效电路中各元件的连接关系为： 所述受控电流源I1的电流输出端分别与所述薄膜电容C2的一端、所述限流电抗刀的一 端相连接； 所述受控电流源I1的电流输入端分别与所述薄膜电容C2的另一端、所述超级电容4的 一端相连接； 所述超级电容”的另一端与所述等效内阻人的一端相连接； 所述等效内阻RI的另一端与所述限流电抗L的另一端相连接。 3 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，所述AD/DC变换器，其等效电路中各元件连接关系为： 所述受控电压源Ue1的正极与所述二级管〃阴极相连接； 所述二级管D］阳极与所述二级管D2阴极及端子AC+相连接作为桥臂电流1a「消勺正输入 端； 所述受控电压源Ue2的正极与所述二级管d2阳极相连接； 所述受控电压源Ue1的负极与所述受控电压源Ue2的负极及端子AC-相连接作为桥臂电流 Iarm的负输入端。 4 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，所述级联H桥变流器，其等效电路中各元件连接关系为： 所述A桥臂受控电压源Ua1、受控电压源Ua2的负极，所述B桥臂受控电压源Ub1、受控电压 源Ub2的负极以及所述C桥臂受控电压源Uc1、受控电压源Uc2的负极相连接； 所述A桥臂受控电压源Ua1的正极与A桥臂二极管Da1的阳极相连接,A桥臂受控电压源Ua2 的正极与A桥臂二极管Da2的阴极相连； 所述B桥臂受控电压源”曾勺正极与B桥臂二极管Db1的阳极相连接,B桥臂受控电压源Ub2 的正极与B桥臂二极管Db2的阴极相连； 所述C桥臂受控电压源几的正极与C桥臂二极管Dc1的阳极相连，C桥臂受控电压源Uc2的 正极与C桥臂二极管Dc2的阴极相连； 所述A桥臂二极管Da1阴极、二极管Da2阳极和端子A相连； 所述B桥臂二极管Db1阴极、二极管Db2阳极和端子B相连； 所述C桥臂二极管Dc1阴极、二极管Dc2阳极和端子C相连。 5 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，步骤S20中进行所述储能单元的数字电磁暂态计算，其方法为： U1 (k+1) =U1(k)-I3(k)*Ts/C1 U2 (k+1) =U2(k)-I2(k)*Ts/C2 I2 (k+1) = I2 (k) +Ts/L1* (U1 (k+1) -I2 (k)) *R-U2 (k+1) I3 (k+1) =I1(k) -I2(k+1) 其中，k为数字离散计算的第k次值，Ts为数字离散计算的时间步长。 6 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，步骤S40中进行所述级联H桥变流器的数字电磁暂态计算，其方法为： Ux1 (k+1) =Ux_e1_1 (k) +Ux_e1_2 (k) +…+Ux_e1_N (k) Ux2 (k+1) =Ux e2 1 (k) +Ux e2 2 (k) +…+Ux e2 N (k) 其中，k为数字离散计算的第k次值,N为每个桥臂功率块个数,x = a、b、c,分别代表A桥 臂、B桥臂、C桥臂，Ux e1双为乂桥臂第N个功率模块Ue1的电压值，Ux e2双为乂桥臂第N个功率模块 Ue2的电压值。 「「 「「 7 .根据权利要求1所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，所述储能单元，其等效电路中各元件状态值与等效前的开关S］、开关S2、开关S3和开关 S4的状态之间的关系为： 当开关S］、开关S2、开关S3和开关S4都为关断状态，所述受控电流源^的电流值L为桥臂 电流Iarm的绝对值； arm 当开关S1和开关S3为开通状态、开关S2和开关S4为关断状态，所述受控电流源I1的电流 值I1为零； 当开关S1和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电流源I1的电流 值I1为零； 当开关S1和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电流源I1的电流 值I1为桥臂电流1arm； 当开关S1和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电流源I1的电流 值I1为桥臂电流1a「消勺负数。 8 .根据权利要求7所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特征 在于，所述AD/DC变换器，其等效电路中各元件状态值与等效前的开关S］、开关S2、开关S3和 开关S4的状态之间的关系为： 当开关S］、开关S2、开关S3和开关S4都为关断状态，所述受控电压源Ue1的电压值Ue1为薄 膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值与的负数； 当开关S1和开关S3为开通状态、开关S2和开关S4为关断状态，所述受控电压源Ue1的电压 值ue1为零，所述受控电压源32的电压值Ue2为零； 当开关S1和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电压源ue1的电压 值ue1为零，所述受控电压源32的电压值Ue2为零； 当开关S1和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电压源Ue1的电压 值Ue1为薄膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值u2； 当开关S1和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电压源Ue1的电压 值Ue1为薄膜电容c2的电压值a的负数，所述受控电压源Ue2的电压值32为6薄膜电容分的电 压值a的负数。 9 .根据权利要求7或8所述的高压大功率储能变流器电磁暂态快速仿真建模方法，其特 征在于，所述开关工、开关s2、开关s3和开关s4的连接关系为： 所述开关注和开关S3的集电极相连接作为受控电流源I1的电流输出端； 所述开关\和开关S4的发射极相连接作为受控电流源I1的电流输入端； 所述开关51的发射极和开关52的集电极及端子AC+相连接作为桥臂电流1a「消勺正输入 端； 所述开关S3的发射极和开关S4的集电极及端子AC-相连接作为桥臂电流1a「消勺负输入 端。 10 .一种高压大功率储能变流器电磁暂态快速仿真建模系统，其特征在于，该系统包 括： 等效电路建立模块，配置为分别建立高压大功率储能变流器的储能单元、AD/DC变换 器、级联H桥变流器的等效电路； 数字电磁暂态计算模块，包括:根据所述储能单元的等效电路中受控电流源1第勺电流值 I『超级电容4的电容值Cr电压值Ur输入电流值13、等效内阻凡的电阻值R,限流电抗刀的 电抗值L，以及薄膜电容分的电容值C2、电压值U2、输入电流值12,进行所述储能单元的数字 电磁暂态计算;根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受控电压 源Ue2的电压值Ue2以及二极管D/口二极管D2的通断，进行所述AD/DC变换器的数字电磁暂态 计算;根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值Ua1、受控电压源 Ua2的电压值Ua2,B桥臂受控电压源”声勺电压值Ub「受控电压源Ub2的电压值Ub2,C桥臂受控电 压源以曾勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二极管Da2的通断,B 桥臂二极管Db1、二极管Db2的通断,C桥臂二极管Dc1、二极管Dc2的通断,进行所述级联H桥变流 器的数字电磁暂态计算； 仿真建模模块，配置为基于所述储能单元、所述AD/DC变换器以及所述级联H桥变流器 的数字电磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模型。 [EN CN113190993A]: 1 A high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method, characterized in that the method comprises: Step S10, based on topology analysis, perform decoupling and disassembly of the high-voltage high-power energy storage converter Divide and reduce the dimension of the matrix, and establish the equivalent circuits of the energy storage unit, AD/DC converter, and cascaded H-bridge converter of the high-voltage and high-power energy storage converter; step S20, according to the energy storage unit The current value I of the controlled current source ^ in the effective circuit The capacitance value of the "super capacitor" Cr voltage value Ur input current value I3, The resistance value R of the equivalent internal resistance, the reactance value of the current-limiting reactor^, and the film capacitor C2The capacitance value C2, Voltage value U2, Input current value I2, Perform the digital electromagnetic transient calculation of the energy storage unit; step S30, according to the controlled voltage source U in the equivalent circuit of the AD/DC convertere1The voltage value Ue1, Controlled voltage source Ue2The voltage value Ue2And diode D/port diode D2Perform the digital electromagnetic transient calculation of the AD/DC converter; Step S40, according to the A-arm controlled voltage source U in the equivalent circuit of the cascaded H-bridge convertera1The voltage value Ua1, Controlled voltage source Ua2The voltage value Ua2, B bridge arm controlled voltage source "Zeng scoop voltage value Ub1, Controlled voltage source Ub2The voltage value Ub2, C bridge arm controlled voltage source Zeng scoop voltage value Uc1, Controlled voltage source Uc2The voltage value Uc2, And A bridge arm diode Da1, Diode Da2On-off, B bridge arm diode Db1, Diode Db2On and off, C bridge arm diode Dc1, Diode Dc2Perform digital electromagnetic transient calculation of the cascaded H-bridge converter; step S50, based on the digital data of the energy storage unit, the AD/DC converter, and the cascaded H-bridge converter According to the electromagnetic transient calculation result, the electromagnetic transient fast simulation model of the high-voltage and high-power energy storage converter is obtained. 2 The electromagnetic transient rapid simulation modeling method of the high-voltage and high-power energy storage converter according to claim 1, wherein the connection relationship of each element in the equivalent circuit of the energy storage unit is: The current output terminal of the controlled current source I1 is connected to the film capacitor C2One end of the current-limiting reactance knife is connected to one end; the current input end of the controlled current source I1 is connected to the film capacitor C2The other end of the super capacitor 4 is connected to one end; the other end of the super capacitor is connected to one end of the equivalent internal resistance; the other end of the equivalent internal resistance RI is connected to the current limiter The other end of the reactance L is connected. 3 The electromagnetic transient fast simulation modeling method of the high-voltage and high-power energy storage converter according to claim 1, wherein the connection relationship of the components in the equivalent circuit of the AD/DC converter is: Controlled voltage source Ue1The anode of the diode is connected to the cathode of the diode; the anode of the diode D] the anode of the diode D2The cathode and terminal AC+ are connected as the bridge arm current 1a"The positive input terminal of the elimination spoon; the controlled voltage source Ue2The anode and the diode d2The anodes are connected; the controlled voltage source Ue1And the controlled voltage source Ue2The negative pole and terminal AC-phase are connected as the bridge arm current IarmThe negative input terminal. 4 The electromagnetic transient fast simulation modeling method of the high-voltage and high-power energy storage converter according to claim 1, wherein the connection relationship of each element in the equivalent circuit of the cascaded H-bridge converter is: The A bridge arm controlled voltage source Ua1, Controlled voltage source Ua2The negative pole of the B bridge arm controlled voltage source Ub1, Controlled voltage source Ub2The negative pole of the C bridge arm and the controlled voltage source Uc1, Controlled voltage source Uc2The negative pole of the A is connected; the A bridge arm controlled voltage source Ua1The anode and A bridge arm diode Da1The anode of A is connected to the controlled voltage source U of the A bridge arma2 The anode and A bridge arm diode Da2The cathode of the B bridge arm is connected; the anode of the B bridge arm diode Db1The anode of the B bridge arm is connected to the controlled voltage source Ub2 The anode of the B bridge arm diode Db2The cathode of the C-arm controlled voltage source is connected to the C-arm diode Dc1Is connected to the anode of the C bridge arm controlled voltage source Uc2The anode of the C bridge arm diode Dc2The cathode is connected; the A bridge arm diode Da1Cathode, diode Da2The anode is connected to the terminal A; the B bridge arm diode Db1Cathode, diode Db2The anode is connected to the terminal B; the C bridge arm diode Dc1Cathode, diode Dc2The anode is connected to the terminal C. 5 The electromagnetic transient rapid simulation modeling method of the high-voltage high-power energy storage converter according to claim 1, wherein the digital electromagnetic transient calculation of the energy storage unit is performed in step S20, and the method is: U1 (k+1) =U1(k)-I3(k)*Ts/C1 U2 (k+1) =U2(k)-I2(k)*Ts/C2 I2 (k+1) = I2 (k) +Ts/L1* (U1 (k+1) -I2 (k)) *RU2 (k+1) I3 (k+1) =I1(k) -I2(k+1) where k is the kth value of digital discrete calculation, TsThe time step for digital discrete calculations. 6 The electromagnetic transient rapid simulation modeling method of the high-voltage high-power energy storage converter according to claim 1, wherein the digital electromagnetic transient calculation of the cascaded H-bridge converter is performed in step S40, which The method is: Ux1 (k+1) =Ux_e1_1 (k) +Ux_e1_2 (k) +…+Ux_e1_N (k)Ux2 (k+1) =Ux e2 1 (k) +Ux e2 2 (k) +…+Ux e2 N (k) Among them, k is the k-th value of the digital discrete calculation, N is the number of power blocks in each bridge arm, x = a, b, c, representing the A bridge arm, the B bridge arm, and the C bridge arm, respectively.x e1Double is the Nth power module U of the bridge arme1The voltage value, Ux e2Double is the Nth power module of the bridge arm Ue2The voltage value. "" "" 7 The electromagnetic transient rapid simulation modeling method of the high-voltage and high-power energy storage converter according to claim 1, wherein the energy storage unit has a state value of each element in the equivalent circuit and the switch before being equivalent. S], switch S2, Switch S3And switch S4The relationship between the states is: When switch S], switch S2, Switch S3And switch S4Are in the off state, and the current value L of the controlled current source ^ is the absolute value of the bridge arm current Iarm; arm is when the switch S1 and the switch S3Is on state, switch S2And switch S4Is the off state, the current value I1 of the controlled current source I1 is zero; when the switch S1 and the switch S3Is off, switch S2And switch S4Is the ON state, the current value I1 of the controlled current source I1 is zero; when the switch S1 and the switch S4Is on state, switch S2And switch S3In the off state, the current value I1 of the controlled current source I1 is the bridge arm current 1.arm; When switch S1 and switch S4Is off state, switch S2And switch S3Is the ON state, and the current value I1 of the controlled current source I1 is the bridge arm current 1.a"Eliminate negative numbers. 8 The electromagnetic transient rapid simulation modeling method of the high-voltage and high-power energy storage converter according to claim 7, wherein the AD/DC converter has a state value of each element in the equivalent circuit and the equivalent state value before the equivalent circuit. Switch S], switch S2, Switch S3And switch S4The relationship between the states is: When switch S], switch S2, Switch S3And switch S4Are all in the off state, the controlled voltage source Ue1The voltage value Ue1Is the voltage value U of the film capacitor"2, The controlled voltage source Ue2The voltage value Ue2Is the negative number of the voltage value and the film capacitor; when switch S1 and switch S3Is on state, switch S2And switch S4Is the off state, the controlled voltage source Ue1Voltage Value ue1Is zero, the controlled voltage source 32The voltage value Ue2Is zero; when switch S1 and switch S3Is off, switch S2And switch S4Is the on state, the controlled voltage source ue1The voltage value ue1Is zero, the controlled voltage source 32The voltage value Ue2Is zero; when switch S1 and switch S4Is on state, switch S2And switch S3Is the off state, the controlled voltage source Ue1The voltage value Ue1Is the voltage value U of the film capacitor"2, The controlled voltage source Ue2The voltage value Ue2Is the voltage value u of the film capacitor"2; When switch S1 and switch S4Is off state, switch S2And switch S3Is the on state, the controlled voltage source Ue1The voltage value Ue1Is the film capacitor c2The negative number of the voltage value a, the controlled voltage source Ue2The voltage value of 32It is the negative number of the voltage value a of 6 film capacitors. 9 The electromagnetic transient fast simulation modeling method of the high-voltage and high-power energy storage converter according to claim 7 or 8, characterized in that the switch work, the switch s2, Switch s3And switch s4The connection relationship is: The open attention and switch S3The collector is connected as the current output end of the controlled current source I1; the switch \ and the switch S4The emitter of the switch 51 is connected to the current input terminal of the controlled current source I1; the emitter of the switch 51 and the switch 52The collector and terminal AC+ are connected as the bridge arm current 1a"The positive input terminal of the elimination spoon; the switch S3Emitter and switch S4The collector and terminal AC-phase are connected as the bridge arm current 1a"Eliminate the negative input. 10 A high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling system, characterized in that the system includes: an equivalent circuit establishment module, configured to separately establish energy storage units of the high-voltage high-power energy storage converter The equivalent circuit of the AD/DC converter and the cascaded H-bridge converter; The digital electromagnetic transient calculation module includes: according to the current value I of the controlled current source 1 in the equivalent circuit of the energy storage unit The capacitance value of the super capacitor 4 Cr voltage value Ur input current value 13, The resistance value R of the equivalent internal resistance, the reactance value L of the current-limiting reactor, and the capacitance value C of the film capacitor2, Voltage value U2, Input current value 12, Perform the digital electromagnetic transient calculation of the energy storage unit; according to the controlled voltage source U in the equivalent circuit of the AD/DC convertere1The voltage value Ue1, Controlled voltage source Ue2The voltage value Ue2And diode D/port diode D2On and off, the digital electromagnetic transient calculation of the AD/DC converter is performed; according to the A bridge arm controlled voltage source U in the equivalent circuit of the cascaded H-bridge convertera1The voltage value Ua1, Controlled voltage source Ua2The voltage value Ua2, B bridge arm controlled voltage source "Sound spoon voltage value Ub"Controlled voltage source Ub2The voltage value Ub2, C bridge arm controlled voltage source is based on the voltage value Uc1, Controlled voltage source Uc2The voltage value Uc2, And A bridge arm diode Da1, Diode Da2On-off, B bridge arm diode Db1, Diode Db2On-off, C-arm diode Dc1, Diode Dc2The digital electromagnetic transient calculation of the cascaded H-bridge converter is performed; the simulation modeling module is configured to be based on the energy storage unit, the AD/DC converter, and the cascaded H-bridge converter According to the digital electromagnetic transient calculation result of the converter, the electromagnetic transient fast simulation model of the high-voltage and high-power energy storage converter is obtained. | [ZH CN113190993A]: 高压大功率储能变流器电磁暂态快速仿真建模方法及系统 技术领域 [0001]本发明属于变流器仿真建模领域，具体涉及了一种高压大功率储能变流器电磁暂 态快速仿真建模方法及系统。 背景技术 [0002]高速电磁驱动系统中变流器是对直线电机供电的关键设备，为了充分发挥直线电 机短时高速、大推力和快速可控等性能，变流器需具备大电流、高电压、宽范围变频、快速调 节、输出电能质量好和冗余性高等特点，这对变流器设备提出了较高要求。 [0003]级联H桥高压大功率储能变流器包含大容量储能单元和电力电子变换电路可满足 上述要求，为直线电机提供短时高压大功率电源。级联H桥由多个功率模块串联方式连接构 成，每个功率模块主要包含储能单元和DC/AC变换器两个环节，采用级联H桥的拓扑结构可 实现高电压和大电流输出。传统级联H桥变流器DC侧通常为薄膜电容，而级联H桥储能变流 器DC侧包含薄膜电容、滤波电感、超级电容及其内阻。为了实现高压大功率，变流器单个桥 臂中串联功率模块数量较多，导致变流器中元件多且结构复杂，较难实现高压大功率储能 变流器快速离线或者实时仿真。领域内提出了一种H桥型MMC换流器的桥臂等效电路[1]，然 而该方法仅适用H桥拓扑结构功率模块换流器的快速仿真，而高压大功率储能变流器功率 模块包括储能单元和DC/AC变换器两个环节。领域内还提出了一种平均值模型变流器建模 方法[2]，该方法只是在平均值模型基础上建立变流器模型，其无法实现级联H桥和储能单 元的电磁暂态仿真。 [0004]以下文献是与本发明相关的技术背景资料： [0005] [1]徐飞、李耀华、王平、李子欣、高范强，一种全桥结构模块化多电平换流器桥臂 等效电路，20150512，CN104866656A. [0006] [2]姜云龙、郑玉平、王小红、王志刚、侯凯、刘竞，一种谐振型双有源桥变换器建 模、降阶、设计方法、装置及系统，20180910，CN109271698A. 发明内容 [0007] 为了解决现有技术中的上述问题，即现有技术无法快速、准确地实现高压大功率 储能变流器的电磁暂态仿真建模的问题，本发明提供了一种高压大功率储能变流器电磁暂 态快速仿真建模方法，该方法包括： [0008]步骤S10，基于拓扑分析，进行所述高压大功率储能变流器的解耦拆分和矩阵降 维，分别建立高压大功率储能变流器的储能单元、AD/DC变换器、级联H桥变流器的等效电 路； [0009] 步骤S20，根据所述储能单元的等效电路中受控电流源^的电流值Ij超级电容4 的电容值“、电压值4、输入电流值I3、等效内阻凡的电阻值R，限流电抗刀的电抗值工，以及 薄膜电容C2的电容值c2、电压值u2、输入电流值i2,进行所述储能单元的数字电磁暂态计算； [0010] 步骤S30，根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受控电 压源Ue2的电压值Ue2以及二极管口1和二极管D2的通断，进行所述AD/DC变换器的数字电磁暂 态计算； [0011]步骤S40，根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值 Ua1、受控电压源Ua2的电压值Ua2，B桥臂受控电压源”曾勺电压值Ub1、受控电压源Ub2的电压值 Ub2，C桥臂受控电压源以声勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二 极管Da2的通断,B桥臂二极管Db1、二极管Db2的通断,C桥臂二极管Dc1、二极管Dc2的通断,进行 所述级联H桥变流器的数字电磁暂态计算； [0012] 步骤S50,基于所述储能单元、所述AD/DC变换器以及所述级联H桥变流器的数字电 磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模型。 [0013]在一些优选的实施例中，所述储能单元，其等效电路中各元件的连接关系为： [0014]所述受控电流源I1的电流输出端分别与所述薄膜电容C2的一端、所述限流电抗^ 的一端相连接； [0015]所述受控电流源L的电流输入端分别与所述薄膜电容C2的另一端、所述超级电容 ^的一端相连接； [0016]所述超级电容J的另一端与所述等效内阻人的一端相连接； [0017]所述等效内阻人的另一端与所述限流电抗工的另一端相连接。 [0018]在一些优选的实施例中，所述AD/DC变换器，其等效电路中各元件连接关系为： [0019] 所述受控电压源Ue1的正极与所述二级管D1阴极相连接； [0020]所述二级管〃阳极与所述二级管D2阴极及端子AC+相连接作为桥臂电流Iarm的正输 入端； [0021] 所述受控电压源Ue2的正极与所述二级管D2阳极相连接； [0022]所述受控电压源Ue1的负极与所述受控电压源Ue2的负极及端子AC-相连接作为桥 臂电流Iarm的负输入端。 [0023]在一些优选的实施例中，所述级联H桥变流器，其等效电路中各元件连接关系为： [0024] 所述A桥臂受控电压源Ua1、受控电压源Ua2的负极，所述B桥臂受控电压源Ub1、受控 电压源Ub2的负极以及所述C桥臂受控电压源Uc1、受控电压源Uc2的负极相连接； [0025]所述A桥臂受控电压源Ua1的正极与A桥臂二极管Da1的阳极相连接,A桥臂受控电压 源Ua2的正极与A桥臂二极管Da2的阴极相连； [0026]所述B桥臂受控电压源”曾勺正极与B桥臂二极管Db1的阳极相连接,B桥臂受控电压 源Ub2的正极与B桥臂二极管Db2的阴极相连； [0027]所述C桥臂受控电压源也曾勺正极与C桥臂二极管Dc1的阳极相连，C桥臂受控电压源 Uc2的正极与C桥臂二极管Dc2的阴极相连； [0028]所述A桥臂二极管Da1阴极、二极管Da2阳极和端子A相连； [0029]所述B桥臂二极管Db1阴极、二极管Db2阳极和端子B相连； [0030]所述C桥臂二极管Dc1阴极、二极管Dc2阳极和端子C相连。 [0031] 在一些优选的实施例中，步骤S20中进行所述储能单元的数字电磁暂态计算，其方 法为： [0032] U1 (k+1) =Ujk) -I3 (k) *Ts/C1 [0033] U2 (k+1) =U2 (k)-I2 (k) *Ts/C2 [0034] I2 (k+1) = I2 (k) +Ts/L1* (U1 (k+1) -I2 (k)) *R-U2 (k+1) [0035] I3(k+1) =I1(k) -I2(k+1) [0036]其中，k为数字离散计算的第k次值，Ts为数字离散计算的时间步长。 [0037] 在一些优选的实施例中，步骤S40中进行所述级联H桥变流器的数字电磁暂态计 算，其方法为： [0038] Ux1 (k+1) =Ux e1 1 (k) +Ux e1 2 (k) +…+Ux e1 N (k) [0039] Ux2 (k+1) =Ux e2 1 (k) +Ux e2 2 (k) +…+Ux e2 N (k) [0040]其中，k为数字离散计算的第k次值,N为每个桥臂功率块个数,x = a、b、c,分别代表 A桥臂、B桥臂、C桥臂，UX e1 N为x桥臂第N个功率模块Ue1的电压值，UX e2 N为x桥臂第N个功率模 块Ue2的电压值。 一 一 [0041]在一些优选的实施例中，所述储能单元，其等效电路中各元件状态值与等效前的 开关工、开关s2、开关s3和开关s4的状态之间的关系为： [0042]当开关S]、开关S2、开关S3和开关S4都为关断状态，所述受控电流源^的电流值^为 桥臂电流的绝对值； arm [0043]当开关S]和开关S3为开通状态、开关S2和开关S4为关断状态，所述受控电流源^的 电流值I1为零； [0044]当开关S]和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电流源^的 电流值I1为零； [0045]当开关S]和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电流源^的 电流值I1为桥臂电流1arm； [0046]当开关S]和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电流源^的 电流值I1为桥臂电流1a「消勺负数。 [0047]在一些优选的实施例中，所述AD/DC变换器，其等效电路中各元件状态值与等效前 的开关工、开关s2、开关s3和开关s4的状态之间的关系为： [0048]当开关S]、开关S2、开关S3和开关S4都为关断状态，所述受控电压源Ue1的电压值Ue1 为薄膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值与的负数； [0049]当开关S]和开关S3为开通状态、开关S2和开关S4为关断状态，所述受控电压源Ue1的 电压值Ue1为零，所述受控电压源Ue2的电压值Ue2为零； [0050]当开关S]和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电压源Ue1的 电压值Ue1为零，所述受控电压源Ue2的电压值Ue2为零； [0051]当开关S]和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电压源Ue1的 电压值Ue1为薄膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值 u2； [0052]当开关S]和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电压源Ue1的 电压值Ue1为薄膜电容C2的电压值a的负数，所述受控电压源Ue2的电压值Ue2为薄膜电容”的 电压值a的负数。 [0053]在一些优选的实施例中，所述开关工、开关S2、开关S3和开关S4的连接关系为： [0054]所述开关注和开关S3的集电极相连接作为受控电流源^的电流输出端； [0055]所述开关务和开关S4的发射极相连接作为受控电流源^的电流输入端； [0056]所述开关注的发射极和开关务的集电极及端子AC+相连接作为桥臂电流Iarm的正输 入端； [0057]所述开关S3的发射极和开关S4的集电极及端子AC-相连接作为桥臂电流Iarm的负输 入端。 [0058]本发明的另一方面，提出了一种高压大功率储能变流器电磁暂态快速仿真建模系 统，该系统包括： [0059]等效电路建立模块，配置为分别建立高压大功率储能变流器的储能单元、AD/DC变 换器、级联H桥变流器的等效电路； [0060]数字电磁暂态计算模块，包括:根据所述储能单元的等效电路中受控电流源^的 电流值Ij超级电容4的电容值“、电压值斗、输入电流值i3、等效内阻凡的电阻值r，限流电 抗工的电抗值Lj以及薄膜电容分的电容值c2、电压值u2、输入电流值i2,进行所述储能单元 的数字电磁暂态计算;根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受 控电压源Ue2的电压值Ue2以及二极管D/口二极管D2的通断，进行所述AD/DC变换器的数字电 磁暂态计算;根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值Ua1、受控 电压源Ua2的电压值Ua2,B桥臂受控电压源”曾勺电压值Ub1、受控电压源Ub2的电压值Ub2,C桥臂 受控电压源〃曾勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二极管Da2的 通断,B桥臂二极管Db1、二极管Db2的通断，C桥臂二极管Dc1、二极管Dc2的通断，进行所述级联H 桥变流器的数字电磁暂态计算； [0061]仿真建模模块，配置为基于所述储能单元、所述AD/DC变换器以及所述级联H桥变 流器的数字电磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模 型。 [0062] 本发明的有益效果： [0063] (1)本发明高压大功率储能变流器电磁暂态快速仿真建模方法，将结构复杂的高 压大功率储能变流器分为储能单元、AD/DC变换器以及级联H桥变流器，分别对这三部分的 等效电路进行仿真和数字电磁暂态计算，最终获得高压大功率储能变流器的电磁暂态快速 仿真模型，仿真建模效率高、实时性强。 [0064] ⑵本发明高压大功率储能变流器电磁暂态快速仿真建模方法，将高压大功率储 能变流器的复杂结构分块简化，仿真建模效果好、准确性高，同时也为领域中其他复杂结构 的器件或电路的仿真建模提供了一个研究方向。 附图说明 [0065] 通过阅读参照以下附图所作的对非限制性实施例所作的详细描述，本申请的其它 特征、目的和优点将会变得更明显： [0066]图1是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的高 压大功率储能变流器结构图； [0067]图2是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的高 压大功率储能变流器的功率模块结构图； [0068]图3是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的高 压大功率储能变流器的分块等效电路图； [0069]图4是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的变 流器输出的电压和电流波形图； [0070]图5是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的超 级电容的电压和电流波形图； [0071]图6是本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实施例的薄 膜电容的电压和电流波形图。 具体实施方式 [0072]下面结合附图和实施例对本申请作进一步的详细说明。可以理解的是，此处所描 述的具体实施例仅用于解释相关发明，而非对该发明的限定。另外还需要说明的是，为了便 于描述，附图中仅示出了与有关发明相关的部分。 [0073]需要说明的是，在不冲突的情况下，本申请中的实施例及实施例中的特征可以相 互组合。下面将参考附图并结合实施例来详细说明本申请。 [0074]本发明提供一种高压大功率储能变流器电磁暂态快速仿真建模方法，针对现有技 术中高压大功率储能变流器结构庞大且复杂，电路的节点数多且非线性器件过多，导致仿 真的矩阵维数大（电路的节点多）、电路矩阵参数变化且迭代多（非线性器件造成），从而海 量的运算量导致无法进行快速或者实时仿真，对变流器的研究和控制器验证工作带来了较 大的困难的问题，一方面，通过对变流器拓扑特点的分析，将对庞大复杂拓扑的变流器进行 解耦拆分成三个等效电路，降低了矩阵的维数，通过受控电压源和受控电流源避免了非线 性器件（开关器件）运算过程中需要迭代和改变矩阵的问题，大大降低了运算的复杂度；另 一方面，给定出离散仿真方法，该仿真的方法具有通用性，应用于matlab或者rtlab等软件 可实现快速离线或者实时仿真。 [0075]本发明的一种高压大功率储能变流器电磁暂态快速仿真建模方法，该方法包括： [0076]步骤S10，基于拓扑分析，进行所述高压大功率储能变流器的解耦拆分和矩阵降 维，分别建立高压大功率储能变流器的储能单元、AD/DC变换器、级联H桥变流器的等效电 路； [0077] 步骤S20，根据所述储能单元的等效电路中受控电流源^的电流值Ij超级电容4 的电容值“、电压值4、输入电流值I3、等效内阻凡的电阻值R，限流电抗刀的电抗值工，以及 薄膜电容C2的电容值c2、电压值u2、输入电流值i2,进行所述储能单元的数字电磁暂态计算； [0078] 步骤S30，根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受控电 压源Ue2的电压值Ue2以及二极管口]和二极管D2的通断，进行所述AD/DC变换器的数字电磁暂 态计算； [0079]步骤S40，根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值 Ua1、受控电压源Ua2的电压值Ua2，B桥臂受控电压源”1的电压值Ub1、受控电压源Ub2的电压值 Ub2，C桥臂受控电压源以声勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二 极管Da2的通断,B桥臂二极管Db1、二极管Db2的通断,C桥臂二极管Dc1、二极管Dc2的通断,进行 所述级联H桥变流器的数字电磁暂态计算； [0080] 步骤S50,基于所述储能单元、所述AD/DC变换器以及所述级联H桥变流器的数字电 磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模型。 [0081]等效电路是本发明高压大功率储能变流器建模最关键的地方，每个变流器的等效 电路都不一样，本发明通过对变流器拓扑特点的分析，对电路进行解耦拆分，将大矩阵分解 为多个小矩阵，减少仿真单个矩阵的维数，大大减少非线性元件的数量，从而也降低了的运 算量。 [0082]为了更清晰地对本发明高压大功率储能变流器电磁暂态快速仿真建模方法进行 说明，下面结合附图对本发明实施例中各步骤展开详述。 [0083]本发明第一实施例的高压大功率储能变流器电磁暂态快速仿真建模方法，包括步 骤S10-步骤S50，各步骤详细描述如下： [0084]步骤S10，基于拓扑分析，进行所述高压大功率储能变流器的解耦拆分和矩阵降 维，分别建立高压大功率储能变流器的储能单元、AD/DC变换器、级联H桥变流器的等效电 路。 [0085]如图1所示，为本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实 施例的高压大功率储能变流器结构图，以三相为例进行说明，该高压大功率储能变流器由 三个桥臂La、Lb和Lc构成，三个桥臂一端与星接点N连接，三个桥臂的另一端为输出A、B和C接 线端子与负载连接；每个桥臂由若干个功率模块串联而成，桥臂La由n个功率模块串联连 a 接，Ma1—Man，n21，桥臂Lb由n个功率模块串联连接，Mb1—Mbn,nN1，桥臂Lc由n个功率模块串 联连接,Mc1—Mcn,n21；1ma、1mb和1mc分别为三个桥臂的输出电流。 [0086]如图2所示，为本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实 施例的高压大功率储能变流器的功率模块结构图，该功率模块包括开关工、开关S2、开关S3、 开关S4、超级电容“、超级电容”的等效内阻凡、限流电抗工、薄膜电容C2。开关S1的发射极与 开关S2的集电极和端子AC+相连接，开关S3的发射极与开关S4的集电极和端子AC-相连接，开 关5]的集电极与开关S3的集电极、薄膜电容C2一端和限流电抗刀一端相连接，开关S2的发射 极与开关S4的发射极、薄膜电容C2另一端和超级电容“一端相连接，超级电容“另一端与超 级电容”的等效内阻人的一端相连接，超级电容”的等效内阻人的另一端与限流电抗工的另 一端相连接。 [0087] 步骤S20,根据所述储能单元的等效电路中受控电流源1曾勺电流值Ij超级电容4 的电容值“、电压值4、输入电流值13、等效内阻凡的电阻值R,限流电抗11的电抗值工，以及 薄膜电容”的电容值c2、电压值u2、输入电流值12,进行所述储能单元的数字电磁暂态计算。 [0088]如图3所示，为本发明高压大功率储能变流器电磁暂态快速仿真建模方法一种实 施例的高压大功率储能变流器的分块等效电路图，图3左上图为储能单元的等效电路图，其 等效电路中各元件的连接关系为： [0089]所述受控电流源I1的电流输出端分别与所述薄膜电容C2的一端、所述限流电抗11 的一端相连接； [0090]所述受控电流源L的电流输入端分别与所述薄膜电容C2的另一端、所述超级电容 ^的一端相连接； [0091]所述超级电容J的另一端与所述等效内阻人的一端相连接； [0092]所述等效内阻人的另一端与所述限流电抗工的另一端相连接。 [0093] 步骤S20中进行所述储能单元的数字电磁暂态计算，其方法如式⑴-式⑷所示： [0094] U1 (k+1) =U1 (k) -I3 (k) *Ts/C] ⑴ ［0095］ U2 (k+1) =U2 (k) -I2 (k) *Ts/C2⑵ ［0096］ I2 (k+1) = I2 (k) +Ts/L1* (U1 (k+1) -I2 (k)) *R-U2 (k+1)(3) ［0097］ I3(k+1)=I1(k) -I2 (k+1)(4) ［0098］其中，k为数字离散计算的第k次值，Ts为数字离散计算的时间步长。 ［0099］储能单元，其等效电路中各元件状态值与等效前的开关S］、开关S2、开关S3和开关 S4的状态之间的关系为： ［0100］当开关S］、开关S2、开关S3和开关S4都为关断状态，所述受控电流源^的电流值^为 桥臂电流的绝对值； arm ［0101］当开关S］和开关s3为开通状态、开关s2和开关s4为关断状态，所述受控电流源1］的 电流值I1为零； ［0102］当开关S］和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电流源1］的 电流值I1为零； ［0103］当开关S］和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电流源^的 电流值I1为桥臂电流1arm； ［0104］当开关S］和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电流源^的 电流值I1为桥臂电流1a「消勺负数。 ［0105］ 步骤S30,根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受控电 压源Ue2的电压值Ue2以及二极管口］和二极管D2的通断，进行所述AD/DC变换器的数字电磁暂 态计算。 ［0106］图3右上图为AD/DC变换器的等效电路图，其等效电路中各元件连接关系为： ［0107］ 所述受控电压源Ue1的正极与所述二级管D1阴极相连接； ［0108］所述二级管〃阳极与所述二级管D2阴极及端子AC+相连接作为桥臂电流Iarm的正输 入端； ［0109］ 所述受控电压源Ue2的正极与所述二级管D2阳极相连接； ［0110］所述受控电压源Ue1的负极与所述受控电压源Ue2的负极及端子AC-相连接作为桥 臂电流Iarm的负输入端。 ［0111］ AD/DC变换器，其等效电路中各元件状态值与等效前的开关S］、开关S2、开关S3和开 关S4的状态之间的关系为： ［0112］当开关S］、开关S2、开关S3和开关S4都为关断状态，所述受控电压源Ue1的电压值Ue1 为薄膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值与的负数； ［0113］当开关S］和开关S3为开通状态、开关S2和开关S4为关断状态，所述受控电压源Ue1的 电压值Ue1为零，所述受控电压源Ue2的电压值Ue2为零； ［0114］当开关S］和开关S3为关闭状态、开关S2和开关S4为开通状态，所述受控电压源Ue1的 电压值Ue1为零，所述受控电压源Ue2的电压值Ue2为零； ［0115］当开关S］和开关S4为开通状态、开关S2和开关S3为关断状态，所述受控电压源Ue1的 电压值Ue1为薄膜电容”的电压值U2,所述受控电压源Ue2的电压值Ue2为薄膜电容”的电压值 u2； ［0116］当开关S］和开关S4为关断状态、开关S2和开关S3为开通状态，所述受控电压源Ue1的 电压值Ue1为薄膜电容C2的电压值a的负数，所述受控电压源Ue2的电压值Ue2为薄膜电容”的 电压值a的负数。 [0117]步骤S40,根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值 Ua1、受控电压源Ua2的电压值Ua2，B桥臂受控电压源几的电压值Ub1、受控电压源Ub2的电压值 Ub2，C桥臂受控电压源以声勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二 极管Da2的通断,B桥臂二极管Db1、二极管Db2的通断,C桥臂二极管Dc1、二极管Dc2的通断,进行 所述级联H桥变流器的数字电磁暂态计算。 [0118]图3下图为级联H桥变流器的等效电路图，其等效电路中各元件连接关系为： [0119] 所述A桥臂受控电压源Ua1、受控电压源Ua2的负极，所述B桥臂受控电压源Ub1、受控 电压源Ub2的负极以及所述C桥臂受控电压源Uc1、受控电压源Uc2的负极相连接； [0120]所述A桥臂受控电压源Ua1的正极与A桥臂二极管Da1的阳极相连接,A桥臂受控电压 源Ua2的正极与A桥臂二极管Da2的阴极相连； [0121]所述B桥臂受控电压源”曾勺正极与B桥臂二极管Db1的阳极相连接,B桥臂受控电压 源Ub2的正极与B桥臂二极管Db2的阴极相连； [0122]所述C桥臂受控电压源也曾勺正极与C桥臂二极管Dc1的阳极相连，C桥臂受控电压源 Uc2的正极与C桥臂二极管Dc2的阴极相连； [0123]所述A桥臂二极管Da1阴极、二极管Da2阳极和端子A相连； [0124]所述B桥臂二极管Db1阴极、二极管Db2阳极和端子B相连； [0125]所述C桥臂二极管Dc1阴极、二极管Dc2阳极和端子C相连。 [0126] 步骤S40中进行所述级联H桥变流器的数字电磁暂态计算，其方法如式⑸和式(6) 所示： [0127] Ux1 (k+1) =Ux e1 1 (k) +Ux e1 2 (k) +…+Ux e1 N (k)⑸ [0128] Ux2 (k+1) =Ux e2 1 (k) +Ux e2 2 (k) +…+Ux e2 N (k)⑹ [0129]其中，k为数字离散计算的第k次值,N为每个桥臂功率块个数,x = a、b、c,分别代表 A桥臂、B桥臂、C桥臂，UX e1 ^x桥臂第N个功率模块Ue1的电压值，UX e2 ^x桥臂第N个功率模 块Ue2的电压值。一「 [0130] 步骤S50,基于所述储能单元、所述AD/DC变换器以及所述级联H桥变流器的数字电 磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模型。 [0131]本发明一实例的仿真系统参数如下： [0132] 超级电容^的电容值C1：8F； [0133] 超级电容^的等效内阻人的电阻值R：0.15Q； [0134] 超级电容^的初始电压：1100V； [0135]薄膜电容C2的电容值C2：30mF； [0136] 限流电抗工的电抗值工：20M [0137] 桥臂中功率模块数n：16； [0138] 开关频率：1500Hz； [0139]仿真步长：1s； [0140]根据上述参数进行高压大功率储能变流器电磁暂态快速仿真，分别获取如图4所 示的变流器输出的电压和电流波形图、如图5所示的超级电容的电压和电流波形图以及如 图6所示的薄膜电容的电压和电流波形图，仿真结果与理论分析一致验证了本发明仿真模 型的准确性。本发明在一台电脑上进行了0.37秒仿真，本发明的功率模块电磁暂态仿真模 型用时40秒，充分体了现本发明仿真模型的快速性。 [0141]上述实施例中虽然将各个步骤按照上述先后次序的方式进行了描述，但是本领域 技术人员可以理解，为了实现本实施例的效果，不同的步骤之间不必按照这样的次序执行， 其可以同时（并行）执行或以颠倒的次序执行，这些简单的变化都在本发明的保护范围之 内。 [0142]本发明第二实施例的高压大功率储能变流器电磁暂态快速仿真建模系统，该系统 包括： [0143]等效电路建立模块，配置为分别建立高压大功率储能变流器的储能单元、AD/DC变 换器、级联H桥变流器的等效电路； [0144]数字电磁暂态计算模块，包括:根据所述储能单元的等效电路中受控电流源^的 电流值Ij超级电容4的电容值“、电压值斗、输入电流值i3、等效内阻凡的电阻值r，限流电 抗工的电抗值Lj以及薄膜电容分的电容值c2、电压值u2、输入电流值i2,进行所述储能单元 的数字电磁暂态计算;根据所述AD/DC变换器的等效电路中受控电压源Ue1的电压值Ue1、受 控电压源Ue2的电压值Ue2以及二极管D/口二极管D2的通断，进行所述AD/DC变换器的数字电 磁暂态计算;根据所述级联H桥变流器的等效电路中A桥臂受控电压源Ua1的电压值Ua1、受控 电压源Ua2的电压值Ua2,B桥臂受控电压源”曾勺电压值Ub1、受控电压源Ub2的电压值Ub2,C桥臂 受控电压源〃曾勺电压值Uc1、受控电压源Uc2的电压值Uc2,以及A桥臂二极管Da1、二极管Da2的 通断,B桥臂二极管Db1、二极管Db2的通断，C桥臂二极管Dc1、二极管Dc2的通断，进行所述级联H 桥变流器的数字电磁暂态计算； [0145]仿真建模模块，配置为基于所述储能单元、所述AD/DC变换器以及所述级联H桥变 流器的数字电磁暂态计算结果，获得所述高压大功率储能变流器的电磁暂态快速仿真模 型。 [0146]所属技术领域的技术人员可以清楚地了解到，为描述的方便和简洁，上述描述的 系统的具体工作过程及有关说明，可以参考前述方法实施例中的对应过程，在此不再赘述。 [0147]需要说明的是，上述实施例提供的高压大功率储能变流器电磁暂态快速仿真建模 系统，仅以上述各功能模块的划分进行举例说明，在实际应用中，可以根据需要而将上述功 能分配由不同的功能模块来完成，即将本发明实施例中的模块或者步骤再分解或者组合， 例如，上述实施例的模块可以合并为一个模块，也可以进一步拆分成多个子模块，以完成以 上描述的全部或者部分功能。对于本发明实施例中涉及的模块、步骤的名称，仅仅是为了区 分各个模块或者步骤，不视为对本发明的不当限定。 [0148]本发明第三实施例的一种电子设备，包括： [0149] 至少一个处理器；以及 [0150]与至少一个所述处理器通信连接的存储器;其中， [0151]所述存储器存储有可被所述处理器执行的指令，所述指令用于被所述处理器执行 以实现上述的高压大功率储能变流器电磁暂态快速仿真建模方法。 [0152]本发明第四实施例的一种计算机可读存储介质，所述计算机可读存储介质存储有 计算机指令，所述计算机指令用于被所述计算机执行以实现上述的高压大功率储能变流器 电磁暂态快速仿真建模方法。 [0153]所属技术领域的技术人员可以清楚地了解到，为描述的方便和简洁，上述描述的 存储装置、处理装置的具体工作过程及有关说明，可以参考前述方法实施例中的对应过程， 在此不再赘述。 [0154]本领域技术人员应该能够意识到，结合本文中所公开的实施例描述的各示例的模 块、方法步骤，能够以电子硬件、计算机软件或者二者的结合来实现，软件模块、方法步骤对 应的程序可以置于随机存储器(RAM)、内存、只读存储器(ROM)、电可编程ROM、电可擦除可编 程ROM、寄存器、硬盘、可移动磁盘、CD-ROM、或技术领域内所公知的任意其它形式的存储介 质中。为了清楚地说明电子硬件和软件的可互换性，在上述说明中已经按照功能一般性地 描述了各示例的组成及步骤。这些功能究竟以电子硬件还是软件方式来执行，取决于技术 方案的特定应用和设计约束条件。本领域技术人员可以对每个特定的应用来使用不同方法 来实现所描述的功能，但是这种实现不应认为超出本发明的范围。 [0155]术语“第一”、“第二”等是用于区别类似的对象，而不是用于描述或表示特定的顺 序或先后次序。 [0156]术语“包括”或者任何其它类似用语旨在涵盖非排他性的包含，从而使得包括一系 列要素的过程、方法、物品或者设备/装置不仅包括那些要素，而且还包括没有明确列出的 其它要素，或者还包括这些过程、方法、物品或者设备/装置所固有的要素。 [0157]至此，已经结合附图所示的优选实施方式描述了本发明的技术方案，但是，本领域 技术人员容易理解的是，本发明的保护范围显然不局限于这些具体实施方式。在不偏离本 发明的原理的前提下，本领域技术人员可以对相关技术特征做出等同的更改或替换，这些 更改或替换之后的技术方案都将落入本发明的保护范围之内。 [EN CN113190993A]: High-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method and system technical field [0001] The present invention belongs to the field of converter simulation modeling, and specifically relates to a high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method and system. Background technique [0002] In the high-speed electromagnetic drive system, the converter is the key equipment for supplying power to the linear motor. In order to give full play to the linear motor's short-term high speed, large thrust, and fast controllability, the converter needs to have large current, high voltage, and wide range. The characteristics of range frequency conversion, fast adjustment, good output power quality and high redundancy put forward higher requirements for converter equipment. [0003] The cascaded H-bridge high-voltage high-power energy storage converter includes a large-capacity energy storage unit and a power electronic conversion circuit to meet the above requirements and provide a short-term high-voltage high-power power supply for the linear motor. The cascaded H-bridge is composed of multiple power modules connected in series. Each power module mainly contains two links: an energy storage unit and a DC/AC converter. The cascaded H-bridge topology can achieve high voltage and large current output. The DC side of a traditional cascaded H-bridge converter is usually a film capacitor, while the DC side of a cascaded H-bridge energy storage converter includes a film capacitor, a filter inductor, a super capacitor and its internal resistance. In order to achieve high-voltage and high-power, the number of series-connected power modules in a single bridge arm of the converter is large, resulting in a large number of components and a complex structure in the converter. It is difficult to achieve fast offline or real-time simulation of the high-voltage and high-power energy storage converter. A bridge arm equivalent circuit of an H-bridge type MMC converter is proposed in the field [1]. However, this method is only suitable for the fast simulation of the H-bridge topology power module converter, while the high-voltage high-power energy storage converter The power module includes two links: an energy storage unit and a DC/AC converter. An average value model converter modeling method [2] is also proposed in the field. This method only builds a converter model on the basis of the average value model. It cannot realize the electromagnetic transient state of the cascaded H-bridge and energy storage unit. simulation. [0004] The following documents are technical background information related to the present invention: [0005] [1] Xu Fei, Li Yaohua, Wang Ping, Li Zixin, Gao Fanqiang, a full-bridge structure modular multilevel converter bridge arm equivalent circuit, 20150512, CN104866656A. [0006] [2] Jiang Yunlong, Zheng Yuping, Wang Xiaohong, Wang Zhigang, Hou Kai, Liu Jing, a resonant dual active bridge converter modeling, order reduction, design method, device and system, 20180910, CN109271698A. Summary of the invention [0007] In order to solve the above-mentioned problems in the prior art, that is, the prior art cannot quickly and accurately realize the electromagnetic transient simulation modeling of high-voltage high-power energy storage converters, the present invention provides a high-voltage high-power converter. A fast electromagnetic transient simulation modeling method for an energy storage converter, the method includes: [0008] Step S10, based on the topology analysis, perform decoupling splitting and matrix dimensionality reduction of the high-voltage high-power energy storage converter, and establish the energy storage unit and AD/DC conversion of the high-voltage high-power energy storage converter respectively The equivalent circuit of the cascaded H-bridge converter; [0009] Step S20, according to the current value Ij of the controlled current source ^ in the equivalent circuit of the energy storage unit, the capacitance value of the supercapacitor 4, the voltage value 4, and the input current value I3, The equivalent internal resistance, the resistance value R, the reactance value of the current-limiting reactor, and the film capacitor C2The capacitance value c2, Voltage value u2, Input current value i2, Perform the digital electromagnetic transient calculation of the energy storage unit; [0010] Step S30, according to the controlled voltage source U in the equivalent circuit of the AD/DC convertere1The voltage value Ue1, Controlled electricity Pressure source Ue2The voltage value Ue2And diode port 1 and diode D2To perform the digital electromagnetic transient calculation of the AD/DC converter; [0011] Step S40, according to the A bridge arm controlled voltage source U in the equivalent circuit of the cascaded H-bridge convertera1The voltage value Ua1, Controlled voltage source Ua2The voltage value Ua2, B bridge arm controlled voltage source "Zeng scoop voltage value Ub1, Controlled voltage source Ub2The voltage value Ub2, The controlled voltage source of C bridge arm takes the voltage value of the sound spoon Uc1, Controlled voltage source Uc2The voltage value Uc2, And A bridge arm diode Da1, Diode Da2On-off, B bridge arm diode Db1, Diode Db2On-off, C-arm diode Dc1, Diode Dc2To perform digital electromagnetic transient calculation of the cascaded H-bridge converter; [0012] Step S50, based on the digital electromagnetic transient calculation results of the energy storage unit, the AD/DC converter, and the cascaded H-bridge converter, obtain the Electromagnetic transient fast simulation model. [0013] In some preferred embodiments, the energy storage unit, the connection relationship of each element in its equivalent circuit is: [0014] The current output terminal of the controlled current source I1 is respectively connected to the film capacitor C2Connected to one end of the current-limiting reactance ^; [0015] The current input end of the controlled current source L is respectively connected to the film capacitor C2The other end of the super capacitor ^ is connected to one end; [0016] The other end of the super capacitor J is connected to one end of the equivalent internal resistance; [0017] The other end of the equivalent internal resistance is connected to the other end of the current-limiting reactor. [0018] In some preferred embodiments, the connection relationship of the components in the equivalent circuit of the AD/DC converter is: [0019] The controlled voltage source Ue1The positive electrode of is connected to the cathode of the diode D1; [0020] The diode "anode and the diode D2The cathode and terminal AC+ are connected as the bridge arm current IarmThe positive input terminal; [0021] The controlled voltage source Ue2The positive pole and the diode D2The anode is connected; [0022] The controlled voltage source Ue1And the controlled voltage source Ue2The negative pole and the terminal AC- phase are connected as the bridge arm current IarmThe negative input terminal. [0023] In some preferred embodiments, the connection relationship of each element in the equivalent circuit of the cascaded H-bridge converter is: [0024] The A bridge arm controlled voltage source Ua1, Controlled voltage source Ua2The negative pole of the B bridge arm controlled voltage source Ub1, Controlled voltage source Ub2The negative pole of the C bridge arm and the controlled voltage source Uc1, Controlled voltage source Uc2The negative pole is connected; [0025] The A bridge arm controlled voltage source Ua1The anode and A bridge arm diode Da1The anode of A is connected, and the controlled voltage source of A bridge arm Ua2The anode and A bridge arm diode Da2The cathode is connected; [0026] The B bridge arm controlled voltage source "Zeng Shao anode and B bridge arm diode Db1The anode of the B bridge arm is connected to the controlled voltage source Ub2The anode of the B bridge arm diode Db2The cathode is connected; [0027] The C-arm controlled voltage source has also had a positive pole and C-arm diode Dc1Connected to the anode of the C bridge arm controlled voltage source Uc2The anode of the C bridge arm diode Dc2The cathode is connected; [0028] The A bridge arm diode Da1Cathode, diode Da2The anode is connected to terminal A; [0029] The B bridge arm diode Db1Cathode, diode Db2The anode is connected to terminal B; [0030] The C bridge arm diode Dc1Cathode, diode Dc2The anode is connected to the terminal C. [0031] In some preferred embodiments, the digital electromagnetic transient calculation of the energy storage unit is performed in step S20, and the method is: [0032] U1 (k+1) =Ujk) -I3 (k) *Ts/C1 [0033] U2 (k+1) =U2 (k)-I2 (k) *Ts/C2 [0034] I2 (k+1) = I2 (k) + Ts/L1* (U1 (k+1) -I2 (k)) *RU2 (k+1) [0035] I3(k+1) =I1(k) -I2(k+1) [0036] where k is the kth value of digital discrete calculation, TsThe time step for digital discrete calculations. [0037] In some preferred embodiments, the digital electromagnetic transient calculation of the cascaded H-bridge converter is performed in step S40, and the method is: [0038] Ux1 (k+1) =Ux e1 1 (k) +Ux e1 2 (k) +…+Ux e1 N (k)[0039] Ux2 (k+1) =Ux e2 1 (k) +Ux e2 2 (k) +…+Ux e2 N (k) [0040] Among them, k is the k-th value of digital discrete calculation, N is the number of power blocks in each bridge arm, x=a, b, c, respectively representing A bridge arm, B bridge arm, C bridge arm, UX e1 NIs the Nth power module U of the x bridge arme1The voltage value, UX e2 NIs the Nth power module U of the x bridge arme2The voltage value. all [0041] In some preferred embodiments, the state value of each element in the equivalent circuit of the energy storage unit is the same as the switch work and switch s before being equivalent.2, Switch s3And switch s4The relationship between the states is: [0042] When switch S], switch S2, Switch S3And switch S4All are in the off state, and the current value ^ of the controlled current source ^ is the absolute value of the bridge arm current; arm [0043] When switch S] and switch S3Is on state, switch S2And switch S4In the off state, the current value I1 of the controlled current source ^ is zero; [0044] When switch S] and switch S3Is off, switch S2And switch S4In the on state, the current value I1 of the controlled current source ^ is zero; [0045] When switch S] and switch S4Is on state, switch S2And switch S3Is the off state, the current value I1 of the controlled current source ^ is the bridge arm current 1arm； [0046] When switch S] and switch S4Is off state, switch S2And switch S3Is the ON state, and the current value I1 of the controlled current source ^ is the bridge arm current 1a"Eliminate negative numbers. [0047] In some preferred embodiments, for the AD/DC converter, the state value of each element in its equivalent circuit is the same as the switch work and switch s before the equivalent circuit.2, Switch s3And switch s4The relationship between the states is: [0048] When switch S], switch S2, Switch S3And switch S4Are all in the off state, the controlled voltage source Ue1The voltage value Ue1 Is the voltage value U of the film capacitor"2, The controlled voltage source Ue2The voltage value Ue2Is the negative number of the voltage value of the film capacitor" and [0049] When the switch S] and the switch S3Is on state, switch S2And switch S4Is the off state, the controlled voltage source Ue1The voltage value Ue1Is zero, the controlled voltage source Ue2The voltage value Ue2Zero [0050] When switch S] and switch S3Is off, switch S2And switch S4Is the on state, the controlled voltage source Ue1The voltage value Ue1Is zero, the controlled voltage source Ue2The voltage value Ue2Zero [0051] When switch S] and switch S4Is on state, switch S2And switch S3Is the off state, the controlled voltage source Ue1The voltage value Ue1Is the voltage value U of the film capacitor"2, The controlled voltage source Ue2The voltage value Ue2Is the voltage value of the film capacitor" u2； [0052] When switch S] and switch S4Is off state, switch S2And switch S3Is the on state, the controlled voltage source Ue1The voltage value Ue1Is the film capacitor C2The negative number of the voltage value a, the controlled voltage source Ue2The voltage value Ue2It is the negative number of the voltage value a of the film capacitor. [0053] In some preferred embodiments, the switch worker, the switch S2, Switch S3And switch S4The connection relationship is: [0054] The open attention and switch S3The collector is connected as the current output end of the controlled current source ^; [0055] The switch service and switch S4The emitters are connected as the current input terminals of the controlled current source ^; [0056] The focused emitter and the collector of the switching service and the terminal AC+ are connected as the bridge arm current IarmThe positive input terminal; [0057] The switch S3Emitter and switch S4The collector and terminal AC-phase are connected as the bridge arm current IarmThe negative input terminal. [0058] Another aspect of the present invention provides a high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling system, the system includes: [0059] The equivalent circuit establishment module is configured to separately establish the equivalent circuits of the energy storage unit, AD/DC converter, and cascaded H-bridge converter of the high-voltage and high-power energy storage converter; [0060] The digital electromagnetic transient calculation module includes: according to the current value of the controlled current source ^ in the equivalent circuit of the energy storage unit, the capacitance value of the super capacitor 4, the voltage value, and the input current value.3, The resistance value r of the equivalent internal resistance, the reactance value Lj of the current-limiting reactor and the capacitance value c of the film capacitor2, Voltage value u2, Input current value i2, Perform the digital electromagnetic transient calculation of the energy storage unit; according to the controlled voltage source U in the equivalent circuit of the AD/DC convertere1The voltage value Ue1, Controlled voltage source Ue2The voltage value Ue2And diode D/port diode D2On and off, the digital electromagnetic transient calculation of the AD/DC converter is performed; according to the equivalent circuit of the cascaded H-bridge converter, the A-arm controlled voltage source Ua1The voltage value Ua1, Controlled voltage source Ua2The voltage value Ua2, B bridge arm controlled voltage source "Zeng scoop voltage value Ub1, Controlled voltage source Ub2The voltage value Ub2, C bridge arm controlled voltage source Zeng scoop voltage value Uc1, Controlled voltage source Uc2The voltage value Uc2, And A bridge arm diode Da1, Diode Da2On-off, B bridge arm diode Db1, Diode Db2On and off, C bridge arm diode Dc1, Diode Dc2To perform the digital electromagnetic transient calculation of the cascaded H-bridge converter; [0061] A simulation modeling module configured to obtain the high-voltage and high-power energy storage based on the digital electromagnetic transient calculation results of the energy storage unit, the AD/DC converter, and the cascaded H-bridge converter The electromagnetic transient fast simulation model of the converter. [0062] The beneficial effects of the present invention: [0063] (1) The electromagnetic transient fast simulation modeling method of the high-voltage high-power energy storage converter of the present invention divides the high-voltage high-power energy storage converter with a complex structure into an energy storage unit, an AD/DC converter, and a stage Connect the H-bridge converter to simulate the equivalent circuit of these three parts and calculate the digital electromagnetic transient, and finally obtain the electromagnetic transient fast simulation model of the high-voltage and high-power energy storage converter. The simulation modeling efficiency is high and real-time. Strong sex. [0064] The electromagnetic transient fast simulation modeling method of the high-voltage high-power energy storage converter of the present invention simplifies the complex structure of the high-voltage high-power energy storage converter in blocks, the simulation modeling effect is good, and the accuracy is high. It also provides a research direction for the simulation modeling of devices or circuits with other complex structures in the field. Description of the drawings [0065] By reading the detailed description of the non-limiting embodiments with reference to the following drawings, other features, purposes and advantages of the present application will become more apparent: [0066] FIG. 1 is a structural diagram of an embodiment of a high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method of the present invention; [0067] FIG. 2 is a structure diagram of a power module of a high-voltage high-power energy storage converter according to an embodiment of the electromagnetic transient fast simulation modeling method of the high-voltage high-power energy storage converter of the present invention; [0068] FIG. 3 is a block equivalent circuit diagram of an embodiment of a high-voltage high-power energy storage converter electromagnetic transient fast simulation modeling method of the present invention; [0069] FIG. 4 is a voltage and current waveform diagram of the converter output according to an embodiment of the electromagnetic transient fast simulation modeling method of the high-voltage and high-power energy storage converter of the present invention; [0070] FIG. 5 is a voltage and current waveform diagram of a supercapacitor according to an embodiment of the electromagnetic transient fast simulation modeling method of the high-voltage high-power energy storage converter of the present invention; [0071] FIG. 6 is a voltage and current waveform diagram of a film capacitor in an embodiment of the electromagnetic transient fast simulation modeling method of the high-voltage high-power energy storage converter of the present invention. Detailed ways [0072] The application will be further described in detail below with reference to the drawings and embodiments. It is understandable that the specific embodiments described here are only used to explain the related invention, but not to limit the invention. In addition, it should be noted that, for ease of description, only the parts related to the relevant invention are shown in the drawings. [0073] It should be noted that the embodiments in the application and the features in the embodiments can be combined with each other if there is no conflict. Hereinafter, the present application will be described in detail with reference to the drawings and in conjunction with the embodiments. [0074] The pre
[EN WO2020248078A1]: MULTI-LEVEL VOLTAGE SOURCE PARALLEL INVERTERS AND COUPLED INDUCTORS [FR WO2020248078A1]: ONDULEURS PARALLÈLES À SOURCE DE TENSION MULTINIVEAU ET BOBINES D'INDUCTION COUPLÉES | [EN WO2020248078A1]: A power inverter for converting a DC voltage from a DC voltage source to AC voltage for a load (e.g., a motor or power grid) includes an inverter input terminal for connection to the DC voltage source, an inverter output terminal for connection to the load, at least two inverter legs connected in parallel with the inverter input terminal, and a coupled inductor assembly. The coupled inductor assembly includes at least one magnetic core, and for each one of the inverter legs, an associated pair of windings around the at least one magnetic core. Each associated pair of windings includes a first winding in series connection with the inverter leg output terminal of the one of the inverter legs, and a second winding in series opposing type connection with the first winding, and in series connection with the inverter output terminal, between the first winding and the inverter output terminal. [FR WO2020248078A1]: La présente invention concerne un onduleur de puissance pour convertir une tension continue d'une source de tension continue en une tension alternative pour une charge (par exemple, un moteur ou un réseau électrique) qui comprend une borne d'entrée d'onduleur pour la connexion à la source de tension continue, une borne de sortie d'onduleur pour la connexion à la charge, au moins deux branches d'onduleur connectées en parallèle avec la borne d'entrée d'onduleur, et un ensemble de bobines d'induction couplées. L'ensemble de bobines d'induction couplées comprend au moins un noyau magnétique, et pour chacune des branches d'onduleur, une paire associée d'enroulements autour du ou des noyaux magnétiques. Chaque paire d'enroulements associée comprend un premier enroulement en connexion en série avec la borne de sortie de branche d'onduleur de l'une des branches d'onduleur, et un second enroulement en connexion de type opposé en série avec le premier enroulement, et en connexion en série avec la borne de sortie d'onduleur, entre le premier enroulement et la borne de sortie d'onduleur. | WO2020248078A1 | 2020-12-17 | CA2020050826W | 2020-06-12 | US201962861922P, 2019-06-14 | WO2020248078A1: 2020-12-17 | UNIV ALBERTA | SALMON JOHN SINGH SUKHJIT | H02M7/5387: I H01F3/00: I H01F17/00: I | H01F27/24: I H01F27/28: I H02M7/493: I H02M7/5395: A H02M1/0064: I | US8885371B2 WO2009132427A1 |  | [EN WO2020248078A1]: CLAIMS 1. A power inverter for converting a DC voltage from a DC voltage source to AC voltage for a load: (a) an inverter input terminal for connection to the DC voltage source; (b) an inverter output terminal for connection to the load; (c) at least two inverter legs in parallel connection with the inverter input terminal, wherein each inverter leg comprises: (i) a pair of switches in series connection; (ii) for each of the switches, a diode in anti-parallel connection to the switch; (iii) an inverter leg output terminal in series connection with and between the pair of switches; and (d) a coupled inductor assembly comprising: (i) at least one magnetic core; and (ii) for each one of the inverter legs, an associated pair of windings around the at least one magnetic core and comprising: (A) a first winding in series connection with the inverter leg output terminal of the one of the inverter legs; and(B) a second winding in "series opposing type connection" with the first winding, and in series connection with the inverter output terminal, wherein the second winding is in series between the first winding and the inverter output terminal; wherein either: (iii) the at least one magnetic core comprises a single magnetic core comprising spatially separated limbs, and wherein for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated limbs; or (iv) the at least one magnetic core comprises a plurality of spatially separated magnetic cores, and wherein for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated magnetic cores; and wherein for each one of the pairs of windings, each of the first and second windings is "differentially coupled" by the at least one magnetic core with one of the windings of a different one of the pairs of windings, in respect to current flow through the windings in the direction towards the inverter output terminal. 2. The power inverter of claim 1, wherein the at least two inverter legs consists of two inverter legs. 3. The power inverter of claim 1, wherein the at least two inverter legs consists of three inverter legs. 4. The power inverter of claim 1, wherein the least two inverter legs consists of four inverter legs. 5. The power inverter of any one of claims 1 to 4, wherein the at least one magnetic core comprises the single magnetic core comprising the spatially separated limbs, and wherein for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated limbs. 6. The power inverter of any one of claims 1 to 4, wherein the at least one magnetic core comprises a plurality of spatially separated magnetic cores, and wherein, for each of the pairs of the windings, the first winding and the second winding are wound around different ones of the spatially separated magnetic cores. 7. The power inverter of any one of claims 1 to 6, wherein the at least one magnetic core has a form that defines a closed loop. 8. The power inverter of claim 7, wherein the closed loop is rectangular in shape. 9. The power inverter of claim 7, wherein the closed loop is toroidal in shape. The power inverter of claim 1 , wherein: (a) the at least two inverter legs comprises first, second, and third inverter legs; (b) the at least one magnetic core comprises the single magnetic core comprising the spatially separated limbs comprising first, second, and third limbs; (c) the pairs of windings comprise first, second, and third pairs of windings, wherein: (i) the first winding of the first pair of windings and the second winding of the second pair of windings are wound around the first limb and "differentially coupled" by the first limb in respect to current flow through the windings in the direction towards the inverter output terminal; (ii) the first winding of the second pair of windings and the second winding of the third pair of windings are wound around the second limb and "differentially coupled" by the second limb in respect to current flow through the windings in the direction towards the inverter output terminal; and (iii) the first winding of the third pair of windings and the second winding of the first pair of windings are wound around the third limb and "differentially coupled" by the third limb in respect to current flow through the windings in the direction towards the inverter output terminal. The power inverter of claim 1 , wherein: (a) the at least two inverter legs comprises first, second, and third inverter legs; (b) the at least one magnetic core comprises the plurality of spatially separate magnetic cores comprising first, second, and third magnetic cores; (c) the pairs of windings comprise first, second, and third pairs of windings, and wherein: (i) the first winding of the first pair of windings and the second winding of the third pair of windings are wound around the first magnetic core and "differentially coupled" by the first magnetic core in respect to current flow through the windings in the direction towards the inverter output terminal; (ii) the first winding of the second pair of windings and the first winding of the third pair of windings are wound around the second magnetic core and "differentially coupled" by the second magnetic core in respect to current flow through the windings in the direction towards the inverter output terminal; and (iii) the second winding of the first pair of windings and the second winding of the second pair of windings are wound around the third magnetic core and "differentially coupled" by the magnetic core in respect to current flow through the windings in the direction towards the inverter output terminal. 12. A power inverter system comprising three power inverters, wherein each of the power inverters is in accordance with any one of claims 1 to 11, and wherein the inverter input terminals of the power inverters are connected to a common DC voltage source. | [EN WO2020248078A1]: MULTI-LEVEL VOLTAGE SOURCE PARALLEL INVERTERS AND COUPLED INDUCTORS CROSS REFERENCE TO RELATED APPLICATIONS [0001] This application claims priority to U.S. Provisional Application serial no. 62/861,922 filed on June 14, 2019 and entitled MULTI-LEVEL VOLTAGE SOURCE PARALLEL INVERTERS AND COUPLED INDUCTORS, which is hereby incorporated by reference in its entirety. FIELD OF THE INVENTION [0002] The present invention relates to power inverters (i.e., electronic devices and/or circuitry for converting direct current (DC) to alternating current (AC)), and to pulse width modulation (PWM) schemes for producing modulated electronic waveforms. BACKGROUND OF THE INVENTION [0003] Power inverters (also referred to simply as inverters, or as converters) are electronic devices and/or circuits for converting direct current (DC) to alternating current (AC) for a variety of industrial applications, such as speed controllers (variable-frequency drives) for electric motors, solar or wind power generation systems, electrical charging and supply systems, and power-grid transmission inverters. Pulse width modulation (PWM) involves switching the power supply to an electronic circuit at a controlled frequency to produce a desired average voltage. A power inverter may be operated in accordance with a PWM control scheme to produce a voltage waveform consisting of numerous pulses. An inductor may be connected to the power inverter to fdter the waveform so that it has a series of discrete voltage levels, which collectively approximate a sine wave. [0004] Parallel connected inverters can be used to share current in high power 3 -phase applications and provide a modular solution for producing multilevel output voltage waveforms. Multilevel pulse width modulated (PWM) output voltage waveforms, with PWM frequencies higher than the inverter switching frequency, can be used to reduce cable and motor interaction issues as well as to reduce the size of full sinewave 3 -phase AC fdters (see reference [1]). Many different multilevel converter topologies have been proposed, such as neutral point clamped, flying capacitor, stacked multicell, and coupled inductor inverters (see references [2] -[4]). [0005] Various PWM techniques have been discussed for multilevel converters, namely sinusoidal PWM (SPWM), selective harmonic elimination (SHE), space-vector PWM (SVPWM), phase disposition (PD) and carrier interleaving techniques (see reference [5]). Parallel connected inverters can produce common mode (CM) circulating currents when using a common DC link (see reference [6]). PWM using carrier interleaving techniques using multiple phase shifted carriers can be used to lower the high frequency output current ripple by using current ripple cancellation (see references [7] and [8]). Carrier interleaving has the further advantage of reducing the size of AC passive components such as series fdter inductors in applications such as aerospace, electric vehicles, electrical AC grids, uninterruptible power systems and motor drives (see references [9] and [10]). [0006] Various solutions have been studied to reduce circulating currents between parallel connected inverters. An isolation transformer has been described (see reference [11]). A common mode choke can be used on the DC side of the converters (see reference [12]). Both of these are effective in reducing the circulating currents, but increase the size and cost of the system. Coupled inductors have been described to prevent common mode circulating currents (see references [13]-[21]). Three phase coupled inductors have been used in each phase of a 3-phase system (see reference [13]). Intercell transformers have been used in place of multi limb coupled inductors to produce a modular system that can use a wide range of inverter legs connected in parallel (see reference [14]). Coupled inductor inverters (CII) can produce multi-level PWM voltage waveforms with a very low series inductance at its output terminals and that is related to the leakage inductance of two windings on the same core or the same limb of a multi limb inductor (see reference [1]). Generally, coupled inductor topologies in AC systems produce low-frequency fundamental output currents without producing fundamental flux in the magnetic core. The size of the cores can be reduced as a result with their size being directly related to the high- frequency switch mode voltages imposed across the inductor windings and the associated high frequency magnetic flux in the core. This contrasts with series AC fdter inductors where the core size can be determined by the low frequency peak flux in the core and its saturation flux. AC fdter inductors placed at inverter output terminals can be reduced in size whilst also using multi-level voltages with high-frequency PWM voltages several times higher than the inverter switching frequency. This, in turn, can have many benefits such as lowering losses in high-speed machines, lowering motor winding voltage stresses and reducing cable interaction. High-speed machines and flywheel energy storage devices naturally have a low inductance and inverters producing multi-level voltages with high PWM frequencies can be useful in lowering the machine harmonic losses. [0007] Multi-module converters have been the subject of study over the years (see references [17]-[21]), with an emphasis on interleaved current ripple cancellation (see references [22]-[24]). Control schemes have addressed the issue of zero-sequence current (see reference [25]). The nature of the PWM scheme plays a significant role when selecting the size of output filters. PWM waveforms with finer alignment of switching edges can be produced by interleaving their switching. Parallel connected inverter legs using interleaved PWM switching can lower losses by introducing a large impedance in the path of circulating currents (see references [10] and [15]). A phase disposition scheme has been described (see reference [26]). This carrier-based scheme uses zero sequence or common mode voltages that are not represented in the line voltage. A discontinuous PWM scheme was introduced for use with a 3-limb coupled inductor (see reference [1]). The common mode voltage drop across the 3-phase inductor is reduced to zero. The inductor high frequency core and Cu losses are reduced as a result, but at the expense of using higher device switching frequencies. A space vector modulation-based PD scheme has been implemented which looks for the nearest voltage switching vector to control the differential currents (see reference [27]). However, it involves complex vector calculation and becomes more computational intensive when more than two parallel inverters are used such as massively parallel systems for high power applications. Reference [28] introduced modified PWM schemes which reduce, but not eliminate, circulating currents by modifying the switching time sequence in every switching sector. A two core coupled inductor system has been introduced in (see reference [29]) which reduces the differential mode circulating current (DMCC) and common mode circulating current (CMCC) separately. [0008] A coupled inductor inverter (CII) can be used with a 3 -limb magnetic core in a variety of 3-phase applications (see references [15], and [30]). As shown in Fig. 1, phase windings can be placed on separate limbs of a 3-limb core using a reduced switch count inverter. The inductor windings experience naturally fluctuating DC current offsets, PWM dead-times are not required and the topology has a low series output impedance. The latter is related to the low flux leakage between two windings in each phase as they are located on the same inductor limb. However, the direct voltage excitation of the two windings restricts the inverter switching patterns and high-quality output voltage PWM waveforms are not possible. As shown in Fig. 2, a 3-limb core can be used in each phase of a 3-phase system, and the Y-connection of the 3 windings alleviates restrictions on the PWM switching patterns. However, the topology suffers from a high series output impedance due to the weak coupling between windings located on separate limbs. As shown in Figs. 3 and 4, this results in a significant fundamental voltage drop across this series impedance, which also restricts this topology from being used with high fundamental output frequencies. SUMMARY OF THE INVENTION [0009] In one aspect, the present invention comprises a power inverter for converting a DC voltage from a DC voltage source to AC voltage for a load. The power inverter comprises: an inverter input terminal for connection to the DC voltage source; and an inverter output terminal for connection to the load. The power inverter comprises at least two inverter legs in parallel connection with the inverter input terminal. Each inverter leg comprises: a pair of switches in series connection; for each of the switches, a diode in anti parallel connection to the switch; and an inverter leg output terminal in series connection with and between the pair of switches. The power inverter comprises a coupled inductor assembly including: at least one magnetic core; and for each one of the inverter legs, an associated pair of windings around the at least one magnetic core. The associated pair of windings comprises: a first winding in series connection with the inverter leg output terminal of the one of the inverter legs; and a second winding in "series opposing type connection" with the first winding, and in series connection with the inverter output terminal; the second winding is in series between the first winding and the inverter output terminal. The at least one magnetic core may comprise a single magnetic core comprising spatially separated limbs; for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated limbs. Alternatively, the at least one magnetic core may comprise a plurality of spatially separated magnetic cores; for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated magnetic cores. In either case, at least one winding associated with one of the inverter legs, and at least one winding associated with a different one of the inverter legs are "differentially coupled" by one of the at least one magnetic core, in respect to current flow through the windings in the direction towards the inverter output terminal. [0010] In embodiments of the power inverter, the at least two inverter legs may consist of two inverter legs, three inverter legs, or four inverter legs. [0011] In any of the foregoing embodiments of the power inverter, the at least one magnetic core may comprise the single magnetic core comprising the spatially separated limbs; and for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated limbs. Alternatively, in any of the foregoing embodiments of the power inverter, the at least one magnetic core may comprise a plurality of spatially separated magnetic cores; and for each of the inverter legs, the first winding and the second winding are wound around different ones of the spatially separated magnetic cores. [0012] In any of the foregoing embodiments of the power inverter, the at least one magnetic core has a form that defines a closed loop. The closed loop may be either rectangular in shape, or toroidal in shape. [0013] In one embodiment of the foregoing power inverter: the at least two inverter legs comprises first, second, and third inverter legs; the single magnetic core comprises the spatially separated limbs comprising first, second, and third limbs; and the pairs of windings comprise first, second and third pairs of windings. The first winding of the first pair of windings and the second winding of the second pair of windings are wound around the first limb and "differentially coupled" by the first limb in respect to current flow through the windings in the direction towards the inverter output terminal. The first winding of the second pair of windings and the second winding of the third pair of windings are wound around the second limb and "differentially coupled" by the second limb in respect to current flow through the windings in the direction towards the inverter output terminal. The first winding of the third pair of windings and the second winding of the first pair of windings are wound around the third limb and "differentially coupled" by the third limb in respect to current flow through the windings in the direction towards the inverter output terminal. [0014] In one embodiment of the foregoing power inverter: the at least two inverter legs comprises first, second, and third inverter legs; spatially separate first, second, and third magnetic cores; the at least one magnetic core comprises the plurality of spatially separate magnetic cores comprising first, second, and third magnetic cores; and the pairs of windings comprise first, second, and third pairs of windings. The first winding of the first pair of windings and the second winding of the third pair of windings are wound around the first magnetic core and "differentially coupled" by the first magnetic core, in respect to current flow through the windings in the direction towards the inverter output terminal. The first winding of the second pair of windings and the first winding of the third pair of windings are wound around the second magnetic core and "differentially coupled" by the second magnetic core, in respect to current flow through the windings in the direction towards the inverter output terminal. The second winding of the first pair of windings and the second winding of the second pair of windings are wound around the third magnetic core and "differentially coupled" by the magnetic core, in respect to current flow through the windings in the direction towards the inverter output terminal. [0015] Without limiting the present invention, the at least one magnetic core and the windings may be configured to create a large magnetizing inductance between the inverter leg output terminals and a low series inductance at the inverter output terminal. The configuration of the power inverter may be used to the following effects: (1) to produce a multilevel output voltage with a PWM frequency higher than the inverter switching frequency, and output voltage steps less than the DC voltage source; (2) to produce high effective inductance between the inverter leg output terminals that lowers the high frequency current ripple in the inductor windings; (3) to produce a low effective inductance at the inverter output terminal so that high quality, flat, PWM voltage steps are produced; and (4) the high inductance between the inverter leg out terminals and low series output inductance keeps balanced current sharing between the inverter leg output terminals. [0016] The inverter of the present invention may be used to produce high quality multi level output voltages with a low series output inductance. The effective inverter series output impedance is designed to be very small and is determined by the low leakage inductance between windings located on the same limb, or individual cores, rather than the larger inter-limb leakage inductance in multi-limb magnetic cores. High quality multi level phase and line voltages may be produced with a very low fundamental voltage drop across the series output impedance in each phase. This makes the inverter suitable for delivering a higher fundamental voltage to the load or electrical AC grid voltage at high frequencies. This is more critical when generating very high fundamental frequencies above 400 Hz and above in the kHz range. CII topologies are validated for 3-phase systems using 3 and 4 inverter legs connected in parallel per phase. The line voltage PWM frequency produced may be 6 and 8 times the inverter switching frequency respectively. A multi-limb inductor can be used. This may be useful for 3-phase systems using 3 inverter legs and a standard 3 limb inductor per phase. Alternatively, a two-winding inductor with one core per inverter leg can be used. This may be useful for a modular inverter design where the number of inverter legs per phase can be increased to 4 or beyond. Negligible fundamental flux may be produced in the coupled inductor cores. The inductor winding voltage drops, and hence magnetic flux, have a frequency equal to the inverter switching frequency. Relatively balanced fundamental currents are produced in the parallel paths in each phase, but DC offset currents can be produced due to variations in device switching edges and on-state voltage drops. CII topologies using 3 inverter legs per phase produce 7 level PWM line voltages. CII topologies using 4 inverter legs per phase produce 9-level line voltages. The proposed topology is validated using simulation and experimental results. [0017] The multi-level inverter topology of the present invention may permit high quality multi-level output voltages with a low series output impedance. This is achieved by a combination of carrier/reference signal manipulation and using specific coupled inductor connections. Since the inverter's output impedance can be designed to be very small, a small fundamental voltage drop is experienced across the coupled inductors and high quality multi-level output voltages can be experienced in the phase and line voltages. These features may make the topology suitable for generating high frequency fundamental voltages without experiencing excessive magnetic core losses or large fundamental voltage drops. [0018] The inverter of the present invention may be implemented using modular design and a variety of commercially available "off-the-shelf magnetic cores with high magnetic flux saturation, e.g. 1.2 to 1.5 Tesla. Modularity and standard components may reduce the topology cost factor. This, with a reduced size and weight, may make the technology suitable for a wide variety of applications such as aerospace and electric vehicle industry. [0019] The present invention may be useful for inductive loads like motors and high speed generators/machines as the fdter inductors can be made very small in size. The present invention may also be useful for converting DC voltage produced by a renewable energy source (e.g., solar or wind power) to AC voltage for an AC power grid. Compared to some existing multi-level voltage topologies such as the NPC that uses a split DC rail, multi-level output voltages are obtained using a single DC rail, and the PWM frequency is much higher than the device switching frequency. Some CII topologies may remove the need for dead times, resulting in higher fundamental voltages being delivered to loads that use high fundamental frequencies. BRIEF DESCRIPTION OF THE DRAWINGS [0020] In the drawings, which form part of the specification, like elements may be assigned like reference numerals. The drawings are not necessarily to scale, with the emphasis instead placed upon the principles of the present invention. Additionally, each of the embodiments depicted are but one of a number of possible arrangements utilizing the fundamental concepts of the present invention. [0021] Fig. 1 shows a prior art 3-phase coupled inductor inverter (CII) topology with phase windings placed on separate limbs of a 3 -limb core using a reduced switch count inverter. [0022] Fig. 2 shows a prior art 3 -phase coupled inductor inverter (CII) topology with a 3-limb magnetic core used in each phase of a 3-phase system, and a Y-connection of three windings. [0023] Fig. 3 shows a prior art 4-level output voltage waveform produced by the CII topology of Fig. 2, exhibiting a voltage waveform consistent with a large output impedance related to inter-limb leakage flux. [0024] Fig. 4 shows a prior art 7-level output voltage waveform produced by the CII topology of Fig. 2, exhibiting a voltage waveform consistent with a large output impedance related to inter-limb leakage flux. [0025] Fig. 5 shows an embodiment of a coupled inductor inverter (CII) topology of the present invention, with a 3-limb magnetic core used for a 3-phase system, a Y-connection of three windings, and coupled inductor windings. [0026] Fig. 6 shows a 4-level output voltage waveform produced by the CII topology of Fig. 5. [0027] Fig. 7 shows a 7-level output line voltage waveform in a 3-phase AC system produced by the CII topology of Fig. 5. [0028] Fig. 8 shows an alternative embodiment of a coupled inductor inverter (CII) topology of the present invention, with a 2-winding coupled inductor, and 3 inverter legs per phase. [0029] Fig. 9 shows an embodiment of a system of the present invention including 3 CII topologies of Fig. 5 connected in a parallel to produce a 3 phase voltage output. [0030] Fig. 10 shows an embodiment of a toroidal magnetic core and pair of windings that can be used as a coupled inductor in CII topologies of the present invention. [0031] Fig. 11A shows a first embodiment of C-shaped magnetic cores and pair of windings that can be used as a coupled inductor in CII topologies of the present invention. Fig. 11B shows a second embodiment of C-shaped magnetic cores and pair of windings that can be used as a coupled inductor in CII topologies of the present invention. Fig. 11C shows a third embodiment of C-shaped magnetic cores and pair of winding that can be used as a coupled inductor in CII topologies of the present invention. [0032] Fig. 12 shows the fundamental current flow in the windings of a 2-winding coupled inductor of the present invention. [0033] Fig. 13 shows the flux in the magnetic core due to fundamental current flow in a 2-winding coupled inductor of the present invention. [0034] Fig. 14 shows a normalized fundamental reference signal waveform (Ref 1) with a third harmonic injection for a standard carrier interleaved PWM. [0035] Fig. 15 shows a normalized fundamental reference signal waveform (Ref 2) with a third harmonic injection for an embodiment of a PWM scheme of the present invention, with reference manipulation between -1/3 to 1/3. [0036] Fig. 16 shows an inverter output voltage using reference signals (Ref 1) of Fig. 14. [0037] Fig. 17 shows an inverter output voltage using waveform (Ref 2) of Fig. 15, between -1/3 to 1/3 only. [0038] Fig. 18 shows a cycle of 3 normalized carrier signals for 3 inverter legs per phase. [0039] Fig. 19 shows a 3 phase PWM line voltage waveform over the cycle of carrier signals shown in Fig. 18, showing that the PWM line voltage frequency is 6 times that of the carrier signal frequency. [0040] Fig. 20 shows a cycle of 4 normalized carrier signals for 4 inverter legs per phase. [0041] Fig. 21 shows a 3 phase PWM line voltage waveform over the cycle of carrier signals shown in Fig. 20, showing that the PWM line voltage frequency is 8 times that of the carrier signal frequency. [0042] Fig. 22 shows a 4-level output voltage waveform produced by the CII topology of Fig. 5. [0043] Fig. 23 shows a 7-level output voltage waveform produced by the CII topology of Fig. 5. [0044] Fig. 24 shows the inductor winding currents produced by the CII topology of Fig. 5. [0045] Fig. 25 shows the 3-phase load currents produced by the CII topology of Fig. 5. [0046] Fig. 26 shows a 5-level output line voltage waveform produced by the CII topology of Fig. 5, modified to have 4 inverter legs. [0047] Fig. 27 shows a 9-level output line voltage waveform produced by the CII topology of Fig. 5, modified to have 4 inverter legs. [0048] Fig. 28 shows the inductor winding currents produced by the CII topology of Fig. 5, modified to have 4 inverter legs. [0049] Fig. 29 shows the 3 phase load currents produced by the CII topology of Fig. 5, modified to have 4 inverter legs. [0050] Fig. 30 shows an experimental prototype CII to validate an embodiment of the system shown in Fig. 8 and Fig. 9. [0051] Fig. 31 shows an output phase current (bottom) and an output phase 4-level voltage waveform (top) produced by the prototype of Fig. 30. [0052] Fig. 32 shows a 3 phase output AC load current (bottom) and an output 7-level line voltage waveform (top) produced by the prototype of Fig. 30. [0053] Fig. 33 shows three inductor winding currents from the same phase, as produced by the prototype of Fig. 30. [0054] Fig. 34 shows conventional dot notation for an inductor with windings on a magnetic core. [0055] Figs. 35A and 35B show conventional dot notation for an inductor with windings coupled in series on a magnetic core, where the windings are in a "series opposing type connection" (Fig. 35 A), in contrast to where the windings are in a "series aiding type connection" (Fig. 35B). DETAILED DESCRIPTION OF EMBODIMENTS OF THE INVENTION [0056] Definitions. [0057] Any term or expression not expressly defined herein shall have its commonly accepted definition understood by a person skilled in the art. [0058] For clarity, it will be understood that "winding" refers to a conductive lead (e.g., a wire) wound around a magnetic core a plurality of times such that the conductive lead has the form of a coil. [0059] Circuit topologies. [0060] In drawings showing electronic circuit topologies or components thereof (including Figs. 1, 2, 5, 8, 9, 10, 11, 12, 13, 34, 35A, 35B), elements are illustrated with conventional electronic circuit symbols as understood by persons of ordinary skill in the art. [0061] Conventional dot notation as shown in Figure 34, as will be understood by persons of ordinary skill in the art, is used to indicate voltage polarity in coupled windings of coupled inductors. The voltage at the dotted terminal of each winding (340, 342) with respect to its own non-dotted terminal have the same polarity. That is, if current enters the dotted terminal of one winding (340), then it induces a positive flux in the magnetic core (72). Conversely, if current leaves from the dotted terminal of winding (340), then it induces a negative flux in the magnetic core (72). Fig. 34 can illustrate this dot notation for two cases, which are dependent on the chirality of the windings (340, 342) about the magnetic core (72), from the perspective of current flow through them. In one case, the two windings are considered "cumulatively coupled" if currents flows into both dotted ends. As used herein, "cumulatively coupled", refers to the chirality of the windings (340, 342) about the core (72) being configured such that the magnetic flux induced in the core (72) by the current flow through the windings (340, 342) are additive. In another case, if currents flow out of the dot of one winding (340) and into the dot of the other winding (342) then they are "differentially coupled". As used herein, "differentially coupled", refers to the chirality of the windings (340, 342) about the core (72) being configured such that the magnetic flux induced in the core (72) by the current flow through the windings (340, 342) are opposed in polarity, or subtractive. [0062] Conventional dot notation, as will be understood by persons of ordinary skill in the art, is also used to indicate polarity of magnetic fields induced in magnetic core by current flowing through coupled windings of inductors in series. Figs. 35A and 35B illustrate this dot notation for two cases, which are differentiated by the chirality of the windings (350, 352) about the magnetic core (72), from the perspective of current flow through them. Fig. 35A shows dot notation for the case of windings in a "series opposing type connection." As used herein, "series opposing type connection" refers to the chirality of the windings (350, 352) about the core (72) being configured such that the magnetic flux induced in the core (72) by current flow through the first winding (350) is opposed (i.e., subtractive or differential) to the magnetic flux induced in the core (72) by current flow through the second winding (352), and vice versa. In other words, the electromotive force (EMF) induced in the second winding (352) by the mutual inductance of the first winding (350) is opposed to the self-induced EMF in the second winding (352), and vice versa. Conversely, Fig. 35B shows dot notation for the case of windings in "series aiding type connection." As used herein "series aiding type connection" refers to the direction of the windings (350, 352) about the core (72) being configured such that the magnetic flux induced in core (72) by current flow through the first winding (352) is additive or cumulative to the magnetic flux induced in the core (72) by current flow through the second winding (352), and vice versa. In other words, the electromotive force (EMF) induced in the second winding (352) by the mutual inductance of the first winding (350) is additive or cumulative to the self-induced EMF in the second winding (352), and vice versa. [0063] Multi-limb CII topology. [0064] Fig. 5 shows the topology of an embodiment of a coupled inductor inverter (CII) (i.e., power inverter) of the present invention. The inverter (10) includes an inverter input terminal (12) for connection to a DC power source (14). The inverter input terminal (12) has a positive bus (16) (i.e. a conductive lead) and a negative bus (18) (i.e., another conductive lead) connected in parallel to three inverter legs (20, 22, 24). Each of the three legs (20, 22, 24) includes a pair of switches (26, 28; 30, 32; 34, 36) connected in series. For convenience of reference to Fig. 5, the switches within each pair are referred to as an "upper" switch (26, 30, 34) and a "lower" switch (28, 32, 36), but it will be understood that the terms "upper" and "lower" do not limit any relative vertical position of the switches. Each of the switches (26, 28, 30, 32, 34, 36) may be an electromechanical or semiconductor device, as known to persons skilled in the art, such as a transistor. Each of the switches (26, 28, 30, 32, 34, 36) is connected in anti-parallel to a diode (38, 40, 42, 44, 46, 48), which may be an electromechanical or semiconductor device, as known to persons skilled in the art. (As used herein "anti-parallel" connection means the switch and diode are connected in parallel, but with their polarities reversed.) As appreciated by persons of ordinary skill in the art, the diode (38, 40, 42, 44, 46, 48) provides an alternative current path for an inductive load when one of the paired switches is in an "off state (i.e., the switch is open so as to prevent conduction of electrical current through the switch). Each inverter leg (20, 22, 24) also includes an inverter leg output terminal (50, 52, 54) connected in series between its pair of switches (26, 28; 30, 32; 34, 36). The inverter (10) also includes a coupled inductor assembly including three pairs of conductive windings (56, 58; 60, 62; 64, 66). The first winding (56, 60, 64) of each pair is connected to the first, second, and third inverter leg output terminal (50, 52, 54), respectively. The second winding (58, 62, 66) of each pair is connected in series with the first winding (56, 60, 64) of the pair. As shown by the dot notation in Fig. 5, the electrical coupling of the first windings (56, 60, 64) and their respective second windings (58, 62, 66) is of the "series opposing type connection" rather than of the "series aiding type connection". The second winding (58, 62, 66) of each pair is also connected in series by a Y-connection (68) to a common inverter output terminal (70), which is used for connection to a load (not shown). "Load", as used herein, refers to one or more electrical devices and/or circuits that receive electric power via the inverter output terminal (70). As a non-limiting examples, the load may be a motor or an electric AC power grid or components thereof. The windings are wound around a multi-limb magnetic core (72) in a configuration to produce a magnetizing inductance between the inverter leg output terminals (50, 52, 54), and a low series inductance at the Y-connection (68), meaning that the inductance of the inverter (10) as a whole from the inverter input terminal (12) to the output terminal (70) is relatively low in value. [0065] This winding configuration is similar to a zig-zag connected 3-phase grounding transforme
[JA JP6926355B1]: 電力変換装置 [EN JP6926355B1]: Power converter | [JA JP6926355B1]: 電力変換装置(100)は、交流回路(2)と直流回路(4)との間で電力変換を行なう自励式電力変換器(6)と、自励式電力変換器(6)に含まれるスイッチング素子(1a,1b)のスイッチング動作を制御する制御装置(5)とを備える。制御装置(5)は、自励式電力変換器(6)に対する制御指令値と、自励式電力変換器(6)からのフィードバック値との偏差を算出し、偏差が第1閾値以上になった場合に、スイッチング素子(1a,1b)のスイッチング周波数を増大させる第1制御を実行する。 [EN JP6926355B1]: The power converter (100) is a self-excited power converter (6) that converts power between an AC circuit (2) and a DC circuit (4), and a switching element included in the self-excited power converter (6). It is equipped with a control device (5) that controls the switching operation of (1a, 1b). The control device (5) calculates the deviation between the control command value for the self-excited power converter (6) and the feedback value from the self-excited power converter (6), and when the deviation exceeds the first threshold value. First, the first control for increasing the switching frequency of the switching elements (1a, 1b) is executed. | JP6926355B1 | 2021-08-25 | JP2021510234A | 2020-09-29 | JP2020036960W, 2020-09-29 | JP6926355B1: 2021-08-25 | 三菱電機株式会社 |  | H02M7/49: I H02M7/48: I |  |  |  | [JA JP6926355B1]: 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記制御指令値は、前記自励式電力変換器から出力される無効電流に対する無効電流指令値であり、 前記フィードバック値は、前記交流回路における交流電流および交流電圧に基づいて算出される無効電流値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記制御指令値は、前記自励式電力変換器から出力される有効電流に対する有効電流指令値であり、 前記フィードバック値は、前記交流回路における交流電流および交流電圧に基づいて算出される有効電流値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記制御指令値は、前記交流回路の系統電圧に対する系統電圧指令値であり、 前記フィードバック値は、前記交流回路の系統電圧値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記自励式電力変換器は、複数のレグ回路を含み、 各前記レグ回路は、互いにカスケード接続された複数の変換器セルを含み、各前記変換器セルは、キャパシタと前記スイッチング素子とを含み、 前記制御指令値は、前記キャパシタの電圧に対する指令値であり、 前記フィードバック値は、前記キャパシタにおいて検出されたキャパシタ電圧実測値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記制御指令値は、前記自励式電力変換器から出力される無効電力に対する無効電力指令値であり、 前記フィードバック値は、前記交流回路における交流電流および交流電圧に基づいて算出される無効電力値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記自励式電力変換器は、複数のレグ回路を含み、 各前記レグ回路は、互いにカスケード接続された複数の変換器セルを含み、各前記変換器セルは、キャパシタと前記スイッチング素子とを含み、 前記制御指令値は、前記自励式電力変換器に含まれる全キャパシタの電圧平均値について与えられた指令値であり、 前記フィードバック値は、前記全キャパシタの電圧平均値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記自励式電力変換器は、複数のレグ回路を含み、 各前記レグ回路は、互いにカスケード接続された複数の変換器セルを含み、各前記変換器セルは、キャパシタと前記スイッチング素子とを含み、 前記制御指令値は、前記自励式電力変換器に含まれる全キャパシタの電圧平均値であり、 前記フィードバック値は、前記レグ回路に含まれる全キャパシタの電圧平均値である、電力変換装置。 交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、 前記自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備え、 前記制御装置は、 前記自励式電力変換器に対する制御指令値と、前記自励式電力変換器からのフィードバック値との偏差を算出し、 前記偏差が第1閾値以上になった場合に、前記スイッチング素子のスイッチング周波数を増大させる第1制御を実行し、 前記自励式電力変換器は、複数のレグ回路を含み、 各前記レグ回路は、互いにカスケード接続された複数の変換器セルを含み、各前記変換器セルは、キャパシタと前記スイッチング素子とを含み、 前記制御指令値は、前記レグ回路の正側アームに含まれる各キャパシタの電圧平均値であり、 前記フィードバック値は、前記レグ回路の負側アームに含まれる各キャパシタの電圧平均値である、電力変換装置。 [EN JP6926355B1]: A self-excited power converter that converts power between an AC circuit and a DC circuit and a control device that controls the switching operation of a switching element included in the self-excited power converter are provided, and the control device is the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or more than the first threshold value, the switching frequency of the switching element is increased. 1 Control is executed, and the control command value isFor reactive current output from the self-excited power converterA reactive current command value, wherein the feedback value is a reactive current value calculated based on an AC current and an AC voltage in the AC circuit. A self-excited power converter that converts power between an AC circuit and a DC circuit and a control device that controls the switching operation of a switching element included in the self-excited power converter are provided, and the control device is the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or more than the first threshold value, the switching frequency of the switching element is increased. 1 Control is executed, and the control command value isFor the active current output from the self-excited power converterA power conversion device, which is an effective current command value, and the feedback value is an effective current value calculated based on an AC current and an AC voltage in the AC circuit. A self-excited power converter that converts power between an AC circuit and a DC circuit and a control device that controls the switching operation of a switching element included in the self-excited power converter are provided, and the control device is the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or more than the first threshold value, the switching frequency of the switching element is increased. 1 Control is executed, and the control command value isWith respect to the system voltage of the AC circuitA power conversion device that is a system voltage command value, and the feedback value is a system voltage value of the AC circuit. It includes a self-excited power converter that converts power between an AC circuit and a DC circuit, and a control device that controls the switching operation of the switching element included in the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or higher than the first threshold value, the switching frequency of the switching element is increased. Performing one control, the self-excited power converter comprises a plurality of leg circuits, each said leg circuit includes a plurality of converter cells cascaded to each other, and each said converter cell includes a capacitor and said. The control command value includes a switching element.With respect to the voltage of the capacitorA power conversion device, which is a command value, and the feedback value is a measured capacitor voltage value detected in the capacitor. A self-excited power converter that converts power between an AC circuit and a DC circuit and a control device that controls the switching operation of a switching element included in the self-excited power converter are provided, and the control device is the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or more than the first threshold value, the switching frequency of the switching element is increased. 1 Control is executed, and the control command value isFor the reactive power output from the self-excited power converterA power conversion device, which is an invalid power command value, and the feedback value is an invalid power value calculated based on an AC current and an AC voltage in the AC circuit. It includes a self-excited power converter that converts power between an AC circuit and a DC circuit, and a control device that controls the switching operation of the switching element included in the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or higher than the first threshold value, the switching frequency of the switching element is increased. Performing one control, the self-excited power converter comprises a plurality of leg circuits, each said leg circuit includes a plurality of converter cells cascaded to each other, and each said converter cell includes a capacitor and said. The control command value including the switching element is a command value given for the voltage average value of all the capacitors included in the self-excited power converter, and the feedback value is the voltage average value of all the capacitors. , Power converter. It includes a self-excited power converter that converts power between an AC circuit and a DC circuit, and a control device that controls the switching operation of the switching element included in the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or higher than the first threshold value, the switching frequency of the switching element is increased. Performing one control, the self-excited power converter comprises a plurality of leg circuits, each said leg circuit includes a plurality of converter cells cascaded to each other, and each said converter cell includes a capacitor and said. The control command value includes a switching element, the control command value is a voltage average value of all capacitors included in the self-excited power converter, and the feedback value is a voltage average value of all capacitors included in the leg circuit. Power converter. It includes a self-excited power converter that converts power between an AC circuit and a DC circuit, and a control device that controls the switching operation of the switching element included in the self-excited power converter. The deviation between the control command value for the excited power converter and the feedback value from the self-excited power converter is calculated, and when the deviation becomes equal to or higher than the first threshold value, the switching frequency of the switching element is increased. Performing one control, the self-excited power converter comprises a plurality of leg circuits, each said leg circuit includes a plurality of converter cells cascaded to each other, and each said converter cell includes a capacitor and said. The control command value includes a switching element, the control command value is the voltage average value of each capacitor included in the positive arm of the leg circuit, and the feedback value is the voltage of each capacitor included in the negative arm of the leg circuit. A power converter that is an average value. | [JA JP6926355B1]: 本開示は、電力変換装置に関する。 電力系統に設置される大容量の電力変換装置として、モジュラーマルチレベル変換器(MMC:Modular Multilevel Converter)が知られている。複数の単位変換器がカスケード接続されるモジュラーマルチレベル変換器は、単位変換器の数を増加させることによって、高電圧化に容易に対応することができる。「単位変換器」は、「サブモジュール(sub module)」あるいは「変換器セル」とも称される。 特開2018-133950号公報(特許文献1)は、直流電圧と交流電圧との間で双方向に電力を変換可能な電力変換装置を開示している。電力変換装置は、交流電圧の絶対値がしきい値電圧の絶対値以上の場合に、第1周波数を有する第1キャリア信号を出力し、交流電圧の絶対値が第1しきい値電圧の絶対値よりも低い場合に、第1周波数よりも高い第2周波数を有する第2キャリア信号を出力するように構成される。 特開2018-133950号公報 特許文献1では、上記のように、交流電圧の絶対値に応じてキャリア信号の周波数を変更することによりスイッチング動作の周波数を変更して、交流側に地絡が生じた場合であっても電力変換装置の運転を継続することを検討している。しかしながら、特許文献1では、交流側に地絡が生じた場合以外のスイッチング周波数の変更については十分に考慮されておらず、電力変換装置の運転の安定化という点において改善の余地がある。 本開示のある局面における目的は、適切なタイミングでスイッチング周波数を増大させることで運転を安定化させることが可能な電力変換装置を提供することである。本開示のその他の目的及び特徴については実施の形態において明らかにする。 ある実施の形態に従う電力変換装置は、交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備える。制御装置は、自励式電力変換器に対する制御指令値と、自励式電力変換器からのフィードバック値との偏差を算出し、偏差が第1閾値以上になった場合に、スイッチング素子のスイッチング周波数を増大させる第1制御を実行する。 他の実施の形態に従う電力変換装置は、交流回路と直流回路との間で電力変換を行なう自励式電力変換器と、自励式電力変換器に含まれるスイッチング素子のスイッチング動作を制御する制御装置とを備える。制御装置は、自励式電力変換器に対する制御指令値の変化率が基準変化率以上になった場合に、スイッチング素子のスイッチング周波数を増大させる制御を実行する。 本開示に係る電力変換装置によれば、適切なタイミングでスイッチング周波数を増大させることで運転を安定化させることができる。 電力変換装置の概略構成図である。 変換器セルの構成例を示すブロック図である。 変換器セルの主回路の変形例を示す回路図である。 制御装置の全体構成を示すブロック図である。 制御装置のハードウェア構成の一例を示すブロック図である。 アーム共通制御器の動作を示すブロック図である。 アーム共通制御器における交流制御部35の動作を説明するための図である。 系統電圧制御器を説明するための図である。 アーム共通制御器における直流制御部36の動作を説明するための図である。 u相アーム制御器の動作を示すブロック図である。 正側アーム用のセル個別制御器の動作を示すブロック図である。 実施の形態1に従う周波数切替部の動作を説明するための図である。 実施の形態1の変形例1に従う周波数切替部の動作を説明するための図である。 実施の形態1の変形例2に従う周波数切替部の動作を説明するための図である。 実施の形態1の変形例3に従うスイッチング周波数の増大方式を説明するための図である。 実施の形態2に従う周波数切替部の動作を説明するための図である。 以下、図面を参照しつつ、本実施の形態について説明する。以下の説明では、同一の部品には同一の符号を付してある。それらの名称および機能も同じである。したがって、それらについての詳細な説明は繰り返さない。 実施の形態1. &lt;電力変換装置の概略構成&gt; 図1は、電力変換装置100の概略構成図である。電力変換装置100は、例えば、高圧直流送電に用いられる電力変換装置、または周波数変換器における順変換用もしくは逆変換用の電力変換装置を示す。 図1を参照して、電力変換装置100は、交流回路2と直流回路4との間で電力変換を行なう自励式の電力変換器6と、制御装置5とを含む。典型的には、電力変換器6は、互いに直列接続された複数の変換器セル1を含むMMC変換方式の電力変換器によって構成される。ただし、電力変換器6は、MMC変換方式以外の変換方式であってもよい。電力変換器6は、正側の直流端子(すなわち、高電位側直流端子)Npと、負側の直流端子(すなわち、低電位側直流端子)Nnとの間に互いに並列に接続された複数のレグ回路8u,8v,8w(以下、総称する場合または任意のものを示す場合、「レグ回路8」と記載する)を含む。 制御装置5は、これらのレグ回路8に含まれるスイッチング素子のスイッチング動作を制御する。詳細は後述するが、制御装置5は、電力変換器6の運転安定化と電力変換効率とを鑑みて、各種条件に従ってスイッチング素子のスイッチング周波数を適宜変更する。 レグ回路8は、多相交流の各相ごとに設けられ、交流回路2と直流回路4との間に接続され、両回路間で電力変換を行なう。図1には交流回路2が三相交流の場合が示されており、u相、v相、w相にそれぞれ対応して3個のレグ回路8u,8v,8wが設けられる。なお、交流回路2が単相交流の場合には、2個のレグ回路が設けられる。 レグ回路8u,8v,8wにそれぞれ設けられた交流端子Nu,Nv,Nwは、変圧器3を介して交流回路2に接続される。交流回路2は、例えば、交流電源などを含む交流電力系統である。図1では、図解を容易にするために、交流端子Nv,Nwと変圧器3との接続は図示していない。各レグ回路8に共通に設けられた直流端子(すなわち、正側直流端子Np,負側直流端子Nn)は、直流回路4に接続される。直流回路4は、例えば、直流送電網および直流出力を行なう他の電力変換装置などを含む直流電力系統である。 図1の変圧器3を用いる代わりに、レグ回路8u,8v,8wは、連系リアクトルを介して交流回路2に接続した構成としてもよい。さらに、交流端子Nu,Nv,Nwに代えてレグ回路8u,8v,8wにそれぞれ一次巻線を設け、この一次巻線と磁気結合する二次巻線を介してレグ回路8u,8v,8wが変圧器3または連系リアクトルに交流的に接続するようにしてもよい。この場合、一次巻線を下記のリアクトル7a,7bとしてもよい。すなわち、レグ回路8は、交流端子Nu,Nv,Nwまたは上記の一次巻線など、各レグ回路8u,8v,8wに設けられた接続部を介して電気的(すなわち、直流的または交流的)に交流回路2に接続される。 レグ回路8uは、正側直流端子Npから交流端子Nuまでの正側アーム13uと、負側直流端子Nnから交流端子Nuまでの負側アーム14uとに区分される。正側アーム13uと負側アーム14uとの接続点が、交流端子Nuとして変圧器3と接続される。正側直流端子Npおよび負側直流端子Nnが直流回路4に接続される。レグ回路8vは正側アーム13vと負側アーム14vとを含み、レグ回路8wは正側アーム13wと負側アーム14wとを含む。レグ回路8v,8wはレグ回路8uと同様の構成を有しているので、以下、レグ回路8uを代表として説明する。 レグ回路8uにおいて、正側アーム13uは、カスケード接続された複数の変換器セル1と、リアクトル7aとを含む。複数の変換器セル1とリアクトル7aとは互いに直列接続されている。負側アーム14uは、カスケード接続された複数の変換器セル1と、リアクトル7bとを含む。複数の変換器セル1とリアクトル7bとは互いに直列接続されている。 リアクトル7aが挿入される位置は、正側アーム13uのいずれの位置であってもよく、リアクトル7bが挿入される位置は、負側アーム14uのいずれの位置であってもよい。リアクトル7a,7bはそれぞれ複数個あってもよい。各リアクトルのインダクタンス値は互いに異なっていてもよい。さらに、正側アーム13uのリアクトル7aのみ、もしくは、負側アーム14uのリアクトル7bのみを設けてもよい。 電力変換装置100は、さらに、交流電圧検出器10と、交流電流検出器15と、直流電圧検出器11a,11bと、各レグ回路8に設けられたアーム電流検出器9a,9bとを含む。これらの検出器は、電力変換装置100の制御に使用される電気量(すなわち、電流、電圧)を計測する。これらの検出器によって検出された信号は、制御装置5に入力される。 具体的には、交流電圧検出器10は、交流回路2のu相の交流電圧実測値Vacu、v相の交流電圧実測値Vacv、およびw相の交流電圧実測値Vacwを検出する。交流電流検出器15は、交流回路2のu相、v相、w相にそれぞれ設けられ、各相の交流電流実測値を検出する。直流電圧検出器11aは、直流回路4に接続された正側直流端子Npの直流電圧実測値Vdcpを検出する。直流電圧検出器11bは、直流回路4に接続された負側直流端子Nnの直流電圧実測値Vdcnを検出する。 u相用のレグ回路8uに設けられたアーム電流検出器9a,9bは、正側アーム13uに流れる正側アーム電流実測値Iupおよび負側アーム14uに流れる負側アーム電流実測値Iunをそれぞれ検出する。v相用のレグ回路8vに設けられたアーム電流検出器9a,9bは、正側アーム電流実測値Ivpおよび負側アーム電流実測値Ivnをそれぞれ検出する。w相用のレグ回路8wに設けられたアーム電流検出器9a,9bは、正側アーム電流実測値Iwpおよび負側アーム電流実測値Iwnをそれぞれ検出する。ここで、各正側アーム電流実測値Iup,Ivp,Iwpおよび負側アーム電流実測値Iun,Ivn,Iwnは、正側直流端子Npから負側直流端子Nnの方向に流れる電流を正とする。 &lt;変換器セルの構成&gt; 図2は、変換器セル1の構成例を示すブロック図である。図2を参照して、一例としての変換器セル1は、セル主回路60Hと、セル個別制御器61と、通信装置62とを含む。図2では、ハーフブリッジ型のセル主回路60Hの構成が示されている。図3を参照して後述するように、セル主回路60Hに代えて他の構成のブリッジ回路を用いてもよい。 図2に示すように、セル主回路60Hは、互いに直列接続されたスイッチング素子1a,1bと、ダイオード1c,1dと、エネルギー蓄積器としてのキャパシタ1eとを含む。ダイオード1c,1dは、スイッチング素子1a,1bとそれぞれ逆並列(すなわち、並列かつ逆バイアス方向)に接続される。キャパシタ1eは、スイッチング素子1a,1bの直列接続回路と並列に接続され、直流電圧を平滑化する。スイッチング素子1a,1bの接続ノードは正側の入出力端子1pと接続され、スイッチング素子1bとキャパシタ1eの接続ノードは負側の入出力端子1nと接続される。 セル主回路60Hにおいて、スイッチング素子1a,1bは、一方がオン状態となり他方がオフ状態となるように制御される。スイッチング素子1aがオン状態であり、スイッチング素子1bがオフ状態のとき、入出力端子1p,1n間にはキャパシタ1eの両端間の電圧が印加される。この場合、入出力端子1pが正側電圧となり、入出力端子1nが負側電圧となる。一方、スイッチング素子1aがオフ状態であり、スイッチング素子1bがオン状態のとき、入出力端子1p,1n間は0Vとなる。このように、セル主回路60Hは、スイッチング素子1a,1bを交互にオン状態とすることによって、零電圧または正電圧を出力できる。正電圧の大きさは、キャパシタ1eの電圧に依存する。ダイオード1c,1dは、スイッチング素子1a,1bに逆方向電圧が印加されたときの保護のために設けられている。 セル個別制御器61は、制御装置5から受信したアーム電圧指令値および循環電圧指令値に基づいて、セル主回路60Hに設けられたスイッチング素子1a,1bのオンおよびオフを制御する。具体的には、セル個別制御器61は、スイッチング素子1a,1bの制御電極にゲート制御信号Ga,Gbをそれぞれ出力する。 さらに、セル個別制御器61は、キャパシタ1eの電圧値(すなわち、キャパシタ電圧実測値)を検出し、検出した電圧値をA/D(Analog to Digital)変換する。セル個別制御器61は、検出したキャパシタ電圧実測値Vciをキャパシタ1eの電圧制御に用いる。さらに、セル個別制御器61は、検出したキャパシタ電圧実測値Vciを、通信装置62によって制御装置5に送信する。 通信装置62は、制御装置5に設けられた通信回路と通信を行なうことにより、制御装置5からアーム電圧指令値および循環電圧指令値を受信する。さらに、通信装置62は、セル個別制御器61によって検出されたA/D変換後のキャパシタ電圧実測値Vciを制御装置5に送信する。通信装置62と制御装置5との間の通信方式には、耐ノイズ性の観点ならびに絶縁性の観点から光通信方式を用いるのが望ましい。 図3は、変換器セル1の主回路の変形例を示す回路図である。図3(a)に示す変換器セル1は、フルブリッジ型のセル主回路60Fを含む。セル主回路60Fは、直列接続されたスイッチング素子1f,1gと、スイッチング素子1f,1gに逆並列にそれぞれ接続されたダイオード1h,1iとをさらに含む点で、図3(a)のセル主回路60Hと異なる。スイッチング素子1f,1gの直列接続回路は、スイッチング素子1a,1bの直列接続回路と並列に接続されるとともに、キャパシタ1eと並列に接続される。入出力端子1pは、スイッチング素子1a,1bの接続ノードと接続され、入出力端子1nは、スイッチング素子1f,1gの接続ノードと接続される。 図3(a)に示すセル主回路60Fは、通常動作時には、スイッチング素子1gをオンとし、スイッチング素子1fをオフとし、スイッチング素子1a,1bを交互にオン状態とするように制御される。これにより、セル主回路60Fは、入出力端子1p,1n間に零電圧または正電圧を出力できる。また、セル主回路60Fは、通常動作時と異なる制御によって、入出力端子1p,1n間に零電圧または負電圧を出力できる。具体的には、スイッチング素子1gをオフし、スイッチング素子1fをオンし、スイッチング素子1a,1bを交互にオン状態にすることによって、零電圧または負電圧を出力できる。 図3(b)に示す変換器セル1は、混合型のセル主回路60Hybを含む。セル主回路60Hybは、図3(a)のセル主回路60Fからスイッチング素子1fを除去した構成を有する。図3(b)のセル主回路60Hybは、通常動作時には、スイッチング素子1gをオンとし、スイッチング素子1a,1bを交互にオン状態とするように制御される。これにより、セル主回路60Hybは、入出力端子1p,1n間に零電圧または正電圧を出力できる。一方、セル主回路60Hybは、スイッチング素子1a,1gをオフし、スイッチング素子1bをオンし、かつ電流が入出力端子1nから入出力端子1pの方向に流れる場合には、負電圧を出力できる。 図2、図3(a)、および図3(b)に示す各スイッチング素子1a,1b,1f,1gには、オン動作とオフ動作の両方を制御可能な自己消弧型の半導体スイッチング素子が用いられる。例えば、IGBT(Insulated Gate Bipolar Transistor)またはGCT(Gate Commutated Turn-off thyristor)などがスイッチング素子1a,1b,1f,1gとして用いられる。 以下では、セル主回路60H,60F,60Hybを総称してセル主回路60と記載する場合がある。変換器セル1を構成するセル主回路60は、図2、図3(a)、および図3(b)に示す以外の構成であってもよい。なお、説明の容易化のため、以下では、変換器セル1が、図2のセル主回路60Hの構成を有する場合を例に説明する。 &lt;制御装置の全体構成&gt; 図4は、制御装置5の全体構成を示すブロック図である。図4には、各変換器セル1に設けられたセル主回路(図4中の「主回路」に対応)60およびセル個別制御器(図4中の「個別制御器」に対応)61も併せて示されている。なお、図解を容易にするために通信装置62の図示は省略されている。 図4を参照して、制御装置5は、アーム共通制御器20と、u相アーム制御器40uと、v相アーム制御器40vと、w相アーム制御器40wとを含む。 アーム共通制御器20は、アーム電流実測値および交流電圧実測値に基づいて、u相,v相,w相の交流電圧指令値Vacuref,Vacvref,Vacwrefを生成する。さらに、アーム共通制御器20は、直流電圧指令値Vdcrefを出力する。さらに、アーム共通制御器20は、各変換器セル1のキャパシタ電圧実測値Vciからキャパシタ電圧の平均値であるVciavを生成する。 u相アーム制御器40uは、アーム共通制御器20から受信した交流電圧指令値Vacurefおよび直流電圧指令値Vdcrefに基づいて、u相アーム電圧指令値を生成する。u相アーム電圧指令値は、正側アーム13uに出力する正側アーム電圧指令値Vuprefと、負側アーム14uに出力する負側アーム電圧指令値Vunrefとを含む。 u相アーム制御器40uは、さらに、アーム共通制御器20から受信したキャパシタ電圧平均値Vciavと現時点のu相循環電流値とに基づいて、循環電圧指令値Vccurefを生成する。循環電圧指令値Vccurefは、u相の循環電流を制御するために正側アーム13uおよび負側アーム14uの各変換器セル1に共通に出力される電圧指令値である。 u相アーム制御器40uは、さらに、正側アーム13uの各セル個別制御器61に、正側キャパシタ電圧平均値Vcupを出力する。また、u相アーム制御器40uは、負側アーム14uの各セル個別制御器61に、負側キャパシタ電圧平均値Vcunを出力する。 v相アーム制御器40vは、交流電圧指令値Vacvrefおよび直流電圧指令値Vdcrefに基づいてv相アーム電圧指令値を生成する。v相アーム電圧指令値は、正側アーム13vに出力する正側アーム電圧指令値Vvprefと、負側アーム14vに出力する負側アーム電圧指令値Vvnrefとを含む。v相アーム制御器40vは、さらに、アーム共通制御器20から受信したキャパシタ電圧平均値Vciavと現時点のv相循環電流値とに基づいて、循環電圧指令値Vccvrefを生成する。循環電圧指令値Vccvrefは、v相の循環電流を制御するために正側アーム13vおよび負側アーム14vの各変換器セル1に共通に出力される電圧指令値である。v相アーム制御器40vは、さらに、正側アーム13vの各セル個別制御器61に、正側キャパシタ電圧平均値Vcvpを出力する。また、v相アーム制御器40vは、負側アーム14vの各セル個別制御器61に、負側キャパシタ電圧平均値Vcvnを出力する。 w相アーム制御器40wは、交流電圧指令値Vacwrefおよび直流電圧指令値Vdcrefに基づいてw相アーム電圧指令値を生成する。w相アーム電圧指令値は、正側アーム13wに出力する正側アーム電圧指令値Vwprefと、負側アーム14wに出力する負側アーム電圧指令値Vwnrefとを含む。w相アーム制御器40wは、さらに、アーム共通制御器20から受信したキャパシタ電圧平均値Vciavと現時点のw相循環電流値とに基づいて、循環電圧指令値Vccwrefを生成する。循環電圧指令値Vccwrefは、w相の循環電流を制御するために正側アーム13wおよび負側アーム14wの各変換器セル1に共通に出力される電圧指令値である。w相アーム制御器40wは、さらに、正側アーム13wの各セル個別制御器61に、正側キャパシタ電圧平均値Vcwpを出力する。また、w相アーム制御器40wは、負側アーム14wの各セル個別制御器61に、負側キャパシタ電圧平均値Vcwnを出力する。 各相のアーム制御器40u,40v,40wは、対応する変換器セル1のセル個別制御器61へ、光通信路を介してアーム電圧指令値、循環電圧指令値、およびキャパシタ電圧平均値を送信する。 &lt;制御装置のハードウェア構成例&gt; 図5は、制御装置5のハードウェア構成の一例を示すブロック図である。図5の場合の制御装置5は、コンピュータに基づいて構成される。図5を参照して、制御装置5は、1つ以上の入力変換器70と、1つ以上のサンプルホールド(S/H)回路71と、マルチプレクサ(MUX:multiplexer)72と、A/D変換器73とを含む。さらに、制御装置5は、1つ以上のCPU(Central Processing Unit)74と、RAM(Random Access Memory)75と、ROM(Read Only Memory)76とを含む。さらに、制御装置5は、1つ以上の入出力インターフェイス77と、補助記憶装置78と、上記の構成要素間を相互に接続するバス79とを含む。 入力変換器70は、入力チャンネルごとに補助変成器を備える。各補助変成器は、図1の各電気量検出器による検出信号を、後続する信号処理に適した電圧レベルの信号に変換する。 サンプルホールド回路71は、入力変換器70ごとに設けられる。サンプルホールド回路71は、対応の入力変換器70から受けた電気量を表す信号を規定のサンプリング周波数でサンプリングして保持する。 マルチプレクサ72は、複数のサンプルホールド回路71に保持された信号を順次選択する。A/D変換器73は、マルチプレクサ72によって選択された信号をデジタル値に変換する。なお、複数のA/D変換器73を設けることによって、複数の入力チャンネルの検出信号に対して並列的にA/D変換を実行するようにしてもよい。 CPU74は、制御装置5の全体を制御し、プログラムに従って演算処理を実行する。揮発性メモリとしてのRAM75および不揮発性メモリとしてのROM76は、CPU74の主記憶として用いられる。ROM76は、プログラムおよび信号処理用の設定値などを収納する。補助記憶装置78は、ROM76に比べて大容量の不揮発性メモリであり、プログラムおよび電気量検出値のデータなどを格納する。 入出力インターフェイス77は、CPU74と外部装置との間で通信する際のインターフェイス回路である。 なお、制御装置5の少なくとも一部をFPGA(Field Programmable Gate Array)およびASIC(Application Specific Integrated Circuit)などの回路を用いて構成してもよい。また、各変換器セル用のセル個別制御器61も、制御装置5の場合と同様にコンピュータをベースに構成することもできるし、その少なくとも一部をFPGAおよびASICなどの回路を用いて構成することができる。もしくは、制御装置5の少なくとも一部およびセル個別制御器61の少なくとも一部は、アナログ回路によって構成することもできる。 &lt;アーム共通制御器の動作&gt; (概要) 図6は、アーム共通制御器20の動作を示すブロック図である。図6を参照して、アーム共通制御器20は、交流制御部35と、直流制御部36と、電流演算器21と、平均値演算器22とを含む。これらの構成要素の機能は、例えば、CPU74によって実現される。 交流制御部35は、交流電圧検出器10で検出された交流電圧実測値Vacu,Vacv,Vacwと、交流電流検出器15で検出された交流電流実測値と、電流演算器21で演算された交流電流値Iacu,Iacv,Iacwとに基づいて、交流電圧指令値Vacuref,Vacvref,Vacwrefを生成する。交流制御部35の詳細な動作については、後述する。 直流制御部36は、直流電圧指令値Vdcrefを生成する。直流制御部36の構成は、交流回路から直流回路に電力を供給する整流器として電力変換装置が動作する場合と、インバータとして電力変換装置が動作する場合とで異なる。電力変換装置が整流器として動作する場合、直流制御部36は、直流電圧実測値Vdcp,Vdcnに基づいて直流電圧指令値Vdcrefを生成する。一方、電力変換装置がインバータとして動作する場合、直流制御部36は、交流電圧実測値Vacu,Vacv,Vacw、交流電流検出器15で検出された各相の交流電流実測値、および、電流演算器21で演算された直流電流値Idcに基づいて直流電圧指令値Vdcrefを生成する。直流制御部36の詳細な動作については、後述する。 (電流演算器の動作) 電流演算器21は、アーム電流実測値に基づいて、直流電流値Idc、交流電流値Iacu,Iacv,Iacw、および循環電流値Iccu,Iccv,Iccwを計算する。具体的には以下の手順による。 図1に示すように、レグ回路8uの正側アーム13uと負側アーム14uとの接続点である交流端子Nuは、変圧器3に接続されている。したがって、交流端子Nuから変圧器3に向かって流れる交流電流値Iacuは、以下の式(1)のように正側アーム電流実測値Iupから負側アーム電流実測値Iunを減算した電流値となる。 Iacu=Iup-Iun ...(1) 正側アーム電流実測値Iupと負側アーム電流実測値Iunとの平均値を、正側アーム13uおよび負側アーム14uに流れる共通の電流とすると、この電流はレグ回路8uの直流端子を流れるレグ電流Icomuである。レグ電流Icomuは、式(2)のように表される。 Icomu=(Iup+Iun)/2 ...(2) v相についても、正側アーム電流実測値Ivpおよび負側アーム電流実測値Ivnを用いて、交流電流値Iacvおよびレグ電流Icomvが算出され、w相についても、正側アーム電流実測値Iwpおよび負側アーム電流実測値Iwnを用いて、交流電流値Iacwおよびレグ電流Icomwが算出される。具体的には、以下の式(3)~(6)で表される。 Iacv=Ivp-Ivn ...(3) Icomv=(Ivp+Ivn)/2 ...(4) Iacw=Iwp-Iwn ...(5) Icomw=(Iwp+Iwn)/2 ...(6) 各相のレグ回路8u,8v,8wの正側の直流端子は正側直流端子Npとして共通に接続され、負側の直流端子は負側直流端子Nnとして共通に接続されている。この構成から、各相のレグ電流Icomu,Icomv,Icomwを加算した電流値は、直流回路4の正側端子から流れ込み、負側端子を介して直流回路4に帰還する直流電流値Idcとなる。したがって、直流電流値Idcは、式(7)のように表される。 Idc=Icomu+Icomv+Icomw ...(7) レグ電流に含まれる直流電流成分は、各相で均等に分担するとセルの電流容量を均等にすることができる。このことを考慮すると、レグ電流と直流電流値の1/3との差分が、直流回路4に流れないが各相のレグ間に流れる循環電流の電流値として演算できる。具体的には、u相、v相、w相の循環電流値Iccu,Iccv,Iccwは、それぞれ以下の式(8),(9),(10)のように表される。 Iccu=Icomu-Idc/3 ...(8) Iccv=Icomv-Idc/3 ...(9) Iccw=Icomw-Idc/3 ...(10) (平均値演算器の動作) 平均値演算器22は、各変換器セル1において検出された個々のキャパシタ電圧実測値Vciから、種々のキャパシタ電圧平均値Vciavを計算する。 具体的には、平均値演算器22は、電力変換器6全体に含まれる全キャパシタの電圧平均値である全キャパシタ電圧平均値Vcallを計算する。また、平均値演算器22は、正側アーム13uに含まれる各キャパシタの電圧平均値である正側キャパシタ電圧平均値Vcupと、負側アーム14uに含まれる各キャパシタの電圧平均値である負側キャパシタ電圧平均値Vcunと、レグ回路8u全体に含まれる全キャパシタの電圧平均値であるキャパシタ電圧平均値Vcuとを計算する。 平均値演算器22は、正側アーム13vにおける正側キャパシタ電圧平均値Vcvpと、負側アーム14vにおける負側キャパシタ電圧平均値Vcvnと、レグ回路8v全体におけるキャパシタ電圧平均値Vcvとを計算する。 平均値演算器22は、正側アーム13wにおける正側キャパシタ電圧平均値Vcwpと、負側アーム14wにおける負側キャパシタ電圧平均値Vcwnと、レグ回路8w全体におけるキャパシタ電圧平均値Vcwとを計算する。本明細書において、キャパシタ電圧平均値Vciavは、上記の種々の平均値の総称として用いられる。 (交流制御部の詳細な動作) 図7は、アーム共通制御器20における交流制御部35の動作を説明するための図である。図7を参照して、交流制御部35は、演算器23、無効電力制御器25、無効電流制御器27、直流キャパシタ電圧制御器29、および有効電流制御器31を含む。交流制御部35は、さらに、減算器24,26,28,30と、2相/3相変換器32とを含む。 演算器23は、各相の交流電圧実測値Vacu,Vacv,Vacwと、交流電流検出器15で検出された交流回路2の各相の交流電流実測値と、電流演算器21で算出された交流電流値Iacu,Iacv,Iacwとを受け取る。演算器23は、各相の交流電圧実測値Vacu,Vacv,Vacwと各相の交流電流実測値とに基づいて、無効電力値Prを計算する。さらに、演算器23は、各相の交流電圧実測値Vacu,Vacv,Vacwと、算出された交流電流値Iacu,Iacv,Iacwとに基づいて、有効電流値Iaおよび無効電流値Irを計算する。 減算器24は、与えられた無効電力指令値Prrefと、演算器23で算出された無効電力値Prとの偏差ΔPrを計算する。無効電力指令値Prrefは固定値であってもよいし、何らかの演算によって得られる変動値であってもよい。 無効電力制御器25は、減算器24によって算出された偏差ΔPrが0となるように電力変換器6から出力される無効電流を制御するための無効電流指令値Irrefを生成する。無効電力制御器25は、偏差ΔPrに対して比例演算および積分演算を行なうPI制御器として構成されていてもよいし、さらに微分演算を行なうPID制御器として構成されていてもよい。もしくは、無効電力制御器25として、フィードバック制御に用いられる他の制御器の構成を用いてもよい。この結果、無効電力値Prが無効電力指令値Prrefに等しくなるようにフィードバック制御される。 減算器26は、無効電流指令値Irrefと、演算器23で算出された無効電流値Irとの偏差ΔIrを計算する。 無効電流制御器27は、減算器26によって算出された偏差ΔIrが0となるように電力変換器6から出力される無効電圧を制御するための無効電圧指令値Vrrefを生成する。無効電流制御器27は、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、無効電流値Irが無効電流指令値Irrefに等しくなるようにフィードバック制御される。 減算器28は、全キャパシタ電圧平均値について与えられた指令値Vcallrefと、全キャパシタ電圧平均値Vcallとの偏差ΔVcallを計算する。上述したように、全キャパシタ電圧平均値Vcallは、個々のセルのキャパシタ電圧実測値Vciを電力変換装置全体で平均化したものである。指令値Vcallrefは固定値であってもよいし、何らかの演算によって得られる変動値であってもよい。 直流キャパシタ電圧制御器29は、減算器28によって算出された偏差ΔVcallが0となるように電力変換器6から出力される有効電流を制御するための有効電流指令値Iarefを生成する。直流キャパシタ電圧制御器29は、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、全キャパシタ電圧平均値Vcallが指令値Vcallrefに等しくなるようにフィードバック制御される。 減算器30は、有効電流指令値Iarefと、演算器23で算出された有効電流値Iaとの偏差ΔIaを計算する。 有効電流制御器31は、減算器30によって算出された偏差ΔIaが0となるように電力変換器6から出力される有効電圧を制御するための有効電圧指令値Varefを生成する。有効電流制御器31は、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、有効電流値Iaが有効電流指令値Iarefに等しくなるようにフィードバック制御される。 2相/3相変換器32は、有効電圧指令値Varefおよび無効電圧指令値Vrrefから座標変換によって、u相の交流電圧指令値Vacuref、v相の交流電圧指令値Vacvref、およびw相の交流電圧指令値Vacwrefを生成する。2相/3相変換器32による座標変換は、例えば、逆パーク(Park)変換と逆クラーク(Clarke)変換とによって実現することができる。もしくは、2相/3相変換器32による座標変換は、逆パーク変換と空間ベクトル変換とによって実現することもできる。 なお、図7では、交流制御部35が、無効電力制御器25を含む構成について説明した。しかしながら、図8に示すように、交流制御部35は、無効電力制御器25の代わりに系統電圧制御器を含んでいてもよい。 図8は、系統電圧制御器121を説明するための図である。図8を参照して、減算器24aは、与えられた系統電圧指令値Vsrefと、系統電圧値Vsとの偏差ΔVsを計算する。系統電圧指令値Vsrefは固定値であってもよいし、何らかの演算によって得られる変動値であってもよい。 系統電圧制御器121は、減算器24aによって算出された偏差ΔVsが0になるように電力変換器6から出力される無効電流を制御するための無効電流指令値Irrefを生成する。系統電圧制御器121は、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、系統電圧値Vsが系統電圧指令値Vsrefに等しくなるようにフィードバック制御される。 なお、系統電圧値Vsは、演算器23によって計算される。例えば、演算器23は、交流電圧実測値Vacu,Vacv,Vacwの二乗平均平方根を系統電圧値Vsとして計算する。 詳細は後述するが、上記の偏差ΔPr,ΔIr,ΔVcall,ΔIa,ΔVsは、各変換器セル1のスイッチング周波数を切り替える際の指標として用いられる。 (直流制御部の詳細な動作) 図9は、アーム共通制御器20における直流制御部36の動作を説明するための図である。図9(a)は、交流回路2から直流回路4に電力を供給する整流器として電力変換装置100が動作する場合における機能ブロック図を示す。図9(b)は、直流回路4から交流回路2に有効電力を供給するインバータとして電力変換装置100が動作する場合における機能ブロック図を示す。直流送電線路の一端に設けられた電力変換装置100は、図9(a)の構成の直流制御部36を含み、直流送電線路の他端に設けられた電力変換装置100は、図9(b)の構成の直流制御部36を含む。 図9(a)を参照して、整流器用の直流制御部36は、減算器80と、直流制御器81とを含む。減算器80は、与えられた直流端子電圧指令値と直流端子電圧値Vdc(=Vdcp-Vdcn)との偏差ΔVdcを計算する。直流端子電圧値Vdcは、直流電圧検出器11a,11bによって検出された直流電圧実測値Vdcp,Vdcnから求められる送電端電圧である。直流制御器81は、偏差ΔVdcが0になるように電力変換器6から出力される直流電圧を制御するための直流電圧指令値Vdcrefを生成する。例えば、直流制御器81は、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、直流端子電圧値Vdcが直流端子電圧指令値に等しくなるようにフィードバック制御される。 図9(b)を参照して、インバータ用の直流制御部36は、演算器82と、減算器83,85と、有効電力制御器84と、直流電流制御器86とを含む。 演算器82は、各相の交流電圧実測値Vacu,Vacv,Vacwと、交流電流検出器15で検出された交流回路2の各相の交流電流実測値とを受け取る。演算器82は、これらの電圧値および電流値に基づいて、有効電力値Paを計算する。減算器83は、与えられた有効電力指令値Parefと、算出された有効電力値Paとの偏差ΔPaを計算する。有効電力指令値Parefは固定値であってもよいし、何らかの演算によって得られる変動値であってもよい。 有効電力制御器84は、減算器83によって算出された偏差ΔPaが0になるように電力変換器6から出力される直流電流を制御するための直流電流指令値Idcrefを生成する。有効電力制御器84は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、有効電力値Paが有効電力指令値Parefに等しくなるようにフィードバック制御される。 減算器85は、直流電流指令値Idcrefと直流電流値Idcとの偏差ΔIdcを計算する。上述したように、直流電流値Idcは、各アーム電流実測値を用いて電流演算器21によって計算される。 直流電流制御器86は、減算器85によって算出された偏差ΔIdcが0になるように電力変換器6から出力される直流電圧を制御するための直流電圧指令値Vdcrefを生成する。直流電流制御器86は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、直流電流値Idcが直流電流指令値Idcrefに等しくなるようにフィードバック制御される。 詳細は後述するが、上記の偏差ΔVdc,ΔPa,ΔIdcは、各変換器セル1のスイッチング周波数を切り替える際の指標として用いられる。 &lt;各相のアーム制御器の動作&gt; 各相のアーム制御器40u,40v,40wの動作について説明する。以下では、u相アーム制御器40uの動作について代表的に説明する。v相アーム制御器40vおよびw相アーム制御器40wの動作は、以下の説明のu相をv相およびw相にそれぞれ読み替えたものと同じである。 図10は、u相アーム制御器40uの動作を示すブロック図である。図10を参照して、u相アーム制御器40uは、正側指令生成器41と、負側指令生成器42と、相間バランス制御器43と、正負バランス制御器44と、循環電流制御器51とを含む。u相アーム制御器40uは、さらに、加算器45,46,47と、減算器48,49,50とを含む。 加算器45は、直流電圧指令値Vdcrefと、正側指令生成器41によって交流電圧指令値Vacurefを-1倍した値とを加算する。これによって、u相の正側アーム電圧指令値Vuprefが生成される。 加算器46は、直流電圧指令値Vdcrefと、負側指令生成器42によって交流電圧指令値Vacurefを+1倍した値とを加算する。これによって、u相の負側アーム電圧指令値Vunrefが生成される。 減算器48は、全キャパシタ電圧平均値Vcallとu相のキャパシタ電圧平均値Vcuとの偏差ΔVcuを計算する。偏差ΔVcuは、異なる相の間での各キャパシタの電圧ばらつき(すなわち、キャパシタ電圧ばらつき)を意味している。 相間バランス制御器43は、減算器48によって算出された偏差ΔVcuに対して演算を施す。相間バランス制御器43は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、キャパシタ電圧平均値Vcuが全キャパシタ電圧平均値Vcallに等しくなるようにフィードバック制御される。 減算器49は、u相の正側キャパシタ電圧平均値Vcupとu相の負側キャパシタ電圧平均値Vcunとの偏差ΔVcupnを計算する。偏差ΔVcupnは、正側アーム13uと負側アーム14uとの間での各キャパシタの電圧ばらつきを意味している。 正負バランス制御器44は、減算器49によって算出された偏差ΔVcupnに対して演算を施す。正負バランス制御器44は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、負側キャパシタ電圧平均値Vcunが正側キャパシタ電圧平均値Vcupに等しくなるようにフィードバック制御される。 加算器47は、相間バランス制御器43による演算結果と正負バランス制御器44による演算結果とを加算することによって、u相の循環電流指令値Iccurefを生成する。 減算器50は、循環電流指令値Iccurefと循環電流値Iccuとの偏差を計算する。循環電流制御器51は、減算器50よって算出された偏差に対して演算を施すことにより、u相の循環電圧指令値Vccurefを生成する。循環電流制御器51は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。 通信装置52は、正側アーム13uを構成する各変換器セル1のセル個別制御器61に対して、正側アーム電圧指令値Vupref、循環電圧指令値Vccuref、および正側キャパシタ電圧平均値Vcupを送信する。通信装置52は、さらに、負側アーム14uを構成する各変換器セル1のセル個別制御器61に対して、負側アーム電圧指令値Vunref、循環電圧指令値Vccuref、および負側キャパシタ電圧平均値Vcunを送信する。 上記において、正側アーム電圧指令値Vuprefおよび負側アーム電圧指令値Vunrefの計算と、循環電圧指令値Vccurefの計算とは互いに独立している。したがって、循環電圧指令値Vccurefの計算周期は、正側アーム電圧指令値Vuprefおよび負側アーム電圧指令値Vunrefの計算周期よりも短くすることができる。この結果、交流回路2の交流電流および直流回路4の直流電流に比べて変化が速い循環電流の制御性を良くすることができる。 詳細は後述するが、上記の偏差ΔVcu,ΔVcupnは、各変換器セル1のスイッチング周波数を切り替える際の指標として用いられる。 &lt;セル個別制御器の動作&gt; 各変換器セル1に設けられたセル個別制御器61の動作について説明する。以下では、正側アーム13u用のセル個別制御器61の動作について代表的に説明する。負側アーム14u用のセル個別制御器61の動作は、以下の説明の正側を負側に読み替えたものと同じである。v相およびw相用のセル個別制御器61の動作は、以下の説明のu相をv相またはw相と読み替えたものと同じである。 図11は、正側アーム13u用のセル個別制御器61の動作を示すブロック図である。図11では、キャパシタ電圧実測値Vciをデジタル値に変換するためのA/D変換器の図示が省略されている。さらに、図11では、セル個別制御器61と制御装置5との間での通信を行なう通信装置62の図示が省略されている。 図11を参照して、セル個別制御器61は、キャパシタ電圧制御器64、キャリア発生器65、コンパレータ67、減算器63、および加算器66を含む。 減算器63は、キャパシタ電圧指令値としての正側キャパシタ電圧平均値Vcupと、キャパシタ電圧実測値Vciとの間の偏差ΔVcupを計算する。図10で説明したように、正側キャパシタ電圧平均値Vcupは、対応するu相アーム制御器40uから受信される。キャパシタ電圧実測値Vciは、対応するセル主回路60において検出される。なお、詳細は後述するが、偏差ΔVcupは、各変換器セル1のスイッチング周波数を切り替える際の指標として用いられる。 キャパシタ電圧制御器64は、減算器63によって算出された偏差ΔVcupに対して演算を施す。キャパシタ電圧制御器64は、例えば、PI制御器、PID制御器、またはフィードバック制御に用いられる他の制御器として構成され得る。この結果、キャパシタ電圧実測値Vciが正側キャパシタ電圧平均値Vcupに等しくなるようにフィードバック制御される。 加算器66は、u相の正側アーム電圧指令値Vuprefとキャパシタ電圧制御器64の出力とを加算することによって、最終的なu相の正側アーム電圧指令値Vupref*を生成する。 キャリア発生器65は、位相シフトPWM(Pulse Width Modulation)制御で用いられるキャリア信号CSを生成する。位相シフトPWM制御とは、正側アーム13uを構成する複数の各変換器セル1に出力されるPWM信号のタイミングを相互にずらすものである。これによって、各変換器セル1の出力電圧の合成電圧に含まれる高調波成分を削減することができる。例えば、各変換器セル1に設けられたセル個別制御器61は、制御装置5から受信した共通の基準位相θiに基づいて、相互に位相のずれたキャリア信号CSを生成する。例えば、キャリア信号CSとして三角波が用いられる。 さらに、キャリア発生器65は、生成したキャリア信号CSを、循環電圧指令値Vccurefに応じて変調する。そして、キャリア発生器65は、変調後のキャリア信号を後段のコンパレータ67に出力する。後段のコンパレータ67において生成されるPWM信号(すなわち、ゲート制御信号Ga,Gb)のパルス幅は、循環電圧指令値Vccurefに応じて変化する。この結果、循環電流指令値Iccurefと循環電流値Iccuとの偏差がより小さくなるように制御される。 コンパレータ67は、正側アーム電圧指令値Vupref*と、循環電圧指令値Vccurefに基づく変調後のキャリア信号CSとを比較する。この比較結果に従って、コンパレータ67は、セル主回路60を構成するスイッチング素子1a,1bを制御するためのPWM変調信号としてのゲート制御信号Ga,Gbを生成する。ゲート制御信号Ga,Gbは、図2のスイッチング素子1a,1bの制御電極にそれぞれ供給される。この結果、セル主回路60の出力電圧は、u相の循環電流値Iccuに応じて制御される。 &lt;スイッチング周波数の切り替え&gt; 上述した偏差を用いて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替える構成について説明する。以下の説明では、図7の偏差ΔPr,ΔIr,ΔVcall,ΔIa、図8の偏差ΔVs、図9の偏差ΔVdc,ΔPa,ΔIdc、図10の偏差ΔVcu,ΔVcupn、および図11の偏差ΔVcupを総称して偏差ΔXとも記載する。 図12は、実施の形態1に従う周波数切替部200の動作を説明するための図である。具体的には、図12(a)は、制御装置5に含まれる周波数切替部200の機能を説明するためのブロック図である。図12(b)は、周波数切替信号が出力されるタイミングを説明するためのタイミングチャートである。周波数切替部200の機能は、典型的には、制御装置5のCPU74によって実現される。 図12(a)を参照して、周波数切替部200は、絶対値演算器131と、比較器132とを含む。絶対値演算器131は、偏差ΔXの入力を受けると偏差ΔXの絶対値(以下、単に偏差¦ΔX¦とも称する。)を算出し、比較器132へ出力する。なお、“¦¦”は、絶対値記号を表わしている。例えば、偏差ΔXが、無効電流指令値Irrefと無効電流値Irとの偏差ΔIrである場合には、絶対値演算器131は、偏差ΔIrの絶対値¦ΔIr¦を算出する。 比較器132は、閾値Th1と、偏差¦ΔX¦とに基づいて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替えるための周波数切替信号を出力する。図12(b)を参照して、波形300は、偏差¦ΔX¦を示す波形である。時刻t1到達前までの期間では、偏差¦ΔX¦は閾値Th1未満である。この場合、比較器132は、ローレベルの周波数切替信号(以下、「周波数切替信号L」とも称する。)を出力する。時刻t1到達後、時刻t2到達前までの期間では、偏差¦ΔX¦は閾値Th1以上である。この場合、比較器132は、ハイレベルの周波数切替信号(以下、「周波数切替信号H」とも称する。)を出力する。時刻t2到達後の期間では、偏差¦ΔX¦は閾値Th1未満である。この場合、比較器132は、周波数切替信号Lを出力する。 比較器132から出力された周波数切替信号は、図11のキャリア発生器65に入力される。キャリア発生器65は、制御装置5から周波数切替信号Lの入力を受け付けている場合には、キャリア信号CSの周波数(以下、「キャリア周波数」と称する。)を、電力変換器6を通常動作させる際に用いられる周波数F(例えば、180Hz)に設定する。これにより、各変換器セル1のスイッチング素子1a,1bは、周波数Fに設定されたキャリア周波数(すなわち、スイッチング周波数)に従ってスイッチング動作する。 一方、キャリア発生器65は、制御装置5から周波数切替信号Hの入力を受け付けている場合には、キャリア周波数を、周波数Fよりも高い周波数FHに設定する。周波数FHは、周波数Fの数倍程度である。これにより、各変換器セル1のスイッチング素子1a,1bは、周波数FHに設定されたキャリア周波数に従って、より高速にスイッチング動作する。 このように、偏差¦ΔX¦の大きさに応じて、キャリア周波数(すなわち、スイッチング周波数)を変更する理由について説明する。具体的には、偏差ΔX(例えば、偏差ΔIr)の絶対値が閾値Th1以上である場合には、電力変換器6からのフィードバック値(例えば、無効電流値Ir)が、電力変換器6に対する制御指令値(例えば、無効電流指令値Irref)に追随していないことを意味する。この場合、フィードバック値を制御指令値に早く収束させる必要がある。そのため、本実施の形態に係る制御装置5は、偏差¦ΔX¦が閾値Th1以上である場合(すなわち、周波数切替信号Hが出力されている場合)には、高いスイッチング周波数(すなわち、周波数FH)で各変換器セル1のスイッチング素子1a,1bをスイッチング動作させる。 一方、偏差¦ΔX¦が閾値Th1未満である場合には、電力変換器6からのフィードバック値が、電力変換器6に対する制御指令値に追随していることを意味する。このように、フィードバック値と制御指令値との偏差が小さい場合には、スイッチング周波数を高くして電力変換器6の応答性を高くする必要がない。また、電力変換器6の電力変換効率は、各変換器セル1のスイッチング素子1a,1b等のスイッチング損失に依存し、スイッチング損失は、スイッチング周波数が高いほど大きくなる。そのため、本実施の形態に係る制御装置5は、偏差¦ΔX¦が閾値Th1未満である場合(すなわち、周波数切替信号Lが出力されている場合)には、低いスイッチング周波数(すなわち、周波数F)で各変換器セル1のスイッチング素子1a,1bをスイッチング動作させて、スイッチング損失を低減する。 図12の例の場合、時刻t1到達前までの期間ではスイッチング周波数は周波数Fであり、時刻t1到達後から時刻t2到達前までの期間では、スイッチング周波数は周波数FHであり、時刻t2到達後の期間では、スイッチング周波数は周波数Fとなる。 まとめると、制御装置5は、電力変換器6に対する制御指令値と、電力変換器6からのフィードバック値との偏差¦ΔX¦を算出する。偏差¦ΔX¦が閾値Th1以上となった場合、制御装置5は、スイッチング素子1a,1bのスイッチング周波数を増大させる(例えば、周波数切替信号Hを出力することで周波数Fを周波数FHに変更する)制御を実行する。そして、スイッチング素子1a,1bのスイッチング周波数を増大させる制御が実行された後、偏差¦ΔX¦が閾値Th1未満となった場合に、制御装置5は、増大させたスイッチング周波数を低下させる(例えば、周波数切替信号Lを出力することで周波数FHを周波数Fに変更する)制御を実行する。 なお、上記では、制御指令値、フィードバック値、および偏差ΔXが、ぞれぞれ無効電流指令値Irref、無効電流値Ir、および偏差ΔIrである場合を例示した。図7の交流制御部35に関する制御指令値、フィードバック値、および偏差ΔXの他の組み合わせは、次の通りである。偏差ΔXが偏差ΔPrである場合、制御指令値およびフィードバック値は、それぞれ無効電力指令値Prrefおよび無効電力値Prである。偏差ΔXが偏差ΔVcallである場合、制御指令値およびフィードバック値は、それぞれ指令値Vcallrefおよび全キャパシタ電圧平均値Vcallである。偏差ΔXが偏差ΔIaである場合、制御指令値およびフィードバック値は、それぞれ有効電流指令値Iarefおよび有効電流値Iaである。偏差ΔXが偏差ΔVsである場合、制御指令値およびフィードバック値は、それぞれ系統電圧指令値Vsrefおよび系統電圧値Vsである。 図9の直流制御部36に関する制御指令値、フィードバック値、および偏差ΔXの組み合わせは次の通りである。偏差ΔXが偏差ΔVdcである場合、制御指令値およびフィードバック値は、それぞれ直流端子電圧指令値および直流端子電圧値Vdcである。偏差ΔXが偏差ΔPaである場合、制御指令値およびフィードバック値は、それぞれ有効電力指令値Parefおよび有効電力値Paである。偏差ΔXが偏差ΔIdcである場合、制御指令値およびフィードバック値は、それぞれ直流電流指令値Idcrefおよび直流電流値Idcである。 図10のu相アーム制御器40uに関する制御指令値、フィードバック値、および偏差ΔXの組み合わせは次の通りである。偏差ΔXが偏差ΔVcuである場合、制御指令値およびフィードバック値は、それぞれ、相間バランス指令値としての全キャパシタ電圧平均値Vcallおよびキャパシタ電圧平均値Vcuである。偏差ΔXが偏差ΔVcupnである場合、制御指令値およびフィードバック値は、それぞれ、正負バランス指令値としての正側キャパシタ電圧平均値Vcupおよび負側キャパシタ電圧平均値Vcunである。 図11のセル個別制御器61に関して、偏差ΔXが偏差ΔVcupである場合、制御指令値およびフィードバック値は、それぞれキャパシタ電圧指令値としての正側キャパシタ電圧平均値Vcupおよびキャパシタ電圧実測値Vciである。 図12の構成によると、フィードバック値が制御指令値に追随しておらず、電力変換器6の応答性を高める必要があるタイミングで、各変換器セル1のスイッチング素子のスイッチング周波数を増大させることができる。その後、フィードバック値が制御指令値に追随するようになった場合には、各変換器セル1のスイッチング素子のスイッチング周波数を低下させて、スイッチング損失を低減することができる。 (変形例1) 図12の例では、偏差¦ΔX¦が閾値Th1付近で振動する場合に、チャタリングが発生する可能性がある。そこで、変形例1では、図12の比較器132に不感帯機能を追加した構成について説明する。 図13は、実施の形態1の変形例1に従う周波数切替部200Aの動作を説明するための図である。具体的には、図13(a)は、周波数切替部200Aの機能を説明するためのブロック図である。図13(b)は、周波数切替信号が出力されるタイミングを説明するためのタイミングチャートである。 図13(a)を参照して、周波数切替部200Aは、絶対値演算器131と、比較器141とを含む。周波数切替部200Aは、周波数切替部200の比較器132を、不感帯機能付きの比較器141に置き換えたものに相当する。 比較器141は、閾値Th1と、閾値Th2(ただし、Th2&lt;Th1)と、偏差¦ΔX¦とに基づいて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替えるための周波数切替信号を出力する。なお、閾値Th1から閾値Th2までの幅dが不感帯に相当する。 図13(b)を参照して、波形310は、偏差¦ΔX¦を示す波形である。時刻t1a到達前までの期間では、偏差¦ΔX¦は閾値Th1未満である。この期間において、比較器141は、周波数切替信号Lを出力する。時刻t1a到達後から時刻t2a到達前までの期間では、偏差¦ΔX¦は閾値Th1以上である。時刻t2a到達後から時刻t3a到達前までの期間では、偏差¦ΔX¦は閾値Th1未満かつ閾値Th2以上である。時刻t3a到達後から時刻t4a到達前までの期間では、偏差¦ΔX¦は閾値Th1以上である。ここで、時刻t1a到達後から時刻t4a到達前までの期間において、比較器141は、周波数切替信号Hを出力する。時刻t4a到達後の期間では、偏差¦ΔX¦は閾値Th2未満である。この期間において、比較器141は、周波数切替信号Lを出力する。 このように、偏差¦ΔX¦が閾値Th1以上となり周波数切替信号Hが出力された場合には、偏差¦ΔX¦が閾値Th2以上である限り、比較器141は、周波数切替信号Hの出力を維持する。そのため、スイッチング素子1a,1bのスイッチング周波数は変化しない。そして、偏差¦ΔX¦が閾値Th2未満になると、比較器141は、周波数切替信号Lを出力する。 したがって、図13の場合、時刻t1a到達前までの期間ではスイッチング周波数は周波数Fであり、時刻t1a到達後から時刻t4a到達前までの期間では、スイッチング周波数は周波数FHであり、時刻t4a到達後の期間では、スイッチング周波数は周波数Fとなる。 まとめると、偏差¦ΔX¦が閾値Th1以上となった場合、制御装置5は、スイッチング素子1a,1bのスイッチング周波数を増大させる(例えば、周波数Fを周波数FHに変更する)制御を実行する。そして、スイッチング素子1a,1bのスイッチング周波数を増大させる制御が実行された後、偏差¦ΔX¦が閾値Th1よりも小さい閾値Th2未満となった場合に、制御装置5は、増大させたスイッチング周波数を低下させる(例えば、周波数FHを周波数Fに変更する)制御を実行する。 図13の構成によると、図12の構成の利点に加えて、スイッチング周波数のチャタリング発生を防止することができる。 (変形例2) 変形例2では、チャタリングの発生を防止するための他の構成について説明する。 図14は、実施の形態1の変形例2に従う周波数切替部200Bの動作を説明するための図である。具体的には、図14(a)は、周波数切替部200Bの機能を説明するためのブロック図である。図14(b)は、周波数切替信号が出力されるタイミングを説明するためのタイミングチャートの一例である。図14(c)は、周波数切替信号が出力されるタイミングを説明するためのタイミングチャートの他の例である。 図14(a)を参照して、周波数切替部200Bは、絶対値演算器131と、比較器151とを含む。周波数切替部200Bは、周波数切替部200の比較器132を、タイマー機能付きの比較器151に置き換えたものに相当する。 比較器151は、閾値Th1と、偏差¦ΔX¦とに基づいて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替えるための周波数切替信号を出力する。 図14(b)を参照して、波形320は、偏差¦ΔX¦を示す波形である。時刻t1b到達前までの期間では、偏差¦ΔX¦は閾値Th1未満である。この期間において、比較器151は、周波数切替信号Lを出力する。時刻t1b到達後から時刻t2b到達前までの期間では、偏差¦ΔX¦は閾値Th1以上である。 比較器151は、周波数切替信号Hを出力してからタイマー時間Tが経過するまでの期間(図14の例では、時刻t1bから時刻t4bまでの時間)において、周波数切替信号Hの出力を維持する。そのため、時刻t2b到達後から時刻t3b到達前までの期間では偏差¦ΔX¦は閾値Th1未満となっているが、比較器151は周波数切替信号Hの出力を維持する。そして、タイマー時間Tが経過する前の時刻t3b到達後から時刻t5b到達前までの期間において、偏差¦ΔX¦は閾値Th1以上となっている。そのため、比較器151は、時刻t3b到達後から時刻t5b到達前までの期間においても、周波数切替信号Hの出力を継続する。結果として、時刻t1b到達後から時刻t5b到達前までの期間において、比較器151は、周波数切替信号Hを出力する。 そして、タイマー時間Tが経過した後の時刻t5bに到達すると、偏差¦ΔX¦は閾値Th1未満となる。そのため、時刻t5b到達後の期間において、比較器151は、周波数切替信号Lを出力する。 このように、偏差¦ΔX¦が閾値Th1以上となり周波数切替信号Hが出力された場合には、タイマー時間Tが経過するまでは、偏差¦ΔX¦が閾値Th1未満となった場合であっても、比較器151は、周波数切替信号Hの出力を維持する。そのため、スイッチング素子1a,1bのスイッチング周波数は変化しない。そして、タイマー時間Tが経過した後に偏差¦ΔX¦が閾値Th1未満になると、比較器151は、周波数切替信号Lを出力する。 図14(b)の場合、時刻t1b到達前までの期間ではスイッチング周波数は周波数Fであり、時刻t1b到達後から時刻t5b到達前までの期間では、スイッチング周波数は周波数FHであり、時刻t5b到達後の期間では、スイッチング周波数は周波数Fとなる。 まとめると、偏差¦ΔX¦が閾値Th1以上となってからタイマー時間Tが経過するまでは、制御装置5は、スイッチング素子1a,1bのスイッチング周波数を増大させる(例えば、周波数Fを周波数FHに変更する)制御を実行する。閾値Th1以上となってからタイマー時間Tの経過後に、偏差¦ΔX¦が閾値Th1未満となった場合に、制御装置5は、増大させたスイッチング周波数を低下させる(例えば、周波数FHを周波数Fに変更する)制御を実行する。 また、比較器151は、図14(c)のようにタイマー時間Tがリセットされる構成であってもよい。具体的には、図14(c)を参照して、波形330は、偏差¦ΔX¦を示す波形である。時刻t1c到達前までの期間では、偏差¦ΔX¦は閾値Th1未満である。この期間において、比較器151は、周波数切替信号Lを出力する。時刻t1c到達後から時刻t2c到達前までの期間では、偏差¦ΔX¦は閾値Th1以上である。 比較器151は、周波数切替信号Hを出力してからタイマー時間Tが経過するまでの期間(図14(c)の例では、時刻t1cから時刻t4cまでの時間)において、周波数切替信号Hの出力を維持する。そのため、時刻t2c到達後から時刻t3c到達前までの期間では偏差¦ΔX¦は閾値Th1未満となっているが、比較器151は周波数切替信号Hの出力を維持する。 そして、タイマー時間Tが経過する時刻t4cよりも前の時刻t3cにおいて、偏差¦ΔX¦は閾値Th1以上となっている。すなわち、偏差¦ΔX¦は、時刻t2cにおいて閾値Th1未満になった後、時刻t3cにおいて再度閾値Th1以上となっている。そのため、前のタイマー時間Tがリセットされ、比較器151は、時刻t3c到達後からタイマー時間Tが経過する前までの期間(図14(c)の例では、時刻t3cから時刻t6cまでの期間)において、周波数切替信号Hの出力を維持する。このように、時刻t5c以降においては、偏差¦ΔX¦は閾値Th1未満であるが、比較器151は、時刻t5c到達後から時刻t6c到達前までの期間では、周波数切替信号Hの出力を継続する。そして、タイマー時間Tが経過する時刻t6cにおいては、偏差¦ΔX¦は閾値Th1未満であるため、比較器151は、周波数切替信号Lを出力する。 図14(c)の場合、時刻t1c到達前までの期間ではスイッチング周波数は周波数Fであり、時刻t1c到達後から時刻t6c到達前までの期間では、スイッチング周波数は周波数FHであり、時刻t6c到達後の期間では、スイッチング周波数は周波数Fとなる。 まとめると、偏差¦ΔX¦が閾値Th1以上となってからタイマー時間Tが経過するまでは、制御装置5は、スイッチング素子1a,1bのスイッチング周波数を増大させる(例えば、周波数Fを周波数FHに変更する)制御を実行する。また、偏差¦ΔX¦が閾値Th1以上になってからタイマー時間Tが経過したとき(例えば、時刻t6cに到達したとき)に偏差¦ΔX¦が閾値Th1未満である場合、制御装置5は、増大させたスイッチング素子のスイッチング周波数を低下させる(例えば、周波数FHを周波数Fに変更する)制御を実行する。 図14の構成によると、図12の構成の利点に加えて、スイッチング周波数のチャタリング発生を防止することができる。 (変形例3) 上記では、キャリア発生器65は、周波数切替信号Lの入力を受け付けている場合には、キャリア周波数(すなわち、スイッチング周波数)を周波数Fに設定し、周波数切替信号Hの入力を受け付けている場合には、スイッチング周波数を周波数FHに設定する構成について説明した。変形例3では、スイッチング周波数の増大方式の変形例について説明する。 図15は、実施の形態1の変形例3に従うスイッチング周波数の増大方式を説明するための図である。図15(a)は、スイッチング周波数の増大方式の一例を示す図である。図15(b)は、スイッチング周波数の増大方式の他の例を示す図である。 図15(a)および図15(b)の例の場合、図12の例と同様に、時刻t1到達前までの期間では、偏差¦ΔX¦は閾値Th1未満であるため、比較器132は、周波数切替信号Lを出力する。時刻t1到達後から時刻t2到達前までの期間では、偏差¦ΔX¦は閾値Th1以上であるため、比較器132は周波数切替信号Hを出力する。時刻t2到達後の期間では、偏差¦ΔX¦は閾値Th1未満であるため、比較器132は周波数切替信号Lを出力する。 図15(a)を参照して、キャリア発生器65は、時刻t1到達時に周波数切替信号Hの入力を受け付けると、キャリア周波数を、現時点の周波数Fから1段階増大した周波数F1に設定する。さらに、キャリア発生器65は、時刻t1到達後から周波数切替信号Hの入力を継続して受け付けている場合、時刻t1到達時から一定期間(例えば、時間Tx)経過後に、キャリア周波数を、現時点の周波数F1からさらに1段階増大した周波数F2に設定する。そして、キャリア発生器65は、時刻t2到達時に周波数切替信号Lの入力を受け付けると、キャリア周波数を、現在の周波数F2から増大前の周波数Fに戻す。このように、キャリア発生器65は、制御装置5からの周波数切替信号Hに従って、スイッチング周波数を段階的に増大させてもよい。 他の例として、図15(b)を参照して、キャリア発生器65は、時刻t1到達時に周波数切替信号Hの入力を受け付けると、キャリア周波数を、現時点の周波数Fから連続的に増大していく。図15(b)の例では、キャリア発生器65は、時刻t1到達後から時刻t2到達前までの期間において周波数切替信号Hの入力を受け付けている。そのため、この期間において、キャリア発生器65は、キャリア周波数を連続的に増大していく。そして、キャリア発生器65は、時刻t2到達時に周波数切替信号Lの入力を受け付けると、キャリア周波数を、現在の周波数から増大前の周波数Fに戻す。このように、キャリア発生器65は、制御装置5からの周波数切替信号Hに従って、スイッチング周波数を連続的に増大させてもよい。 なお、キャリア周波数に上限値を設けてもよい。この場合、キャリア発生器65は、上限値に到達するまではキャリア周波数を連続的に増大し、上限値到達後はキャリア周波数を上限値で維持する。また、図15(b)では、スイッチング周波数は、直線的に増大する構成について説明したが、曲線的に増大する構成であってもよい。 このように、制御装置5は、キャリア発生器65に周波数切替信号Hを出力することによって、スイッチング素子1a,1bのスイッチング周波数を段階的または連続的に増大させる構成であってもよい。 実施の形態2. 上述の実施の形態1では、各種の偏差ΔXに着目して、スイッチング周波数を増大させる構成について説明した。実施の形態2では、上述した制御指令値を用いて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替える構成について説明する。以下の説明では、図7の無効電力指令値Prref、無効電流指令値Irref、指令値Vcallref、有効電流指令値Iaref、図8の系統電圧指令値Vsref、図9の直流端子電圧指令値、有効電力指令値Paref、直流電流指令値Idcref、図10の全キャパシタ電圧平均値Vcall、正側キャパシタ電圧平均値Vcup、および図11の正側キャパシタ電圧平均値Vcupを総称して制御指令値SXと記載する。 図16は、実施の形態2に従う周波数切替部210の動作を説明するための図である。具体的には、図16(a)は、制御装置5に含まれる周波数切替部210の機能を説明するためのブロック図である。図16(b)は、切替信号が出力されるタイミングを説明するためのタイミングチャートである。 図16(a)を参照して、周波数切替部210は、変化率演算器161と、比較器162とを含む。変化率演算器161は、制御指令値SXの入力を受け付けると、単位時間(例えば、図16(b)の単位時間Ta)当たりの制御指令値SXの変化率Rを算出し、比較器162へ出力する。 比較器162は、基準変化率Rxと、変化率Rとに基づいて、各変換器セル1のスイッチング素子のスイッチング周波数を切り替えるための周波数切替信号を出力する。図16(b)を参照して、波形340は、制御指令値SXを示す波形である。比較器162は、時刻td1到達前の期間では、変化率Rが基準変化率Rx未満であると判断している。そのため、この期間において、比較器162は周波数切替信号Lを出力する。続いて、比較器162は、時刻td1到達時において、変化率Rが基準変化率Rx以上であると判断すると、周波数切替信号Hを出力する。 比較器162から出力された周波数切替信号は、図11のキャリア発生器65に入力される。キャリア発生器65は、周波数切替信号Lの入力を受け付けている場合には、キャリア周波数を周波数Fに設定する。キャリア発生器65は、周波数切替信号Hの入力を受け付けている場合には、キャリア周波数を、周波数Fよりも高い周波数FHに設定する。なお、実施の形態1の変形例3で説明したように、キャリア発生器65は、制御装置5からの周波数切替信号Hに従って、キャリア周波数を段階的または連続的に増大させてもよい。 また、比較器162の出力は、実施の形態1で説明した偏差¦ΔX¦に基づいて、周波数切替信号Hから周波数切替信号Lに変更される。例えば、図12の構成に従う場合、比較器162は、偏差¦ΔX¦が閾値Th1未満であると判断したときに周波数切替信号Lを出力する。 実施の形態2によると、制御装置5は、電力変換器6に対する制御指令値の変化率Rが基準変化率Rx以上になった場合に、スイッチング素子1a,1bのスイッチング周波数を増大させる制御を実行する。したがって、制御指令値が急峻に変化すると直ちにスイッチング周波数が増大されるため、より早くスイッチング周波数を増大させることができる。 その他の実施の形態. (1)上述した実施の形態1において、偏差¦ΔX¦が閾値Th1以上になり、スイッチング周波数を周波数Fから周波数FHに増大させた後、偏差¦ΔX¦が閾値Th1未満になった場合に周波数FHから周波数Fに戻す構成について説明したが、当該構成に限られない。例えば、偏差¦ΔX¦が閾値Th1未満になった場合に、周波数FHから周波数を低下させる構成であればよく、全く同一の周波数Fに戻さなくてもよい。 (2)上述した実施の形態1では、各種の偏差ΔXのいずれか1つを用いて、スイッチング周波数を変更する構成について説明したが、当該構成に限られない。複数の偏差ΔXのそれぞれに対応する複数の周波数切替部200を設け、各周波数切替部200の出力の組み合わせに基づいて、最終的な周波数切替信号が出力される構成であってもよい。例えば、複数の偏差ΔXの少なくとも1つに対応する周波数切替部200が周波数切替信号Hを出力した場合に、最終的な周波数切替信号Hがキャリア発生器65に入力されるような構成であってもよい。あるいは、複数の偏差ΔXのうちの第1偏差(例えば、偏差ΔIr)に対応する周波数切替部200が周波数切替信号Hを出力し、第2偏差(例えば、偏差ΔVs)に対応する周波数切替部200が周波数切替信号Hを出力した場合に、最終的な周波数切替信号Hがキャリア発生器65に入力されるような構成であってもよい。 同様に、上述した実施の形態2についても、複数の制御指令値SXのそれぞれに対応する複数の周波数切替部210を設け、各周波数切替部210の出力の組み合わせに基づいて、最終的な周波数切替信号が出力される構成であってもよい。 (3)上述の実施の形態として例示した構成は、本開示の構成の一例であり、別の公知の技術と組み合わせることも可能であるし、本開示の要旨を逸脱しない範囲で、一部を省略する等、変更して構成することも可能である。また
[ZH CN112332658A]: 一种多电平变换器的控制方法 [EN CN112332658A]: Control method of multi-level converter | [ZH CN112332658A]: 本发明适用于电力技术领域，提供了一种多电平变换器的控制方法，所述方法包括：采集LC滤波器在一个驱动脉冲周期内的电感电流；基于电感电流的上升时段的斜率确定待调节的第一开关管以及待调节的第一开关管的占空比调节量，基于待调节的第一开关管的占空比调节量对待调节的第一开关管的占空比进行调节；基于电感电流的下降时段的斜率确定待调节的第二开关管以及待调节的第二开关管的占空比调节量，基于待调节的第二开关管的占空比调节量对待调节的第二开关管的占空比进行调节。本发明只需采集LC滤波器的电感电流即可控制多电平变换器的各个飞跨电容电压达到均衡，实现方法简单且不受多电平变换器的电平数量的影响。 [EN CN112332658A]: The invention is applicable to the technical field of electric power, and provides a control method of a multi-level converter, which comprises the following steps of: acquiring the inductive currentof an LC filter in a driving pulse period; determining a to-be-adjusted first switching tube and a duty ratio adjustment amount of the to-be-adjusted first switching tube based on the slope of the rising period of the inductive current, and adjusting the duty ratio of the to-be-adjusted first switching tube based on the duty ratio adjustment amount of the to-be-adjusted first switching tube; and determining a to-be-adjusted second switching tube and a duty ratio adjustment amount of the to-be-adjusted second switching tube based on the slope of the falling period of the inductive current, andadjusting the duty ratio of the to-be-adjusted second switching tube based on the duty ratio adjustment amount of the to-be-adjusted second switching tube. According to the invention, the voltage of each flying capacitor of the multilevel converter can be controlled to be balanced only by acquiring the inductive current of the LC filter, and the implementation method is simple and is not influenced by the level number of the multilevel converter. | CN112332658A | 2021-02-05 | CN202011134919A | 2020-10-21 | CN202011134919A, 2020-10-21 | CN112332658A: 2021-02-05 | CN ELECT TECH NO 13 RES INST | GU ZHANBIAO ZHANG ZHILIANG CHENG SHIPENG REN XIAOYONG XU SENFENG TAN CHAO | H02M3/07: I H02M1/14: I | H02M1/14: I H02M3/073: I | CN103872920A CN104143914A US2017093270A1 CN109687704A CN111371320A |  | [ZH CN112332658A]: 1 .一种多电平变换器的控制方法，其特征在于，所述方法应用于多电平变换器，所述多 电平变换器包括串接的至少两个开关管组、并联在相邻两个开关管组之间的飞跨电容、以 及LC滤波器;每个开关管组包括第一开关管和第二开关管;各个开关管组的第一开关管串 联连接后的第一端接外部电源的正极，各个开关管组的第二开关管串联连接后的第一端接 外部电源的负极，各个开关管组的第一开关管串联连接后的第二端、各个开关管组的第二 开关管串联连接后的第二端均接LC滤波器的输入端，LC滤波器的输出端用于外接负载;其 中，对于并联在相邻两个开关管组之间的某个飞跨电容，第一开关管组的第一开关管与第 二开关管组的第一开关管串联所形成的串接点接该飞跨电容的第一端，第一开关管组的第 二开关管与第二开关管组的第二开关管串联所形成的串接点接该飞跨电容的第二端； 所述多电平变换器的控制方法包括： 采集所述LC滤波器在一个驱动脉冲周期内的电感电流； 基于所述电感电流的上升时段的斜率确定待调节的第一开关管以及所述待调节的第 一开关管的占空比调节量，基于所述待调节的第一开关管的占空比调节量对所述待调节的 第一开关管的占空比进行调节； 基于所述电感电流的下降时段的斜率确定待调节的第二开关管以及所述待调节的第 二开关管的占空比调节量，基于所述待调节的第二开关管的占空比调节量对所述待调节的 第二开关管的占空比进行调节。 2 .如权利要求1所述的多电平变换器的控制方法，其特征在于，所述基于所述电感电流 的上升时段的斜率确定待调节的第一开关管以及所述待调节的第一开关管的占空比调节 量，包括： 计算所述电感电流的各个上升时段的斜率，以及所述电感电流的各个上升时段的斜率 的平均值； 分别计算每一个上升时段的斜率与所述平均值的差值，并确定最大差值； 基于所述最大差值确定待调节的第一开关管以及所述待调节的第一开关管的占空比 调节量。 3 .如权利要求2所述的多电平变换器的控制方法，其特征在于，基于所述最大差值确定 待调节的第一开关管，包括： 确定所述最大差值对应的上升时段； 根据所述最大差值对应的上升时段在所述驱动脉冲周期内的位置确定待调节的第一 开关管。 4 .如权利要求2所述的多电平变换器的控制方法，其特征在于，基于所述最大差值确定 所述待调节的第一开关管的占空比调节量，包括： 将所述最大差值输入预设的比例积分控制器，得到所述待调节的第一开关管的占空比 调节量。 5 .如权利要求1所述的多电平变换器的控制方法，其特征在于，在采集所述LC滤波器在 一个驱动脉冲周期内的电感电流之前，还包括： 基于所述多电平变换器的预设输入电压和预设输出电压设定各个第一开关管的驱动 脉冲的占空比。 6 .如权利要求5所述的多电平变换器的控制方法，其特征在于，若所述多电平变换器的 参考地为外部电源负极，则所述基于所述多电平变换器的预设输入电压和预设输出电压设 定各个第一开关管的驱动脉冲的占空比,包括： 嗫 式中,D为驱动脉冲的占空比,Vin为预设输入电压,V°ut为预设输出电压。 7 .如权利要求5所述的多电平变换器的控制方法，其特征在于，若所述多电平变换器的 参考地为外部电源的中间点，则所述基于所述多电平变换器的预设输入电压和预设输出电 压设定各个第一开关管的驱动脉冲的占空比,包括： /) = ^ + 0.5 嗫 式中,D为驱动脉冲的占空比,Vin为预设输入电压,V°ut为预设输出电压。 8 .如权利要求1所述的多电平变换器的控制方法，其特征在于,在采集所述LC滤波器在 一个驱动脉冲周期内的电感电流之前，还包括： 对于串联连接的各个第一开关管，从所述LC滤波器的输入端至所述外部电源的正极, 以3607N为延时间隔依次设定串联连接的各个第一开关管的驱动脉冲的相位;其中,Ν为开 关管组的个数。 9 .如权利要求1所述的多电平变换器的控制方法，其特征在于，在采集所述LC滤波器在 一个驱动脉冲周期内的电感电流之前，还包括： 对于任意一个开关管组，将第一开关管的驱动脉冲和第二开关管的驱动脉冲设定为互 补。 10 .如权利要求9所述的多电平变换器的控制方法，其特征在于，在采集所述LC滤波器 在一个驱动脉冲周期内的电感电流之前，还包括： 对于任意一个开关管组，设定所述第一开关管的驱动脉冲和所述第二开关管的驱动脉 冲的死区时间。 [EN CN112332658A]: 1 A control method of a multi-level converter, characterized in that the method is applied to a multi-level converter, the multi-level converter includes at least two switch tube groups connected in series, connected in parallel to two adjacent Flying capacitors and LC filters between two switch tube groups; each switch tube group includes a first switch tube and a second switch tube; the first terminal of each switch tube group connected in series after the first switch tube is connected to the outside The positive pole of the power supply, the first end of the second switch tube of each switch tube group connected in series is connected to the negative electrode of the external power supply, the second end of the first switch tube of each switch tube group connected in series, the second end of each switch tube group The second end of the switch tube connected in series is connected to the input end of the LC filter, and the output end of the LC filter is used for an external load; among them, for a flying capacitor connected in parallel between two adjacent switch tube groups, The series connection formed by the first switching tube of the first switching tube group and the first switching tube of the second switching tube group in series is connected to the first end of the flying capacitor, and the second switching tube of the first switching tube group is connected to the second switching tube. The series connection point formed by the series connection of the second switching tubes of the switching tube group is connected to the second end of the flying capacitor; the control method of the multilevel converter includes: collecting the inductance of the LC filter in a driving pulse period Current; determining the first switch tube to be adjusted and the duty cycle adjustment amount of the first switch tube to be adjusted based on the slope of the rising period of the inductor current, based on the duty cycle of the first switch tube to be adjusted The ratio adjustment amount adjusts the duty cycle of the first switch tube to be adjusted; The second switching tube to be adjusted and the duty cycle adjustment amount of the second switching tube to be adjusted are determined based on the slope of the falling period of the inductor current, and the duty cycle adjustment is based on the second switching tube to be adjusted Adjust the duty cycle of the second switch tube to be adjusted. 2 The control method of the multilevel converter of claim 1, wherein the first switch to be adjusted and the first switch to be adjusted are determined based on the slope of the rising period of the inductor current The duty cycle adjustment amount of the tube includes: calculating the slope of each rising period of the inductor current and the average value of the slope of each rising period of the inductor current; calculating the slope of each rising period and the average value respectively And determine the maximum difference; determine the first switch tube to be adjusted and the duty cycle adjustment amount of the first switch tube to be adjusted based on the maximum difference. 3 The control method of a multilevel converter according to claim 2, wherein determining the first switch tube to be adjusted based on the maximum difference value comprises: determining the rising period corresponding to the maximum difference value; The position of the rising period corresponding to the maximum difference value within the driving pulse period determines the first switch tube to be adjusted. 4 The control method of the multi-level converter according to claim 2, wherein determining the duty cycle adjustment amount of the first switch tube to be adjusted based on the maximum difference value comprises: reducing the maximum The difference is input to a preset proportional integral controller to obtain the duty cycle adjustment value of the first switch tube to be adjusted. 5 The control method of the multi-level converter according to claim 1, wherein before collecting the inductor current of the LC filter in a driving pulse period, the method further comprises: based on the multi-level converter The preset input voltage and the preset output voltage set the duty ratio of the driving pulse of each first switch tube. 6 The control method of the multi-level converter according to claim 5, wherein if the multi-level converter is The reference ground is the negative electrode of the external power supply, and the setting of the duty cycle of the driving pulse of each first switching tube based on the preset input voltage and the preset output voltage of the multilevel converter includes: Move one's lips In the formula, D is the duty ratio of the driving pulse, Vin is the preset input voltage, and V°ut is the preset output voltage. 7 The control method of the multilevel converter according to claim 5, wherein if the reference ground of the multilevel converter is an intermediate point of the external power supply, the multilevel converter is based on the The preset input voltage and the preset output voltage set the duty cycle of the driving pulse of each first switching tube, including: /) = ^ + 0.5 whistle In the formula, D is the duty ratio of the driving pulse, Vin is the preset input voltage, and V°ut is the preset output voltage. 8 The control method of the multi-level converter according to claim 1, wherein before collecting the inductor current of the LC filter in one driving pulse period, the method further comprises: for each first switch connected in series From the input end of the LC filter to the positive pole of the external power supply, the phase of the drive pulse of each first switching tube connected in series is sequentially set with a delay interval of 3607N; where N is the switching tube group Number. 9 The control method of the multi-level converter according to claim 1, characterized in that, before collecting the inductance current of the LC filter in a driving pulse period, the method further comprises: For any switch tube group, The driving pulse of the first switching tube and the driving pulse of the second switching tube are set to be complementary. 10 The control method of the multilevel converter according to claim 9, characterized in that, before collecting the inductance current of the LC filter in a driving pulse period, it further comprises: For any switch tube group, set Determine the dead time of the driving pulse of the first switching tube and the driving pulse of the second switching tube. | [ZH CN112332658A]: 一种多电平变换器的控制方法 技术领域 [0001]本发明属于电力技术领域，尤其涉及一种多电平变换器的控制方法。 背景技术 [0002]多电平变换器利用飞跨电容使得输入电压在串联的各开关管之间均分，以及降低 各开关管的压力。 [0003] 然而，由于输入电源不是理想电压源以及门极驱动信号延迟不一致等原因，在实 际工作时，多电平变换器的飞跨电容电压不能完全均衡，当飞跨电容电压偏离其理论值时， 会导致与之连接的开关管应力增大，容易造成开关管损坏，同时偏压也会增大电感电流纹 波，降低输出电压的质量。目前，现有技术主要通过直接检测各个飞跨电容电压的方法来对 偏压进行控制和调整，但是该方法存在浮地电压检测困难、电平数较多时检测电路复杂等 缺点。 发明内容 [0004]有鉴于此，本发明实施例提供了一种多电平变换器的控制方法，以解决现有技术 中难以控制多电平变换器的飞跨电容电压均衡的问题。 [0005] 本发明实施例提供了一种多电平变换器的控制方法，该方法应用于多电平变换 器，多电平变换器包括串接的至少两个开关管组、并联在相邻两个开关管组之间的飞跨电 容、以及LC滤波器；每个开关管组包括第一开关管和第二开关管；各个开关管组的第一开关 管串联连接后的第一端接外部电源的正极，各个开关管组的第二开关管串联连接后的第一 端接外部电源的负极，各个开关管组的第一开关管串联连接后的第二端、各个开关管组的 第二开关管串联连接后的第二端均接LC滤波器的输入端，LC滤波器的输出端用于外接负 载;其中，对于并联在相邻两个开关管组之间的某个飞跨电容，第一开关管组的第一开关管 与第二开关管组的第一开关管串联所形成的串接点接该飞跨电容的第一端，第一开关管组 的第二开关管与第二开关管组的第二开关管串联所形成的串接点接该飞跨电容的第二端； [0006] 多电平变换器的控制方法包括： [0007]采集LC滤波器在一个驱动脉冲周期内的电感电流； [0008]基于电感电流的上升时段的斜率确定待调节的第一开关管以及待调节的第一开 关管的占空比调节量，基于待调节的第一开关管的占空比调节量对待调节的第一开关管的 占空比进行调节； [0009]基于电感电流的下降时段的斜率确定待调节的第二开关管以及待调节的第二开 关管的占空比调节量，基于待调节的第二开关管的占空比调节量对待调节的第二开关管的 占空比进行调节。 [0010]可选的，基于电感电流的上升时段的斜率确定待调节的第一开关管以及待调节的 第一开关管的占空比调节量，包括： [0011]计算电感电流的各个上升时段的斜率，以及电感电流的各个上升时段的斜率的平 均值； [0012]分别计算每一个上升时段的斜率与平均值的差值，并确定最大差值； [0013]基于最大差值确定待调节的第一开关管以及待调节的第一开关管的占空比调节 量。 [0014]可选的，基于最大差值确定待调节的第一开关管，包括： [0015]确定最大差值对应的上升时段； [0016]根据最大差值对应的上升时段在驱动脉冲周期内的位置确定待调节的第一开关 管。 [0017]可选的，基于最大差值确定待调节的第一开关管的占空比调节量,包括： [0018]将最大差值输入预设的比例积分控制器，得到待调节的第一开关管的占空比调节 量。 [0019]可选的，采集LC滤波器在一个驱动脉冲周期内的电感电流之前，还包括： [0020] 基于多电平变换器的预设输入电压和预设输出电压设定各个第一开关管的驱动 脉冲的占空比。 [0021]可选的，若多电平变换器的参考地为外部电源负极，则基于多电平变换器的预设 输入电压和预设输出电压设定各个第一开关管的驱动脉冲的占空比,包括： [0022] D 匕力 [0023] 式中，D为驱动脉冲的占空比,Vm为预设输入电压,V°ut为预设输出电压。 [0024]可选的，若多电平变换器的参考地为外部电源的中间点，则基于多电平变换器的 预设输入电压和预设输出电压设定各个第一开关管的驱动脉冲的占空比,包括： [0025] D = 十 0,5 [0026] 式中，D为驱动脉冲的占空比,Vm为预设输入电压,V°ut为预设输出电压。 [0027]可选的，采集LC滤波器在一个驱动脉冲周期内的电感电流之前，还包括： [0028]对于串联连接的各个第一开关管，从LC滤波器的输入端至外部电源的正极，以 360 7N为延时间隔依次设定串联连接的各个第一开关管的驱动脉冲的相位;其中,Ν为开关 管组的个数。 [0029]可选的，采集LC滤波器在一个驱动脉冲周期内的电感电流之前，还包括： [0030]对于任意一个开关管组,将第一开关管的驱动脉冲和第二开关管的驱动脉冲设定 为互补。 [0031]可选的，采集LC滤波器在一个驱动脉冲周期内的电感电流之前，还包括： [0032]对于任意一个开关管组,设定第一开关管的驱动脉冲和第二开关管的驱动脉冲的 死区时间。 [0033]本发明实施例与现有技术相比存在的有益效果是： [0034]本发明实施例提供的多电平变换器的控制方法，通过采集LC滤波器在一个驱动脉 冲周期内的电感电流，并根据电感电流的上升时段和下降时段的斜率确定需要调节的开关 管以及该开关管的占空比调节量,并根据占空比调节量对需要调节的开关管的占空比进行 调整，进而改变与开关管连接的飞跨电容的电压，最终使多电平变换器的各个飞跨电容电 压达到均衡。本发明只需采集LC滤波器的电感电流即可控制多电平变换器的各个飞跨电容 电压达到均衡，实现方法简单且不受多电平变换器的电平数量的影响。 附图说明 [0035]为了更清楚地说明本发明实施例中的技术方案，下面将对实施例或现有技术描述 中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本发明的一些 实施例，对于本领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可以根据这些 附图获得其他的附图。 [0036]图1是本发明实施例提供的多电平变换器的结构示意图； [0037]图2是本发明实施例提供的多电平变换器的控制方法的实现流程示意图； [0038]图3是本发明实施例提供的四电平变换器的结构示意图； [0039]图4是本发明实施例提供的四电平变换器在理想工作状态下的驱动脉冲和关键参 数波形示意图； [0040]图5是本发明实施例提供的在一个驱动脉冲周期内对四电平变换器进行控制前和 控制后的驱动脉冲和关键参数波形示意图； [0041]图6是本发明实施例提供的对四电平变换器进行多个驱动脉冲周期控制的驱动脉 冲和关键参数波形示意图。 具体实施方式 [0042]以下描述中，为了说明而不是为了限定，提出了诸如特定系统结构、技术之类的具 体细节，以便透彻理解本发明实施例。然而，本领域的技术人员应当清楚，在没有这些具体 细节的其它实施例中也可以实现本发明。在其它情况中，省略对众所周知的系统、装置、电 路以及方法的详细说明，以免不必要的细节妨碍本发明的描述。 [0043]为了说明本发明所述的技术方案，下面通过具体实施例来进行说明。 [0044] 本发明实施例提供了一种多电平变换器的控制方法，该方法应用于多电平变换 器,如图1所示,多电平变换器包括串接的至少两个开关管组S1-SN （N叁2）、并联在相邻两个 开关管组之间的飞跨电容C1-CN-1、以及LC滤波器。每个开关管组Sn包括第一开关管SNa和第 二开关管SNb,各个开关管组的第一开关管Sla-SNa串联连接后的第一端接外部电源的正极， 各个开关管组的第二开关管S1b-SNb串联连接后的第一端接外部电源的负极，各个开关管组 的第一开关管S1a-SNa串联连接后的第二端、各个开关管组的第二开关管S1b-SNb串联连接后 的第二端均接LC滤波器的输入端，LC滤波器的输出端用于外接负载R。其中，对于并联在相 邻两个开关管组之间的某个飞跨电容，例如C1,第一开关管组S1的第一开关管S1a与第二开 关管组S2的第一开关管S2a串联所形成的串接点接该飞跨电容C1的第一端，第一开关管组S1 的第二开关管S1b与第二开关管组S2的第二开关管S2b串联所形成的串接点接该飞跨电容C1 的第二端。 [0045]参照图2所示，本发明实施例提供的多电平变换器的控制方法具体包括以下步骤： [0046] 步骤S101,采集LC滤波器在一个驱动脉冲周期内的电感电流。 [0047]在本发明实施例中，可以利用电流传感器采集LC滤波器在一个驱动脉冲周期内的 电感电流;如采用串联电阻的方案，设电流采样电阻为Rsense,采样芯片的增益为Av,控制器 模数转换模块测量到的电压为VADC,则可以得到电感电流II为： [0049]步骤S102,基于电感电流的上升时段的斜率确定待调节的第一开关管以及待调节 的第一开关管的占空比调节量，基于待调节的第一开关管的占空比调节量对待调节的第一 开关管的占空比进行调节。 [0050]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式，基于电感电流的上升时段的斜率确定待调节的第一开关管以及待调节的第一开关管的 占空比调节量，包括： [0051]计算电感电流的各个上升时段的斜率，以及电感电流的各个上升时段的斜率的平 均值； [0052]分别计算每一个上升时段的斜率与平均值的差值，并确定最大差值； [0053]基于最大差值确定待调节的第一开关管以及待调节的第一开关管的占空比调节 量。 [0054]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式,基于最大差值确定待调节的第一开关管，包括： [0055]确定最大差值对应的上升时段； [0056]根据最大差值对应的上升时段在驱动脉冲周期内的位置确定待调节的第一开关 管。 [0057]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式,基于最大差值确定待调节的第一开关管的占空比调节量，包括： [0058]将最大差值输入预设的比例积分控制器，得到待调节的第一开关管的占空比调节 量。 [0059] 在本发明实施例中，若一个驱动脉冲周期内充入飞跨电容的电荷量和飞跨电容放 出的电荷量总和为零，即流过飞跨电容电流的积分为零，则飞跨电容两端的电压保持不变。 而在移相PWM控制模式下,在一个驱动脉冲周期内的任意时刻，开关管的节点电压Vsw总是对 应某个飞跨电容电压或某两个飞跨电容电压的和，且输出电压基本保持不变，因此,LC滤波 器的电感L两端的电压能够反映飞跨电容的电压情况，而电感L两端的电压又体现在电感电 流的变化率上，也就是电感电流II的斜率，因此，可以通过控制电感电流的斜率来控制飞跨 电容的电压达到均衡。 [0060] 在本发明实施例中，当各个飞跨电容的电压达到均衡时，电感电流的各个上升时 间段斜率应当是相同的，各个下降时间段斜率也应当是相同的，当某个时间段的斜率出现 差异时，则表明该时间段对应的飞跨电容的电压不再均衡，通过对该时间段对应的开关管 占空比进行调节，即可对不均衡的飞跨电容的电压进行调整。 [0061]步骤S103,基于电感电流的下降时段的斜率确定待调节的第二开关管以及待调节 的第二开关管的占空比调节量，基于待调节的第二开关管的占空比调节量对待调节的第二 开关管的占空比进行调节。 [0062]在本发明实施例中，对第二开关管进行调节的过程与步骤S102类似，即计算电感 电流的各个下降时段的斜率，以及电感电流的各个下降时段的斜率的平均值，分别计算每 一个下降时段的斜率与平均值的差值，并确定最大差值，基于最大差值确定待调节的第二 开关管以及待调节的第二开关管的占空比调节量，基于待调节的第一开关管的占空比调节 量对待调节的第一开关管的占空比进行调节。具体实施过程可以参考上述步骤S102。 [0063]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式,在步骤S101之前，还包括： [0064] 步骤S1001,基于多电平变换器的预设输入电压和预设输出电压设定各个第一开 关管Sla-SNa的驱动脉冲的占空比。 [0065]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式，若多电平变换器的参考地为外部电源负极,则基于多电平变换器的预设输入电压和预 设输出电压设定各个第一开关管Sla-SNa的驱动脉冲的占空比，包括： [0066] D = [0067] 式中，D为驱动脉冲的占空比,Vm为预设输入电压,V°ut为预设输出电压。 [0068]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式，若多电平变换器的参考地为外部电源的中间点，则基于多电平变换器的预设输入电压 和预设输出电压设定各个第一开关管Sla-SNa的驱动脉冲的占空比，包括： [0069] D = —+。·5 匕收 [0070] 式中,D为驱动脉冲的占空比,Vm为预设输入电压,V°ut为预设输出电压。 [0071] 在本发明实施例中，根据多电平变换器的预设输入电压和预设输出电压设置各个 第一开关管Sla-SNa的驱动脉冲的占空比，以使多电平变换器处于不考虑偏压情况下的理想 工作状态。另外，参照图1所示，若多电平变换器的参考地为外部电源的中间点，则需要在外 部电源的两端并联两个串联的电容Cil和Ci2,以获得输入电压的中间点。 [0072]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式,在步骤S101之前，还包括： [0073] 步骤S1002,对于串联连接的各个第一开关管Sla-SNa,从LC滤波器的输入端至外部 电源的正极，以360°/N为延时间隔依次设定串联连接的各个第一开关管Sla-SNa的驱动脉冲 的相位;其中，Ν为开关管组的个数。 [0074]可选的，作为本发明实施例提供的多电平变换器的控制方法的一种具体实施方 式,在步骤S101之前，还包括： [0075] 步骤S1003,对于任意一个开关管组Si,将第一开关管Sia的驱动脉冲和第二开关管 Sib的驱动脉冲设定为互补，并设定第一开关管Sia的驱动脉冲和第二开关管Sib的驱动脉冲 的死区时间。 [0076]在本发明实施例中，对于任意一个开关管组Si,第一开关管Sia与第二开关管Sib总 是互补导通，并且，通过在互补导通的第一开关管Sia与第二开关管Sib之间设置死区时间， 在死区时间内，互补导通的第一开关管Sia与第二开关管Sib均为关断状态，可以避免互补导 通的第一开关管Sia与第二开关管Sib可能在状态变化瞬间同时导通导致飞跨电容短接。 [0077]示例性的，以下将通过一种直流-直流变换的四电平变换器来对本发明实施例提 供的多电平变换器的控制方法进行说明。 [0078] 参照图3所示，四电平变换器具有三个开关管组Si、S2、S3,该四电平变换器的具体 参数如表1所示。 [0079] 表1四电平变换器参数 48V 匕 ut 12V [0080] 2.2μΕ L 50μΗ C 100户 /； 100kHz [0081]首先设定四电平变换器的第一开关管Sla、S2a、S3a和第二开关管Slb、S2b、S3b的驱动 脉冲,包括： [0082] ⑴设定第一开关管Sla、S2a、S3a的驱动脉冲的占空比 [0083]由于四电平变换器的参考地为外部直流电源负极，因此，根据公式D = Vw/Vin计算 得到驱动脉冲的占空比为0.25。 [0084] ⑵设置第一开关管Sla、S2a、S3a的驱动脉冲的相位关系为S2a滞后Sia 120。，S3a滞后 S2a 120Οο [0085] ⑶将Sib的驱动脉冲设定为与Sia互补，S2b的驱动脉冲设定为与S2a互补，S3b的驱动 脉冲设定为与S3a互补，并预留一定的死区时间，由于Sla、S2a、S3a的驱动脉冲确定，因此，也能 够确定Slb、S2b、S3b的驱动脉冲。 [0086] 当四电平变换器工作在理想状态下时，第一开关管Sla、S2a、S3a的驱动脉冲以及四 电平变换器中的关键参数波形如图4所示，可以看出，当飞跨电容Ci与C2的电压均衡时，即 Ici向飞跨电容C1中充入的电荷量与飞跨电容C1放出的电荷量相等，IC2向飞跨电容C2中充入 的电荷与飞跨电容C2放出的电荷量相等时，各个开关管的节点电压Vsw是相同的，也就是飞 跨电容C1与飞跨电容C2的电压是均衡的，相应的，电感电流II的各个上升段斜率kLupl、kLup2、 kLup3相同，各个下降段斜率kLdnl、kLdn2、kLdn3相同。然而，在实际应用中，由于输入电源不是理 想电压源以及门极驱动信号延迟不一致等原因，飞跨电容C1和飞跨电容C2的电荷不能完全 一致，进而导致电感电流II的斜率产生差异。 [0087]对于本发明实施例提供的四电平变换器，由于在电感电流的下降时段，电感两端 的电压均为输出电压，而输出电压认为保持不变，因此电感电流下降斜率永远相同，因此只 需要对上升时段的斜率进行控制。 [0088] 参照图5所示，通过采集四电平变换器的LC滤波器在一个驱动脉冲周期内的电感 电流，计算电感电流的各个上升时段的斜率kLupl、kLup2、kLup3 ,以及kLupl、kLup2、kLup3的平均值, 分别计算kLupl、kLup2、kLup3与平均值的差值，并确定最大差值，发现斜率kLup2产生了较大差 异，因此，将最大差值输入预设的比例积分控制器，得到占空比调节量AD,并根据占空比调 节量Δ D调节与斜率kLup2对应的第一开关管S2a的占空比。在本实施例中，为了提高控制效 率，基于占空比调节量AD同时调节了 Sla、S2a的占空比，即减小了 Sia的占空比，增大了 S2a的 占空比，实际应用中也可以只调节S2a的占空比。 [0089]由图5可以看出，在一个驱动脉冲周期内，通过减小S1a的驱动脉冲的占空比，增大 S2a的驱动脉冲的占空比，进而增大了飞跨电容C1的电荷量QC1,相应的，斜率kLup2与斜率 kLup1、kLup3之间的差异也变小了。如图6所示，经过多个驱动脉冲周期的调节，各上升时段的 斜率kLup1、kLup2、kLup3逐渐趋于相等，最终使电压出现偏移的飞跨电容纠正到理论稳态值。 [0090]需要指出的是，以上仅示出了直流-直流变换的四电平变换器的控制过程，对于直 流-直流变换的多电平变换器或交流-直流变换的多电平变换器，也可采用本发明实施例提 供的多电平变换器的控制方法进行控制，控制过程与上述实施例的控制过程类似，本发明 在此不再进行详述。 [0091]由以上内容可知，本发明实施例提供的多电平变换器的控制方法，通过采集LC滤 波器在一个驱动脉冲周期内的电感电流，并根据电感电流的上升时段和下降时段的斜率确 定需要调节的开关管以及该开关管的占空比调节量，以及根据占空比调节量对需要调节的 开关管的占空比进行调整，进而改变与开关管连接的飞跨电容的电压，最终使多电平变换 器的各个飞跨电容电压达到均衡。本发明只需采集LC滤波器的电感电流即可控制多电平变 换器的各个飞跨电容电压达到均衡，实现方法简单且不受多电平变换器的电平数量的影 响。 [0092]应理解，上述实施例中各步骤的序号的大小并不意味着执行顺序的先后，各过程 的执行顺序应以其功能和内在逻辑确定，而不应对本发明实施例的实施过程构成任何限 定。 [0093]以上所述实施例仅用以说明本发明的技术方案，而非对其限制；尽管参照前述实 施例对本发明进行了详细的说明，本领域的普通技术人员应当理解:其依然可以对前述各 实施例所记载的技术方案进行修改，或者对其中部分技术特征进行等同替换;而这些修改 或者替换，并不使相应技术方案的本质脱离本发明各实施例技术方案的精神和范围，均应 包含在本发明的保护范围之内。 [EN CN112332658A]: Technical field of a control method of multilevel converter [0001] The present invention belongs to the field of power technology, and in particular relates to a control method of a multilevel converter. Background technique [0002] The multilevel converter uses flying capacitors to make the input voltage evenly divided among the switch tubes connected in series, and to reduce the pressure of each switch tube. [0003] However, due to the fact that the input power is not an ideal voltage source and the gate drive signal delay is inconsistent, in actual operation, the flying capacitor voltage of the multilevel converter cannot be completely balanced. When the flying capacitor voltage deviates from its theoretical value At the same time, the stress of the switch tube connected to it will increase, which is easy to damage the switch tube. At the same time, the bias voltage will also increase the inductor current ripple and reduce the quality of the output voltage. At present, the prior art mainly controls and adjusts the bias voltage by directly detecting the voltage of each flying capacitor, but this method has disadvantages such as difficulty in detecting the floating voltage and complicated detection circuit when the number of levels is large. Summary of the invention [0004] In view of this, an embodiment of the present invention provides a control method of a multi-level converter to solve the problem that it is difficult to control the flying capacitor voltage balance of the multi-level converter in the prior art. [0005] The embodiment of the present invention provides a control method of a multi-level converter, which is applied to a multi-level converter. The multi-level converter includes at least two switch tube groups connected in series and connected in parallel in adjacent ones. The flying capacitor and the LC filter between the two switching tube groups; each switching tube group includes a first switching tube and a second switching tube; the first terminal connection after the first switching tube of each switching tube group is connected in series The positive pole of the external power supply, the first end of the second switch tube of each switch tube group connected in series is connected to the negative electrode of the external power supply, the second end of the first switch tube of each switch tube group connected in series, the first end of each switch tube group After the two switch tubes are connected in series, the second end is connected to the input end of the LC filter, and the output end of the LC filter is used for an external load; among them, for a flying capacitor connected in parallel between two adjacent switch tube groups , The series connection formed by the first switch tube of the first switch tube group and the first switch tube of the second switch tube group in series is connected to the first end of the flying capacitor, and the second switch tube of the first switch tube group is connected to the first terminal of the flying capacitor. The series connection point formed by the series connection of the second switching tubes of the two switching tube groups is connected to the second end of the flying capacitor; [0006] The control method of the multilevel converter includes: [0007] Collect the inductance current of the LC filter in one drive pulse period; [0008] The first switch tube to be adjusted and the duty cycle adjustment amount of the first switch tube to be adjusted are determined based on the slope of the rising period of the inductor current, and the duty cycle adjustment amount of the first switch tube to be adjusted is to be adjusted The duty cycle of the first switch tube is adjusted; [0009] The second switching tube to be adjusted and the duty cycle adjustment amount of the second switching tube to be adjusted are determined based on the slope of the falling period of the inductor current, and the duty cycle adjustment amount of the second switching tube to be adjusted is to be adjusted The duty cycle of the second switch tube is adjusted. [0010] Optionally, determining the first switch tube to be adjusted and the duty cycle adjustment amount of the first switch tube to be adjusted based on the slope of the rising period of the inductor current includes: [0011] Calculate the slope of each rising period of the inductor current, and the flat of the slope of each rising period of the inductor current Mean [0012] Calculate the difference between the slope of each rising period and the average value, and determine the maximum difference; [0013] The first switch tube to be adjusted and the duty cycle adjustment amount of the first switch tube to be adjusted are determined based on the maximum difference. [0014] Optionally, determining the first switch tube to be adjusted based on the maximum difference includes: [0015] Determine the rising period corresponding to the maximum difference; [0016] The first switch tube to be adjusted is determined according to the position of the rising period corresponding to the maximum difference in the driving pulse period. [0017] Optionally, determining the duty cycle adjustment amount of the first switch tube to be adjusted based on the maximum difference includes: [0018] The maximum difference is input to the preset proportional integral controller to obtain the duty cycle adjustment value of the first switch tube to be adjusted. [0019] Optionally, before collecting the inductor current of the LC filter within a driving pulse period, the method further includes: [0020] The duty cycle of the driving pulse of each first switch tube is set based on the preset input voltage and the preset output voltage of the multilevel converter. [0021] Optionally, if the reference ground of the multilevel converter is the negative electrode of the external power supply, the duty of the driving pulse of each first switching tube is set based on the preset input voltage and the preset output voltage of the multilevel converter. Air ratio, including: [0022] D dagger force [0023] In the formula, D is the duty ratio of the driving pulse, Vm is the preset input voltage, and V°ut is the preset output voltage. [0024] Optionally, if the reference ground of the multi-level converter is the midpoint of the external power supply, the drive pulse of each first switching tube is set based on the preset input voltage and the preset output voltage of the multi-level converter The duty cycle includes: [0025] D = ten 0,5 [0026] In the formula, D is the duty cycle of the driving pulse, Vm is the preset input voltage, and V°ut is the preset output voltage. [0027] Optionally, before collecting the inductor current of the LC filter within a driving pulse period, the method further includes: [0028] For each first switching tube connected in series, from the input end of the LC filter to the positive electrode of the external power supply, the phase of the drive pulse of each first switching tube connected in series is sequentially set with a delay interval of 360 7N; Among them, N is the number of switch tube groups. [0029] Optionally, before collecting the inductor current of the LC filter within a driving pulse period, the method further includes: [0030] For any switch tube group, the drive pulse of the first switch tube and the drive pulse of the second switch tube are set to be complementary. [0031] Optionally, before collecting the inductor current of the LC filter within a driving pulse period, the method further includes: [0032] For any switch tube group, set the dead time of the drive pulse of the first switch tube and the drive pulse of the second switch tube. [0033] Compared with the prior art, the embodiments of the present invention have the following beneficial effects: [0034] The control method of the multilevel converter provided by the embodiment of the present invention collects the inductor current of the LC filter in a driving pulse period, and determines the switch that needs to be adjusted according to the slope of the rising period and the falling period of the inductor current The duty cycle adjustment amount of the switch tube and the switch tube, and the duty cycle of the switch tube that needs to be adjusted is performed according to the duty cycle adjustment amount. Adjust, and then change the voltage of the flying capacitor connected with the switch tube, and finally make the voltage of each flying capacitor of the multilevel converter reach equilibrium. The invention only needs to collect the inductance current of the LC filter to control the voltages of the flying capacitors of the multilevel converter to reach equilibrium, and the realization method is simple and is not affected by the number of levels of the multilevel converter. Description of the drawings [0035] In order to more clearly illustrate the technical solutions in the embodiments of the present invention, the following will briefly introduce the embodiments or the accompanying drawings needed in the description of the prior art. Obviously, the drawings in the following description are merely For some of the embodiments of the present invention, for those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative labor. [0036] FIG. 1 is a schematic structural diagram of a multilevel converter provided by an embodiment of the present invention; [0037] FIG. 2 is a schematic diagram of an implementation process of a control method of a multilevel converter provided by an embodiment of the present invention; [0038] FIG. 3 is a schematic structural diagram of a four-level converter provided by an embodiment of the present invention; [0039] FIG. 4 is a schematic diagram of driving pulses and key parameter waveforms of a four-level converter in an ideal working state according to an embodiment of the present invention; [0040] FIG. 5 is a schematic diagram of driving pulses and key parameter waveforms before and after controlling the four-level converter within a driving pulse period according to an embodiment of the present invention; [0041] FIG. 6 is a schematic diagram of driving pulses and key parameter waveforms for controlling multiple driving pulse cycles of a four-level converter according to an embodiment of the present invention. Detailed ways [0042] In the following description, for the purpose of illustration rather than limitation, specific details such as a specific system structure and technology are proposed for a thorough understanding of the embodiments of the present invention. However, it should be clear to those skilled in the art that the present invention can also be implemented in other embodiments without these specific details. In other cases, detailed descriptions of well-known systems, devices, circuits, and methods are omitted to avoid unnecessary details from obstructing the description of the present invention. [0043] In order to illustrate the technical solutions of the present invention, specific embodiments are used for description below. [0044] The embodiment of the present invention provides a method for controlling a multilevel converter, which is applied to a multilevel converter. As shown in FIG. 1, the multilevel converter includes at least two switching tubes connected in series. Group S1-SN (N3 2), flying capacitor C1-CN-1 and LC filter connected in parallel between two adjacent switch tube groups. Each switch tube group Sn includes a first switch tube SNa and a second switch tube SNb. The first terminal of the first switch tube Sla-SNa of each switch tube group connected in series is connected to the positive pole of the external power supply. The first end of the two switching tubes S1b-SNb connected in series is connected to the negative electrode of the external power supply, the second end of the first switching tube S1a-SNa of each switching tube group is connected in series, and the second switching tube S1b- of each switching tube group is connected in series. The second ends of the SNb connected in series are all connected to the input end of the LC filter, and the output end of the LC filter is used for an external load R. Among them, for a flying capacitor connected in parallel between two adjacent switching tube groups, such as C1, the first switching tube S1a of the first switching tube group S1 and the first switching tube S2a of the second switching tube group S2 are connected in series. The series connection point formed is connected to the first end of the flying capacitor C1, and the series connection point formed by the second switching tube S1b of the first switching tube group S1 and the second switching tube S2b of the second switching tube group S2 in series is connected to the flying capacitor. Cross the second end of capacitor C1. [0045] Referring to FIG. 2, the control method of the multilevel converter provided by the embodiment of the present invention specifically includes the following steps: [0046] Step S101: Collect the inductance current of the LC filter in one driving pulse period. [0047] In the embodiment of the present invention, the current sensor can be used to collect the LC filter in a driving pulse period Inductor current; if the series resistance scheme is adopted, set the current sampling resistor to Rsense, the gain of the sampling chip to Av, and the voltage measured by the controller analog-to-digital conversion module to VADC, then the inductor current II can be obtained as: [0049] Step S102, determining the first switching tube to be adjusted and the duty cycle adjustment amount of the first switching tube to be adjusted based on the slope of the rising period of the inductor current, and adjusting based on the duty cycle of the first switching tube to be adjusted Adjust the duty cycle of the first switch tube to be adjusted. [0050] Optionally, as a specific implementation of the control method of the multilevel converter provided by the embodiment of the present invention, the first switch tube to be adjusted and the second switch tube to be adjusted are determined based on the slope of the rising period of the inductor current. The duty cycle adjustment value of a switch tube includes: [0051] Calculate the slope of each rising period of the inductor current, and the average value of the slope of each rising period of the inductor current; [0052] Calculate the difference between the slope of each rising period and the average value, and determine the maximum difference; [0053] Determine the first switching tube to be adjusted and the duty cycle adjustment amount of the first switching tube to be adjusted based on the maximum difference. [0054] Optionally, as a specific implementation of the control method of the multilevel converter provided in the embodiment of the present invention, determining the first switch tube to be adjusted based on the maximum difference includes: [0055] Determine the rising period corresponding to the maximum difference; [0056] The first switch tube to be adjusted is determined according to the position of the rising period corresponding to the maximum difference in the driving pulse period. [0057] Optionally, as a specific implementation of the control method of the multilevel converter provided by the embodiment of the present invention, determining the duty cycle adjustment amount of the first switch tube to be adjusted based on the maximum difference includes: [0058] The maximum difference is input to the preset proportional integral controller to obtain the duty cycle adjustment value of the first switch tube to be adjusted. [0059] In the embodiment of the present invention, if the sum of the amount of charge charged into the flying capacitor and the amount of charge discharged from the flying capacitor in a driving pulse period is zero, that is, the integral of the current flowing through the flying capacitor is zero, then the flying capacitor The voltage across the capacitor remains unchanged. In the phase-shift PWM control mode, at any time within a driving pulse period, the node voltage Vsw of the switch tube always corresponds to a certain flying capacitor voltage or the sum of two flying capacitor voltages, and the output voltage is basically maintained No change. Therefore, the voltage across the inductor L of the LC filter can reflect the voltage of the flying capacitor, and the voltage across the inductor L is reflected in the rate of change of the inductor current, that is, the slope of the inductor current II. Therefore, By controlling the slope of the inductor current to control the voltage across the flying capacitor to achieve equilibrium. [0060] In the embodiment of the present invention, when the voltage of each flying capacitor reaches equilibrium, the slope of each rising period of the inductor current should be the same, and the slope of each falling period should also be the same. When a certain period of time When the slope of is different, it indicates that the voltage of the flying capacitor corresponding to the time period is no longer balanced. By adjusting the duty cycle of the switch tube corresponding to the time period, the voltage of the unbalanced flying capacitor can be adjusted . [0061] Step S103, determine the second switching tube to be adjusted and the duty cycle adjustment amount of the second switching tube to be adjusted based on the slope of the falling period of the inductor current, and adjust based on the duty cycle of the second switching tube to be adjusted Adjust the duty cycle of the second switch tube to be adjusted. [0062] In the embodiment of the present invention, the process of adjusting the second switch tube is similar to step S102, that is, calculating the slope of each falling period of the inductor current, and the average value of the slope of each falling period of the inductor current, respectively. The difference between the slope of each falling period and the average value, and the maximum difference is determined, and the second switching tube to be adjusted and the duty cycle adjustment amount of the second switching tube to be adjusted are determined based on the maximum difference. The duty cycle adjustment amount of the first switching tube is adjusted to the duty cycle of the first switching tube to be adjusted. For the specific implementation process, refer to the above step S102. [0063] Optionally, as a specific implementation manner of the control method of the multilevel converter provided by the embodiment of the present invention, before step S101, the method further includes: [0064] Step S1001, based on the preset input voltage and the preset output voltage of the multilevel converter, the duty cycle of the driving pulse of each first switching tube Sla-SNa is set. [0065] Optionally, as a specific implementation of the multilevel converter control method provided by the embodiment of the present invention, if the reference ground of the multilevel converter is the negative pole of the external power supply, it is based on the multilevel converter The preset input voltage and the preset output voltage set the duty cycle of the driving pulse of each first switching tube Sla-SNa, including: [0066] D = [0067] In the formula, D is the duty ratio of the driving pulse, Vm is the preset input voltage, and V°ut is the preset output voltage. [0068] Optionally, as a specific implementation of the control method of the multilevel converter provided by the embodiment of the present invention, if the reference ground of the multilevel converter is the middle point of the external power supply, it is based on the multilevel The preset input voltage and the preset output voltage of the converter set the duty ratio of the driving pulse of each first switching tube Sla-SNa, including: [0069] D = -+. ·5 Dagger collection [0070] In the formula, D is the duty cycle of the driving pulse, Vm is the preset input voltage, and V°ut is the preset output voltage. [0071] In the embodiment of the present invention, the duty cycle of the driving pulse of each first switching tube Sla-SNa is set according to the preset input voltage and the preset output voltage of the multilevel converter, so that the multilevel converter It is in an ideal working state without considering the bias voltage. In addition, referring to FIG. 1, if the reference ground of the multilevel converter is the midpoint of the external power supply, two capacitors Cil and Ci2 connected in series need to be connected in parallel at both ends of the external power supply to obtain the midpoint of the input voltage. [0072] Optionally, as a specific implementation manner of the control method of the multilevel converter provided by the embodiment of the present invention, before step S101, the method further includes: [0073] Step S1002, for each first switch tube Sla-SNa connected in series, from the input end of the LC filter to the positive pole of the external power supply, each first switch tube connected in series is sequentially set with a delay interval of 360°/N. The phases of the driving pulses of the switching tubes Sla-SNa; where N is the number of switching tube groups. [0074] Optionally, as a specific implementation manner of the control method of the multilevel converter provided by the embodiment of the present invention, before step S101, the method further includes: [0075] Step S1003, for any switch tube group Si, set the drive pulse of the first switch tube Sia and the drive pulse of the second switch tube Sib to be complementary, and set the drive pulse of the first switch tube Sia and the first switch tube Sia. The dead time of the driving pulse of the second switch tube Sib. [0076] In the embodiment of the present invention, for any one switching tube group Si, the first switching tube Sia and the second switching tube Sib are always in complementary conduction, and through the complementary conduction of the first switching tube Sia and the first switching tube Sia A dead time is set between the two switching tubes Sib. During the dead time, the first switching tube Sia and the second switching tube Sib that are complementarily turned on are both in the off state, which can avoid complementary conduction. The first switching tube Sia and the second switching tube Sib that are turned on may be turned on at the same time at the moment of state change, causing the flying capacitor to be short-circuited. [0077] Illustratively, the control method of the multi-level converter provided by the embodiment of the present invention will be described below through a four-level converter of DC-DC conversion. [0078] Referring to FIG. 3, the four-level converter has three switch tube groups Si, S2, and S3. The specific parameters of the four-level converter are shown in Table 1. [0079] Table 1 Four-level converter parameters 48V Dagger ut 12V [0080] 2.2μΕ L 50μΗ C 100 households /; 100kHz [0081] First, set the driving pulses of the first switching tubes S1a, S2a, and S3a and the second switching tubes Slb, S2b, and S3b of the four-level converter, including: [0082] Set the duty ratio of the driving pulses of the first switch tubes Sla, S2a, S3a [0083] Since the reference ground of the four-level converter is the negative electrode of the external DC power supply, the duty cycle of the driving pulse is calculated as 0.25 according to the formula D=Vw/Vin. [0084] (2) Set the phase relationship of the driving pulses of the first switch t
[ZH CN111953221A]: 一种模块化多电平换流器及换流站 [EN CN111953221A]: Modular multilevel converter and converter station | [ZH CN111953221A]: 本发明公开了一种模块化多电平换流器及换流站，所述模块化多电平换流器包括三相桥臂，每相桥臂包括上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联的换流器子模块，所述换流器子模块包括第一全控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中，所述第一全控型开关模块和第二全控型开关模块串联形成开关支路；所述开关支路、缓冲电路和第一电容相互并联；所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联的第一二极管。换流器中设有IGCT器件，实现了将换流器和负荷开关集成于一个换流站中，减小了换流站整体的体积和成本，实现换流站高度集成化，使得换流站可靠性高，且能广泛的应用到柔性直流输电系统中。 [EN CN111953221A]: The invention discloses a modular multilevel converter and a converter station. The modular multilevel converter comprises three phases of bridge arms, each phase of bridge arm comprises an upper bridge arm and a lower bridge arm, and the upper bridge arm and the lower bridge arm are provided with a plurality of cascaded converter sub-modules. Each converter sub-module comprises a first full-control type switch module, a second full-control type switch module, a buffer circuit and a first capacitor, wherein the first full-control type switch module and the second full-control type switch module are connected in series to form a switch branch; the switch branch, the buffer circuit and the first capacitor are connected in parallel. The first full-control type switch module and the second full-control type switch module each comprise an IGCT device and a first diode in anti-parallel connection with the IGCT device. The IGCT device is arranged in the converter, so that the converter and aload switch are integrated in one converter station, the overall size and cost of the converter station are reduced, high integration of the converter station is realized, the reliability of the converter station is high, and the converter and the converter station can be widely applied to a flexible direct-current power transmission system. | CN111953221A | 2020-11-17 | CN202010774459A | 2020-08-04 | CN202010774459A, 2020-08-04 | CN111953221A: 2020-11-17 | CHINA THREE GORGES CORP UNIV TSINGHUA | ZENG RONG GUO MINGZHU ZHAO BIAO TANG BOJIN XU CHAOQUN ZHAI DONGLING YU ZHANQING SONG QIANG QU LU | H02M7/483: I H02M7/521: I | H02M7/483: I H02M7/521: I H02M1/0048: A Y02B70/10: A | CN201774259U CN104767185A CN106026048A CN108829989A CN108886320A |  | [ZH CN111953221A]: 1 .一种模块化多电平换流器，包括三相桥臂，每相桥臂包括上桥臂和下桥臂，所述上桥 臂和下桥臂设置有多个级联的换流器子模块，其特征在于，所述换流器子模块包括第一全 控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中， 所述第一全控型开关模块和第二全控型开关模块串联形成开关支路； 所述开关支路、缓冲电路和第一电容相互并联； 所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联的第 一二极管。 2 .根据权利要求1所述的模块化多电平换流器，其特征在于，所述第二全控型开关模块 并联在所述换流器子模块的输出端。 3 .根据权利要求2所述的模块化多电平换流器，其特征在于，所述换流器子模块中第一 全控型开关模块中的IGCT器件的阴极与第二全控型开关模块中的IGCT器件的阳极连接。 4 .根据权利要求1-3任一所述的模块化多电平换流器，其特征在于，所述缓冲电路包括 第一电感、第一电阻、第二二极管和第二电容，其中， 所述第一电感的第一端与分别与所述第一电容的第一端和第一电阻的第一端连接，其 第二端分别与第一全控型开关模块和第二二极管的正极连接； 第二二极管的负极分别与第一电阻的第二端和第二电容的第一端连接； 第二电容的第二端分别与第二全控型开关模块和第一电容的第二端连接。 5 .一种换流站，其特征在于，包括权利要求1所述的模块化多电平换流器、负荷开关和 第一电抗器，其中， 所述模块化多电平换流器与所述负荷开关的一端连接； 所述负荷开关的另一端与所述第一电抗器的一端连接。 6 .根据权利要求5所述的换流站，其特征在于，所述模块化多电平换流器还包括直流侧 和交流侧，其中， 所述模块化多电平换流器的直流侧正极通过依次连接负荷开关和第一电抗器后与直 流线路连接； 所述模块化多电平换流器的交流侧与交流电网连接。 7 .根据权利要求6所述的换流站，其特征在于，模块化多电平换流器中所有第一全控型 开关模块和第二全控型开关模块中的IGCT器件，用于在直流线路发生短路故障时，通过控 制第一全控型开关模块中的IGCT器件闭锁，第二全控型开关模块的IGCT器件导通，令交流 电网处于三相短路状态以及直流线路的直流端口电势为零，最终令故障电流停止上升。 8 .根据权利要求7所述的换流站，其特征在于，所述第一电抗器为平波电抗器。 9 .根据权利要求8所述的换流站，其特征在于，所述负荷开关为额定负荷开关，用于在 直流线路的故障电流达到负荷开关的额定电流值时，进行分闸切断故障电流。 10 .根据权利要求9所述的换流站，其特征在于，所述额定负荷开关为机械式负荷开关、 电子式负荷开关或混合式负荷开关。 [EN CN111953221A]: 1 A modular multi-level converter, comprising a three-phase bridge arm, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper bridge arm and the lower bridge arm are provided with a plurality of cascaded converters The sub-module is characterized in that the converter sub-module includes a first full-control switch module, a second full-control switch module, a buffer circuit and a first capacitor, wherein the first full-control switch module and The second full control switch module is connected in series to form a switch branch; the switch branch, the buffer circuit, and the first capacitor are connected in parallel with each other; the first full control switch module and the second full control switch module both include an IGCT device and The first diode in anti-parallel. 2 The modular multilevel converter according to claim 1, wherein the second fully-controlled switch module is connected in parallel to the output end of the converter sub-module. 3 The modular multilevel converter according to claim 2, wherein the cathode of the IGCT device in the first fully-controlled switch module in the converter sub-module and the second fully-controlled switch module The anode connection of the IGCT device in. 4 The modular multilevel converter according to any one of claims 1 to 3, wherein the buffer circuit comprises a first inductor, a first resistor, a second diode and a second capacitor, wherein: The first end of the first inductor is connected to the first end of the first capacitor and the first end of the first resistor, and the second end is connected to the first fully-controlled switch module and the second diode respectively. The cathode of the second diode is connected to the second end of the first resistor and the first end of the second capacitor respectively; the second end of the second capacitor is connected to the second fully-controlled switch module and the first capacitor respectively The second end of the connection. 5 A converter station, characterized by comprising the modular multilevel converter, load switch and first reactor of claim 1, wherein the modular multilevel converter and the One end of the load switch is connected; the other end of the load switch is connected to one end of the first reactor. 6 The converter station according to claim 5, wherein the modular multilevel converter further comprises a DC side and an AC side, wherein the DC side anode of the modular multilevel converter The load switch and the first reactor are connected in sequence and then connected to the DC line; the AC side of the modular multilevel converter is connected to the AC power grid. 7 The converter station according to claim 6, wherein all the IGCT devices in the first full-control switch module and the second full-control switch module in the modular multilevel converter are used in DC When a short-circuit fault occurs in the line, by controlling the IGCT device in the first full-control switch module to block, the IGCT device of the second full-control switch module is turned on, so that the AC grid is in a three-phase short-circuit state and the DC port potential of the DC line is Zero, eventually stopping the fault current from rising. 8 The converter station of claim 7, wherein the first reactor is a smoothing reactor. 9 The converter station according to claim 8, wherein the load switch is a rated load switch, which is used to switch off the fault current when the fault current of the DC line reaches the rated current value of the load switch. 10 The converter station according to claim 9, wherein the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. | [ZH CN111953221A]: 一种模块化多电平换流器及换流站 技术领域 [0001]本发明属于电力输电领域，特别涉及一种模块化多电平换流器及换流站。 背景技术 [0002]柔性直流输电已经成为目前最有潜质的新型电力传输方式，并且已经在大容量输 电系统中得到了应用。模块化多电平换流器是目前最为主流的拓扑结构。现已投运的柔性 直流输电工程多是采用基于IGBT（Insulated Gate Bipolar Transistor：绝缘栅双极型晶 体管）的模块化多电平换流器，但是在直流故障清除方面有很大的实现困难，往往在直流短 路故障发生时会产生极大的直流短路故障电流，为此需要分断直流短路故障电流，需要极 大分断电流能力的直流断路器，此类直流断路器的造价高且体积非常巨大。因此，如图1所 示，换流站采用的是基于IGBT的模块化多电平换流器，且将换流器和断路器分别置于两个 独立的换流站中。 [0003]从而如何提供一种模块化多电平换流器以及能够实现换流站集成换流和开关一 体化的功能越来越成为亟待解决的技术问题。 发明内容 [0004]针对上述问题，本发明提供一种模块化多电平换流器及换流站，提高换流器的可 靠性以及实现了换流站集成换流和开关一体化的功能。 [0005]本发明的目的在于提供一种模块化多电平换流器，包括三相桥臂，每相桥臂包括 上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联的换流器子模块，所述换流器子模 块包括第一全控型开关模块、第二全控型开关模块、缓冲电路和第一电容，其中， [0006]所述第一全控型开关模块和第二全控型开关模块串联形成开关支路； [0007]所述开关支路、缓冲电路和第一电容相互并联； [0008]所述第一全控型开关模块和第二全控型开关模块均包括IGCT器件及与其反并联 的第一二极管。 [0009]进一步地，所述第二全控型开关模块并联在所述换流器子模块的输出端。 [0010]进一步地，所述换流器子模块中第一全控型开关模块中的IGCT器件的阴极与第二 全控型开关模块中的IGCT器件的阳极连接。 [0011]进一步地，所述缓冲电路包括第一电感、第一电阻、第二二极管和第二电容，其中， [0012] 所述第一电感的第一端与分别与所述第一电容的第一端和第一电阻的第一端连 接，其第二端分别与第一全控型开关模块和第二二极管的正极连接； [0013]第二二极管的负极分别与第一电阻的第二端和第二电容的第一端连接； [0014]第二电容的第二端分别与第二全控型开关模块和第一电容的第二端连接。 [0015]本发明的另一目的在于提供一种换流站，包括上述所述的模块化多电平换流器、 负荷开关和第一电抗器，其中， [0016]所述模块化多电平换流器与所述负荷开关的一端连接； [0017] 所述负荷开关的另一端与所述第一电抗器的一端连接。 [0018] 进一步地，所述模块化多电平换流器还包括直流侧和交流侧，其中， [0019]所述模块化多电平换流器的直流侧正极通过依次连接负荷开关和第一电抗器后 与直流线路连接； [0020]所述模块化多电平换流器的交流侧与交流电网连接。 [0021]进一步地，模块化多电平换流器中所有第一全控型开关模块和第二全控型开关模 块中的IGCT器件，用于在直流线路发生短路故障时，通过控制第一全控型开关模块中的 IGCT器件闭锁，第二全控型开关模块的IGCT器件导通，令交流电网处于三相短路状态以及 直流线路的直流端口电势为零，最终令故障电流停止上升。 [0022] 进一步地，所述第一电抗器为平波电抗器。 [0023]进一步地，所述负荷开关为额定负荷开关，用于在直流线路的故障电流达到负荷 开关的额定电流值时，进行分闸切断故障电流。 [0024]进一步地，所述额定负荷开关为机械式负荷开关、电子式负荷开关或混合式负荷 开关。 [0025]本发明中的所述模块化多电平换流器中的第一全控型开关模块和第二全控型开 关模块均采用了IGCT器件，相比于IGBT，由于IGCT具有非常高的浪涌电流承受能力、通态电 流能力、正向阻断电压能力以及可靠性，并且还具有非常低的通态压降，从而使得模块化多 电平换流器具有电流大、阻断电压高、可靠性高、结构紧凑以及低导通损耗等优点。 [0026]进一步，换流站能够将模块化多电平换流器和负荷开关集成于一个站中，大幅减 小了换流站整体的体积和成本，实现了高度集成化和很高的经济性，可以在未来的柔性直 流输电系统中得到广泛的应用。 [0027] 此外，由于通过控制第一全控型开关模块中的IGCT器件闭锁，第二全控型开关模 块的IGCT器件导通，能够有效地令故障电流停止上升，从而负荷开关仅需要分断额定电流 大小的直流电流，从而也大幅减小了负荷开关所需的体积、用量和成本。且换流站中只需要 平波电抗器，平波电抗器电感值小，不需要考虑限流功能。 [0028]本发明的其它特征和优点将在随后的中阐述，并且，部分地从中变 得显而易见，或者通过实施本发明而了解。本发明的目的和其他优点可通过在、权利 要求书以及附图中所指出的结构来实现和获得。 附图说明 [0029]为了更清楚地说明本发明实施例或现有技术中的技术方案，下面将对实施例或现 有技术描述中所需要使用的附图作简单地介绍，显而易见地，下面描述中的附图是本发明 的一些实施例，对于本领域普通技术人员来讲，在不付出创造性劳动的前提下，还可以根据 这些附图获得其他的附图。 [0030]图1示出了现有技术中的一种换流站和断路器的结构示意图； [0031]图2示出了本发明实施例中的一种模块化多电平换流器的结构示意图； [0032]图3示出了本发明实施例中的一种换流站的结构示意图； [0033]图4示出了本发明实施例中的换流站中Ummc、Udc和iDC在控制过程中的变化曲线图。 具体实施方式 [0034]为使本发明实施例的目的、技术方案和优点更加清楚，下面将结合本发明实施例 中的附图，对本发明实施例中的技术方案进行清楚、完整地说明，显然，所描述的实施例是 本发明一部分实施例，而不是全部的实施例。基于本发明中的实施例，本领域普通技术人员 在没有做出创造性劳动前提下所获得的所有其他实施例，都属于本发明保护的范围。 [0035]如图2所示，本发明实施例中介绍了一种模块化多电平换流器，包括三相桥臂，每 相桥臂包括上桥臂和下桥臂，所述上桥臂和下桥臂设置有多个级联换流器子模块，其中，每 相桥臂的上桥臂中的换流器子模块分别为n个，在图2中分别为：SMap1、SMap2……SMapn， SMbp 1、SMbp2 SMbpn，SMcp 1、SMcp2 SMcpn。每相桥臂的下桥臂中的换流器子模块分 别为n个，在图 2 中分别为：SMan 1、SMan2 ……SMann，SMbn 1、SMbn2 ……SMbpnn，SMcn 1、 SMcn2……SMcnn。进一步，所述换流器子模块包括第一全控型开关模块、第二全控型开关模 块、缓冲电路和第一电容。所述第一全控型开关模块包括IGCT （integrated Gate Commutated Thyristors：集成门极换流晶闸管）器件Sxi1及与其反并联的第一二极管Dxi1； 所述第二全控型开关模块包括IGCT器件Sxi2及与其反并联的第一二极管Dxi2；且所述第一全 控型开关模块和第二全控型开关模块串联形成开关支路;所述开关支路、缓冲电路和第一 电容Cxi相互并联。进一步，所述第一全控型开关模块和第二全控型开关模块串联时，所述 IGCT器件Sxi1与IGCT器件Sxi2方向相同，即所述IGCT器件Sxi1的阴极与所述IGCT器件Sxi2的阳 极连接。所述模块化多电平换流器中的第一全控型开关模块和第二全控型开关模块均采用 了IGCT器件，相比于IGBT，由于IGCT具有非常高的浪涌电流承受能力、通态电流能力、正向 阻断电压能力以及可靠性，并且还具有非常低的通态压降，从而使得模块化多电平换流器 具有电流大、阻断电压高、可靠性高、结构紧凑以及低导通损耗等优点。 [0036]本实施例中，每个与IGCT器件反并联的第一二极管能够有效对故障电流进行反向 截止，从而保护所述IGCT器件。 [0037]进一步具体的，如图2所示，所述第二全控型开关模块并联在所述换流器子模块的 输出端，上桥臂和下桥臂上的多个换流器子模块均通过各自的输出端实现连接。进一步，所 述缓冲电路包括第一电感Lxis、第一电阻Rxis、第二二极管Dxis和第二电容Cxis，其中，所述第 一电感Lxis的第一端与分别与所述第一电容Cxi的第一端和第一电阻Rxis的第一端连接，其第 二端分别与第一全控型开关模块和第二二极管Dxis的正极连接;第二二极管的负极分别与 第一电阻Rxis的第二端和第二电容Cxis的第一端连接;第二电容Cxis的第二端分别与第二全 控型开关模块和第一电容Cxi的第二端连接。第一电容Cxi的第一端为正极，第二端为负极， 且电压采用Vc表示。采用缓冲电路，在模块化多电平换流器正常工作时，能够有效地抑制第 一全控型开关模块和/或第二全控型开关模块上电流或者电压的上升率。而模块化多电平 换流器工作在直流线路短路故障状态下时，由于采取了第一全控型开关模块中的IGCT器件 闭锁，第二全控型开关模块的IGCT器件导通的方法，所述缓冲电路在故障处理时处于旁路 状态。 [0038]本实施例中，所述每相桥臂的上桥臂和下桥臂上还设置有第二电抗器（图2-3中未 示出），且与相应桥臂上级联的多个换流器子模块串联。 [0039]如图3所示，本发明实施例中还介绍了一种换流站，所述换流站包括上述所述的模 块化多电平换流器以及负荷开关和第一电抗器，其中，所述模块化多电平换流器包括直流 侧和交流侧;所述模块化多电平换流器直流侧的正极与所述负荷开关的一端连接，所述负 荷开关的另一端与所述第一电抗器的一端连接，所述第一电抗器的另一端与直流线路连 接。进一步，所述模块化多电平换流器的负极与所述第一电抗器的另一端形成所述换流站 的直流端口，即为换流站的直流端口，通过该直流端口，实现所述换流站与直流线路连接。 所述模块化多电平换流器的交流侧形成换流站的交流端口与交流电网连接。本发明实施例 中的将换流器和负荷开关集成于一个换流站中，大幅减小了换流站整体的体积和成本，实 现了高度集成化和很高的经济性，可以在未来的柔性直流输电系统中得到广泛的应用。此 外，将上述所述的模块化多电平换流器应用到换流站中，从而使得基于IGCT的换流站在面 对直流短路故障时，能够实现直流故障自清除的功能，且能够很好地限制直流短路故障电 流的上升。 [0040]图3中，所述负荷开关为额定负荷开关。用于在直流线路的故障电流达到负荷开关 的额定电流值时，进行分闸切断故障电流。由于通过控制第一全控型开关模块中的IGCT器 件闭锁，第二全控型开关模块的IGCT器件导通，能够有效地令故障电流停止上升。负荷开关 仅需要分断额定电流大小的直流电流即可，从而也大幅减小了负荷开关所需的体积、用量 和成本。进一步，所述额定负荷开关为机械式负荷开关、电子式负荷开关或混合式负荷开 关。所述第一电抗器为平波电抗器。由于上述所述的模块化多电平换流器能够直接限制直 流线路短路故障时故障电流的上升，因此，本发明实施例中的换流器不需要配备大电感值 的电抗器用于限流，仅将电抗器用于平波。从而本发明实施例中的第一电抗器的电感值小， 无需考虑限流功能。但对于基于IGBT-MMC（Modular Multilevel Converter：模块化多电平 变流器），由于其无法限制故障时故障电流的快速上升，为此需要配备大电感值的电抗器， 用于限流，同时还利用电抗器来平波。 [0041] 本发明实施例中还介绍了一种上述所述换流站的控制方法，所述控制方法的控制 过程具体包括以下步骤： [0042] 1）t0时刻：假定在t0时刻发生直流线路短路故障，直流线路短路故障导致的故障 电流开始快速上升。 [0043] 2）t1时刻:检测到短路故障发生且换流器子模块保护动作时刻。当检测到直流线 路短路故障后，模块化多电平变流器中所有换流器子模块中的第一全控型开关模块的IGCT 器件Sxii闭锁，第二全控型开关模块的IGCT器件Sxi2导通。具体的，t0〜tl时间段的长度为直 流线路发生短路故障后的延时时间，其中，t0〜tl时间段的长度为0.3ms （毫秒）。 [0044]当直流线路发生短路故障后，换流站中模块化多电平变流器的所有换流器子模块 中的第一全控型开关模块的IGCT器件Sxii闭锁，第二全控型开关模块的IGCT器件Sxi2导通, 从而使得模块化多电平换流器交流侧连接的交流电网处于三相短路状态，具体的，相当于 通过模块化多电平换流器所有桥臂上的第二电抗器三相短路，换流站直流端口电势相当于 零，同时，所述模块化多电平变流器直流侧的电势也为零，且此时故障电流停止上升。 [0045] 3）t2时刻：负荷开关切断故障电流时刻，此时通过负荷开关的直流线路短路故障 的故障电流达到最大值。tl〜t2时间段的长度为负荷开关接收到动作命令并分开开关的时 间，tl〜t2时间段的长度约为3ms。负荷开关切断之后，隔绝了直流线路和模块化多电平换 流器，所述故障电流开始衰减，且自此，直流线路开始去游离。进一步，所述故障电流的最大 值为负荷开关额定电流值。 [0046] 4)t3时刻:模块化多电平换流器中所有换流器子模块中的第二全控型开关模块的 IGCT器件Sxi2的闭锁时刻。在负荷开关分断完故障电流之后，已不需要再通过IGCT器件主动 短路来钳制模块化多电平换流器直流侧端口的电压。因此，IGCT器件可以在所处的每相桥 臂的电流过零点或者小电流时控制关断，结束交流电网的三相短路状态，t2〜t3时间段的 长度为控制模块化多电平换流器闭锁的时间，t2〜t3时间段的长度小于10ms。本发明实施 例中，所述小电流为每相桥臂上的电流不大于IGCT器件重复可关断电流的预设值，所述 IGCT器件重复可关断电流的预设值为IGCT的重复可关断电流最大能力，市场占有率最高的 四英寸IGCT器件的重复可关断电流最大能力可以为4.5kA(千安培)，但不限于4.5kA,5kA、 6kA等都适用于本发明。 [0047] 5)t4时刻：模块化多电平换流器解除闭锁的时刻，此时重新打开所有换流器子模 块中的IGCT器件，即令所有IGCT器件Sxii和IGCT器件Sxi2导通。模块化多电平换流器由闭锁 状态慢慢恢复电压到正常运行状态。恢复所述电压的过程往往需要一到两个周波，共约 40ms的时间。但只需保证在负荷开关重合闸之前已经完成恢复起电压即可。所述电压为模 块化多电平换流器正常运行时的额定直流电压。 [0048] 6)t5时刻:控制负荷开关重合闸的时刻。此时模块化多电平换流器已经解锁，且恢 复到正常运行时的电压。t2〜t5时间段的长度为直流线路去游离的时间，从而，t2〜t5时间 段的长度约为300ms。 [0049] 7)t6时刻：负荷开关完成重合的时刻，模块化多电平换流器恢复向直流侧传输功 率。t5〜t6时间段的长度为负荷开关重合闸的时间，对于机械式负荷开关，t5〜t6时间段的 长度约为15〜20ms。 [0050] 通过上述控制过程,模块化多电平换流器的电压Ummc以及直流线路直流端口的电 压Udc和电流iDC的变化如图4所示。且控制过程中，涉及的每个时间段的长度时间长度均有 效地说明对本发明实施例中的换流站能够快速的对直流线路短路故障进行处理和恢复，且 可靠性更高。 [0051]将设置有IGCT器件的模块化多电平换流器和负荷开关共同布置于一个换流站内， 使得结构更紧凑，使得换流站同时具备换流和开关的功能。 [0052]尽管参照前述实施例对本发明进行了详细的说明，本领域的普通技术人员应当理 解:其依然可以对前述各实施例所记载的技术方案进行修改，或者对其中部分技术特征进 行等同替换；而这些修改或者替换，并不使相应技术方案的本质脱离本发明各实施例技术 方案的精神和范围。 [EN CN111953221A]: A modular multilevel converter and converter station technical field [0001] The present invention belongs to the field of power transmission, and in particular relates to a modular multilevel converter and a converter station. Background technique [0002] Flexible direct current transmission has become the most promising new power transmission method at present, and has been applied in large-capacity power transmission systems. Modular multilevel converters are currently the most mainstream topology. Most of the flexible DC transmission projects that have been put into operation use modular multilevel converters based on IGBT (Insulated Gate Bipolar Transistor), but there are great difficulties in implementing DC fault clearance. Very large DC short-circuit fault currents are often generated when a DC short-circuit fault occurs. For this reason, it is necessary to break the DC short-circuit fault current, and a DC circuit breaker with a great breaking current capability is required. This type of DC circuit breaker is expensive and very large. Therefore, as shown in Figure 1, the converter station uses IGBT-based modular multilevel converters, and the converter and circuit breaker are placed in two independent converter stations. [0003] Therefore, how to provide a modular multi-level converter and the function of integrating the converter and the switch of the converter station has become an urgent technical problem to be solved. Summary of the invention [0004] In view of the above-mentioned problems, the present invention provides a modular multi-level converter and converter station, which improves the reliability of the converter and realizes the functions of integrated converter and switch integration of the converter station. [0005] The object of the present invention is to provide a modular multi-level converter, including three-phase bridge arms, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper bridge arm and the lower bridge arm are provided with A plurality of cascaded converter sub-modules, the converter sub-modules include a first fully-controlled switch module, a second fully-controlled switch module, a buffer circuit and a first capacitor, wherein [0006] the first A full control switch module and a second full control switch module are connected in series to form a switch branch; [0007] The switch branch, the buffer circuit and the first capacitor are connected in parallel with each other; [0008] The first full control switch module and the second full control switch module both include an IGCT device and a first diode anti-parallel to it. [0009] Further, the second full control switch module is connected in parallel to the output end of the converter sub-module. [0010] Further, the cathode of the IGCT device in the first full control switch module in the converter sub-module is connected to the anode of the IGCT device in the second full control switch module. [0011] Further, the buffer circuit includes a first inductor, a first resistor, a second diode, and a second capacitor, wherein, [0012] the first terminal of the first inductor and the first The first end of the capacitor is connected to the first end of the first resistor, and the second end of the capacitor is respectively connected to the first full-control switch module and the anode of the second diode; [0013] The cathode of the second diode is respectively connected to the second end of the first resistor and the first end of the second capacitor; [0014] The second end of the second capacitor is respectively connected to the second fully-controlled switch module and the second end of the first capacitor. [0015] Another object of the present invention is to provide a converter station, including the above-mentioned modular multilevel converter, load switch and first reactor, wherein, [0016] The modular multilevel converter is connected to one end of the load switch; [0017] The other end of the load switch is connected to one end of the first reactor. [0018] Further, the modular multilevel converter further includes a DC side and an AC side, wherein, [0019] The positive pole of the DC side of the modular multilevel converter is connected to the DC line by sequentially connecting the load switch and the first reactor; [0020] The AC side of the modular multilevel converter is connected to an AC power grid. [0021] Further, the IGCT devices in all the first fully-controlled switch modules and the second fully-controlled switch modules in the modular multilevel converter are used to control the first The IGCT device in the full control switch module is blocked, and the IGCT device of the second full control switch module is turned on, so that the AC grid is in a three-phase short-circuit state and the DC port potential of the DC line is zero, and finally the fault current stops rising. [0022] Further, the first reactor is a smoothing reactor. [0023] Further, the load switch is a rated load switch, which is used to switch off the fault current when the fault current of the DC line reaches the rated current value of the load switch. [0024] Further, the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. [0025] The first fully-controlled switch module and the second fully-controlled switch module in the modular multilevel converter in the present invention both use IGCT devices. Compared with IGBTs, IGCT has a very high The surge current withstand capability, on-state current capability, forward blocking voltage capability and reliability, and also has a very low on-state voltage drop, so that the modular multi-level converter has large current and blocking voltage High, high reliability, compact structure and low conduction loss. [0026] Further, the converter station can integrate the modular multi-level converter and load switch into one station, which greatly reduces the overall volume and cost of the converter station, and achieves a high degree of integration and high economy. It can be widely used in future flexible DC transmission systems. [0027] In addition, by controlling the IGCT device in the first full-control switch module to be blocked, the IGCT device of the second full-control switch module is turned on, which can effectively stop the fault current from rising, so that the load switch only needs to be rated for breaking. The current size of the direct current also greatly reduces the volume, consumption and cost required by the load switch. Moreover, only the smoothing reactor is needed in the converter station, and the inductance of the smoothing reactor is small, so there is no need to consider the current limiting function. [0028] Other features and advantages of the present invention will be described in the following, and partly become obvious from them, or understood by implementing the present invention. The objects and other advantages of the present invention can be realized and obtained by the structures indicated in the claims, the claims and the drawings. Description of the drawings [0029] In order to more clearly illustrate the embodiments of the present invention or the technical solutions in the prior art, the following will briefly introduce the accompanying drawings that need to be used in the description of the embodiments or the prior art. Obviously, in the following description The drawings are some embodiments of the present invention. For those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative work. [0030] FIG. 1 shows a schematic structural diagram of a converter station and a circuit breaker in the prior art; [0031] FIG. 2 shows a schematic structural diagram of a modular multilevel converter in an embodiment of the present invention; [0032] FIG. 3 shows a schematic structural diagram of a converter station in an embodiment of the present invention; [0033] FIG. 4 shows the change curve diagram of Ummc, Udc and iDC in the converter station in the embodiment of the present invention during the control process. Detailed ways [0034] In order to make the objectives, technical solutions, and advantages of the embodiments of the present invention clearer, the following will clearly and completely describe the technical solutions in the embodiments of the present invention with reference to the accompanying drawings in the embodiments of the present invention. Obviously, the description The embodiments are a part of the embodiments of the present invention, but not all of the embodiments. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0035] As shown in FIG. 2, an embodiment of the present invention introduces a modular multi-level converter, including three-phase bridge arms, each phase bridge arm includes an upper bridge arm and a lower bridge arm, the upper bridge The arm and the lower bridge arm are provided with multiple cascaded converter sub-modules. Among them, there are n converter sub-modules in the upper bridge arm of each phase bridge arm, which are respectively: SMap1, SMap2... ...SMapn, SMbp 1, SMbp2 SMbpn, SMcp 1, SMcp2 SMcpn. There are n converter sub-modules in the lower bridge arm of each phase bridge arm. In Figure 2 they are: SMan 1, SMan2 ......SMann, SMbn 1, SMbn2 ......SMbpnn, SMcn 1, SMcn2......SMcnn . Further, the converter sub-module includes a first full-control switch module, a second full-control switch module, a buffer circuit and a first capacitor. The first fully-controlled switch module includes an IGCT (integrated Gate Commutated Thyristors) device Sxi1 and a first diode Dxi1 connected in anti-parallel with it; the second fully-controlled switch module includes an IGCT device Sxi2 and the first diode Dxi2 anti-parallel to it; and the first fully-controlled switch module and the second fully-controlled switch module are connected in series to form a switch branch; the switch branch, the buffer circuit and the first The capacitors Cxi are connected in parallel. Further, when the first full control switch module and the second full control switch module are connected in series, the IGCT device Sxi1 and the IGCT device Sxi2 have the same orientation, that is, the cathode of the IGCT device Sxi1 and the anode of the IGCT device Sxi2 connection. Both the first fully-controlled switch module and the second fully-controlled switch module in the modular multilevel converter use IGCT devices. Compared with IGBTs, IGCT has a very high surge current tolerance, On-state current capability, forward blocking voltage capability and reliability, and also has a very low on-state voltage drop, so that the modular multi-level converter has large current, high blocking voltage, high reliability, and structure The advantages of compactness and low conduction loss. [0036] In this embodiment, each first diode anti-parallel to the IGCT device can effectively reverse the fault current, thereby protecting the IGCT device. [0037] More specifically, as shown in FIG. 2, the second fully-controlled switch module is connected in parallel to the output end of the converter sub-module, and the multiple converter sub-modules on the upper and lower bridge arms The modules are connected through their respective output terminals. Further, the buffer circuit includes a first inductor Lxis, a first resistor Rxis, a second diode Dxis, and a second capacitor Cxis, wherein the first terminal of the first inductor Lxis is connected to the first capacitor Cxis, respectively The first end is connected to the first end of the first resistor Rxis, and the second end is respectively connected to the first full-control switch module and the anode of the second diode Dxis; the cathode of the second diode is connected to the first The second end of the resistor Rxis is connected to the first end of the second capacitor Cxis; the second end of the second capacitor Cxis is respectively connected to the second fully-controlled switch module and the second end of the first capacitor Cxi. The first terminal of the first capacitor Cxi is a positive electrode, and the second terminal is a negative electrode, and the voltage is represented by Vc. By adopting the buffer circuit, when the modular multi-level converter is working normally, it can effectively suppress the rising rate of current or voltage on the first full control switch module and/or the second full control switch module. When the modular multilevel converter works in the DC line short-circuit fault state, because the IGCT device in the first full-control switch module is blocked, and the IGCT device in the second full-control switch module is turned on, The buffer circuit is in a bypass state during fault processing. [0038] In this embodiment, a second reactor (not shown in Figure 2-3) is also provided on the upper bridge arm and the lower bridge arm of each phase bridge arm, and is cascaded with the corresponding bridge arm. Two converter sub-modules are connected in series. [0039] As shown in FIG. 3, the embodiment of the present invention also introduces a converter station, the converter station includes the above-mentioned modular multilevel converter, load switch and first reactor, Wherein, the modular multilevel converter includes DC Side and AC side; the positive pole of the DC side of the modular multilevel converter is connected to one end of the load switch, the other end of the load switch is connected to one end of the first reactor, the first The other end of the reactor is connected to the DC line. Further, the negative pole of the modular multilevel converter and the other end of the first reactor form the DC port of the converter station, that is, the DC port of the converter station, through which the DC port is realized. The converter station is connected to the DC line. The AC side of the modular multilevel converter forms the AC port of the converter station to connect to the AC power grid. In the embodiment of the present invention, the converter and load switch are integrated into one converter station, which greatly reduces the overall volume and cost of the converter station, realizes high integration and high economy, and can be used in future It is widely used in flexible direct current transmission systems. In addition, the above-mentioned modular multilevel converter is applied to the converter station, so that when the IGCT-based converter station faces a DC short-circuit fault, it can realize the function of self-clearing the DC fault, and it can be very Well limit the rise of DC short-circuit fault current. [0040] In Figure 3, the load switch is a rated load switch. It is used to switch off the fault current when the fault current of the DC line reaches the rated current value of the load switch. Since the IGCT device in the first full control switch module is controlled to be blocked, the IGCT device in the second full control switch module is turned on, which can effectively stop the fault current from rising. The load switch only needs to break the DC current of the rated current, thus greatly reducing the volume, consumption and cost required by the load switch. Further, the rated load switch is a mechanical load switch, an electronic load switch or a hybrid load switch. The first reactor is a smoothing reactor. Since the above-mentioned modular multi-level converter can directly limit the rise of the fault current when the DC line is short-circuited, the converter in the embodiment of the present invention does not need to be equipped with a reactor with a large inductance for current limiting. Only use reactors for smoothing waves. Therefore, the inductance value of the first reactor in the embodiment of the present invention is small, and the current limiting function does not need to be considered. But for IGBT-MMC (Modular Multilevel Converter), because it cannot limit the rapid rise of the fault current in the event of a fault, a reactor with a large inductance value is required to limit the current. A reactor is also used to smooth the waves. [0041] The embodiment of the present invention also introduces a control method of the above-mentioned converter station, and the control process of the control method specifically includes the following steps: [0042] 1) Time t0: Assuming that a short-circuit fault of the DC line occurs at time t0, the fault current caused by the short-circuit fault of the DC line starts to rise rapidly. [0043] 2) Time t1: The time when a short-circuit fault is detected and the protection of the converter sub-module is activated. When the DC line short-circuit fault is detected, the IGCT device Sxii of the first fully-controlled switch module of all the converter sub-modules in the modular multilevel converter is blocked, and the IGCT device Sxi2 of the second fully-controlled switch module is blocked Conduction. Specifically, the length of the time period t0˜tl is the delay time after a short-circuit fault occurs on the DC line, where the length of the time period t0˜tl is 0.3 ms (milliseconds). [0044] When a short-circuit fault occurs on the DC line, the IGCT device Sxii of the first fully-controlled switch module of all the converter sub-modules of the modular multilevel converter in the converter station is blocked, and the second fully-controlled The IGCT device Sxi2 of the switch module is turned on, so that the AC grid connected to the AC side of the modular multilevel converter is in a three-phase short-circuit state. Specifically, it is equivalent to passing through all the bridge arms of the modular multilevel converter. The second reactor is short-circuited in three phases, and the potential of the DC port of the converter station is equivalent to zero. At the same time, the potential of the DC side of the modular multilevel converter is also zero, and the fault current stops rising at this time. [0045] 3) Time t2: the moment when the load switch cuts off the fault current, at this time the fault current of the short-circuit fault of the DC line through the load switch reaches the maximum value. The length of the time period tl~t2 is the time when the load switch receives the action command and separates the switches, and the length of the time period tl~t2 is about 3 ms. After the load switch is cut off, the DC line and the modular multi-level converter are isolated, the fault current begins to attenuate, and since then, the DC line begins to dissociate. Further, the maximum value of the fault current is the rated current value of the load switch. [0046] 4) Time t3: the blocking time of the IGCT device Sxi2 of the second fully-controlled switch module in all the converter sub-modules of the modular multilevel converter. After the load switch breaks the fault current, there is no need to actively short-circuit the IGCT device to clamp the voltage at the DC side port of the modular multilevel converter. Therefore, the IGCT device can be turned off when the current of each phase bridge arm is at the zero-crossing point or when the current is small, and the three-phase short-circuit state of the AC grid is ended. The length of the t2~t3 period is to control the modular multi-level commutation The length of the time period t2~t3 is less than 10ms. In the embodiment of the present invention, the low current is that the current on each phase bridge arm is not greater than the preset value of the repetitive turn-off current of the IGCT device, and the preset value of the repetitive turn-off current of the IGCT device is the repetitive turn-off current of IGCT. The maximum turn-off current capability, the maximum repetitive turn-off current capability of the four-inch IGCT device with the highest market share can be 4.5kA (kiloamps), but it is not limited to 4.5kA, 5kA, 6kA, etc. are all applicable to the present invention. [0047] 5) Time t4: the time when the modular multilevel converter is unlocked. At this time, all IGCT devices in the converter sub-modules are reopened, that is, all IGCT devices Sxii and IGCT devices Sxi2 are turned on. The modular multilevel converter slowly restores the voltage from the locked state to the normal operating state. The process of restoring the voltage often requires one to two cycles, a total of about 40 ms. But it only needs to ensure that the voltage recovery has been completed before the load switch reclosing. The voltage is the rated DC voltage of the modular multilevel converter during normal operation. [0048] 6) Time t5: the time when the load switch is controlled to reclose. At this time, the modular multilevel converter has been unlocked and restored to the voltage during normal operation. The length of the time period from t2 to t5 is the time for the DC line to be disconnected, and thus, the length of the time period from t2 to t5 is about 300 ms. [0049] 7) Time t6: At the time when the load switch completes the overlap, the modular multilevel converter resumes transmitting power to the DC side. The length of the time period from t5 to t6 is the time for the load switch to reclose. For a mechanical load switch, the length of the time period from t5 to t6 is about 15 to 20 ms. [0050] Through the above control process, the voltage Ummc of the modular multi-level converter and the changes of the voltage Udc and the current iDC of the DC port of the DC line are shown in FIG. 4. In addition, in the control process, the length of each time period involved effectively shows that the converter station in the embodiment of the present invention can quickly handle and restore the DC line short-circuit fault, and has higher reliability. [0051] The modular multilevel converter and load switch equipped with IGCT devices are arranged together in a converter station, making the structure more compact, so that the converter station has both the functions of converter and switch. [0052] Although the present invention has been described in detail with reference to the foregoing embodiments, those of ordinary skill in the art should understand that they can still modify the technical solutions described in the foregoing embodiments, or equivalently replace some of the technical features. ; And these modifications or replacements do not make the essence of the corresponding technical solutions deviate from the spirit and scope of the technical solutions of the embodiments of the present invention.
[ZH CN113364311A]: 一种多中压交流端口固态变压器及其控制方法 [EN CN113364311A]: Multi-medium voltage AC port solid-state transformer and control method thereof | [ZH CN113364311A]: 本发明公开了一种多中压交流端口固态变压器及其控制方法，包括：多端口柔性互联模块；级联全桥变换器，级联全桥变换器的交流输入端串联接入多端口柔性互联模块；以及，隔离型直流变换器，各个隔离型直流变换器的一端与级联全桥变换器的子模块的直流输出侧相连接，其另一端相互并联构成低压直流母线。本发明能实现多交流馈线互联，并通过调节串联在线路上的等效电压源幅值相位，进行线路有功功率和无功功率解耦的主动控制，从而实现多交流馈线间的功率互济，有利于配电网经济高效运行；本发明中的多端口柔性互联模块具备模块化的特点，通过增加互联模块中并联电压源型单相变换器数量，可快速、经济地实现互联端口的拓展。 [EN CN113364311A]: The invention discloses a multi-medium voltage AC port solid-state transformer and a control method thereof, including: a multi-port flexible interconnection module; a cascaded full-bridge converter, the AC input end of the cascaded full-bridge converter is connected in series to the multi-port flexible interconnection Modules; and, isolated DC converters, one end of each isolated DC converter is connected to the DC output side of the sub-module of the cascaded full-bridge converter, and the other ends are connected in parallel to each other to form a low-voltage DC bus. The invention can realize the interconnection of multiple AC feeders, and by adjusting the amplitude and phase of the equivalent voltage source on the series line, the active control of active power and reactive power decoupling of the line is performed, thereby realizing the power mutual aid between the multiple AC feeders. It is conducive to the economic and efficient operation of the distribution network; the multi-port flexible interconnection module of the present invention has the characteristics of modularity, and by increasing the number of parallel voltage source single-phase converters in the interconnection module, the expansion of interconnection ports can be realized quickly and economically. | CN113364311A | 2021-09-07 | CN202110714166A | 2021-06-25 | CN202110714166A, 2021-06-25 | CN113364311A: 2021-09-07 | 上海交通大学 |  | H02M7/162: I H02J3/02: I H02M1/32: I H02M3/335: I |  |  |  | [ZH CN113364311A]: L 一种多中压交流端口固态变压器，其特性在于，包括： 多端口柔性互联模块； 级联全桥变换器，所述级联全桥变换器的交流输入端串联接入所述多端口柔性互联模 块；以及， 隔离型直流变换器，各个隔离型直流变换器的一端与所述级联全桥变换器的子模块的 直流输出侧相连接，所述各个隔离型直流变换器的另一端相互并联构成低压直流母线。 2 .如权利要求1所述的多中压交流端口固态变压器，其特征在于:所述多端口柔性互联 模块包括多个共享直流母线的电压源型单相变换器组成，所述变换器交流侧输出电压与馈 线串联。 3 .如权利要求1所述的多中压交流端口固态变压器，其特征在于:所述级联全桥变换器 包括中压级电压源型变换器，其子模块拓扑为全桥型变换器。 4 .如权利要求1所述的多中压交流端口固态变压器，其特征在于:所述隔离型直流变换 器包括中间带有中高频隔离变压器的DODC变换器，其拓扑为双有源全桥变换器或者半桥 型变换器或者功率可控的隔离型DC-DC变换器。 5 .如权利要求1或2所述的多中压交流端口固态变压器，其特征在于：组成所述多端口 柔性互联模块的电压源型单相变换器拓扑包括两电平电压源型单相变换器或者三电平电 压源型单相变换器或者能进行功率双向流动的电压源型单相变换器。 6 .如权利要求5所述的多中压交流端口固态变压器，其特征在于:所述多端口柔性互联 模块通过一个隔离型双向DODC变换器与低压直流母线连接或者不加装隔离型双向DODC 变换器。 7 .如权利要求6所述的多中压交流端口固态变压器，其特征在于:包括， 功率方程： 其中，Pk为所述多中压交流端口互联互济式固态变压器的第k条线路的有功功率表达 式,Pl为所述多中压交流端口互联互济式固态变压器低压直流端口功率。 8 .如权利要求7所述的多中压交流端口固态变压器,其特征在于:所述变压器的启动方 案包括， 第一阶段:不控整流阶段,交流侧串联限流电阻后并网，所有开关闭锁,经过二极管构 成的整流电路对装置内电容进行充电； 第二阶段:受控整流阶段，所述第一阶段充电结束后，通过将电容轮流切入切除充电回 路但总投入充电回路电容个数一定的方式，将拓扑内电容电压充至额定值附近； 第三阶段：斜坡升压阶段，所述第二阶段充电结束后,通过给定斜坡上升的参考电压， 利用电压控制环将电容电压充电至额定值。 9 .如权利要求8所述的多中压交流端口固态变压器,其特征在于:所述变压器的启动方 案包括， 在所述多端口柔性互联模块中的单相电压源型变换器的交流侧端口间并联一个保护 装置； 所述保护装置由金属氧化物限压器和晶闸管旁路开关并联组成，所述金属氧化物限压 器将电压限制在保护水平，所述晶闸管旁路开关将单相电压源型变换器的交流侧端口旁 路。 10 .如权利要求9所述的多中压交流端口固态变压器，其特征在于：所述晶闸管旁路开 关包括， 由反并联晶闸管、阻容回路、静态电阻并联后再与一个饱和电抗器串联构成。 11 . 一种应用于如权利要求1所述的多中压交流端口固态变压器的控制方法，其特征在 于:包括线路潮流控制环、级联Η桥控制环、DC-DC变换器控制环和公共连接母线电压平衡控 制环。 12 .如权利要求11所述的多中压交流端口固态变压器的控制方法，其特征在于:包括， 电压源分配方式满足以下基本条件方程： --------1- -------1 -------Vet — Fa -『刖 *(左—2,3,...,») Rea/(X『(：t ·Ζj- -Vsm ·ΐρ) — P!ii!X 其中，hc4为多端口柔性交流互联装置在第k条线路上等效串联的电压源交流分量的矢 量表达式，声刖*为实现第k条线路上目标潮流时所需串联在第1条线路和第k条线路之间的 等效电压源矢量表达式，P,加为与所述级联Η桥相连的所述多端口柔性互联模块中的半桥 型变换器交流端口输出的等效电压交流分量的矢量表达式，7；为第k条线路上的交流电流 的共猴矢量表达式，7；为所述级联Η桥的桥臂交流电流的共猴矢量表达式,P]BDC为所述与多 端口柔性互联模块相连的隔离型双向DC-DC变换器的传输功率表达式,η为通过所述多端口 柔性交流互联模块互联的馈线数量。 13 .如权利要求12所述的多中压交流端口固态变压器的控制方法，其特征在于：所述 Fei的选取包括， 简化性取歹a =讶沏*/2，定义电压源型单相变换器所需输出电压交流成分最小，即所述 建i的选取满足= VSM 取到最小值； 或者令Pibdc = °，即： Rca/(^Kά-·Λ - V加= 0 I [EN CN113364311A]: L A multi-medium voltage AC port solid-state transformer, characterized by comprising: a multi-port flexible interconnection module; a cascaded full-bridge converter, the AC input end of the cascaded full-bridge converter is connected in series to the multi-port flexible Interconnection modules; and, isolated DC converters, one end of each isolated DC converter is connected to the DC output side of the sub-module of the cascaded full-bridge converter, and the other ends of each isolated DC converter are mutually connected Connect in parallel to form a low-voltage DC bus. 2 The multi-medium voltage AC port solid-state transformer according to claim 1, wherein the multi-port flexible interconnection module comprises a plurality of voltage source single-phase converters sharing a DC bus, and the converter AC side output The voltage is connected in series with the feeder. 3 The multi-medium-voltage AC port solid-state transformer of claim 1, wherein the cascaded full-bridge converter comprises a medium-voltage-level voltage source converter, and its sub-module topology is a full-bridge converter. 4 The multi-medium voltage AC port solid-state transformer according to claim 1, characterized in that: the isolated DC converter comprises a DODC converter with a middle and high frequency isolation transformer in the middle, and its topology is a dual active full bridge converter Or a half-bridge converter or a power-controllable isolated DC-DC converter. 5 The multi-medium voltage AC port solid-state transformer according to claim 1 or 2, characterized in that: the voltage source single-phase converter topology constituting the multi-port flexible interconnection module includes a two-level voltage source single-phase converter Either a three-level voltage source single-phase converter or a voltage source single-phase converter capable of bidirectional power flow. 6 The multi-medium voltage AC port solid-state transformer according to claim 5, wherein the multi-port flexible interconnection module is connected to the low-voltage DC bus through an isolated bidirectional DODC converter or no isolated bidirectional DODC converter is installed. . 7 The multi-medium-voltage AC-port solid-state transformer according to claim 6, characterized in that it includes, a power equation: where Pk is the active power of the k-th line of the multi-medium-voltage AC-port interconnection mutual aid solid-state transformer Expression, Pl is the power of the low-voltage DC port of the multi-medium-voltage AC port interconnection mutual aid type solid-state transformer. 8 The multi-medium voltage AC port solid-state transformer according to claim 7, characterized in that: the startup scheme of the transformer includes, the first stage: an uncontrolled rectification stage, the AC side is connected to the grid after a series current limiting resistor, and all open and close locks , The capacitor in the device is charged through a rectifier circuit composed of diodes; the second stage: controlled rectification stage, after the first stage of charging is completed, the capacitor is cut into the charging circuit by turns, but the total number of capacitors in the charging circuit is fixed The method of charging the capacitor voltage in the topology to near the rated value; The third stage: the ramp-up stage, after the second stage of charging is completed, the capacitor voltage is charged to the capacitor voltage through a given ramp-up reference voltage Rated value. 9 The multi-medium voltage AC port solid-state transformer according to claim 8, wherein: the start-up scheme of the transformer comprises, between the AC side ports of the single-phase voltage source type converter in the multi-port flexible interconnection module Connect a protection device in parallel; The protection device is composed of a metal oxide voltage limiter and a thyristor bypass switch in parallel. The metal oxide voltage limiter limits the voltage to a protection level. Side port bypass. 10 The multi-medium voltage AC port solid-state transformer according to claim 9, wherein the thyristor bypass switch comprises an anti-parallel thyristor, a resistance-capacitance circuit, and a static resistance connected in parallel and then connected in series with a saturable reactor. 11 . A control method applied to the multi-medium voltage AC port solid-state transformer of claim 1, characterized in that it includes a line power flow control loop, a cascaded H-bridge control loop, a DC-DC converter control loop, and a common connection Bus voltage balance control loop. 12 The control method of a multi-medium voltage AC port solid-state transformer according to claim 11, characterized in that it comprises: the voltage source distribution method satisfies the following basic condition equations: --------1- -------1 -------Vet - Fa -"cut off the feet*(Left -2,3,...,») Rea/(X(:t ·Ζj- -Vsm ·ΐρ) - P!ii!X Among them, hc4 is the vector expression of the voltage source AC component of the multi-port flexible AC interconnection device in equivalent series on the k-th line, and the sound* is the first line that needs to be connected in series to achieve the target power flow on the k-th line. The equivalent voltage source vector expression between and the k-th line, P, is added as the equivalent voltage output by the AC port of the half-bridge converter in the multi-port flexible interconnection module connected to the cascaded H-bridge The vector expression of the AC component, 7; is the common monkey vector expression of the AC current on the k-th line, 7; is the common monkey vector expression of the AC current of the bridge arm of the cascaded H bridge, P]BDC is The transmission power expression of the isolated bidirectional DC-DC converter connected to the multi-port flexible interconnection module, η is the number of feeders interconnected through the multi-port flexible AC interconnection module. 13 The control method of a multi-medium voltage AC port solid-state transformer according to claim 12, characterized in that: the selection of Fei includes, simplifying a = surprise*/2, defining a voltage source single-phase transformer The AC component of the required output voltage is the smallest, that is, the selection of the built-in i satisfies = VSM Take the minimum value; or let Pibdc = °, that is: Rca/(^Kά-·Λ-V plus = 0 I | [ZH CN113364311A]: 一种多中压交流端口固态变压器及其控制方法 技术领域 [0001]本发明涉及电力系统中交直流电网柔性互联、电力电子的技术领域，尤其涉及一 种多中压交流端口固态变压器及其控制方法。 背景技术 [0002] 配电网作为经济和社会发展的重要基础设施，对实现能源互联网战略目标起着关 键作用，随着分布式电源的不断渗透，储能、电动汽车及可控负荷的大量接入，以分布式电 源为核心的多元电力供应系统将改变配电网的现有形态，采用多电压等级的交直流混合配 电架构，可极大提升系统控制及设备接入的灵活性，是未来配电网的重要发展方向。 [0003] 固态变压器(Solid State Transformer,SST)是一种新型电力电子设备，其特征 在于每个功率模块中均包含高频变压器和大量电力电子开关，SST可以实现交直流电压转 换、电气隔离、功率传输和大规模分布式新能源并网接入等功能，为交直流配网中的核心设 备之一。目前，成熟的SST结构以级联H桥型SST(Cascaded H-Bridge Type SST,CHB-SST)为 主，该拓扑每一相包含多个级联功率子模块，每个功率子模块由输入侧的H桥和输出侧高频 链DC-DC变换器构成；CHB-SST的输入串联输出并联(Input-Series-Output-Parallel, ISOP)连接特征使其可以接入较高电压的交流电网，并以低压直流端口为媒介在交直流系 统间传输功率，具有非常广泛的应用场景。 [0004] 配电网末端的电能消费者对于供电可靠性和电能质量的要求日渐提升，希望从配 电网运营者处获取更多能量灵活流动、电力议价谈判等自主性，而现有配电系统由于各自 独立运行，无法有效解决线路堵塞问题，馈线负荷不均衡问题突出，配网系统实际容量受最 先达到容量上限的单条线路限制，严重影响电网经济运行。 [0005]为解决上述问题，一种方案为新建或改造现有线路，这种方案成本高昂且耗时长 久；另一种方案为通过固态变压器实现多中压交流端口互联互济，形成互联化的交直流混 合配电网。利用电力电子变换器控制的实时性和快速性，实现不同馈线间的功率交互，解决 负荷在空间上分布动态不平衡造成的设备及线路利用率下降问题，该方案方便直流负荷、 分布式电源以及储能装置的即插即用式接入，具有经济高效、优化潮流分布、改善配电网电 能质量等多种功能。 发明内容 [0006] 本部分的目的在于概述本发明的实施例的一些方面以及简要介绍一些较佳实施 例。在本部分以及本申请的摘要和发明名称中可能会做些简化或省略以避免使本部 分、摘要和发明名称的目的模糊，而这种简化或省略不能用于限制本发明的范围。 [0007] 鉴于上述现有存在的问题，提出了本发明。 [0008]因此，本发明解决的技术问题是:现有的固态变压器只具备电压变换和功率传输 功能，不具备多交流馈线互联互济功能。 [0009]为解决上述技术问题，本发明提供如下技术方案:多端口柔性互联模块；级联全桥 变换器，所述级联全桥变换器的交流输入端串联接入所述多端口柔性互联模块；以及，隔离 型直流变换器，各个隔离型直流变换器的一端与所述级联全桥变换器的子模块的直流输出 侧相连接，所述各个隔离型直流变换器的另一端相互并联构成低压直流母线。 [0010]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述多端 口柔性互联模块包括多个共享直流母线的电压源型单相变换器组成,所述变换器交流侧输 出电压与馈线串联。 [0011]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述级联 全桥变换器包括中压级电压源型变换器，其子模块拓扑为全桥型变换器。 [0012]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述隔离 型直流变换器包括中间带有中高频隔离变压器的DODC变换器，其拓扑为双有源全桥变换 器或者半桥型变换器或者功率可控的隔离型DC-DC变换器。 [0013]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：组成所述 多端口柔性互联模块的电压源型单相变换器拓扑包括两电平电压源型单相变换器或者三 电平电压源型单相变换器或者能进行功率双向流动的电压源型单相变换器。 [0014]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述多端 □柔性互联模块通过一个隔离型双向DC-DC变换器与低压直流母线连接或者不加装隔离型 双向DODC变换器。 [0015]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：包括，功率 方程： [0016] [0017]其中，Pk为所述多中压交流端口互联互济式固态变压器的第k条线路的有功功率 表达式,Pl为所述多中压交流端口互联互济式固态变压器低压直流端口功率。 [0018]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述变压 器的启动方案包括，第一阶段:不控整流阶段，交流侧串联限流电阻后并网，所有开关闭锁, 经过二极管构成的整流电路对装置内电容进行充电;第二阶段:受控整流阶段，所述第一阶 段充电结束后，通过将电容轮流切入切除充电回路但总投入充电回路电容个数一定的方 式，将拓扑内电容电压充至额定值附近;第三阶段:斜坡升压阶段，所述第二阶段充电结束 后，通过给定斜坡上升的参考电压，利用电压控制环将电容电压充电至额定值。 [0019]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述变压 器的启动方案包括，在所述多端口柔性互联模块中的单相电压源型变换器的交流侧端口间 并联一个保护装置;所述保护装置由金属氧化物限压器和晶闸管旁路开关并联组成，所述 金属氧化物限压器将电压限制在保护水平，所述晶闸管旁路开关将单相电压源型变换器的 交流侧端口旁路。 [0020]作为本发明所述的多中压交流端口固态变压器的一种优选方案，其中：所述晶闸 管旁路开关包括，由反并联晶闸管、阻容回路、静态电阻并联后再与一个饱和电抗器串联构 成。 [0021]作为本发明所述的多中压交流端口固态变压器的控制方法的一种优选方案，其 中：包括线路潮流控制环、级联Η桥控制环、DC-DC变换器控制环和公共连接母线电压平衡控 制环。 [0022]作为本发明所述的多中压交流端口固态变压器的控制方法的一种优选方案，其 中：包括,电压源分配方式满足以下基本条件方程： [0023] p--------------* Vn — Vck- P刖出(左二 2,3, 7* -Vsm *ΐp) = Pibdc .. I [0024]其中，歹0*为多端口柔性交流互联装置在第k条线路上等效串联的电压源交流分量 的矢量表达式，沅5*为实现第k条线路上目标潮流时所需串联在第1条线路和第k条线路之 间的等效电压源矢量表达式为与所述级联Η桥相连的所述多端口柔性互联模块中的 半桥型变换器交流端口输出的等效电压交流分量的矢量表达式，7；为第k条线路上的交流 电流的共猴矢量表达式，7；为所述级联Η桥的桥臂交流电流的共猴矢量表达式,P]bdc为所述 与多端口柔性互联模块相连的隔离型双向DODC变换器的传输功率表达式,η为通过所述多 端口柔性交流互联模块互联的馈线数量。 [0025]作为本发明所述的多中压交流端口固态变压器的控制方法的一种优选方案，其 中：所述Pg的选取包括， [0026]简化性取户口 =V^/2，定义电压源型单相变换器所需输出电压交流成分最小，即 所述建i的选取满足max版做左= 1,2,...,叫Vsm 取到最小值； [0027] 或者令P]bdc = 0,即： [0028] Rca/(^Kά·Λ - Vμ/ ·7ρ) = 0 £21 □ [0029]本发明的有益效果:本发明通过引入多端口柔性互联模块,提供多个交流互联端 口，实现多交流馈线互联，并通过调节串联在线路上的等效电压源幅值相位,可进行线路有 功功率和无功功率解耦的主动控制，从而实现多交流馈线间的功率互济，有利于配电网经 济高效运行;本发明中的多端口柔性互联模块具备模块化的特点，通过增加互联模块中并 联电压源型单相变换器数量，可快速、经济地实现互联端口的拓展。 附图说明 [0030]为了更清楚地说明本发明实施例的技术方案,下面将对实施例描述中所需要使用 的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本发明的一些实施例，对于本 领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可以根据这些附图获得其它 的附图。其中： [0031]图1为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 拓扑结构及其互联多端交流系统/馈线的系统示意图； [0032]图2为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 多端口柔性互联模块通过一个隔离型双向DC-DC变换器与低压直流母线连接的拓扑结构及 其互联多端交流系统/馈线的系统示意图； [0033]图3为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 级联H桥子模块、隔离型DC-DC变换器和单相电压源型变换器典型拓扑举例示意图； [0034]图4为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 交直流电网多馈线柔性互联系统示意图； [0035]图5为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 实施方案一中多端口互联模块采用并联两电平半桥型变换器、级联H桥子模块采用全桥拓 扑、IDC采用双有源全桥拓扑的双端口互联互济式固态变压器的拓扑结构及其实现两个交 流系统/馈线互联的系统示意图； [0036]图6为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 实施方案一中多端口互联模块采用并联两电平半桥型变换器、级联H桥子模块采用全桥拓 扑、IDC采用双有源全桥拓扑的双端口互联互济式固态变压器的控制策略框图； [0037]图7为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 实施方案一中第一种工况的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压直 流母线电压波形图； [0038]图8为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 实施方案一中第二种工况的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压直 流母线电压波形图； [0039]图9为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法的 实施方案一中第三种工况的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压直 流母线电压波形图； [0040]图10为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案一中第四种工况的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压 直流母线电压波形图； [0041]图11为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案一中第五种工况的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压 直流母线电压波形图； [0042]图12为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案二中的多端口互联模块采用并联两电平半桥型变换器且通过一个隔离型双向 DC-DC变换器与低压直流母线连接、级联H桥子模块采用全桥拓扑、IDC采用双有源全桥拓扑 的双端口互联互济式固态变压器的拓扑结构及其实现两个交流系统/馈线互联的系统示意 图； [0043]图13为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案二中的多端口互联模块采用并联两电平半桥型变换器且通过一个隔离型双向 DC-DC变换器与低压直流母线连接、级联H桥子模块采用全桥拓扑、IDC采用双有源全桥拓扑 的双端口互联互济式固态变压器的控制策略框图； [0044]图14为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案二的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压直流母线电压 波形图； [0045]图15为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案三中多端口互联模块采用并联两电平半桥型变换器、级联H桥子模块采用全桥 拓扑、IDC采用双有源全桥拓扑的三端口互联互济式固态变压器的拓扑结构及其实现三个 交流系统/馈线互联的系统示意图； [0046]图16为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案三中的多端口互联模块采用两电平半桥型变换器、级联H桥子模块采用全桥拓 扑、IDC采用双有源全桥拓扑的三端口互联互济式固态变压器的控制策略框图； [0047]图17为本发明一个实施例提供的一种多中压交流端口固态变压器及其控制方法 的实施方案三的仿真各馈线潮流、各电容电压、各馈线电流、负荷功率、低压直流母线电压 波形图。 具体实施方式 [0048]为使本发明的上述目的、特征和优点能够更加明显易懂，下面结合附图对 本发明的具体实施方式做详细的说明，显然所描述的实施例是本发明的一部分实施例，而 不是全部实施例。基于本发明中的实施例，本领域普通人员在没有做出创造性劳动前提下 所获得的所有其他实施例，都应当属于本发明的保护的范围。 [0049]在下面的描述中阐述了很多具体细节以便于充分理解本发明，但是本发明还可以 采用其他不同于在此描述的其它方式来实施，本领域技术人员可以在不违背本发明内涵的 情况下做类似推广，因此本发明不受下面公开的具体实施例的限制。 [0050]其次，此处所称的“一个实施例”或“实施例”是指可包含于本发明至少一个实现方 式中的特定特征、结构或特性。在本中不同地方出现的“在一个实施例中“并非均指 同一个实施例，也不是单独的或选择性的与其他实施例互相排斥的实施例。 [0051]本发明结合示意图进行详细描述，在详述本发明实施例时，为便于说明，表示器件 结构的剖面图会不依一般比例作局部放大，而且所述示意图只是示例，其在此不应限制本 发明保护的范围。此外，在实际制作中应包含长度、宽度及深度的三维空间尺寸。 [0052]同时在本发明的描述中，需要说明的是，术语中的“上、下、内和外”等指示的方位 或位置关系为基于附图所示的方位或位置关系，仅是为了便于描述本发明和简化描述，而 不是指示或暗示所指的装置或元件必须具有特定的方位、以特定的方位构造和操作，因此 不能理解为对本发明的限制。此外，术语“第一、第二或第三”仅用于描述目的，而不能理解 为指示或暗示相对重要性。 [0053]本发明中除非另有明确的规定和限定，术语“安装、相连、连接“应做广义理解，例 如:可以是固定连接、可拆卸连接或一体式连接；同样可以是机械连接、电连接或直接连接， 也可以通过中间媒介间接相连，也可以是两个元件内部的连通。对于本领域的普通技术人 员而言，可以具体情况理解上述术语在本发明中的具体含义。 [0054] 实施例1 [0055]参照图1〜4,为本发明的一个实施例，提供了一种多中压交流端口固态变压器及 其控制方法，包括： [0056]多端口柔性互联模块； [0057]级联全桥变换器，级联全桥变换器的交流输入端串联接入多端口柔性互联模块; 以及， [0058]隔离型直流变换器，各个隔离型直流变换器的一端与级联全桥变换器的子模块的 直流输出侧相连接,各个隔离型直流变换器的另一端相互并联构成低压直流母线。 [0059]具体的，根据本发明的第一方面，提供一种适用于交直流混合配电网的具备多馈 线互联互济功能的多中压交流端口互联互济式固态变压器，其中，多端口交流互联互济式 固态变压器由一个多端口柔性互联模块、一个级联Η桥(CHB)和多个隔离型DODC变换器 QDC)共同组成。 [0060] 进一步的，多端口柔性互联模块由多个共享直流母线的电压源型单相变换器组 成,变换器交流侧输出电压与馈线串联，通过调节串联在线路上的等效电压源幅值相位，实 现线路有功功率和无功功率的主动控制;级联Η桥为中压级电压源型变换器，其子模块拓扑 为全桥型变换器;隔离型DODC变换器为中间带有中高频隔离变压器的DODC变换器，其拓 扑可以是双有源全桥变换器，也可以是半桥型变换器,或者其他可实现功率可控的隔离型 DC-DC变换器。 [0061]优选地，组成多端口柔性互联模块的电压源型单相变换器拓扑可以是两电平电压 源型单相变换器，也可以是三电平电压源型单相变换器，或者其他可实现功率双向流动的 电压源型单相变换器;多端口柔性互联模块可以通过一个隔离型双向DODC变换器与低压 直流母线连接，也可以不加装隔离型双向DC-DC变换器。 [0062]为了满足系统级别的能量平衡，多中压交流端口互联互济式固态变压器满足下列 功率方程： [0063] Σ”. [0064]其中，Pk为多中压交流端口互联互济式固态变压器的第k条线路的有功功率表达 式,Pl为多中压交流端口互联互济式固态变压器低压直流端口功率。 [0065] 优选的，本发明提供一种适用于交直流混合配电网的多中压交流端口互联互济式 固态变压器的控制方法，该控制方法包括线路潮流控制环、级联Η桥控制环、DC-DC变换器控 制环和公共连接母线电压平衡控制环。 [0066] 优选的，本发明提供一种适用于交直流混合配电网的多中压交流端口互联互济式 固态变压器在配网馈线上等效串联的电压源的分配方式，该电压源分配方式满足以下基本 条件方程： [0067] ρ--------------* Vn — Vck- P刖出(左二 2,3, _打 _ _ T * Rcal(y'7ck*lk - Vsm *ΐp) = PIBDC [0068]其中，歹0k为多端口柔性交流互联装置在第k条线路上等效串联的电压源交流分量 的矢量表达式，声引女为实现第k条线路上目标潮流时所需串联在第1条线路和第k条线路之 间的等效电压源矢量表达式，讥，”为与级联Η桥相连的多端口柔性互联模块中的半桥型变 换器交流端口输出的等效电压交流分量的矢量表达式，7；为第k条线路上的交流电流的共 猴矢量表达式，了；为级联Η桥的桥臂交流电流的共辗矢量表达式,P]bdc为与多端口柔性互联 模块相连的隔离型双向DC-DC变换器的传输功率表达式,n为通过多端口柔性交流互联模块 互联的馈线数量。 [0069] 其中，适用于交直流混合配电网的多中压交流端口互联互济式固态变压器在配网 馈线上等效串联的电压源的分配方式为满足基本条件方程的任何一组犷= 2，…,叫元必｝ 的解。 [0070] 进一步的，适用于交直流混合配电网的多中压交流端口互联互济式固态变压器在 配网馈线上等效串联的电压源的分配方式的求解可以考虑简化性取万α =0.5声时2，也可以 考虑令Pibdc = °，即歹门的选取满足： [0071] ReaAXLaJ*-Psm伉）=0 [0072] 从而在拓扑上省去与多端口柔性互联模块相连的隔离型双向DC-DC变换器，也可 以考虑电压源型单相变换器所需输出电压交流成分幅值最小，即声ci的选取满足 max｛反*（才= 12.·.Μ，¦以ϊ ¦｝取到最小值，还可以是任何一种满足基本条件方程的选取方 式。 [0073]更进一步的，多端口柔性互联模块中的半桥型变换器交流端口输出电压成分中含 有相同大小的直流分量和控制所需的不同交流分量。 [0074]优选的，电压源型单相变换器交流端口输出电压的直流分量可以是公共连接母线 电压值的一半，也可以是其他小于公共连接母线电压值大于零的值。 [0075]优选的，本发明提供一种多馈线柔性互联交直流混合配电系统，核心设备为适用 于交直流混合配电网的多中压交流端口互联互济式固态变压器。 [0076] 优选的，多馈线柔性互联交直流混合配电系统可以包含一个多中压交流端口互联 互济式固态变压器，也可以包含多个多中压交流端口互联互济式固态变压器，形成更复杂 的环状/网状系统拓扑。 [0077] 优选的，本发明提供一种适用于交直流混合配电网的多中压交流端口互联互济式 固态变压器串联在馈线上的电压的过压保护方案。 [0078] 优选的，多中压交流端口互联互济式固态变压器串联在馈线上的电压的过压保护 方案可以通过在多端口柔性互联模块中的单相电压源型变换器的交流侧端口间并联一个 保护装置实现，保护装置由金属氧化物限压器和晶闸管旁路开关并联组成，金属氧化物限 压器实现将电压限制在保护水平，晶闸管旁路开关将单相电压源型变换器的交流侧端口旁 路，实现过压保护。 [0079]其中，晶闸管旁路开关由反并联晶闸管、阻容回路、静态电阻并联后再与一个饱和 电抗器串联构成。 [0080] 优选的，本发明提供一种适用于交直流混合配电网的多中压交流端口互联互济式 固态变压器的启动方案。 [0081]优选的，多中压交流端口互联互济式固态变压器的启动方案可以由三个阶段构 成： [0082]第一阶段为不控整流阶段，交流侧串联限流电阻后并网,所有开关闭锁，经过二极 管构成的整流电路对装置内电容进行充电； [0083]第二阶段为受控整流阶段，第一阶段充电结束后，通过将电容轮流切入切除充电 回路但总投入充电回路电容个数一定的方式，将拓扑内电容电压充至额定值附近； [0084]第三阶段为斜坡升压阶段，第二阶段充电结束后，通过给定斜坡上升的参考电压， 利用电压控制环将电容电压充电至额定值。 [0085] 优选的，本发明提供一种适用于交直流混合配电网的多中压交流端口互联互济式 固态变压器的控制系统。 [0086]其中，多中压交流端口互联互济式固态变压器的控制系统可以采用集中式控制架 构，也可以采用分布式控制架构，还可以采用集中式控制和分布式控制相结合的分层式控 制架构。 [0087]本发明通过引入多端口柔性互联模块，提供多个交流互联端口，实现多交流馈线 互联，并通过调节串联在线路上的等效电压源幅值相位，可进行线路有功功率和无功功率 解耦的主动控制，从而实现多交流馈线间的功率互济，有利于配电网经济高效运行;本发明 中的多端口柔性互联模块具备模块化的特点，通过增加互联模块中并联电压源型单相变换 器数量，可快速、经济地实现互联端口的拓展。 [0088] 实施例2 [0089] 参照图5〜17为本发明另一个实施例，为对本方法中采用的技术效果加以验证说 明，本实施例结合具体三种实施例对一种多中压交流端口固态变压器及其控制方法进行具 体说明并针对上述实施例进行仿真，以本发明提出的结构及方法的有效性和可行性进行验 证，以科学论证的手段验证本方法所具有的真实效果。 [0090]如图5所示，为本发明一实施例使用多中压交流端口互联互济式固态变压器实现 双交流系统互联互济的拓扑和系统连接示意图；本实施例中，多中压交流端口互联互济式 固态变压器包括一个多端口柔性互联模块、一个三相级联全桥拓扑和与之串联的多个双有 源全桥变换器;多端口柔性互联模块包含三个共享直流母线的两电平半桥型变换器，分别 与两条交流馈线和级联全桥拓扑串联;通过调节串联在馈线上的等效电压交流分量、与级 联全桥拓扑串联的半桥型变换器输出的等效电压的交流分量、级联全桥拓扑输出的等效交 流电压的幅值相位、双有源全桥变换器输出的直流电压幅值，一方面实现多中压交流端口 互联互济式固态变压器的能量平衡，另一方面实现交流馈线上的有功功率和无功功率的主 动控制，即实现馈线潮流的互济。 [0091] 在另一优选实例中，参照图12,使用多中压交流端口互联互济式固态变压器实现 双交流系统互联互济;该实施例中,多中压交流端口互联互济式固态变压器包括一个多端 □柔性互联模块、一个三相级联全桥拓扑和与之串联的多个双有源全桥变换器;多端口柔 性互联模块包含三个共享直流母线的两电平半桥型变换器,分别与两条交流馈线和级联全 桥拓扑串联，此外该多端口柔性互联模块通过一个双有源全桥变换器与低压直流母线连 接;通过调节串联在馈线上的等效电压交流分量、与多端口柔性互联模块相连的双有源全 桥变换器输入的直流电压幅值、级联全桥拓扑输出的等效交流电压的幅值相位、与级联H桥 相连的双有源全桥变换器输出的直流电压幅值，一方面实现多中压交流端口互联互济式固 态变压器的能量平衡,另一方面实现交流馈线上的有功功率和无功功率的主动控制,即实 现馈线潮流的互济。 [0092] 在另一优选实例中，参照图15,使用多中压交流端口互联互济式固态变压器实现 三个交流系统互联;该实施例中，多中压交流端口互联互济式固态变压器包括一个多端口 柔性互联模块、一个三相级联全桥拓扑和与之串联的多个双有源全桥变换器。多端口柔性 互联模块包含四个共享直流母线的两电平半桥型变换器，分别与三条交流馈线和级联全桥 拓扑相连;通过调节串联在馈线上的等效电压交流分量、与级联全桥拓扑串联的半桥型变 换器输出的等效电压的交流分量、级联全桥拓扑输出的等效交流电压的幅值相位、双有源 全桥变换器输出的直流电压幅值，一方面实现多中压交流端口互联互济式固态变压器的能 量平衡，另一方面实现交流馈线上的有功功率和无功功率的主动控制，即实现馈线潮流的 互济。 [0093]以下结合具体的仿真实例来对上述结构和方法的应用进行进一步说明；结合上述 实施例，以下采用MATLAB/Simulink软件针对系统进行仿真验证，仿真参数如表1所示。 [0094]表1：仿真参数表。 参数 数值 线路额定视在功率 Sn=1MV . A 节点1电压 Vi.RMs = 10・5kV,、= 0。 线路1阻抗 Li = 35mH,R] = 0.55Q 节点2电压 N9 RM =10.5kV,9 =-3° /,KM、 / 线路2阻抗 L2 = 35mH,R2 = 0.55Q 节点3电压 V„ RM =10.5kV,9 =-6° J ,KM、 J 线路3阻抗 L3 = 35mH,R3 = 0.55Q 低压直流母线电压 VlvL50V 公共连接电容 C. . . =2500Vlink link 级联Η桥子模块电容 CrH=lmF,VrHR= 2500VCHB CHB 级联Η桥子模块个数 4 隔离型DC-DC变换器电容 C =ImF,V =2500V 隔离型DC-DC变换器个数 4 开关频率 3kHz [0096] 实施方案一： [0097]由多中压交流端口互联互济式固态变压器实现互联互济的双交流系统，其连接示 意图参照图5,实施方案一的控制策略如图6所示；多端口柔性交流互联模块包含三个半桥 型变换器，其中与交流馈线相连的两个半桥型变换器控制馈线2上的有功功率和无功功率, 对应的控制环为潮流控制环;与级联全桥拓扑相连的半桥型变换器控制公共连接母线电压 平衡，对应的控制环为公连接母线电压平衡控制环;级联全桥拓扑控制子模块电容电压平 衡，对应的控制环为CHB控制环;与级联全桥拓扑控制子模块串联的双有源全桥变换器控制 低压直流母线电压平衡,对应的控制环为低压直流母线电压平衡控制环。 [0098]实施方案一的多中压交流端口互联互济式固态变压器在配网馈线上等效串联的 电压源的分配方式，考虑简化性取5c =此心/2。 [0099] 为验证多中压交流端口互联互济式固态变压器的互联互济能力，仿真设定了五种 运行工况。 [0100] 工况一：负荷为0.8p.u.有功功率，节点1吸收0.3p.u.无功功率，节点2发出 0.4p.u.有功功率，吸收0.3p.u.无功功率，仿真负荷重载，两条馈线有功功率平均分配的情 况； [0101] 工况二：负荷为0.8p.u.有功功率，节点1吸收0.3p.u.无功功率，节点2发出 0.7p.u.有功功率，吸收0.3p.u.无功功率，仿真负荷重载，线路2有功功率重载的情况； [0102] 工况三：负荷为0.8p.u.有功功率，节点1吸收0.3p.u.无功功率，节点2吸收 0.1p.u.有功功率，吸收0.3p.u.无功功率，仿真负荷重载，线路2有功功率轻载且反向的情 况； [0103] 工况四：负荷为0.2p.u.有功功率，节点1吸收0.3p.u.无功功率，节点2发出 0.1p.u.有功功率，吸收0.3p.u.无功功率，仿真负荷轻载，两条馈线有功功率平均分配情 况； [0104] 工况五：负荷为0.2p.u.有功功率，节点1吸收0.3p.u.无功功率，节点2吸收 0.8p.u.有功功率，吸收0.3p.u.无功功率，仿真负荷轻载，线路2有功功率重载且反向的情 况； [0105]如图7、图8、图9、图10、图11所示，分别为实施方案一中工况一到工况五的仿真结 果，每幅图包含10幅波形图，从左到右、从上到下依次为线路1有功功率P1波形图，线路1无 功功率Q1波形图，线路2有功功率P2波形图，线路2无功功率Q2波形图，三相公共连接母线电 压Vlink_abc波形图，三相级联H桥子模块电容电压VCHB_capacitor_abc波形图，线路1三相 电流I1abc波形图，线路2三相电流12abe波形图，负荷有功功率PL波形图，低压直流母线电 压V_LVDC波形图。 [0106]仿真波形结果表明,多中压交流端口互联互济式固态变压器在保持能量平衡,即 电容电压稳定、馈线有功功率之和等于负荷有功功率的情况下，可实现端口互联馈线上的 潮流互济。 [0107] 实施方案二： [0108]由多中压交流端口互联互济式固态变压器实现互联互济的双交流系统，其连接示 意图参照图12,实施方案二的控制策略如图13所示。多端口柔性交流互联模块包含三个半 桥型变换器，其中与交流馈线相连的两个半桥型变换器控制馈线2上的有功功率和无功功 率，对应的控制环为潮流控制环，与级联全桥拓扑相连的半桥型变换器用来承受桥臂的直 流电压。多端口柔性交流互联模块通过一个双有源全桥变换器连接到低压直流母线上，该 双有源全桥变换器控制公共连接母线电压平衡，对应的控制环为公连接母线电压平衡控制 环。级联全桥拓扑控制子模块电容电压平衡，对应的控制环为CHB控制环。与级联全桥拓扑 子模块串联的双有源全桥变换器控制低压直流母线电压平衡，对应的控制环为低压直流母 线电压平衡控制环。 [0109]仿真设定的工况与实施方案一中的工况四相同，即：负荷为0.2p.u.有功功率，节 点1吸收0.3p.u.无功功率，节点2发出0.1p.u.有功功率，吸收0.3p.u.无功功率。 [0110]如图14所示为工况仿真结果，每幅图包含10幅波形图，从左到右、从上到下依次为 线路1有功功率P1波形图，线路1无功功率Q1波形图，线路2有功功率P2波形图,线路2无功功 率Q2波形图，三相公共连接母线电压Vlink_abc波形图，三相级联H桥子模块电容电压VCHB_ capacitojabc波形图，线路1三相电流Habe波形图，线路2三相电流12abe波形图，负荷有 功功率PL波形图，低压直流母线电压V_LVDC波形图。 [0111]仿真波形结果表明，多中压交流端口互联互济式固态变压器在保持能量平衡，即 电容电压稳定、馈线有功功率之和等于负荷有功功率的情况下，可实现端口互联馈线上的 潮流互济。 [01⑵实施方案三： [0113]由多中压交流端口互联互济式固态变压器实现柔性互联的三个交流系统，其连接 示意图如图15所示,实施方案三的控制策略如图16所示；多中压交流端口互联互济式固态 变压器包含四个半桥型变换器，其中与交流馈线相连的三个半桥型变换器控制馈线2、馈线 3上的有功功率和无功功率，对应的控制环为潮流控制环;与级联全桥拓扑相连的半桥型变 换器控制公共连接母线电压平衡，对应的控制环为公连接母线电压平衡控制环;级联全桥 拓扑控制子模块电容电压平衡，对应的控制环为CHB控制环;与级联全桥拓扑控制子模块串 联的双有源全桥变换器控制低压直流母线电压平衡，对应的控制环为低压直流母线电压平 衡控制环。 [0114]实施方案三的多中压交流端口互联互济式固态变压器在配网馈线上等效串联的 电压源的分配方式,考虑半桥型变换器所需输出电压交流成分幅值最小，即方门的选取满足 max{¦ Vη Vci ¦,¦ 匕?31,¦ 曰¦}取至[¦最小值。 [0115] 仿真设定的工况如下：负荷为0.8p.u.,节点1发出0.2p.u.无功功率，节点2发出 0.3p.u.有功功率,吸收0.1p.u.无功功率,节点3发出0.2p.u.有功功率,发出0.1p.u.无功 功率。 [0116]如图17所示为工况仿真结果，每幅图包含13幅波形图，从左到右、从上到下依次为 线路1有功功率Pi波形图，线路1无功功率Q1波形图，线路2有功功率P2波形图，线路2无功功 率Q2波形图，线路3有功功率P3波形图，线路3无功功率Q3波形图，三相公共连接母线电压 Vlink_abc波形图，三相级联Η桥子模块电容电压VCHB_capacitor_abc波形图，线路1三相电 流Habe波形图，线路2三相电流12abe波形图，线路3三相电流13abe波形图，负荷有功功率 PL波形图，低压直流母线电压V_LVDC波形图。 [0117]仿真波形结果表明，多中压交流端口互联互济式固态变压器在互联了三个交流系 统的情况下，既实现了端口互联馈线上的功率互济，同时又保持了能量平衡，即电容电压稳 定、馈线有功功率之和等于负荷有功功率,具备端口拓展能力。 [0118]应说明的是，以上实施例仅用以说明本发明的技术方案而非限制，尽管参照较佳 实施例对本发明进行了详细说明，本领域的普通技术人员应当理解，可以对本发明的技术 方案进行修改或者等同替换，而不脱离本发明技术方案的精神和范围，其均应涵盖在本发 明的权利要求范围当中。 [EN CN113364311A]: A multi-medium voltage AC port solid-state transformer and its control method technical field [0001] The present invention relates to the technical field of flexible interconnection of AC and DC power grids and power electronics in power systems, and in particular to a solid-state transformer with multiple medium voltage AC ports and a control method thereof. Background technique [0002] As an important infrastructure for economic and social development, the distribution network plays a key role in achieving the strategic goal of the Energy Internet. With the continuous penetration of distributed power sources, a large number of access to energy storage, electric vehicles and controllable loads, The diversified power supply system with distributed power sources as the core will change the current form of the distribution network. The use of a multi-voltage AC and DC hybrid power distribution architecture can greatly improve the flexibility of system control and equipment access, which is a future distribution system. An important development direction of the power grid. [0003] Solid State Transformer (SST) is a new type of power electronic equipment, which is characterized in that each power module contains a high-frequency transformer and a large number of power electronic switches. SST can achieve AC-DC voltage conversion, electrical isolation, Power transmission and large-scale distributed new energy grid-connected functions are one of the core equipment in the AC and DC distribution network. At present, the mature SST structure is mainly based on Cascaded H-Bridge Type SST (CHB-SST). Each phase of this topology contains multiple cascaded power sub-modules, and each power sub-module is connected to the input side. H-bridge and output-side high-frequency chain DC-DC converter; CHB-SST input-series-output-parallel (Input-Series-Output-Parallel, ISOP) connection characteristics enable it to be connected to a higher voltage AC power grid, and low voltage The DC port is a medium for transmitting power between AC and DC systems, which has a very wide range of application scenarios. [0004] Electric energy consumers at the end of the distribution network are increasingly demanding power supply reliability and power quality. They hope to obtain more autonomy such as flexible energy flow and electricity negotiation and negotiation from the distribution network operator. However, the existing power distribution network Because the systems operate independently, they cannot effectively solve the problem of line congestion, and the problem of feeder load imbalance is prominent. The actual capacity of the distribution network system is limited by the single line that first reaches the upper limit of the capacity, which seriously affects the economic operation of the power grid. [0005] In order to solve the above problems, one solution is to build or renovate existing lines, which is costly and time-consuming; the other solution is to realize the interconnection of multiple medium voltage AC ports through solid-state transformers to form interconnection. AC/DC hybrid distribution network. Utilize the real-time and rapidity of power electronic converter control to realize the power interaction between different feeders, and solve the problem of equipment and line utilization drop caused by the dynamic unbalance of load distribution in space. This solution is convenient for DC loads, distributed power supplies, and The plug-and-play access of energy storage devices has multiple functions such as cost-effectiveness, optimization of power flow distribution, and improvement of power quality in the distribution network. Summary of the invention [0006] The purpose of this section is to summarize some aspects of the embodiments of the present invention and briefly introduce some preferred embodiments. Some simplifications or omissions may be made in this section, the abstract and the title of the invention in this application to avoid obscuring the purpose of this section, the abstract and the title of the invention, and such simplifications or omissions cannot be used to limit the scope of the present invention. [0007] In view of the above-mentioned existing problems, the present invention is proposed. [0008] Therefore, the technical problem solved by the present invention is: the existing solid-state transformer only has the function of voltage conversion and power transmission, and does not have the function of interconnecting multiple AC feeders. [0009] In order to solve the above technical problems, the present invention provides the following technical solutions: multi-port flexible interconnection module; cascaded full bridge Converter, the AC input end of the cascaded full-bridge converter is connected in series with the multi-port flexible interconnection module; The DC output sides of the sub-modules of the converter are connected, and the other ends of the isolated DC converters are connected in parallel to form a low-voltage DC bus. [0010] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the multi-port flexible interconnection module includes a plurality of voltage source single-phase converters sharing a DC bus, and the conversion The output voltage of the AC side of the converter is connected in series with the feeder. [0011] As a preferred solution of the multi-medium-voltage AC port solid-state transformer of the present invention, wherein: the cascaded full-bridge converter includes a medium-voltage-level voltage source converter, and its sub-module topology is a full-bridge type Converter. [0012] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the isolated DC converter includes a DODC converter with a middle and high frequency isolation transformer in the middle, and its topology is dual active Full-bridge converter or half-bridge converter or power controllable isolated DC-DC converter. [0013] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the voltage source single-phase converter topology constituting the multi-port flexible interconnection module includes a two-level voltage source single-phase The converter is either a three-level voltage source single-phase converter or a voltage source single-phase converter capable of bidirectional power flow. [0014] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the multi-terminal flexible interconnection module is connected to the low-voltage DC bus through an isolated bidirectional DC-DC converter or not installed Isolated bidirectional DODC converter. [0015] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, which includes: the power equation: [0016] [0017] Wherein, Pk is the active power expression of the k-th line of the multi-medium voltage AC port interconnection mutual aid solid-state transformer, and P1 is the low-voltage DC port power of the multi-medium voltage AC port interconnection mutual aid solid-state transformer . [0018] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the startup solution of the transformer includes, the first stage: the uncontrolled rectification stage, the AC side is connected to the grid after the current limiting resistor is connected in series , All opening and closing locks are charged through the rectifier circuit composed of diodes to charge the capacitors in the device; the second stage: controlled rectification stage, after the first stage of charging is completed, the capacitors are cut into the charging circuit in turn, but the charging circuit capacitors are always put into the charging circuit. A certain number of methods are used to charge the capacitor voltage in the topology to near the rated value; the third stage: the ramp-up stage, after the second stage of charging is completed, the reference voltage is given a ramp-up, and the voltage control loop is used to The capacitor voltage is charged to the rated value. [0019] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the starting solution of the transformer includes, the single-phase voltage source type converter in the multi-port flexible interconnection module A protection device is connected in parallel between the AC side ports; the protection device is composed of a metal oxide voltage limiter and a thyristor bypass switch in parallel, the metal oxide voltage limiter limits the voltage to the protection level, and the thyristor bypass switch will The AC side port of the single-phase voltage source converter is bypassed. [0020] As a preferred solution of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the thyristor bypass switch includes an anti-parallel thyristor, a resistance-capacitance circuit, and a static resistance in parallel and then connected to a saturated reactance in parallel The device is formed in series. [0021] As a preferred solution for the control method of the multi-medium-voltage AC port solid-state transformer of the present invention, it includes a line power flow control loop, a cascaded H-bridge control loop, a DC-DC converter control loop, and a common connection Bus voltage balance control . System ring. System ring. [0022] As a preferred solution for the control method of the multi-medium voltage AC port solid-state transformer of the present invention, including: the voltage source distribution mode satisfies the following basic condition equations: [0023] p--------------* Vn - Vck- P cut out (2,3, 7* -Vsm *ΐp) = Pibdc .. I [0024] Among them, 0* is the vector expression of the voltage source AC component of the multi-port flexible AC interconnection device in equivalent series on the kth line, and 5* is the series connection required to achieve the target power flow on the kth line. The equivalent voltage source vector expression between the first line and the k-th line is the equivalent of the output of the AC port of the half-bridge converter in the multi-port flexible interconnection module connected to the cascaded H-bridge The vector expression of the voltage AC component, 7; is the common monkey vector expression of the AC current on the k-th line, 7; is the common monkey vector expression of the AC current of the cascaded H bridge arm, P]bdc Is the transmission power expression of the isolated bidirectional DODC converter connected to the multi-port flexible interconnection module, and n is the number of feeders interconnected through the multi-port flexible AC interconnection module. [0025] As a preferred solution of the control method of the multi-medium voltage AC port solid-state transformer of the present invention, wherein: the selection of Pg includes: [0026] The simplification takes account=V^/2, which defines that the AC component of the output voltage required by the voltage source single-phase converter is the smallest, that is, the selection of the built i satisfies the max version and left = 1, 2,..., Call Vsm to get the minimum value; [0027] Or let P]bdc=0, that is: [0028] Rca/(^Kά·Λ-Vμ/ ·7ρ) = 0 £21 [0029] The beneficial effects of the present invention: by introducing a multi-port flexible interconnection module, the present invention provides multiple AC interconnection ports to realize the interconnection of multiple AC feeders, and by adjusting the amplitude and phase of the equivalent voltage source on the series line, the line can be connected. Active power and reactive power decoupling are actively controlled so as to realize the power mutual aid between multiple AC feeders, which is beneficial to the economic and efficient operation of the distribution network; the multi-port flexible interconnection module of the present invention has the characteristics of modularity, and the interconnection The number of parallel voltage source single-phase converters in the module can quickly and economically realize the expansion of interconnection ports. Description of the drawings [0030] In order to more clearly illustrate the technical solutions of the embodiments of the present invention, the following will briefly introduce the drawings needed in the description of the embodiments. Obviously, the drawings in the following description are only some implementations of the present invention. For example, for those of ordinary skill in the art, other drawings can be obtained based on these drawings without creative labor. in: [0031] FIG. 1 is a topological structure of a multi-medium-voltage AC port solid-state transformer and its control method and a system schematic diagram of interconnecting a multi-terminal AC system/feeder according to an embodiment of the present invention; [0032] FIG. 2 is a topological structure in which a multi-port flexible interconnection module of a multi-medium voltage AC port solid-state transformer and its control method provided by an embodiment of the present invention is connected to a low-voltage DC bus through an isolated bidirectional DC-DC converter and Schematic diagram of the interconnected multi-terminal AC system/feeder; [0033] FIG. 3 is a typical example of a cascaded H-bridge sub-module, an isolated DC-DC converter, and a single-phase voltage source converter of a multi-medium voltage AC port solid-state transformer and its control method provided by an embodiment of the present invention Schematic diagram of topology example; [0034] FIG. 4 is a schematic diagram of an AC/DC grid multi-feeder flexible interconnection system of a multi-medium voltage AC port solid-state transformer and its control method according to an embodiment of the present invention; [0035] FIG. 5 is an implementation of a multi-medium-voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. The multi-port interconnection module adopts parallel two-level half-bridge converters and cascaded H-bridges. The sub-module adopts the full-bridge topology, the topological structure of the dual-port interconnection mutual aid solid-state transformer with the IDC adopts the dual-active full-bridge topology and the schematic diagram of the system for realizing the interconnection of two AC systems/feeders; [0036] FIG. 6 is an implementation of a multi-medium-voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. The multi-port interconnection module adopts a parallel two-level half-bridge converter and a cascaded H-bridge. The sub-module adopts the full-bridge topology, and the IDC adopts the dual-port interconnection mutual aid type solid-state transformer control strategy block diagram of the dual-active full-bridge topology; [0037] FIG. 7 is a simulation of the first working condition of a multi-medium-voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. Load power, low-voltage DC bus voltage waveform diagram; [0038] FIG. 8 is a simulation of each feeder power flow, each capacitor voltage, and each feeder current in the second working condition in the first embodiment of a multi-medium voltage AC port solid-state transformer and its control method provided by an embodiment of the present invention. Load power, low-voltage DC bus voltage waveform diagram; [0039] FIG. 9 is a simulation of the third working condition of a multi-medium voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. Each feeder power flow, each capacitor voltage, each feeder current, Load power, low-voltage DC bus voltage waveform diagram; [0040] FIG. 10 is a simulation of the fourth working condition in the fourth working condition of a multi-medium voltage AC port solid-state transformer and its control method provided by an embodiment of the present invention. Each feeder power flow, each capacitor voltage, each feeder current, Load power, low-voltage DC bus voltage waveform diagram; [0041] FIG. 11 is a simulation of each feeder power flow, each capacitor voltage, and each feeder current in the fifth working condition in the first embodiment of a multi-medium voltage AC port solid-state transformer and its control method provided by an embodiment of the present invention. Load power, low-voltage DC bus voltage waveform diagram; [0042] FIG. 12 is a multi-medium-voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. Type two-way DC-DC converter is connected to the low-voltage DC bus, the cascaded H-bridge sub-module adopts the full-bridge topology, and the IDC adopts the topology of the dual-port interconnection mutual aid solid-state transformer with the dual-active full-bridge topology and its realization of two ACs System diagram of system/feeder interconnection; [0043] FIG. 13 is a multi-medium-voltage AC port solid-state transformer and its control method according to an embodiment of the present invention. The block diagram of the control strategy of the dual-port interconnection mutual aid solid-state transformer with the dual-type bidirectional DC-DC converter connected to the low-voltage DC bus, the cascaded H-bridge sub-module adopts the full-bridge topology, and the IDC adopts the dual-active full-bridge topology; [0044] FIG. 14 is a sim
[ZH CN113193581A]: 一种储能系统并网装置 [EN CN113193581A]: Grid-connected device for energy storage system | [ZH CN113193581A]: 本发明公开了一种储能系统并网装置，包括用于连接电源与电网的并网变压器，并网装置还包括新增绕组、新增母线以及四象限级联型储能装置；新增绕组设置在并网变压器内，与并网变压器的网侧绕组耦合；新增母线连接新增绕组和四象限级联型储能装置；四象限级联型储能装置包括储能变流器，通过储能变流器监测电源，根据电源的状态通过新增绕组对电网进行无功补偿，且储能变流器包括串联的储能功率单元，通过串联的储能功率单元直接输出新增母线电压等级的相电压。该储能系统并网装置内无需设置升压变压器就能实现与电网连接，节省了设备成本和能量损耗，并且在实现储能的同时，还可以对电网进行无功补偿。 [EN CN113193581A]: The invention discloses a grid-connected device for an energy storage system, which includes a grid-connected transformer for connecting a power supply and a power grid. The grid-connected device also includes a newly-added winding, a newly-added bus, and a four-quadrant cascade energy storage device; and a newly-added winding Set in the grid-connected transformer, coupled with the grid-side winding of the grid-connected transformer; newly added busbars are connected with the newly added windings and the four-quadrant cascade energy storage device; the four-quadrant cascade energy storage device includes the energy storage converter, through The energy storage converter monitors the power supply, and performs reactive power compensation for the grid through the newly added windings according to the state of the power supply, and the energy storage converter includes a series-connected energy storage power unit, which directly outputs the newly added bus voltage through the series-connected energy storage power unit The phase voltage of the level. The grid-connected device of the energy storage system can be connected to the grid without setting up a step-up transformer, saving equipment cost and energy loss, and while realizing energy storage, it can also perform reactive power compensation for the grid. | CN113193581A | 2021-07-30 | CN202110535730A | 2021-05-17 | CN202110535730A, 2021-05-17 | CN113193581A: 2021-07-30 | 广州智光储能科技有限公司 |  | H02J3/32: I H02J3/18: I H02J3/38: I |  |  |  | [ZH CN113193581A]: 1 .一种储能系统并网装置，包括用于连接电源与电网的并网变压器，其特征在于，所述 并网装置还包括新增绕组、新增母线以及四象限级联型储能装置； 所述新增绕组设置在所述并网变压器内，与所述并网变压器的网侧绕组耦合； 所述新增母线连接所述新增绕组和所述四象限级联型储能装置； 所述四象限级联型储能装置包括储能变流器，通过所述储能变流器监测所述电源，根 据所述电源的状态通过所述新增绕组对电网进行无功补偿，且所述储能变流器包括串联的 储能功率单元，通过串联的储能功率单元直接输出所述新增母线电压等级的相电压。 2 .根据权利要求1所述的储能系统并网装置，其特征在于，所述新增母线的电压等级为 10kV或6kV。 3 .根据权利要求2所述的储能系统并网装置，其特征在于，所述储能变流器通过每一相 串联12-24个相同的所述储能功率单元，直接输出10kV或6kV的相电压。 4 .根据权利要求1所述的储能系统并网装置，其特征在于，每个所述储能功率单元均包 括功率变换电路;对应每个所述储能功率单元分别设置有独立的电池簇； 各所述功率变换电路的直流侧端口连接各自对应的电池簇，各所述功率变换电路的交 流侧端口彼此串联。 5 .根据权利要求4所述的储能系统并网装置，其特征在于，所述功率变换电路包括由 IGBT组成的H桥以及滤波电容，所述滤波电容与所述电池簇并联。 6 .根据权利要求4所述的储能系统并网装置，其特征在于，所述四象限级联型储能装置 包括三个相集装箱，每个相集装箱用于放置产生一相电压的全部电池簇和储能变流器； 所述电池簇和所述储能变流器分别布置在相互独立的两个室内，两个室之间通过防火 门隔离布置。 7 .根据权利要求6所述的储能系统并网装置，其特征在于，放置所述储能变流器的室底 部采用蜂窝孔结构，两侧设有若干个用于散热的排风装置。 8 .根据权利要求6所述的储能系统并网装置，其特征在于，放置所述电池簇的室顶部设 有若干个调温装置，放置所述电池簇的电池架之间设有风道。 9 .根据权利要求6所述的储能系统并网装置，其特征在于，各所述电池簇之间通过防火 板材阻隔。 10 .根据权利要求1所述的储能系统并网装置，其特征在于，所述四象限级联型储能装 置的各相链路上均设有电抗器。 [EN CN113193581A]: 1 A grid-connected device for an energy storage system, comprising a grid-connected transformer for connecting the power supply and the grid, characterized in that the grid-connected device also includes a newly-added winding, a newly-added bus, and a four-quadrant cascade-type energy storage device; The newly added winding is arranged in the grid-connected transformer and is coupled with the grid-side winding of the grid-connected transformer; the newly-added bus bar connects the newly-added winding and the four-quadrant cascade energy storage device; The four-quadrant cascaded energy storage device includes an energy storage converter, the power source is monitored by the energy storage converter, and the power grid is compensated for reactive power through the newly added winding according to the state of the power source, and The energy storage converter includes energy storage power units connected in series, and the phase voltage of the newly added bus voltage level is directly output through the energy storage power units connected in series. 2 The grid-connected device for an energy storage system according to claim 1, wherein the voltage level of the newly added bus is 10kV or 6kV. 3 The energy storage system grid-connected device according to claim 2, wherein the energy storage converter directly outputs 10kV or 6kV through 12-24 identical energy storage power units connected in series for each phase Phase voltage. 4 The grid-connected device for an energy storage system according to claim 1, wherein each of the energy storage power units includes a power conversion circuit; an independent battery cluster is provided for each energy storage power unit; The DC side ports of each of the power conversion circuits are connected to their corresponding battery clusters, and the AC side ports of each of the power conversion circuits are connected in series with each other. 5 The grid-connected device for an energy storage system according to claim 4, wherein the power conversion circuit comprises an H bridge composed of IGBTs and a filter capacitor, and the filter capacitor is connected in parallel with the battery cluster. 6 The grid-connected device for an energy storage system according to claim 4, wherein the four-quadrant cascaded energy storage device includes three phase containers, and each phase container is used to place all battery clusters that generate one phase voltage. And the energy storage converter; the battery cluster and the energy storage converter are respectively arranged in two independent rooms, and the two rooms are separated by a fire door. 7 The grid-connected device of the energy storage system according to claim 6, characterized in that the bottom of the chamber where the energy storage converter is placed adopts a honeycomb structure, and a number of exhaust devices for heat dissipation are provided on both sides. 8 The grid-connected device of the energy storage system according to claim 6, wherein a plurality of temperature regulating devices are provided on the top of the room where the battery cluster is placed, and an air duct is provided between the battery racks where the battery cluster is placed. 9 The grid-connected device for an energy storage system according to claim 6, wherein each of the battery clusters is blocked by a fireproof board. 10 The energy storage system grid-connected device according to claim 1, wherein each phase link of the four-quadrant cascaded energy storage device is provided with a reactor. | [ZH CN113193581A]: 一种储能系统并网装置 技术领域 [0001]本发明属于储能技术领域，特别涉及一种储能系统并网装置。 背景技术 [0002]随着电力电子技术的高速发展，国家政策的大力扶持，电化学储能系统已经广泛 应用于火力电厂的调峰调频、平滑风力和光伏发电的功率波动、用户侧后备电源调峰等诸 多领域。 [0003]目前在新能源项目中，较多采用常规储能系统，即多簇电池架并联接入一台集中 式低压PCS（Process Control System，过程控制系统），多台集中式低压PCS并联，然后经升 压变压器升压，通过环网柜接入集成线路，最终接入电网。采用传统的集中式低压储能系 统，每个2.5MW的储能单元都需配置1台升压变压器，且还需要投入无功补偿装置及其升压 设备。 [0004]现有新能源场景下的储能系统方案存在以下缺点：1.储能系统的转换效率会因为 每个储能单元都必备的变压器和相关配套设备产生的损耗而降低3 %左右；2.每个储能单 元的变压器和相关配套设备成本之和占成套储能系统的6%左右，导致储能电站投资成本 上升;3.新能源项目必须配置的无功补偿装置需通过变压器才能接入新能源母线的开关间 隔,而无功补偿装置在新能源场站中的利用率并不高，但一旦启动就会产生非常大的损耗。 发明内容 [0005] 针对上述问题，本发明公开了一种储能系统并网装置，以克服上述问题或者至少 部分地解决上述问题。 [0006]为了实现上述目的，本发明采用以下技术方案： [0007]本发明公开一种储能系统并网装置，包括用于连接电源与电网的并网变压器，所 述并网装置还包括新增绕组、新增母线以及四象限级联型储能装置； [0008]所述新增绕组设置在所述并网变压器内，与所述并网变压器的网侧绕组耦合； [0009] 所述新增母线连接所述新增绕组和所述四象限级联型储能装置； [0010] 所述四象限级联型储能装置包括储能变流器，通过所述储能变流器监测所述电 源,根据所述电源的状态通过所述新增绕组对电网进行无功补偿,且所述储能变流器包括 串联的储能功率单元，通过串联的储能功率单元直接输出所述新增母线电压等级的相电 压。 [0011] 进一步地，所述新增母线的电压等级为10kV或6kV。 [0012] 进一步地，所述储能变流器通过每一相串联12-24个相同的所述储能功率单元，直 接输出10kV或6kV的相电压。 [0013]进一步地，每个所述储能功率单元均包括功率变换电路;对应每个所述储能功率 单元分别设置有独立的电池簇； [0014]各所述功率变换电路的直流侧端口连接各自对应的电池簇，各所述功率变换电路 的交流侧端口彼此串联。 [0015]进一步地，所述功率变换电路包括由IGBT组成的H桥以及滤波电容，所述滤波电容 与所述电池簇并联。 [0016]进一步地，所述四象限级联型储能装置包括三个相集装箱，每个相集装箱用于放 置产生一相电压的全部电池簇和储能变流器； [0017] 所述电池簇和所述储能变流器分别布置在相互独立的两个室内，两个室之间通过 防火门隔离布置。 [0018]进一步地，放置所述储能变流器的室底部采用蜂窝孔结构，两侧设有若干个用于 散热的排风装置。 [0019]进一步地，放置所述电池簇的室顶部设有若干个调温装置，放置所述电池簇的电 池架之间设有风道。 [0020] 进一步地，各所述电池簇之间通过防火板材阻隔。 [0021] 进一步地，所述四象限级联型储能装置的各相链路上均设有电抗器。 [0022]本发明的优点及有益效果是： [0023]本发明的储能系统并网装置中，四象限级联型储能装置直接通过新增母线与并网 变压器内的新增绕组连接，能够向电网直接输出与新增母线电压等级相匹配的三相交流 电，相比于现有技术中储能系统通过设置额外的并网变压器与电网连接，该储能系统并网 装置只需在原并网变压器中设置新增绕组，就可实现并网，省去了设置额外并网变压器。并 且，由于四象限级联型储能装置可以直接输出与新增母线电压等级相同的相电压，因而在 四象限级联型储能装置与新增母线之间无需设置变压器以及变压器的相关设备，提高了整 体能量传递的效率。该并网装置中变压器使用数量少，节约了储能设备的成本，降低了整体 装置的能量损耗，减小了占地面积。同时，该并网装置可实现对电网进行无功补偿，省去了 无功补偿装置的配置。 附图说明 [0024] 通过阅读下文优选实施方式的详细描述，各种其他的优点和益处对于本领域普通 技术人员将变得清楚明了。附图仅用于示出优选实施方式的目的，而并不认为是对本发明 的限制。而且在整个附图中，用相同的参考符号表示相同的部件。在附图中： [0025]图1为本发明的一个实施例中储能系统并网装置的连接结构图； [0026]图2为本发明的一个实施例中四象限级联型储能装置的连接结构图； [0027]图3为本发明的一个实施例中储能功率单元的连接结构图； [0028]图4为本发明的一个实施例中相集装箱内部结构的俯视图； [0029]图5为本发明的一个实施例中中控集装箱内部结构的俯视图； [0030]图6为本发明的一个实施例中控制室的截面图； [0031]图7为本发明的一个实施例中电池室的截面图。 [0032]图中：1、电源；2、并网变压器；3、新增绕组；4、新增母线；5、四象限级联型储能装 置;6、储能功率单元;7、功率变换电路；8、电池簇;9、防火门；10、排风装置；11、调温装置; 12、风道；13、风机；14、电抗器。 具体实施方式 [0033]为使本发明的目的、技术方案和优点更加清楚，下面将结合本发明具体实施例及 相应的附图对本发明技术方案进行清楚、完整的描述。显然，所描述的实施例仅是本发明一 部分实施例，而不是全部的实施例。基于本发明中的实施例，本领域普通技术人员在没有做 出创造性劳动前提下所获得的所有其他实施例，都属于本发明保护的范围。 [0034]以下结合附图，详细说明本发明各实施例提供的技术方案。 [0035]本发明一个实施例公开一种储能系统并网装置，如图1所示，该并网装置包括用于 连接电源1与电网的并网变压器2,并网装置还包括新增绕组3、新增母线4以及四象限级联 型储能装置5；其中，电源1为新能源发电装置，比如通过太阳能、生物质能、风能、地热能、波 浪能、洋流能或潮汐能等实现发电的装置。 [0036] 新增绕组3设置在并网变压器2内，与并网变压器2的网侧绕组耦合;并网变压器2 内具体包括网侧绕组、阀侧绕组和新增绕组3,网侧绕组与电网连接，阀侧绕组与电源1连 接，新增绕组3通过新增母线4与四象限级联型储能装置5连接。例如，新增母线4为10kV母 线，并网变压器2为10-15MVA的变压器，并网变压器2的一次侧额定电压为110kV甚至更高， 二次侧额定电压分别为35kV\10kV。 [0037]四象限级联型储能装置5包括储能变流器，通过储能变流器监测电源1，四象限级 联型储能装置5根据电源1的状态通过新增绕组3对电网进行无功补偿；当监测到电源1的输 出功率高于额定功率，电压过高时，电网中的电能通过新增绕组3和新增母线4流向储能变 流器，实现多余电能的存储，进而降低电网的电压；当监测到电源1的输出功率低于额定功 率，电压过低时，储能变流器中的电能通过新增母线4和新增绕组3流向电网，实现电网电能 的补偿，进而提高电网的电压;且储能变流器包括串联的储能功率单元，通过串联的储能功 率单元6直接输出新增母线4电压等级的相电压，因此在储能功率单元6与新增母线4之间无 需设置升压变压器。具体地，储能变流器包括三条储能功率链路，分别为A相、B相和C相，每 条储能功率链路上串联设置若干个储能功率单元6。 [0038]综上，本实施例的储能系统并网装置中，四象限级联型储能装置5直接通过新增母 线4与并网变压器2内的新增绕组3连接，能够向电网直接输出满足要求的较高电压的三相 交流电，相比与现有技术中储能系统通过设置额外的并网变压器与电网连接，该储能系统 并网装置只需在电源1的并网变压器2中设置新增绕组3,就可实现并网，节省了额外的并网 变压器。并且，由于四象限级联型储能装置5可以直接输出与新增母线4电压等级相同的相 电压，因而在四象限级联型储能装置5与新增母线4之间无需设置变压器以及变压器的相关 设备，提高了整体能量传递的效率。该并网装置中只需设置一台站用变压器用于站内设备 操作控制、照明、直流充电装置和检修电源，变压器使用数量变少，节约了储能设备的成本， 降低了整体装置的能量损耗，减小了占地面积。同时，该并网装置采用的四象限解耦与控制 技术可以有效解决储能系统并网运行过程中有功功率和无功功率的独立控制与快速调节 问题，实现对电网进行无功补偿，省去了无功补偿装置的配置。 [0039] 优选地，新增母线4的电压等级为10kV或6kV。当然可以根据需要，新增母线4为其 他电压等级。 [0040]在一个实施例中，为了使储能变流器直接输出新增母线电压等级的相电压，储能 变流器通过每一相串联12-24个相同的储能功率单元6,进而直接输出10kV或6kV的相电压， 如图2所示，储能变流器每一相串联20个储能功率单元6。其中，储能变流器每相中储能功率 单元6的数量相同，且各储能功率单元6的规格相同，进而保证各相输出电压相同。 [0041] 在一个实施例中，如图3所示，每个储能功率单元6均包括:功率变换电路7；对应每 个储能功率单元6分别设置有独立的电池簇8。 [0042]各功率变换电路7的直流侧端口连接各自对应的电池簇8,各功率变换电路7的交 流侧端口彼此串联，每个功率变换电路7和一个电池簇8构成一个回路，减少甚至杜绝了电 池簇8与电池簇8之间的并联，由于单个电池簇8不会影响其他电池簇8的充放电情况，大大 提高了电池簇8的一致性，提高了储能系统的可利用容量。 [0043] 储能功率单元6还包括单元控制器;单元控制器与功率变换电路7电性连接，单元 控制器用于功率变换电路7的信号采样、信号转换、驱动控制以及监控设备间的通讯。 [0044] 优选地，如图3所示，功率变换电路包括由IGBT（Insulated Gate Bipolar Transistor，绝缘栅双极型晶体管）组成的H桥以及滤波电容C，滤波电容C与电池簇8并联。 功率变换电路的具体连接为:第一IGBT Q1的集电极与储能功率单元6的直流侧端口的正极 相连,发射极与第二IGBT Q2的集电极相连，第二IGBT Q2的发射极与储能功率单元6的直流 侧端口的负极相连，构成H桥的第一桥臂，第三IGBT Q3的发射极与第四IGBT Q4的集电极相 连，构成H桥的第二桥臂，第一桥臂、第二桥臂和滤波电容C并联连接。滤波电容C的作用为储 能和滤波。 [0045] 根据监测的电源状态，通过控制IGBT的工作状态,实现储能或功率补偿。四象限级 联型储能装置的输出电压由多个储能功率单元6输出电压移相叠加而成，该储能装置中无 需滤波即可输出接近正弦波的电压波形，且输出的电能质量满足相关国家标准要求。 [0046]在一个实施例中，四象限级联型储能装置包括三个相集装箱，每个相集装箱用于 放置产生一相电压的全部电池簇和储能变流器;三个相集装箱通过互差120。进行设置，三 个相集装箱组成即可输出三相对称的输出电压等级。 [0047]如图4所示，相集装箱分为控制室和电池室，电池簇和储能变流器分别布置在这两 个相互独立的室内，控制室和电池室之间通过防火门9隔离布置。 [0048] 控制室内可设置多个控制柜，用于放置储能变流器；电池室内可设置多个电池架, 用于放置电池簇。 [0049]四象限级联型储能装置还包括中控集装箱，如图5所示，中控集装箱内设有进线 柜、启动柜、主控制柜和EMS（Energy Management System，能量管理系统）柜等，用于放置主 控设备以及新增母线与储能变流器之间的接线、隔离开关等，实现对各相集装箱内设备的 控制。 [0050]在一个优选实施例中，放置储能变流器的室底部采用蜂窝孔结构,保证箱外的空 气能流入箱内，并且蜂窝孔结构中的小孔可有效防止蚊子等小动物的进入箱内，另外也会 对空气进行过滤处理，减少粉尘的进入箱内。如图4和图6所示,控制室的两侧设有若干个用 于散热的排风装置10，排风装置10可以把控制室内的热空气排出箱外，使箱外的冷空气从 蜂窝孔结构进入箱内，实现空气循环，进而降低箱内温度。 [0051] 在一个实施例中，如图7所示,放置电池簇的室顶部设有若干个调温装置11，调温 装置11可为空调，放置电池簇的电池架之间设有风道12,风机13把电池簇产生的热空气吸 入风道12内，调温装置11把风道12内的热空气吸进，然后制成冷风吹出，形成一个热量循环 系统，进而降低电池簇因为充放电而产生的热量，提高电池簇的使用寿命;各电池簇之间通 过防火板材阻隔，例如采用涂覆有防火材料的钢板阻隔，用于阻断火势的蔓延。 [0052] 优选地，如图2所示，四象限级联型储能装置的各相链路上均设有电抗器14,电抗 器14主要起到限流和滤波的作用。 [0053]以上所述仅为本发明的实施方式，并非用于限定本发明的保护范围。凡在本发明 的精神和原则之内所作的任何修改、等同替换、改进、扩展等，均包含在本发明的保护范围 内。 [EN CN113193581A]: Technical field of grid-connected device for energy storage system [0001] The present invention belongs to the field of energy storage technology, and particularly relates to a grid-connected device of an energy storage system. Background technique [0002] With the rapid development of power electronics technology and the strong support of national policies, electrochemical energy storage systems have been widely used in thermal power plants for peak shaving and frequency modulation, smoothing wind power and photovoltaic power fluctuations, and user-side backup power peak shaving, etc. Many areas. [0003] At present, in new energy projects, more conventional energy storage systems are used, that is, multiple clusters of battery racks are connected in parallel to a centralized low-voltage PCS (Process Control System), and multiple centralized low-voltage PCS are connected in parallel. Then it is boosted by a step-up transformer, connected to the integrated circuit through the ring network cabinet, and finally connected to the power grid. Using a traditional centralized low-voltage energy storage system, each 2.5MW energy storage unit needs to be equipped with a step-up transformer, and it is also necessary to invest in reactive power compensation devices and their step-up equipment. [0004] The existing energy storage system solution under the new energy scenario has the following shortcomings: 1. The conversion efficiency of the energy storage system will be reduced by about 3% due to the loss of the transformer and related supporting equipment necessary for each energy storage unit 2. The sum of the cost of the transformer and related supporting equipment for each energy storage unit accounts for about 6% of the complete energy storage system, leading to an increase in the investment cost of the energy storage power station; 3. The reactive power compensation device that must be configured for new energy projects needs to pass the transformer It can be connected to the switching interval of the new energy bus, and the utilization rate of the reactive power compensation device in the new energy field station is not high, but once it is started, it will produce very large losses. Summary of the invention [0005] In view of the above-mentioned problems, the present invention discloses a grid-connected device for an energy storage system to overcome the above-mentioned problems or at least partially solve the above-mentioned problems. [0006] In order to achieve the above objectives, the present invention adopts the following technical solutions: [0007] The present invention discloses a grid-connected device for an energy storage system, which includes a grid-connected transformer for connecting a power source and a power grid. The grid-connected device also includes a newly-added winding, a newly-added bus, and a four-quadrant cascaded energy storage device. ; [0008] The newly added winding is arranged in the grid-connected transformer and is coupled with the grid-side winding of the grid-connected transformer; [0009] The newly-added bus bar connects the newly-added winding and the four-quadrant cascade-type energy storage device; [0010] The four-quadrant cascaded energy storage device includes an energy storage converter, the power supply is monitored by the energy storage converter, and the power grid is reactive to the power grid through the newly added winding according to the state of the power supply Compensation, and the energy storage converter includes a series-connected energy storage power unit, and the series-connected energy storage power unit directly outputs the phase voltage of the newly added busbar voltage level. [0011] Further, the voltage level of the newly added busbar is 10kV or 6kV. [0012] Further, the energy storage converter directly outputs a phase voltage of 10kV or 6kV through 12-24 identical energy storage power units connected in series for each phase. [0013] Further, each of the energy storage power units includes a power conversion circuit; corresponding to each of the energy storage power units are provided with independent battery clusters; [0014] The DC side port of each power conversion circuit is connected to a respective battery cluster, and each power conversion circuit The AC side ports of each other are connected in series. [0015] Further, the power conversion circuit includes an H bridge composed of IGBTs and a filter capacitor, and the filter capacitor is connected in parallel with the battery cluster. [0016] Further, the four-quadrant cascaded energy storage device includes three phase containers, and each phase container is used to place all battery clusters and energy storage converters that generate one-phase voltage; [0017] The battery cluster and the energy storage converter are respectively arranged in two independent rooms, and the two rooms are separated by a fire door. [0018] Further, the bottom of the chamber where the energy storage converter is placed adopts a honeycomb structure, and a number of exhaust devices for heat dissipation are provided on both sides. [0019] Further, the top of the room where the battery cluster is placed is provided with a number of temperature regulating devices, and an air duct is provided between the battery racks where the battery cluster is placed. [0020] Further, each of the battery clusters is blocked by a fireproof board. [0021] Further, a reactor is provided on each phase link of the four-quadrant cascade energy storage device. [0022] The advantages and beneficial effects of the present invention are: [0023] In the grid-connected device of the energy storage system of the present invention, the four-quadrant cascaded energy storage device is directly connected to the newly-added winding in the grid-connected transformer through the newly-added busbar, and can directly output to the grid the voltage level of the newly-added busbar. The matched three-phase AC power is connected to the grid by installing additional grid-connected transformers compared to the existing energy storage system. The grid-connected device of the energy storage system only needs to install new windings in the original grid-connected transformer to realize the integration. Grid, eliminating the need to install additional grid-connected transformers. In addition, because the four-quadrant cascaded energy storage device can directly output the same phase voltage as the newly added busbar voltage level, there is no need to install a transformer and transformer-related equipment between the four-quadrant cascade energy storage device and the new bus. Improve the efficiency of overall energy transfer. The number of transformers in the grid-connected device is small, the cost of energy storage equipment is saved, the energy loss of the overall device is reduced, and the floor space is reduced. At the same time, the grid-connected device can realize reactive power compensation to the power grid, eliminating the need for the configuration of reactive power compensation devices. Description of the drawings [0024] By reading the detailed description of the preferred embodiments below, various other advantages and benefits will become clear to those of ordinary skill in the art. The drawings are only used for the purpose of illustrating the preferred embodiments, and are not considered as a limitation to the present invention. Also, throughout the drawings, the same reference symbols are used to denote the same components. In the attached picture: [0025] FIG. 1 is a connection structure diagram of an energy storage system grid-connected device in an embodiment of the present invention; [0026] FIG. 2 is a connection structure diagram of a four-quadrant cascade type energy storage device in an embodiment of the present invention; [0027] FIG. 3 is a connection structure diagram of an energy storage power unit in an embodiment of the present invention; [0028] FIG. 4 is a top view of the internal structure of the corresponding container in an embodiment of the present invention; [0029] FIG. 5 is a top view of the internal structure of the central control container in an embodiment of the present invention; [0030] FIG. 6 is a cross-sectional view of the control room in an embodiment of the present invention; [0031] FIG. 7 is a cross-sectional view of a battery compartment in an embodiment of the present invention. [0032] In the figure: 1. Power supply; 2. Grid-connected transformer; 3. New winding; 4. New bus; 5. Four-quadrant cascade energy storage device; 6. Energy storage power unit; 7. Power conversion Circuit; 8. Battery cluster; 9. Fire door; 10. Exhaust device; 11. Temperature adjustment device; 12. Air duct; 13. Fan; 14. Reactor. Detailed ways [0033] In order to make the objectives, technical solutions and advantages of the present invention clearer, the technical solutions of the present invention will be clearly and completely described below in conjunction with specific embodiments of the present invention and the corresponding drawings. Obviously, the described embodiments are only a part of the embodiments of the present invention, rather than all the embodiments. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0034] The following describes in detail the technical solutions provided by the embodiments of the present invention with reference to the accompanying drawings. [0035] An embodiment of the present invention discloses a grid-connected device for an energy storage system, as shown in FIG. 3. Newly added bus 4 and four-quadrant cascade energy storage device 5; among them, power supply 1 is a new energy power generation device, such as solar energy, biomass energy, wind energy, geothermal energy, wave energy, ocean current energy or tidal energy. Device for generating electricity. [0036] The newly added winding 3 is arranged in the grid-connected transformer 2, and is coupled with the grid-side winding of the grid-connected transformer 2. The grid-connected transformer 2 specifically includes the grid-side winding, the valve-side winding and the newly-added winding 3, and the grid-side winding is connected to the grid-side winding. The power grid is connected, the valve-side winding is connected to the power source 1, and the new winding 3 is connected to the four-quadrant cascade energy storage device 5 through the new bus 4. For example, the newly added bus 4 is a 10kV bus, the grid-connected transformer 2 is a 10-15MVA transformer, the primary-side rated voltage of the grid-connected transformer 2 is 110kV or higher, and the secondary-side rated voltage is 35kV\10kV, respectively. [0037] The four-quadrant cascaded energy storage device 5 includes an energy storage converter, and the power source 1 is monitored through the energy storage converter. Perform reactive power compensation; when it is monitored that the output power of the power supply 1 is higher than the rated power and the voltage is too high, the electric energy in the grid flows to the energy storage converter through the new winding 3 and the new bus 4 to realize the storage of excess electric energy. Then the voltage of the grid is reduced; when the output power of the power supply 1 is lower than the rated power and the voltage is too low, the electric energy in the energy storage converter flows to the grid through the newly added bus 4 and the newly added winding 3 to realize the compensation of the grid power , And then increase the voltage of the grid; and the energy storage converter includes a series of energy storage power units, through the series of energy storage power unit 6 directly output the phase voltage of the newly added bus 4 voltage level, so the energy storage power unit 6 and the new There is no need to install a step-up transformer between the increased bus 4. Specifically, the energy storage converter includes three energy storage power links, namely A-phase, B-phase and C-phase, and a number of energy storage power units 6 are arranged in series on each energy storage power link. [0038] In summary, in the grid-connected device of the energy storage system of this embodiment, the four-quadrant cascaded energy storage device 5 is directly connected to the newly-added winding 3 in the grid-connected transformer 2 through the newly-added bus bar 4, and can be directly connected to the grid The output meets the requirements of higher voltage three-phase alternating current. Compared with the energy storage system in the prior art, an additional grid-connected transformer is installed to connect to the grid. The grid-connected device of the energy storage system only needs to be connected to the grid-connected transformer 2 of the power source 1. Set up a new winding 3 in the middle to achieve grid-connected, saving additional grid-connected transformers. Moreover, since the four-quadrant cascaded energy storage device 5 can directly output the same phase voltage as the voltage level of the newly added bus 4, there is no need to install a transformer and a transformer between the four-quadrant cascaded energy storage device 5 and the newly added bus 4 Related equipment to improve the efficiency of overall energy transfer. The grid-connected device only needs to set up a station transformer for the operation control, lighting, DC charging device and maintenance power supply of the station equipment. The number of transformers used is reduced, the cost of energy storage equipment is saved, and the energy loss of the overall device is reduced. , Reduce the footprint. At the same time, the four-quadrant decoupling and control technology adopted by the grid-connected device can effectively solve the independent control and rapid adjustment of active power and reactive power during the grid-connected operation of the energy storage system, and realize reactive power compensation for the grid, saving The configuration of reactive power compensation device. [0039] Preferably, the voltage level of the newly added bus 4 is 10kV or 6kV. Of course, you can add bus 4 to other voltage levels as needed. [0040] In one embodiment, in order to make the energy storage converter directly output the phase voltage of the newly added bus voltage level, the energy storage converter connects 12-24 identical energy storage power units 6 in series for each phase, and then Directly output 10kV or 6kV phase voltage, As shown in Figure 2, 20 energy storage power units 6 are connected in series for each phase of the energy storage converter. Among them, the number of energy storage power units 6 in each phase of the energy storage converter is the same, and the specifications of each energy storage power unit 6 are the same, thereby ensuring that the output voltage of each phase is the same. [0041] In one embodiment, as shown in FIG. 3, each energy storage power unit 6 includes: a power conversion circuit 7; and an independent battery cluster 8 is provided corresponding to each energy storage power unit 6. [0042] The DC-side ports of each power conversion circuit 7 are connected to their corresponding battery clusters 8, and the AC-side ports of each power conversion circuit 7 are connected in series with each other. Each power conversion circuit 7 and a battery cluster 8 form a loop to reduce or even eliminate The parallel connection between the battery cluster 8 and the battery cluster 8, since a single battery cluster 8 will not affect the charging and discharging conditions of other battery clusters 8, the consistency of the battery cluster 8 is greatly improved, and the usable capacity of the energy storage system is improved. [0043] The energy storage power unit 6 also includes a unit controller; the unit controller is electrically connected to the power conversion circuit 7. The unit controller is used for signal sampling, signal conversion, drive control, and communication between monitoring devices of the power conversion circuit 7. [0044] Preferably, as shown in FIG. 3, the power conversion circuit includes an H bridge composed of an IGBT (Insulated Gate Bipolar Transistor, insulated gate bipolar transistor) and a filter capacitor C, and the filter capacitor C is connected in parallel with the battery cluster 8. The specific connection of the power conversion circuit is as follows: the collector of the first IGBT Q1 is connected to the positive electrode of the DC side port of the energy storage power unit 6, the emitter is connected to the collector of the second IGBT Q2, and the emitter of the second IGBT Q2 is connected to the storage. The negative pole of the DC side port of the power unit 6 is connected to form the first leg of the H bridge, and the emitter of the third IGBT Q3 is connected to the collector of the fourth IGBT Q4 to form the second leg of the H bridge, the first bridge The arm, the second bridge arm and the filter capacitor C are connected in parallel. The function of the filter capacitor C is to store energy and filter. [0045] According to the monitored power state, energy storage or power compensation is realized by controlling the working state of the IGBT. The output voltage of the four-quadrant cascaded energy storage device is formed by the phase-shifted superposition of the output voltages of multiple energy storage power units 6. The energy storage device can output a voltage waveform close to a sine wave without filtering, and the output power quality meets Relevant national standard requirements. [0046] In one embodiment, the four-quadrant cascade type energy storage device includes three phase containers, and each phase container is used to place all battery clusters and energy storage converters that generate one phase voltage; the three phase containers pass The difference is 120. After setting, the three-phase container can output three-phase symmetrical output voltage level. [0047] As shown in Figure 4, the phase container is divided into a control room and a battery room. The battery clusters and the energy storage converter are arranged in these two independent rooms. The control room and the battery room are separated by a fire door 9. Layout. [0048] Multiple control cabinets can be provided in the control room for placing energy storage converters; multiple battery racks can be provided in the battery room for placing battery clusters. [0049] The four-quadrant cascading energy storage device also includes a central control container, as shown in FIG. Cabinets, etc., are used to place the main control equipment and the wiring and isolation switches between the newly added bus and the energy storage converter to realize the control of the equipment in the container of each phase. [0050] In a preferred embodiment, the bottom of the chamber where the energy storage converter is placed adopts a honeycomb structure to ensure that the air outside the box can flow into the box, and the small holes in the honeycomb structure can effectively prevent mosquitoes and other small animals from being damaged. When entering the box, the air will also be filtered to reduce the dust entering the box. As shown in Figures 4 and 6, there are several exhaust devices 10 for heat dissipation on both sides of the control room. The exhaust devices 10 can exhaust the hot air in the control room out of the box, so that the cold air outside the box can be removed from the honeycomb. The hole structure enters the box to realize air circulation, thereby reducing the temperature in the box. [0051] In one embodiment, as shown in FIG. 7, a number of temperature adjustment devices 11 are provided on the top of the room where the battery clusters are placed. 12. The fan 13 sucks the hot air generated by the battery cluster into the air duct 12, and the temperature regulating device 11 sucks the hot air in the air duct 12, and then blows it out as cold air, forming a heat cycle The system further reduces the heat generated by the battery clusters due to charging and discharging, and improves the service life of the battery clusters; each battery cluster is blocked by a fireproof plate, such as a steel plate coated with a fireproof material to block the spread of fire. [0052] Preferably, as shown in FIG. 2, a reactor 14 is provided on each phase link of the four-quadrant cascade energy storage device, and the reactor 14 mainly plays a role of current limiting and filtering. [0053] The above are only the embodiments of the present invention, and are not used to limit the protection scope of the present invention. Any modification, equivalent replacement, improvement, expansion, etc. made within the spirit and principle of the present invention are all included in the protection scope of the present invention.
[ZH CN112290818B]: 一种串级式多电平变流器及其实现方法 [EN CN112290818B]: A cascade type multilevel converter and its realization method | [ZH CN112290818B]: 本发明提供了一种串级式多电平变流器及其实现方法，该串级式多电平变流器装置包括双电容基础模块、双电容子模块和H桥单元；该变流器通过模块中双电容的阶梯充电与串联叠加以及模块间的串并联转换，实现变流器高电平和高增益的输出效果；H桥单元完成变流器的双极性电平转换；所述变流器通过双电容子模块单元的扩展可以进一步增加输出电平数以及提高输出电压增益。本发明所述变流器的优势在于电容具有电压自平衡的能力，避免了额外的电容电压控制回路；模块单元中采用双电容协同工作方式，有效减少了变流器装置的功率器件使用数量，降低了变流器的制造成本。 [EN CN112290818B]: The invention provides a cascade multilevel converter and an implementation method thereof. The cascade multilevel converter device comprises a double-capacitor basic module, a double-capacitor sub-module and an H-bridge unit. According to the converter, high-level and high-gain output effects of the converter are realized through stepped charging and series superposition of double capacitors in the modules and series-parallel conversion between the modules; the H-bridge unit completes bipolar level conversion of the converter; the converter can further increase the number of output levels andimprove the output voltage gain through the expansion of the double-capacitor sub-module unit. The converter disclosed by the invention has the advantages that the capacitor has a voltage self-balancing capability, so that an extra capacitor voltage control loop is avoided; a double-capacitor cooperative work mode is adopted in the module unit, the number of used power devices of the converter device is effectively reduced, and the manufacturing cost of the converter is reduced. | CN112290818B | 2021-01-29 2021-08-31 | CN202011108549A | 2020-10-16 2020-10-16 | CN202011108549A, 2020-10-16 CN202011108549A, 2020-10-16 | CN112290818B: 2021-08-31 | UNIV ZHENGZHOU 郑州大学 | WANG YAOQIANG WANG CHANGLONG WANG YI WANG MINGDONG WANG KEWEN LIANG JUN | H02M7/483: I | H02M7/483: I | CN108599604A CN109194170A CN110071654A CN110149065A CN111740625A |  | [ZH CN112290818B]: 1 .一种串级式多电平变流器，其特征在于:包括双电容基础模块、多级双电容子模块和 H桥单元； 所述双电容基础模块包括开关管Sr开关管S2、开关管S3、开关管S4、开关管S5、电解电容 J、电解电容C2、二极管D0和直流电压源Vdc； 所述开关管S^TC端与直流电压源Vdc的正极和二极管％的正极相连接； 所述开关管工的£端与所述开关管S4的E端和所述开关管S5的C端相连接； 所述开关管S2TC端与二极管D0的负极和电解电容^的阳极相连接； 所述开关管S3的C端与所述开关管务的£端和电解电容^的阳极相连接； 所述开关管S4的C端与所述开关管S3的E端和电解电容^的阴极相连接； 所述开关管S5的C端与电解电容C2的阴极相连接，所述开关管S5的E端与直流电压源Vdc 的负极相连接； 每级双电容子模块包括开关管S^、开关管Si2、开关管Si3、开关管Si4、开关管Si5、开关管 Si6、开关管Si7、电解电容C^与电解电容Ci2和二极管Di ； 所述开关管5莉仅端与前级双电容子模块开关管S（一）6的E端和二极管Dj的正极相连 接,所述开关管S^TE端与所述开关管Si4的E端和所述开关管Si5的C端相连接； 所述开关管S/TC端与所述开关管Si6的C端相连接；所述开关管Si3的C端与所述开关管 S或TE端和电解电容Ci2的阳极相连接;所述开关管Si4的C端与所述开关管Si7的C端相连接; 所述开关管Si5的C端与所述开关管Si4的E端和电解电容Ci2的阴极相连接，所述开关管Si5的E 端与前级双电容子模块开关管S（一）5的E端相连接;所述开关管Si6的E端与二极管Dj的负极 和电解电容J的阳极相连接;所述开关管Si7的E端与所述开关管Si3的E端和电解电容J的 阴极相连接； 第一级双电容子模块的开关管Si5的E端与直流电压源Vdc的负极相连接，第一级双电容 子模块的二极管〃的正极与双电容基础模块的开关管SjTC端相连接； 所述H桥单元包括开关管S01、开关管S02、开关管S03和开关管S04； 所述开关管S01的C端与所述开关管S03的C端和二极管Dj相连接;所述开关管S02的C端与 所述开关管S01的E端相连接；所述开关管S03的E端与所述开关管S04的C端相连接；所述开关 管S04的E端与所述开关管S02的E端和所述开关管Si5的E端相连接； 所述开关管S01的E端和所述开关管S03的E端作为该串级式多电平变流器交流电压的输 出端。 2 . 一种串级式多电平变流器的实现方法，应用于权利要求1所述的串级式多电平变流 器，其特征在于： 设置开关管S2与开关管S4、开关管Si2与开关管Si4、开关管Si6与开关管Si7工作状态一致； 设置开关管5］与开关管s5、开关管Sj］与开关管Si5、开关管S2与开关管S3、开关管Si2与开 关管Si3、开关管S01与开关管S02、开关管S03与开关管S04工作在互补状态； 控制开关管S2、开关管s3和开关管s4的导通和关断状态，以实现电解电容“与分的串并 联转换； 控制开关管Si2、开关管Si3和开关管Si4的导通和关断状态，以实现电解电容Cn与Ci2的串 并联转换； 控制开关管Sj］的导通和关断状态，以实现双电容基础模块与双电容子模块的串并联转 换； 控制双电解电容的串并联转换以及双电容基础模块与双电容子模块的串并联转换，以 实现双电容子模块的电解电容Ci1和Ci2的充电电压均为3iVdc； 通过增加双电容子模块的扩展极数，以实现具有i个双电容子模块的串级式多电平变 流器输出3i+1X2+1个电平，获得3i+1倍的电压增益。 3 .根据权利要求2所述的串级式多电平变流器的实现方法，其特征在于:采用载波层叠 脉宽调制技术，使用正弦波作为调制波，以40倍于调制波频率的三角波作为载波;调制波与 3i+1X 2个载波进行比较，在调制波大于载波的部分输出高电平，在调制波小于载波的部分 输出低电平，由此得到3i+1X 2组矩形脉冲信号,将得到的矩形脉冲信号进行合适的逻辑组 合，得到各个开关管的门极驱动信号； 变流器的调制比M由调制波的幅值Aref和载波的幅值Ac共同决定，即： M=Aref/(3i+1Ac) 调制比M的取值范围为0&lt;MW1： 当[(j-1)/3i+1)]&lt;MW (j/3i+1)时，je[1、2、-・、3i+1],变流器输出(2Xj+1)电平。 4 .一种串级式多电平变流系统，包括控制器和逆变器，其特征在于:所述逆变器为权利 要求1所述的串级式多电平变流器。 5 .根据权利要求4所述的串级式多电平变流系统，其特征在于:所述控制器控制所述串 级式多电平变流系统中的开关管动作时，执行权利要求2-3任一项所述的实现方法的步骤。 [EN CN112290818B]: 1 A cascade multi-level converter, characterized in that it includes a dual-capacitor basic module, a multi-level dual-capacitor sub-module, and an H-bridge unit; the dual-capacitor basic module includes a switch tube Sr switch tube S2, Switch tube S3, Switch tube S4, Switch tube S5, Electrolytic capacitor J, electrolytic capacitor C2, Diode D0And DC voltage source Vdc; The switch tube S^TC terminal and the DC voltage source VdcThe anode of the switch tube is connected to the anode of the diode %; the terminal of the switch tube is connected to the switch tube S4The E end and the switch tube S5The C terminal is connected; the switch tube S2TC terminal and diode D0The negative electrode of the electrolytic capacitor ^ is connected to the anode; the switch tube S3The terminal C of the switch tube is connected to the terminal of the switch tube and the anode of the electrolytic capacitor ^; the switch tube S4The C terminal and the switch tube S3The E terminal of the electrolytic capacitor is connected to the cathode of the electrolytic capacitor ^; the switch tube S5C terminal and electrolytic capacitor C2The cathode is connected, the switch tube S5E terminal and DC voltage source Vdc The negative pole of each stage of the dual-capacitor sub-module includes a switch tube S^, a switch tube Si2, Switch tube Si3, Switch tube Si4, Switch tube Si5, Switch tube Si6, Switch tube Si7, Electrolytic capacitor C^ and electrolytic capacitor Ci2And the diode Di; the switch tube 5 Li is only connected to the front-stage dual-capacitor sub-module switch tube S (one）6The E terminal and the anode of the diode Dj are connected, and the switch tube S^TE terminal is connected to the switch tube Si4The E end and the switch tube Si5The terminal C of the switch tube is connected; the terminal S/TC of the switch tube is connected to the switch tube Si6The C terminal is connected; the switch tube Si3The C terminal and the switch tube S or TE terminal and the electrolytic capacitor Ci2The anode is connected; the switch tube Si4The C terminal and the switch tube Si7The C terminal is connected; the switch tube Si5The C terminal and the switch tube Si4E terminal and electrolytic capacitor Ci2The cathode is connected, the switch tube Si5The E terminal of the previous stage dual-capacitor sub-module switch tube S (one）5The E end is connected; the switch tube Si6The E terminal is connected to the cathode of the diode Dj and the anode of the electrolytic capacitor J; the switch tube Si7The E end of the switch tube Si3The E terminal of is connected to the cathode of the electrolytic capacitor J; the switch tube S of the first-stage dual-capacitor sub-modulei5E terminal and DC voltage source VdcThe cathode of the first-level dual-capacitor sub-module is connected to the anode of the diode of the dual-capacitor base module, and the switch tube SjTC of the dual-capacitor base module is connected; the H-bridge unit includes a switch tube S01, Switch tube S02, Switch tube S03And switch tube S04; The switch tube S01The C terminal and the switch tube S03The C terminal and the diode Dj are connected; the switch tube S02The C terminal and the switch tube S01The E terminal is connected; the switch tube S03The E end of the switch tube S04The C terminal is connected; the switch tube S04The E end of the switch tube S02The E end and the switch tube Si5The E end is connected; the switch tube S01The E end and the switch tube S03The E terminal is used as the output terminal of the AC voltage of the cascade multilevel converter. 2 A method for implementing a cascade multilevel converter, applied to the cascade multilevel converter of claim 1, characterized in that: a switch tube S is provided2With switch tube S4, Switch tube Si2With switch tube Si4, Switch tube Si6With switch tube Si7Working status is the same; set switch tube 5] and switch tube s5, Switch tube Sj] and switch tube Si5, Switch tube S2With switch tube S3, Switch tube Si2With switch tube Si3, Switch tube S01With switch tube S02, Switch tube S03With switch tube S04Working in complementary state; control switch tube S2, Switch tube s3And switch tube s4The on and off state of the electrolytic capacitor to realize the series-parallel conversion of the electrolytic capacitor and the sub-connection; control the switch tube Si2, Switch tube Si3And switch tube Si4The on and off state of the electrolytic capacitors Cn and Ci2The series-parallel conversion of the switch tube Sj] is controlled to realize the series-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module Conversion; Control the series-parallel conversion of the dual electrolytic capacitors and the series-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module to realize the electrolytic capacitors Ci1 and C of the dual-capacitor sub-modulei2The charging voltage is 3iVdc; By increasing the number of extended poles of the dual-capacitor sub-modules, the output of a cascade multi-level converter with i dual-capacitor sub-modules is realized 3i+1X2+1 levels, get 3i+1Times the voltage gain. 3 The implementation method of the cascade multilevel converter according to claim 2, characterized in that: carrier-stacked pulse-width modulation technology is adopted, sine wave is used as the modulating wave, and a triangular wave 40 times the frequency of the modulating wave is used as the modulating wave. Carrier; modulated wave and 3i+1X 2 carriers are compared, the part where the modulation wave is larger than the carrier will output a high level, and the part where the modulation wave is smaller than the carrier will output a low level, thus 3i+1X 2 groups of rectangular pulse signals, the obtained rectangular pulse signals are appropriately logically combined to obtain the gate drive signal of each switch tube; the modulation ratio M of the converter is determined by the amplitude A of the modulation waverefAnd carrier amplitude AcJoint decision, namely: M=Aref/(3i+1Ac) The value range of modulation ratio M is 0&lt;MW1: When [(j-1)/3i+1)]&lt;MW (j/3i+1), je[1,2,-,3i+1], the converter output (2Xj+1) level. 4 A cascade multilevel converter system, comprising a controller and an inverter, characterized in that: the inverter is the cascade multilevel converter according to claim 1. 5 The cascade multilevel converter system according to claim 4, characterized in that: when the controller controls the action of the switch tube in the cascade multilevel converter system, claim 2 is executed. 3. Steps of any one of the implementation methods. | [ZH CN112290818B]: 一种串级式多电平变流器及其实现方法 技术领域 [0001]本发明涉及变流器技术领域，具体涉及一种串级式多电平变流器及其实现方法。 背景技术 [0002]随着分布式发电机的大规模部署，其中，逆变环节作为分布式能源与电网或交流 负载的转换接口备受关注。相较于传统的两电平变流器，多电平变流器因其具有能够输出 近似正弦阶梯波形、减小器件电压应力和降低电压谐波畸变率等优点，在分布式发电领域 也得到了广泛的关注。 [0003]传统多电平变流器分为二极管钳位型、飞跨电容型和H桥级联型三类典型结构。其 中，二极管钳位型和飞跨电容型多电平变流器在输出较多电平时通常结构较为复杂，器件 数量较多，并且需要额外的电容电压平衡控制;H桥级联型多电平变流器则需要大量的独立 直流电源，在一定程度上限制了其应用范围。此外，上述传统多电平变流器多为降压型变流 器，在需要升压的应用场合如分布式发电领域中，光伏发电装置的光伏阵列通常为直流低 压源，在并网过程中需增加升压环节，这将会增加系统的复杂性和制造成本。 [0004]为了适应新能源领域的发展需求，克服传统多电平变流器的不足，具有独立升压、 电容电压自平衡等优点的开关电容技术被应用到多电平变流器中。 发明内容 [0005] 本发明针对上述问题，有必要提供一种串级式多电平变流器及其实现方法。 [0006]本发明第一方面提出一种串级式多电平变流器，包括双电容基础模块、多级双电 容子模块和H桥单元； [0007] 所述双电容基础模块包括开关管Sr开关管S2、开关管S3、开关管S4、开关管S5、电解 电容q、电解电容c2、二极管d0和直流电压源Vdc； [0008]所述开关管S^qc端与直流电压源Vdc的正极和二极管d0的正极相连接； [0009]所述开关管工的£端与所述开关管S4的E端和所述开关管S5的C端相连接； [0010]所述开关管SjTC端与二极管D0的负极和电解电容”的阳极相连接； [0011]所述开关管S3的C端与所述开关管\的£端和电解电容^的阳极相连接； [0012]所述开关管S4的C端与所述开关管S3的E端和电解电容”的阴极相连接； [0013]所述开关管S5的C端与电解电容C2的阴极相连接，所述开关管S5的E端与直流电压 源Vdc的负极相连接； [0014]每级双电容子模块包括开关管S^、开关管Si2、开关管Si3、开关管Si4、开关管Si5、开 关管Si6、开关管Si7、电解电容Cj]与电解电容Ci2和二极管Di ； [0015]所述开关管S^TC端与前级双电容子模块开关管S(i.1)6的E端和二极管Di的正极相 连接,所述开关管S^TE端与所述开关管Si4的E端和所述开关管Si5的C端相连接； [0016]所述开关管S/qc端与所述开关管Si6的c端相连接;所述开关管Si3的c端与所述开 关管S/TE端和电解电容Ci2的阳极相连接;所述开关管Si4的C端与所述开关管Si7的C端相连 接;所述开关管Si5的C端与所述开关管Si4的E端和电解电容Ci2的阴极相连接，所述开关管Si5 的E端与前级双电容子模块开关管S(i.1)5的E端相连接;所述开关管Si6的E端与二极管Dj的负 极和电解电容J的阳极相连接;所述开关管Si7的E端与所述开关管Si3的E端和电解电容J 的阴极相连接； [0017]第一级双电容子模块的开关管Si5的E端与直流电压源Vdc的负极相连接，第一级双 电容子模块的二极管D1的正极与双电容基础模块的开关管SjTC端相连接； [0018]所述H桥单元包括开关管S01、开关管S02、开关管S03和开关管S04； [0019]所述开关管S01的C端与所述开关管S03的C端和二极管Dj相连接;所述开关管S02的C 端与所述开关管S01的E端相连接；所述开关管S03的E端与所述开关管S04的C端相连接；所述 开关管S04的E端与所述开关管S02的E端和所述开关管Si5的E端相连接； [0020]所述开关管S01的E端和所述开关管S03的E端作为该串级式多电平变流器交流电压 的输出端。 [0021] 本发明第二方面提供一种串级式多电平变流器的实现方法，应用于所述的串级式 多电平变流器，设置开关管52与开关管S4、开关管Si2与开关管Si4、开关管Si6与开关管Si7工 作状态一致； [0022]设置开关管工与开关管S5、开关管5口与开关管Si5、开关管务与开关管S3、开关管Si2 与开关管Si3、开关管S01与开关管S02、开关管S03与开关管S04工作在互补状态； [0023]控制开关管S2、开关管S3和开关管S4的导通和关断状态，以实现电解电容^与^的 串并联转换； [0024]控制开关管Si2、开关管Si3和开关管Si4的导通和关断状态，以实现电解电容^1与 Ci2的串并联转换； [0025]控制开关管Sn的导通和关断状态，以实现双电容基础模块与双电容子模块的串并 联转换； [0026]控制双电解电容的串并联转换以及双电容基础模块与双电容子模块的串并联转 换，以实现双电容子模块的电解电容J]和Ci2的充电电压均为3iVdc； [0027]通过增加双电容子模块的扩展极数，以实现具有i个双电容子模块的串级式多电 平变流器输出3i+1X2+1个电平，获得3i+1倍的电压增益。 [0028]基于上述，采用载波层叠脉宽调制技术，使用正弦波作为调制波，以40倍于调制波 频率的三角波作为载波；调制波与3i+1X2个载波进行比较，在调制波大于载波的部分输出 高电平，在调制波小于载波的部分输出低电平，由此得到3i+1X2组矩形脉冲信号，将得到的 矩形脉冲信号进行合适的逻辑组合，得到各个开关管的门极驱动信号； [0029] 变流器的调制比M由调制波的幅值Aref和载波的幅值Ac共同决定，即： [0030] M = Aref/(3i + 1Ac) [0031] 调制比M的取值范围为0&lt;MW1： [0032]当[(j -1) /3i+1) ]&lt;MW (j/3i+1)时，je[1、2、…、3i+1],变流器输出(2 X j+1)电平。 [0033]本发明第三方面提供一种串级式多电平变流系统，包括控制器和逆变器，所述逆 变器为所述的串级式多电平变流器。 [0034]基于上述，所述控制器控制所述串级式多电平变流系统中的开关管动作时，执行 所述的实现方法的步骤。 [0035]本发明具有突出的实质性特点和显著的进步，具体的说： [0036] (1)本发明的串级式多电平变流器采用双电容组合，通过双电容基础模块与双电 容子模块中的双电容阶梯充电与串联叠加以及模块的串并联转换，在输出较多电平数量时 能减少器件的使用，降低系统成本； [0037] (2)本发明的串级式多电平变流器具有电容电压自平衡的优点，避免了额外的电 容电压控制回路； [0038] (3)本发明的串级式多电平变流器可以通过双电容子模块进行扩展，进一步增加 输出电平数并同时提高输出电压增益 [0039] ⑷本发明的串级式多电平变流器采用单电源输入，拓宽了其应用范围。 [0040]本发明的附加方面和优点将在下面的描述部分中变得明显，或通过本发明的实践 了解到。 附图说明 [0041]本发明的上述和/或附加的方面和优点从结合下面附图对实施例的描述中将变得 明显和容易理解，其中： [0042]图1为本发明实施例中所述串级式多电平变流器结构图。 [0043]图2为本发明实施例中所述19电平变流器工作模态1的工作原理图。 [0044]图3为本发明实施例中所述19电平变流器工作模态2的工作原理图。 [0045]图4为本发明实施例中所述19电平变流器工作模态3的工作原理图。 [0046]图5为本发明实施例中所述19电平变流器工作模态4的工作原理图。 [0047]图6为本发明实施例中所述19电平变流器工作模态5的工作原理图。 [0048]图7为本发明实施例中所述19电平变流器工作模态6的工作原理图。 [0049]图8为本发明实施例中所述19电平变流器工作模态7的工作原理图。 [0050]图9为本发明实施例中所述19电平变流器工作模态8的工作原理图。 [0051]图10为本发明实施例中所述19电平变流器工作模态9的工作原理图。 [0052]图11为本发明实施例中所述19电平变流器工作模态10的工作原理图。 [0053]图12为本发明实施例中所述19电平变流器的载波层叠脉冲宽度调制原理图。 [0054]图13为本发明实施例中所述19电平变流器纯阻性负载时的输出电压和负载电流 波形图。 [0055]图14为本发明实施例中所述19电平变流器阻抗性负载时的输出电压和负载电流 波形图。 具体实施方式 [0056]下面将结合本发明实施例中的附图，对本发明实施例中的技术方案进行清楚、完 整地描述，显然，所描述的实施例仅仅是本发明一部分实施例，而不是全部的实施例。基于 本发明中的实施例，本领域普通技术人员在没有做出创造性劳动前提下所获得的所有其他 实施例，都属于本发明保护的范围。 [0057]需要说明的是，当一个组件被认为是“连接”另一个组件，它可以是直接连接到另 一个组件或者可能同时存在居中组件。 [0058]除非另有定义，本文所使用的所有的技术和科学术语与属于本发明的技术领域的 技术人员通常理解的含义相同。本文中在本发明的中所使用的术语只是为了描述具 体的实施例的目的，不是旨在于限制本发明。 [0059] 实施例1 [0060]如图1所示，本发明第一方面提出一种串级式多电平变流器，包括双电容基础模块 (Double Capacitor Basic Module ,DCBM)、多级双电容子模块(Double Capacitor Submodule,DCSM)和H桥单元； [0061]所述双电容基础模块包括开关管Sr开关管S2、开关管S3、开关管S4、开关管S5、电解 电容q、电解电容C2、二极管D0和直流电压源Vdc； [0062]所述开关管S^TC端与直流电压源Vdc的正极和二极管D0的正极相连接； [0063]所述开关管工的£端与所述开关管S4的E端和所述开关管S5的C端相连接； [0064]所述开关管SjTC端与二极管D0的负极和电解电容”的阳极相连接； [0065]所述开关管S3的C端与所述开关管\的£端和电解电容^的阳极相连接； [0066]所述开关管S4的C端与所述开关管S3的E端和电解电容”的阴极相连接； [0067]所述开关管S5的C端与电解电容C2的阴极相连接，所述开关管S5的E端与直流电压 源Vdc的负极相连接； [0068]每级双电容子模块包括开关管Sq开关管Si2、开关管Si3、开关管Si4、开关管Si5、开 关管Si6、开关管Si7、电解电容C^与电解电容Ci2和二极管Dj ； [0069]所述开关管S^TC端与前级双电容子模块开关管5(一)6的E端和二极管Dj的正极相 连接,所述开关管S^TE端与所述开关管Si4的E端和所述开关管Si5的C端相连接； [0070]所述开关管S/TC端与所述开关管Si6的C端相连接;所述开关管Si3的C端与所述开 关管S/TE端和电解电容Ci2的阳极相连接;所述开关管Si4的C端与所述开关管Si7的C端相连 接;所述开关管Si5的C端与所述开关管Si4的E端和电解电容Ci2的阴极相连接，所述开关管Si5 的E端与前级双电容子模块开关管S(i.1)5的E端相连接;所述开关管Si6的E端与二极管Dj的负 极和电解电容J的阳极相连接;所述开关管Si7的E端与所述开关管Si3的E端和电解电容J 的阴极相连接； [0071]第一级双电容子模块的开关管Si5的E端与直流电压源Vdc的负极相连接，第一级双 电容子模块的二极管〃的正极与双电容基础模块的开关管S2TC端相连接； [0072]所述H桥单元包括开关管S01、开关管S02、开关管S03和开关管S04； [0073]所述开关管S01的C端与所述开关管S03的C端和二极管Dj相连接;所述开关管S02的C 端与所述开关管S01的E端相连接；所述开关管S03的E端与所述开关管S04的C端相连接；所述 开关管S04的E端与所述开关管S02的E端和所述开关管Si5的E端相连接； [0074]所述开关管S01的E端和所述开关管S03的E端作为该串级式多电平变流器交流电压 的输出端。 [0075] 本发明串级式多电平变流器的实现方法，包括： [0076]设置开关管S2与开关管S4、开关管Si2与开关管Si4、开关管Si6与开关管Si7工作状态 一致； [0077]设置开关管工与开关管S5、开关管S^与开关管Si5、开关管务与开关管S3、开关管Si2 与开关管Si3、开关管S01与开关管S02、开关管S03与开关管S04工作在互补状态； [0078]特别的，电解电容”和与工作状态具有同步性，电解电容^1和Ci2工作状态具有同 步性。 [0079]控制开关管S2、开关管S3和开关管S4的导通和关断状态，以实现电解电容^与^的 串并联转换； [0080]控制开关管Si2、开关管Si3和开关管Si4的导通和关断状态，以实现电解电容^1与 Ci2的串并联转换； [0081]控制开关管Si1的导通和关断状态，以实现双电容基础模块与双电容子模块的串并 联转换； [0082]控制双电解电容的串并联转换以及双电容基础模块与双电容子模块的串并联转 换，以实现双电容子模块的电解电容^1和Ci2的充电电压均为3%^；特别的，开关管Si6和开 关管Si7的反并联二极管在变流器输出0、土Vdc和土 2Vde时截止以保证电解电容^1和Ci2不参 与放电； [0083]通过增加双电容子模块的扩展极数，以实现具有i个双电容子模块的串级式多电 平变流器输出3i+1X2+1个电平，获得3i+1倍的电压增益。 [0084]需要注意的时，在具体实施过程中，双电容基础模块中的电解电容“和^的充电电 压均为直流输入电压Vdc,双电容子模块中的电解电容Cn和Ci2的充电电压均为3iVdc。 [0085]具体的，采用载波层叠脉宽调制技术，使用正弦波作为调制波，以40倍于调制波频 率的三角波作为载波；调制波与3i+1X2个载波进行比较，在调制波大于载波的部分输出高 电平，在调制波小于载波的部分输出低电平，由此得到3i+1X2组矩形脉冲信号，将得到的矩 形脉冲信号进行合适的逻辑组合，得到各个开关管的门极驱动信号； [0086] 变流器的调制比M由调制波和载波的幅值共同决定，即： [0087] gAref/®%) [0088] 调制比M的取值范围为0&lt;MW1： [0089]当[(j -1) /3i+1) ]&lt;MW (j/3i+1)时，je[1、2、…、3i+1],变流器输出(2 X j+1)电平。 [0090] 实施例2 [0091] 以该变流器的19电平配置(i = 1)为例，所述变流器在一个周期内可划分为19个工 作模态;所述的双电容基础模块和双电容子模块在变流器一个周期的正半周期和负半周期 工作模态一致;在变流器工作的正半周期，所述的工作模态如图2-图11所示。具体工作原理 分析如下： [0092]工作模态1：如图2所示，所述变流器模块单元中开关管52、邑、$5、512、工4和515导通， 其余开关管关断。电容“'G'J和C12分别与电源并联充电到Vdc。同时,H桥单元开关管S01与 S03导通,S02与S04关断,变流器输出电平为0。 [0093]工作模态2：如图3所示，所述变流器模块单元中开关管工作状态与工作模态1一 致,H桥单元开关管S01与S04导通，“与S03关断，变流器输出电平为+Vdc。 [0094]工作模态3：如图4所示，所述变流器模块单元中开关管SrJ,SgS^,Sa和S15导通， 其余开关管关断。电容CrC2并联后与电源串联向负载供电，电容”rC^并联预充电到2Vdc。 二极管D0反向截止,H桥单元开关管S01与S04导通，S02与S03关断，变流器输出电平为+2Vdc。 [0095]工作模态4：如图5所示，所述变流器模块单元中开关管SqS^S^,S^和S15导通，其 余开关管关断。电容C]、C2串联后通过5]与电源串联向负载供电，电容C^,C^并联充电到 3Vde。二极管口0反向截止,H桥单元开关管S01与S04导通，S02与S03关断，变流器输出电平为+ 3Vde。 [0096]工作模态5：如图6所示，所述变流器模块单元中开关管S2、S4、S5、S1rsi2、S14、S16和 S17导通，其余开关管关断。电容CrC2并联充电到Vde。电容”「C^并联后通过Su与电源串联 向负载供电。二极管口]反向截止,H桥单元开关管S01与S04导通，S02与S03关断，变流器输出电 平为+4Vde。 [0097]工作模态6：如图7所示，所述变流器模块单元中开关管SrS凄SgS1rsi2、S1Psi6和 S17导通，其余开关管关断。电容CrC2并联，电容J、”?并联，电源通过S^DSu与两级电容串 联向负载供电。二极管D0和口]反向截止,H桥单元开关管S01与S04导通，S02与S03关断，变流器 输出电平为+5Vde。 [0098]工作模态7：如图8所示，所述变流器模块单元中开关管S^S^S1rsi2、S1Psi6和S17 导通，其余开关管关断。电容CrC2串联，电容J,C^并联，电源通过S/DS]]与两级电容串联 向负载供电。二极管D0和口]反向截止,H桥单元开关管S01与S04导通,S02与S03关断,变流器输 出电平为+6Vde。 [0099]工作模态8：如图9所示，所述变流器模块单元中开关管S^SgS^S]]和S13导通，其 余开关管关断。电容CrC2并联充电到Vde。电容J'C重串联后通过S]]与电源串联向负载供 电。二极管〃反向截止,H桥单元开关管s01与s04导通，s02与s03关断，变流器输出电平为+7Vde。 [0100]工作模态9：如图10所示，所述变流器模块单元中开关管SrS凄SgSu和S13导通，其 余开关管关断。电容CrC2并联，电容”「”2串联，电源通过s^DSu与两级电容串联向负载供 电。二极管D0和口]反向截止,H桥单元开关管s01与s04导通，s02与s03关断，变流器输出电平为+ 8Vde。 [0101]工作模态10：如图11所示，所述变流器模块单元中开关管S^S^Su和S13导通，其余 开关管关断。电容C1、C2串联，电容41312串联，电源通过S/DS]]与两级电容串联向负载供 电。二极管D0和DA向截止,H桥单元开关管S01与S04导通，S02与S03关断，变流器输出电平为+ 吗。。 [0102]在上述多电平变流器电路的基础上，本实施例还给出了载波层叠脉冲宽度调制方 式下，各个开关管的驱动信号的具体实施方式； [0103]如图12所示，所述19电平变流器装置以18个频率相同，相位相同，幅值为Ae的三角 载波与一个幅值为Aref的正弦调制波进行比较，在调制波大于载波的部分输出高电平，在调 制波小于载波的部分输出低电平，由此得到十八组矩形脉冲信号。将得到的矩形脉冲信号 进行合适的逻辑组合，得到各个开关管的门极驱动信号。 [0104] 本实施例中，所述变流器的调制比M由调制波和载波的幅值共同决定，即： [0105] M=Aref/(9Ae) [0106] 调制比M的取值范围为0&lt;MW1：当0&lt;MW0.11时，变流器输出3电平；当0.11&lt;MW 0.22时，变流器输出5电平；当0.22VMW0.33时，变流器输出7电平；当0.33VMW0.44时，变流 器输出9电平；当0.44VMW0.55时，变流器输出11电平；当0.55VMW0.66时，变流器输出13电 平；当0.66VMW0.77时，变流器输出15电平；当0.77VMW0.88时，变流器输出17电平；当0.88 &lt;MW1时，变流器输出19电平。 [0107] 本实施例根据上述调制方式通过仿真对所述19电平变流器装置进行了验证，图13 和图14分别为变流器带纯阻性负载和阻感性负载时的输出电压和负载电流仿真波形图。仿 真结果显示，当变流器带纯阻性负载时，负载电流与输出电压波形相似，呈现19电平正弦阶 梯PWM波形；当变流器带阻感性负载时，由于感性负载的滤波作用，负载电流具有更好的正 弦性，输出电压与负载电流相位差证明了变流器具有较好的带感性负载的能力。 [0108] 实施例3 [0109] 本实施例提供一种串级式多电平变流系统，包括控制器和逆变器，所述逆变器为 所述的串级式多电平变流器。所述控制器控制所述串级式多电平变流系统中的开关管动作 时，执行所述的实现方法的步骤。 [0110]以上所述仅为本发明的优选实施例而已，并不用于限制本发明，对于本领域的技 术人员来说，本发明可以有各种更改和变化。凡在本发明的精神和原则之内，所作的任何修 改、等同替换、改进等，均应包含在本发明的保护范围之内。 [EN CN112290818B]: A cascade type multilevel converter and its realization method Technical field [0001] The present invention relates to the technical field of converters, in particular to a cascade multilevel converter and an implementation method thereof. Background technique [0002] With the large-scale deployment of distributed generators, the inverter link has attracted much attention as a conversion interface between the distributed energy and the grid or AC load. Compared with the traditional two-level converter, the multi-level converter has the advantages of being able to output an approximate sine ladder waveform, reducing the voltage stress of the device, and reducing the voltage harmonic distortion rate. It is also used in the field of distributed power generation. Received extensive attention. [0003] Traditional multilevel converters are divided into three types of typical structures: diode clamp type, flying capacitor type and H-bridge cascade type. Among them, the diode clamp type and flying capacitor type multilevel converters usually have a more complicated structure when outputting more levels, a large number of components, and additional capacitor voltage balance control; H-bridge cascaded multilevel The converter requires a large number of independent DC power supplies, which limits its application range to a certain extent. In addition, the above-mentioned traditional multi-level converters are mostly step-down converters. In applications that require boosting, such as the field of distributed power generation, the photovoltaic array of the photovoltaic power generation device is usually a DC low-voltage source. Need to increase the step-up link, which will increase the complexity and manufacturing cost of the system. [0004] In order to adapt to the development needs of the new energy field and overcome the shortcomings of traditional multi-level converters, switched capacitor technology with the advantages of independent boosting, capacitor voltage self-balancing, etc. is applied to the multi-level converter. Summary of the invention [0005] In view of the above-mentioned problems, the present invention needs to provide a cascade multilevel converter and an implementation method thereof. [0006] The first aspect of the present invention proposes a cascade multi-level converter, including a dual-capacitor basic module, a multi-level dual-capacitor sub-module, and an H-bridge unit; [0007] The dual-capacitor basic module includes a switch tube Sr, a switch tube S2, Switch tube S3, Switch tube S4, Switch tube S5, Electrolytic capacitor q, electrolytic capacitor c2, Diode d0And DC voltage source Vdc； [0008] The switch tube S^qc terminal and the DC voltage source VdcThe anode and diode d0Connect the positive pole of; [0009] The switch foreman's end and the switch for S4The E end and the switch tube S5Connect the C terminal; [0010] The switch tube SjTC terminal and diode D0Connect the negative pole of the electrolytic capacitor to the anode of the electrolytic capacitor; [0011] The switch tube S3The terminal C of the switch tube is connected with the terminal of the switch tube and the anode of the electrolytic capacitor ^; [0012] The switch tube S4The C terminal and the switch tube S3Connect the E terminal of the electrolytic capacitor to the cathode of the electrolytic capacitor; [0013] The switch tube S5C terminal and electrolytic capacitor C2The cathode is connected, the switch tube S5E terminal and DC voltage source VdcThe negative pole is connected; [0014] Each level of the dual-capacitor sub-module includes a switch tube S^, a switch tube Si2, Switch tube Si3, Switch tube Si4, Switch tube Si5, Switch tube Si6, Switch tube Si7, Electrolytic capacitor Cj] and electrolytic capacitor Ci2And diode Di; [0015] The switch tube S^TC end and the previous stage dual-capacitor sub-module switch tube S(i.1)6The E terminal of the diode Di is connected to the anode of the diode Di, and the switch tube S^TE terminal is connected to the switch tube Si4The E end and the switch tube Si5Connect the C terminal; [0016] The switch tube S/qc terminal and the switch tube Si6The c terminal is connected; the switch tube Si3The c terminal is connected to the S/TE terminal of the switch tube and the electrolytic capacitor Ci2The anode is connected; the switch tube Si4The C terminal and the switch tube Si7The C terminal is connected Connect; the switch tube Si5The C terminal and the switch tube Si4E terminal and electrolytic capacitor Ci2The cathode is connected, the switch tube Si5 The E-end and the front-stage dual-capacitor sub-module switch tube S(i.1)5The E end is connected; the switch tube Si6The E terminal is connected to the cathode of the diode Dj and the anode of the electrolytic capacitor J; the switch tube Si7The E end of the switch tube Si3The E terminal of is connected to the cathode of the electrolytic capacitor J; [0017] Switch tube S of the first-stage dual-capacitor sub-modulei5E terminal and DC voltage source VdcThe anode of the diode D1 of the first-level dual-capacitor sub-module is connected to the switch tube SjTC terminal of the dual-capacitor basic module; [0018] The H bridge unit includes a switch tube S01, Switch tube S02, Switch tube S03And switch tube S04； [0019] The switch tube S01The C terminal and the switch tube S03The C terminal and the diode Dj are connected; the switch tube S02The C terminal and the switch tube S01The E terminal is connected; the switch tube S03The E end of the switch tube S04The C terminal is connected; the switch tube S04The E end of the switch tube S02The E end and the switch tube Si5Connect to the E end; [0020] The switch tube S01The E end and the switch tube S03The E terminal is used as the output terminal of the AC voltage of the cascade multilevel converter. [0021] The second aspect of the present invention provides a method for implementing a cascade multilevel converter, which is applied to the cascade multilevel converter, and a switch tube 5 is provided.2With switch tube S4, Switch tube Si2With switch tube Si4, Switch tube Si6With switch tube Si7Consistent working status; [0022] Set switch foreman and switch tube S5, Switch tube 5 ports and switch tube Si5, Switch management and switch management S3, Switch tube Si2 With switch tube Si3, Switch tube S01With switch tube S02, Switch tube S03With switch tube S04Work in a complementary state; [0023] Control switch tube S2, Switch tube S3And switch tube S4The on and off states of the electrolytic capacitors ^ and ^ are converted in series and parallel; [0024] Control switch tube Si2, Switch tube Si3And switch tube Si4The on and off state of the electrolytic capacitor ^1 and Ci2Series-parallel conversion; [0025] Control the on and off states of the switch Sn to realize the serial-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module; [0026] Control the series-parallel conversion of the dual electrolytic capacitors and the series-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module to realize the electrolytic capacitors J] and C of the dual-capacitor sub-modulei2The charging voltage is 3iVdc； [0027] By increasing the number of extended poles of the dual-capacitor sub-modules, the output of the cascade multi-level converter with i dual-capacitor sub-modules is realized 3i+1X2+1 levels, get 3i+1Times the voltage gain. [0028] Based on the above, the carrier stack pulse width modulation technology is used, a sine wave is used as the modulating wave, and a triangular wave 40 times the frequency of the modulating wave is used as the carrier; the modulating wave and 3i+1X2 carriers are compared, the part where the modulation wave is larger than the carrier will output a high level, and the part where the modulation wave is smaller than the carrier will output a low level, thus 3i+1X2 group of rectangular pulse signals, appropriate logical combination of the obtained rectangular pulse signals to obtain the gate drive signal of each switch tube; [0029] The modulation ratio M of the converter is determined by the amplitude A of the modulating waverefAnd carrier amplitude AcJoint decision, namely: [0030] M = Aref/(3i + 1Ac) [0031] The value range of the modulation ratio M is 0&lt;MW1: [0032] When [(j -1) /3i+1) ]&lt;MW (j/3i+1), je[1,2,...,3i+1], the converter output (2 X j+1) level. [0033] A third aspect of the present invention provides a cascade multilevel converter system, including a controller and an inverter, and the inverter is the cascade multilevel converter. [0034] Based on the above, when the controller controls the action of the switch in the cascade multi-level converter system, it executes the steps of the implementation method. [0035] The present invention has outstanding substantive features and significant progress, specifically: [0036] (1) The cascade multilevel converter of the present invention adopts a dual-capacitor combination, through dual-capacitor step charging and series superposition in the dual-capacitor basic module and dual-capacitor sub-module, and the series-parallel conversion of the modules. When outputting a large number of levels, it can reduce the use of components and reduce the system cost; [0037] (2) The cascade multilevel converter of the present invention has the advantage of capacitor voltage self-balancing, avoiding an additional capacitor voltage control loop; [0038] (3) The cascade multi-level converter of the present invention can be expanded by dual-capacitor sub-modules to further increase the number of output levels and at the same time increase the output voltage gain [0039] The cascade multilevel converter of the present invention adopts a single power input, which broadens its application range. [0040] Additional aspects and advantages of the present invention will become apparent in the following description, or be understood through the practice of the present invention. Description of the drawings [0041] The above and/or additional aspects and advantages of the present invention will become obvious and easy to understand from the description of the embodiments in conjunction with the following drawings, in which: [0042] FIG. 1 is a structural diagram of the cascade multilevel converter in an embodiment of the present invention. [0043] FIG. 2 is a working principle diagram of the working mode 1 of the 19-level converter in the embodiment of the present invention. [0044] FIG. 3 is a working principle diagram of the working mode 2 of the 19-level converter in the embodiment of the present invention. [0045] FIG. 4 is a working principle diagram of the working mode 3 of the 19-level converter in the embodiment of the present invention. [0046] FIG. 5 is a working principle diagram of the working mode 4 of the 19-level converter in the embodiment of the present invention. [0047] FIG. 6 is a working principle diagram of the working mode 5 of the 19-level converter in the embodiment of the present invention. [0048] FIG. 7 is a working principle diagram of the working mode 6 of the 19-level converter in the embodiment of the present invention. [0049] FIG. 8 is a working principle diagram of the working mode 7 of the 19-level converter in the embodiment of the present invention. [0050] FIG. 9 is a working principle diagram of the working mode 8 of the 19-level converter in the embodiment of the present invention. [0051] FIG. 10 is a working principle diagram of the working mode 9 of the 19-level converter in the embodiment of the present invention. [0052] FIG. 11 is a working principle diagram of the working mode 10 of the 19-level converter in the embodiment of the present invention. [0053] FIG. 12 is a schematic diagram of the carrier stacked pulse width modulation of the 19-level converter in the embodiment of the present invention. [0054] FIG. 13 is a waveform diagram of the output voltage and load current of the 19-level converter under a purely resistive load in the embodiment of the present invention. [0055] FIG. 14 is a waveform diagram of the output voltage and load current of the 19-level converter under resistive load in the embodiment of the present invention. Detailed ways [0056] The following will clearly and completely describe the technical solutions in the embodiments of the present invention with reference to the accompanying drawings in the embodiments of the present invention. Obviously, the described embodiments are only a part of the embodiments of the present invention, rather than all of them. example. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0057] It should be noted that when a component is considered to be "connected" to another component, it may be directly connected to another component or a centered component may exist at the same time. [0058] Unless otherwise defined, all technical and scientific terms used herein have the same meaning as commonly understood by those skilled in the technical field of the present invention. The terminology used in the present invention herein is only for the purpose of describing specific embodiments, and is not intended to limit the present invention. Example 1 [0060] As shown in FIG. 1, the first aspect of the present invention proposes a cascade multilevel converter, including a double capacitor basic module (Double Capacitor Basic Module, DCBM), a multi-level double capacitor sub-module (Double Capacitor Submodule, DCSM) and H bridge unit; [0061] The dual-capacitor basic module includes a switch tube Sr, a switch tube S2, Switch tube S3, Switch tube S4, Switch tube S5, Electrolytic capacitor q, electrolytic capacitor C2, diode D0And DC voltage source Vdc； [0062] The switching tube S^TC terminal and the DC voltage source VdcThe anode and diode D0Connect the positive pole of; [0063] The P end of the switch foreman and the switch tube S4The E end and the switch tube S5Connect the C terminal; [0064] The switch tube SjTC terminal and diode D0Connect the negative pole of the electrolytic capacitor to the anode of the electrolytic capacitor; [0065] The switch tube S3The terminal C of the switch tube is connected to the terminal of the switch tube and the anode of the electrolytic capacitor ^; [0066] the switch tube S4The C terminal and the switch tube S3Connect the E terminal of the electrolytic capacitor to the cathode of the electrolytic capacitor; [0067] The switch tube S5C terminal and electrolytic capacitor C2The cathode is connected, the switch tube S5E terminal and DC voltage source VdcThe negative pole is connected; [0068] Each level of the dual-capacitor sub-module includes a switch tube Sq switch tube Si2, Switch tube Si3, Switch tube Si4, Switch tube Si5, Switch tube Si6, Switch tube Si7, Electrolytic capacitor C^ and electrolytic capacitor Ci2And diode Dj; [0069] The switch tube S^TC terminal and the previous stage dual-capacitor sub-module switch tube 5 (one)6The E terminal and the anode of the diode Dj are connected, and the switch tube S^TE terminal is connected to the switch tube Si4The E end and the switch tube Si5Connect the C terminal; [0070] The switch tube S/TC terminal and the switch tube Si6The C terminal is connected; the switch tube Si3The C terminal is connected to the S/TE terminal of the switch tube and the electrolytic capacitor Ci2The anode is connected; the switch tube Si4The C terminal and the switch tube Si7The C terminal is connected; the switch tube Si5The C terminal and the switch tube Si4E terminal and electrolytic capacitor Ci2The cathode is connected, the switch tube Si5 The E-end and the front-stage dual-capacitor sub-module switch tube S(i.1)5The E end is connected; the switch tube Si6The E terminal is connected to the cathode of the diode Dj and the anode of the electrolytic capacitor J; the switch tube Si7The E end of the switch tube Si3The E terminal of is connected to the cathode of the electrolytic capacitor J; [0071] Switch tube S of the first-stage dual-capacitor sub-modulei5E terminal and DC voltage source VdcConnect the cathode of the first-level dual-capacitor sub-module with the anode of the diode of the dual-capacitor sub-module and the switch tube S of the dual-capacitor basic module2TC terminal is connected; [0072] The H bridge unit includes a switch tube S01, Switch tube S02, Switch tube S03And switch tube S04； [0073] The switch tube S01The C terminal and the switch tube S03The C terminal and the diode Dj are connected; the switch tube S02The C terminal and the switch tube S01The E terminal is connected; the switch tube S03The E end of the switch tube S04The C terminal is connected; the switch tube S04The E end of the switch tube S02The E end and the switch tube Si5Connect to the E end; [0074] The switch tube S01The E end and the switch tube S03The E terminal is used as the output terminal of the AC voltage of the cascade multilevel converter. [0075] The implementation method of the cascade multilevel converter of the present invention includes: [0076] Set switch tube S2With switch tube S4, Switch tube Si2With switch tube Si4, Switch tube Si6With switch tube Si7Consistent working status; [0077] Set switch foreman and switch tube S5, Switch tube S^ and switch tube Si5, Switch management and switch management S3, Switch tube Si2 With switch tube Si3, Switch tube S01With switch tube S02, Switch tube S03With switch tube S04Work in a complementary state; [0078] In particular, the electrolytic capacitor is synchronized with the working state, the electrolytic capacitor ^1 and Ci2The working status is synchronized. [0079] Control switch tube S2, Switch tube S3And switch tube S4The on and off states of the electrolytic capacitors ^ and ^ are converted in series and parallel; [0080] Control switch tube Si2, Switch tube Si3And switch tube Si4The on and off state of the electrolytic capacitor ^1 and Ci2Series-parallel conversion; [0081] Control the on and off states of the switch Si1 to realize the series-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module; [0082] Control the series-parallel conversion of the dual electrolytic capacitors and the series-parallel conversion of the dual-capacitor basic module and the dual-capacitor sub-module to realize the electrolytic capacitors ^1 and C of the dual-capacitor sub-modulei2The charging voltage is 3%^; in particular, the switch tube Si6And switch tube Si7The anti-parallel diode in the converter outputs 0, soil VdcHetu 2VdeTime cut off to ensure the electrolytic capacitor ^1 and Ci2Not involved in discharge; [0083] By increasing the number of extended poles of the dual-capacitor sub-modules, the output of the cascade multi-level converter with i dual-capacitor sub-modules is realized 3i+1X2+1 levels, get 3i+1Times the voltage gain. [0084] It should be noted that in the specific implementation process, the charging voltages of the electrolytic capacitors and ^ in the dual-capacitor basic module are all DC input voltages Vdc, The electrolytic capacitors Cn and C in the dual-capacitor sub-modulei2The charging voltage is 3iVdc。 [0085] Specifically, the carrier stack pulse width modulation technology is adopted, a sine wave is used as the modulating wave, and a triangular wave 40 times the frequency of the modulating wave is used as the carrier; the modulating wave and 3i+1X2 carriers are compared, the part where the modulating wave is larger than the carrier will output a high level, and the part where the modulating wave will be smaller than the carrier will output a low level, thus obtaining 3i+1X2 group of rectangular pulse signals, appropriate logical combination of the obtained rectangular pulse signals to obtain the gate drive signal of each switch tube; [0086] The modulation ratio M of the converter is determined by the amplitude of the modulating wave and the carrier wave, namely: [0087] gAref/®%) [0088] The value range of the modulation ratio M is 0&lt;MW1: [0089] When [(j -1) /3i+1) ]&lt;MW (j/3i+1), je[1,2,...,3i+1], the converter output (2 X j+1) level. Example 2 [0091] Taking the 19-level configuration (i=1) of the converter as an example, the converter can be divided into 19 working modes in one cycle; the dual-capacitor basic module and the dual-capacitor The module has the same working mode in the positive half cycle and negative half cycle of one cycle of the converter; in the positive half cycle of the converter, the working mode is shown in Figure 2-11. The specific working principle is analyzed as follows: [0092] Working mode 1: As shown in FIG. 2, the switch tube 5 in the converter module unit2, Yup, $5、512,work4And 515Turn on, and the other switch tubes are turned off. Capacitance "'G'J and C12Respectively charge to V in parallel with the power supplydc. At the same time, the H bridge unit switch tube S01With S03On, S02With S04Turn off, the output level of the converter is 0. [0093] Working mode 2: As shown in FIG. 3, the working state of the switching tube in the converter module unit is consistent with the working mode 1, and the switching tube S of the H-bridge unit01With S04Conduction, "and S03Turn off, the output level of the converter is +Vdc。 [0094] Working mode 3: As shown in FIG. 4, the switch tubes SrJ, SgS^, Sa and S in the converter module unit15Turn on, and the other switch tubes are turned off. Capacitance CrC2After being connected in parallel with the power supply in series to supply power to the load, the capacitor "rC^" is precharged in parallel to 2Vdc. Diode D0Reverse cut-off, H bridge unit switch tube S01With S04On, S02With S03Turn off, the output level of the converter is +2Vdc。 [0095] Working mode 4: As shown in FIG. 5, the switch tubes SqS^S^, S^ and S in the converter module unit15Turn on, and the other switch tubes are turned off. Capacitance C], C2After the series connection, 5] is connected in series with the power supply to supply power to the load, and the capacitors C^ and C^ are charged in parallel to 3Vde. Diode port0Reverse cut-off, H bridge unit switch tube S01With S04On, S02With S03Turn off, the output level of the converter is + 3Vde。 [0096] Working mode 5: As shown in FIG. 6, the switch tube S in the converter module unit2, S4, S5, S1rsi2, S14, S16And S17Turn on, and the other switch tubes are turned off. Capacitance CrC2Charge in parallel to Vde. Capacitor "" C^ is connected in parallel with the power supply to supply power to the load through Su. The diode port] reversely cuts off, the H-bridge unit switch tube S01With S04On, S02With S03Turn off, the output level of the converter is +4Vde。 [0097] Working mode 6: As shown in FIG. 7, the switching tubes SrS and SgS in the converter module unit1rsi2, S1Psi6And S17Turn on, and the other switch tubes are turned off. Capacitance CrC2In parallel, the capacitors J and "? are connected in parallel, and the power supply supplies power to the load through S^DSu and two-stage capacitors in series. Diode D0Hekou] Reverse cutoff, H bridge unit switch tube S01With S04On, S02With S03Turn off, the output level o
[ZH CN113394982A]: 一种级联H桥型电力电子变压器暂态电压与功率均衡方法 [EN CN113394982A]: A cascaded H-bridge type power electronic transformer transient voltage and power balance method | [ZH CN113394982A]: 本发明涉及电力系统输配电领域，公开了一种级联H桥型电力电子变压器暂态电压与功率均衡方法，以实现电力电子变压器暂态的中间直流电容电压均衡与各DAB变换器传输功率均衡。它包括以下步骤：以级联H桥输出的各中间直流电压与中间直流电压均值的差值进行闭环控制，得到DAB变换器的计算漏感值，以此计算漏感值对DAB变换器实际漏感值和设计漏感值之间的差异进行补偿，计算得到各DAB变换器的移相角，彻底消除了由于变压器漏感参数差异引起的功率不均衡问题。本发明实现了稳态和暂态的中间直流电压均衡与DAB变换器传输功率均衡，避免了电力电子变压器因为均衡问题而导致器件过电压或者过电流。且本发明易于实现，具有可靠性高和适用范围广等优点。 [EN CN113394982A]: The invention relates to the field of power system transmission and distribution, and discloses a cascaded H-bridge type power electronic transformer transient voltage and power balance method to realize the transient intermediate DC capacitor voltage balance of the power electronic transformer and the transmission power of each DAB converter balanced. It includes the following steps: Close-loop control is performed by the difference between each intermediate DC voltage output by the cascaded H-bridge and the average value of the intermediate DC voltage, and the calculated leakage inductance value of the DAB converter is obtained. The difference between the inductance value and the designed leakage inductance value is compensated, and the phase shift angle of each DAB converter is calculated, which completely eliminates the problem of power imbalance caused by the difference in transformer leakage inductance parameters. The invention realizes steady-state and transient intermediate DC voltage balance and DAB converter transmission power balance, and avoids the power electronic transformer from causing device overvoltage or overcurrent due to the balance problem. In addition, the present invention is easy to implement, has the advantages of high reliability and wide application range. | CN113394982A | 2021-09-14 | CN202110697724A | 2021-06-23 | CN202110697724A, 2021-06-23 | CN113394982A: 2021-09-14 | 湘潭大学 |  | H02M3/335: I |  |  |  | [ZH CN113394982A]: L一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其特征在于，包括以下步 骤： 1）采用ΡΙ控制器对低压直流电压进行基础电压闭环控制，得到所有DAB变换器的基础 移相角d； 2）计算各个整流器输出的中间直流电容电压的平均值3c，将整流器输出的中间直流电 容电压的平均值％。与各个整流器输出的中间直流电容电压Ug （i = l〜N）做差,并采用PI控 制器对做差的结果进行闭环控制,得到各DAB变换器的计算漏感值； 3）根据DAB功率计算公式，以计算漏感值对各DAB变换器的实际漏感值和设计漏感 值之间的差异进行补偿，直接计算得到各DAB变换器的最终移相角dj并以最终的移相角包 调节各个DAB变换器的传输功率,以实现中间直流电压均衡与DAB变换器传输功率均衡； 4=0.5—卜.25—组— V 4 其中,为设计的漏感值。 2 .根据权利要求1所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的总中间直流电压闭环控制器的输入信号为电力电子变压器的低压直流电 压设定值⑷与低压直流电压测量值或的差值。 3 .根据权利要求2所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的电压与功率均衡闭环控制器的输入信号为各中间直流电容电压与中间直 流电容电压的平均值的差值。 4 .根据权利要求3所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于,所述的DAB变换器传输功率均衡可以进一步实现中间直流电容电压均衡。 5 .根据权利要求2所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的低压直流电压闭环控制得到的移相角为DAB变换器的基础移相角，它将参 与各DAB变换器最终移相角的计算。 6 .根据权利要求1所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的电压与功率均衡闭环控制器的ΡΙ控制器的输出为各DAB变换器的计算漏 感值，它将直接对DAB变换器的漏感参数差异进行补偿。 7 .根据权利要求6所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的电压与功率均衡闭环控制器中，计算漏感值将在各DAB变换器的最终移相 比的计算中直接对漏感参数进行补偿，可从软件上直接消除漏感参数差异的影响。 8 .根据权利要求7所述的一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，其 特征在于，所述的辅助均衡控制的ΡΙ控制器输出的计算漏感值不受负载参数的影响。 [EN CN113394982A]: L A cascaded H-bridge type power electronic transformer transient voltage and power balance method, which is characterized in that it includes the following steps: 1) The PI controller is used to perform closed-loop control of the basic voltage of the low-voltage DC voltage to obtain the basic phase shift angle d of all DAB converters; 2) Calculate the average value 3c of the intermediate DC capacitor voltage output by each rectifier, and calculate the average value% of the intermediate DC capacitor voltage output by the rectifier. Make a difference with the intermediate DC capacitor voltage Ug (i = l~N) output by each rectifier, and use a PI controller to perform closed-loop control on the difference result to obtain the calculated leakage inductance value of each DAB converter; 3) According to the DAB power calculation formula, the leakage inductance value is calculated to compensate the difference between the actual leakage inductance value and the designed leakage inductance value of each DAB converter, and the final phase shift angle dj of each DAB converter is directly calculated and then The final phase shift angle package adjusts the transmission power of each DAB converter to achieve intermediate DC voltage balance and DAB converter transmission power balance; 4=0.5-Bu. 25-group- V 4 Among them, is the designed leakage inductance value. 2 A cascaded H-bridge type power electronic transformer transient voltage and power equalization method according to claim 1, wherein the input signal of the total intermediate DC voltage closed-loop controller is the low voltage DC of the power electronic transformer The difference between the voltage setting value and the measured value of the low-voltage DC voltage. 3 A cascaded H-bridge type power electronic transformer transient voltage and power balance method according to claim 2, wherein the input signal of the voltage and power balance closed-loop controller is the voltage of each intermediate DC capacitor and The difference between the average value of the intermediate DC capacitor voltage. 4 A cascaded H-bridge type power electronic transformer transient voltage and power equalization method according to claim 3, wherein the DAB converter transmission power equalization can further realize intermediate DC capacitor voltage equalization. 5 The transient voltage and power equalization method of a cascaded H-bridge power electronic transformer according to claim 2, wherein the phase shift angle obtained by the closed-loop control of the low-voltage DC voltage is the basic shift angle of the DAB converter. Phase angle, it will participate in the calculation of the final phase shift angle of each DAB converter. 6 The transient voltage and power balance method of a cascaded H-bridge power electronic transformer according to claim 1, wherein the output of the PI controller of the voltage and power balance closed-loop controller is each DAB transform The calculated leakage inductance value of the DAB converter will directly compensate for the difference in leakage inductance parameters of the DAB converter. 7 A cascaded H-bridge type power electronic transformer transient voltage and power balance method according to claim 6, characterized in that, in the voltage and power balance closed-loop controller, the leakage inductance value will be calculated in each DAB The leakage inductance parameter is directly compensated in the calculation of the final shift of the converter, which can directly eliminate the influence of the leakage inductance parameter difference from the software. 8 The transient voltage and power balance method of a cascaded H-bridge power electronic transformer according to claim 7, wherein the calculated leakage inductance value output by the PI controller of the auxiliary balance control is not affected by the load parameter Impact. | [ZH CN113394982A]: 一种级联H桥型电力电子变压器暂态电压与功率均衡方法 技术领域 [0001]本发明涉及电力系统输配电领域，更具体地，涉及一种级联H桥型电力电子变压器 暂态电压与功率均衡方法。 背景技术 [0002]电力电子变压器作为一种新型电力变换装置，它不仅能够实现传统变压器所具备 的电压等级变换和电气隔离，还具有电能质量隔离、主动交直流能量管理、无功补偿等功 能。此外，电力电子变压器还具有高功率密度，模块化设计易冗余等优点。两级级联的级联H 桥型电力电子变压器包括前级交流侧的级联H桥整流器和后级的DAB变换器。其中，级联H桥 的交流测与交流配电网直接连接，为后级DAB变换器提供高压直流端口；而后级的DAB变换 器通过高压直流端口与前级的级联H桥级联，通过高频变压器实现电压变换和电气隔离，并 提供低压直流端口。 [0003] 针对级联H桥型电力电子变压器，为解决电力电子变压器的电压均衡与功率均衡 问题，传统控制方法为:首先对DAB变换器输出的低压直流电压进行闭环控制得到DAB变换 器的共同移相角，再通过对各中间直流电容电压与中间直流电容电压的平均值的差值进行 闭环控制，以得到各个DAB变换器的补偿移相角，将补偿移相角与共同移相角相加，得到各 个DAB变换器的最终移相角。该方法通过PI控制器对DAB变换器的移相角进行修改，在不同 负载下需要补偿的移相角不用，暂态均衡性能受限，在负载波动较频繁的场合易造成电力 电子变压器过电压或过电流，最终导致电力电子变压器故障停机。 发明内容 [0004] 针对现有技术的缺陷，本发明目的在于公开一种级联H桥型电力电子变压器暂态 电压与功率均衡方法，以在负载波动的情况下依然能够实现电力电子变压器的电压均衡与 功率均衡。 [0005]为实现上述目的，本发明提供了一种级联H桥型电力电子变压器暂态电压与功率 均衡方法，该方法包括以下步骤： [0006] 1）采用PI控制器对低压直流电压进行基础电压闭环控制，得到所有DAB变换器的 基础移相角d； [0007] 2）计算各个整流器输出的中间直流电容电压的平均值Udc,将整流器输出的中间直 流电容电压的平均值Udc与各个整流器输出的中间直流电容电压Udci（i = 1〜N）做差，并采 用PI控制器对做差的结果进行闭环控制，得到各DAB变换器的计算漏感值Lcki； [0008] 3）根据DAB功率计算公式，以计算漏感值Lcki对各DAB变换器的实际漏感值和设计 漏感值之间的差异进行补偿，直接计算得到各DAB变换器的最终移相角dj并以最终的移相 角dj调节各个DAB变换器的传输功率，以实现中间直流电压均衡与DAB变换器传输功率均 衡； [0009] 4 - 0.5 — Jo.25 ——. d (I — d) y ^kd [0010]其中，Lkd为设计的漏感值。 [0011] 所述的基础电压闭环控制器的输入信号为电力电子变压器的低压直流电压设定 值UJ与低压直流电压测量值或的差值。 [0012]所述的电压与功率均衡闭环控制器的输入信号为各中间直流电容电压与中间直 流电容电压的平均值的差值。 [0013] 所述的DAB变换器传输功率均衡可以进一步实现中间直流电容电压均衡。 [0014] 所述的低压直流电压闭环控制得到的移相角为DAB变换器的基础移相角，它将参 与各DAB变换器最终移相角的计算。 [0015]所述的电压与功率均衡闭环控制器的PI控制器的输出为各DAB变换器的计算漏感 值，它将直接对DAB变换器的漏感参数差异进行补偿。 [0016]所述的电压与功率均衡闭环控制器中，计算漏感值将在各DAB变换器的最终移相 比的计算中直接对漏感参数进行补偿，可从软件上直接消除漏感参数差异的影响。 [0017]所述的辅助均衡控制的PI控制器输出的计算漏感值不受负载参数的影响。 [0018]本发明的有益效果是:本发明对DAB变换器输出的低压直流电压进行单电压闭环 移相控制，并将电压环输出的移相比作为基础移相比。然后通过对各中间直流电容电压与 中间直流电容电压的平均值的差值进行闭环控制，得到各DAB变换器的计算漏感值，再根 据计算漏感值对理论设计漏感值与实际漏感值之间的误差进行补偿,可直接计算得到各个 DAB变换器最终的移相角，实现中间直流电容电压均衡与DAB变换器传输功率均衡。本发明 直接对DAB变换器的漏感值进行补偿,彻底解决了电压与功率不均衡问题。相比于传统的控 制方法，本发明所提均衡控制器的PI控制器输出的计算漏感值并不会受到负载波动的影 响，因此在负载波动时也能够提供均衡的中间直流电压与均衡的传输功率。该控制方法对 提高电力电子变压器在功率波动频繁的场合下的可靠性有着重要意义。 附图说明 [0019]构成本申请的一部分的附图用来提供对本发明的进一步理解，本发明的示意性实 施例及其说明用于解释本发明，并不构成对本发明的不当限定。在附图中： [0020]图1是本发明实施案例提供的级联Η桥型电力电子变压器的拓扑结构示意图； [0021]图2是本发明实施案例提供的一种级联Η桥型电力电子变压器暂态电压与功率均 衡方法的控制框图。 具体实施方式 [0022]为了使本发明的目的、技术方案以及优点更加清楚明白，以下结合附图对本发明 的实施例进行详细说明，但是本发明可以由权利要求限定和覆盖的多种不同方式实施。 [0023]级联Η桥型电力电子变压器，其拓扑采用串入并出的结构，如图1所示。前级的单相 整流器串联形成级联Η桥，达到串联分压的作用,而级联Η桥输出的中间直流电容电压，将作 为后级DAB变换器的输入电源;后级的DAB变换器并联形成电力电子变压器的隔离级，达到 并联分流的作用，并提供一个低压直流电压输出端口，该端口可作为供电端口直接对外输 出功率，也可以连接逆变器再提供交流电源端口对外供电。 [0024] 本发明通过分析引起电力电子变压器电压与功率不均衡的根本原因，公开了一种 级联Η桥型电力电子变压器暂态电压与功率均衡方法。 [0025]隔离级中DAB变换器可通过移相控制来实现功率传输,其传输功率可计算为 0026] Λ,λ=—竺·Ο——L 2* [0027] 式中，η为变压器变比为DAB变换器输入电压,或为DAB变换器输出电压,d为DAB 变换器移相角,fs为高频变压器开关频率，Lk为高频变压器漏感值。 [0028] 当每个DAB变换器的传输功率均衡时，电力电子变压器的中间直流电压也是均衡 的。假设初期电力电子变压器的各中间直流电压Ug均衡，由于各DAB变换器输出并联，其 输出电压或也相同，而开关频率也设置为同一数值,此时，DAB变换器的传输功率将由其高 频变压器变比、漏感值决定。变压器漏感设计困难且误差较大，因此应用同一移相角时各 DAB变换器之间的漏感差异将引起各DAB变换器的传输功率不一致，进而引起电力电子变压 器中间直流电容电压不均衡。 [0029]为了彻底解决由DAB变换器的高频变压器漏感参数差异带来的电压与功率不均衡 的问题，应对各个DAB变换器的漏感参数进行补偿,再用补偿过后的漏感参数计算得到各个 DAB变换器的最终移相角，此时，电力电子变压器相当于在控制算法上实现了 DAB变换器的 高频变压器漏感参数一致，从根本上解决了电力电子变压器的电压与功率不均衡问题。 [0030]图2为本发明实施案例提供的一种级联Η桥型电力电子变压器暂态电压与功率均 衡方法的控制框图，现结合图2详细说明本发明的实现过程。 [0031] 一种级联Η桥型电力电子变压器暂态电压与功率均衡方法，该方法分为两部分，第 一部分为基础电压控制,第二部分为辅助均衡控制。 [0032] 基础电压控制采用ΡΙ控制器对电力电子变压器的低压直流电压设定值”*与低压 直流电压测量值”的差值进行闭环控制，旨在实现低压直流电压的恒电压控制。由ΡΙ控制 器得到的移相角为DAB变换器的基础移相角d,基础移相角d将参与各DAB变换器最终移相 角的计算。 [0033] 辅助均衡控制采用PI控制器对各中间直流电容电压与中间直流电容电压的平均 值的差值进行闭环控制，以得到每个DAB变换器的计算漏感值Ly该计算漏感值%后将补偿 理论设计漏感值与实际漏感值之间的误差，该误差补偿可表示为比例系数Lki/Lkd，此比 例系数将参与各DAB变换器最终移相比的计算： [0034] d- = 0.5 — /0.25——· — y % [0035]该控制系统通过的计算漏感参数补偿漏感误差，并利用补偿的比例系数直接对基 础移相比进行修改，可直接计算得到各DAB变换器的最终移相比包，以最终的移相比调节中 间直流电容电压与各个DAB变换器的传输功率。 [EN CN113394982A]: A cascaded H-bridge type power electronic transformer transient voltage and power balance methodTechnical field [0001] The present invention relates to the field of power system transmission and distribution, and more specifically, to a method for balancing transient voltage and power of cascaded H-bridge power electronic transformers. Background technique [0002] As a new type of power conversion device, a power electronic transformer can not only realize the voltage level conversion and electrical isolation of traditional transformers, but also has functions such as power quality isolation, active AC and DC energy management, and reactive power compensation. In addition, power electronic transformers also have the advantages of high power density, modular design and easy redundancy. The two-stage cascaded cascaded H-bridge power electronic transformer includes a cascaded H-bridge rectifier on the AC side of the front stage and a DAB converter on the back stage. Among them, the AC test of the cascaded H bridge is directly connected to the AC distribution network to provide a high-voltage DC port for the subsequent DAB converter; and the subsequent DAB converter is cascaded with the previous cascaded H bridge through the high-voltage DC port. The high-frequency transformer realizes voltage conversion and electrical isolation, and provides a low-voltage DC port. [0003] For cascaded H-bridge power electronic transformers, in order to solve the voltage balance and power balance problems of power electronic transformers, the traditional control method is: firstly, the low-voltage DC voltage output by the DAB converter is closed-loop controlled to obtain the common DAB converter Shift the phase angle, and then close-loop control the difference between the average value of the intermediate DC capacitor voltage and the intermediate DC capacitor voltage to obtain the compensation phase shift angle of each DAB converter, and the compensation phase shift angle and the common phase shift angle phase Add to get the final phase shift angle of each DAB converter. This method modifies the phase shift angle of the DAB converter through the PI controller. The phase shift angle that needs to be compensated under different loads is not used, and the transient balance performance is limited. It is easy to cause overvoltage of the power electronic transformer in the occasions with frequent load fluctuations. Or overcurrent, which will eventually cause the power electronic transformer to fail and shut down. Summary of the invention [0004] In view of the shortcomings of the prior art, the purpose of the present invention is to disclose a cascaded H-bridge type power electronic transformer transient voltage and power balance method, so that the voltage balance and power electronic transformer can still be achieved in the case of load fluctuations. Power balance. [0005] In order to achieve the above objective, the present invention provides a cascaded H-bridge type power electronic transformer transient voltage and power balance method, the method includes the following steps: [0006] 1) The PI controller is used to perform closed-loop control of the basic voltage of the low-voltage DC voltage to obtain the basic phase shift angle d of all DAB converters; [0007] 2) Calculate the average value U of the intermediate DC capacitor voltage output by each rectifierdc, The average value U of the intermediate DC capacitor voltage output by the rectifierdcAnd the intermediate DC capacitor voltage U output by each rectifierdci(I = 1~N) Make the difference, and use the PI controller to perform closed-loop control on the difference result to obtain the calculated leakage inductance value L of each DAB convertercki； [0008] 3) Calculate the leakage inductance value L according to the DAB power calculation formulackiCompensate the difference between the actual leakage inductance value of each DAB converter and the designed leakage inductance value, directly calculate the final phase shift angle dj of each DAB converter, and adjust the transmission of each DAB converter with the final phase shift angle dj Power to achieve the balance of intermediate DC voltage and DAB converter transmission power; [0009] 4-0.5 - Jo.25 . d (I - d) y ^kd [0010] Among them, Lkd is the designed leakage inductance value. [0011] The input signal of the basic voltage closed-loop controller is the difference between the low-voltage DC voltage set value UJ of the power electronic transformer and the measured value of the low-voltage DC voltage or. [0012] The input signal of the voltage and power balance closed-loop controller is the difference between each intermediate DC capacitor voltage and the average value of the intermediate DC capacitor voltage. [0013] The DAB converter transmission power balance can further realize the intermediate DC capacitor voltage balance. [0014] The phase shift angle obtained by the low-voltage DC voltage closed-loop control is the basic phase shift angle of the DAB converter, which will participate in the calculation of the final phase shift angle of each DAB converter. [0015] The output of the PI controller of the voltage and power balance closed-loop controller is the calculated leakage inductance value of each DAB converter, which will directly compensate for the difference in leakage inductance parameters of the DAB converter. [0016] In the voltage and power balance closed-loop controller, the calculation of the leakage inductance value will directly compensate the leakage inductance parameter in the calculation of the final shift of each DAB converter, and the leakage inductance parameter can be directly eliminated from the software. The impact of differences. [0017] The calculated leakage inductance value output by the PI controller of the auxiliary balance control is not affected by the load parameter. [0018] The beneficial effects of the present invention are: the present invention performs a single voltage closed-loop phase shift control on the low-voltage DC voltage output by the DAB converter, and uses the shift phase of the voltage loop output as the basic shift phase. Then, the calculated leakage inductance value of each DAB converter is obtained by closed-loop control of the difference between the average value of each intermediate DC capacitor voltage and the intermediate DC capacitor voltage, and then the theoretical design leakage inductance value and the actual leakage inductance are compared according to the calculated leakage inductance value. The error between the values is compensated, and the final phase shift angle of each DAB converter can be directly calculated to achieve the balance of the intermediate DC capacitor voltage and the transmission power of the DAB converter. The invention directly compensates the leakage inductance value of the DAB converter, and completely solves the problem of voltage and power imbalance. Compared with the traditional control method, the calculated leakage inductance value output by the PI controller of the balanced controller provided by the present invention will not be affected by load fluctuations, so it can provide a balanced intermediate DC voltage and a balanced DC voltage even when the load fluctuates. Transmission power. This control method is of great significance to improve the reliability of power electronic transformers under frequent power fluctuations. Description of the drawings [0019] The drawings constituting a part of the present application are used to provide a further understanding of the present invention. The exemplary embodiments and descriptions of the present invention are used to explain the present invention, and do not constitute an improper limitation of the present invention. In the attached picture: [0020] FIG. 1 is a schematic diagram of the topological structure of a cascaded H-bridge power electronic transformer provided by an embodiment of the present invention; [0021] FIG. 2 is a control block diagram of a method for balancing transient voltage and power of a cascaded H-bridge power electronic transformer provided by an embodiment of the present invention. Detailed ways [0022] In order to make the objectives, technical solutions, and advantages of the present invention clearer, the embodiments of the present invention will be described in detail below with reference to the accompanying drawings, but the present invention can be implemented in a variety of different ways defined and covered by the claims. [0023] Cascaded H-bridge type power electronic transformers, whose topology adopts a series-in and parallel-out structure, as shown in Figure 1. The single-phase rectifiers of the front stage are connected in series to form a cascaded H bridge to achieve the role of series voltage division, and the intermediate DC capacitor voltage output by the cascaded H bridge will be used as the input power of the subsequent DAB converter; the subsequent DAB converters are connected in parallel Form the isolation stage of the power electronic transformer, achieve the role of shunting in parallel, and provide a low-voltage DC voltage output port, which can be used as a power supply port for direct external transmission To output power, you can also connect an inverter to provide an AC power port for external power supply. [0024] The present invention discloses a cascaded H-bridge type power electronic transformer transient voltage and power balance method by analyzing the root cause of the unbalanced voltage and power of the power electronic transformer. [0025] The DAB converter in the isolation stage can realize power transmission through phase shift control, and its transmission power can be calculated as 0026] Λ,λ=-Zhu·ΟL 2* [0027] In the formula, n is the transformer transformation ratio, which is the DAB converter input voltage, or the DAB converter output voltage, d is the DAB converter phase shift angle, fs is the switching frequency of the high-frequency transformer, and Lk is the leakage inductance of the high-frequency transformer value. [0028] When the transmission power of each DAB converter is balanced, the intermediate DC voltage of the power electronic transformer is also balanced. Assuming that the intermediate DC voltages Ug of the power electronic transformers are balanced in the initial stage, since the outputs of the DAB converters are connected in parallel, their output voltages may also be the same, and the switching frequency is also set to the same value. The transformer ratio and leakage inductance are determined. Transformer leakage inductance design is difficult and the error is relatively large. Therefore, when the same phase shift angle is applied, the leakage inductance difference between the DAB converters will cause the transmission power of each DAB converter to be inconsistent, and then cause the DC capacitor voltage of the power electronic transformer to be unbalanced. [0029] In order to completely solve the problem of voltage and power imbalance caused by the difference in leakage inductance parameters of the high-frequency transformer of the DAB converter, the leakage inductance parameters of each DAB converter should be compensated, and then the compensated leakage inductance parameters should be used to calculate Obtain the final phase shift angle of each DAB converter. At this time, the power electronic transformer is equivalent to achieving the same high-frequency transformer leakage inductance parameters of the DAB converter in the control algorithm, which fundamentally solves the voltage and power difference of the power electronic transformer. Balance problem. [0030] FIG. 2 is a control block diagram of a cascaded H-bridge type power electronic transformer transient voltage and power balance method provided by an embodiment of the present invention. Now, the implementation process of the present invention will be described in detail with reference to FIG. 2. [0031] A cascaded H-bridge type power electronic transformer transient voltage and power balance method, the method is divided into two parts, the first part is basic voltage control, and the second part is auxiliary balance control. [0032] The basic voltage control adopts a PI controller to perform closed-loop control of the difference between the low-voltage DC voltage setting value "* and the low-voltage DC voltage measurement value" of the power electronic transformer, so as to realize the constant voltage control of the low-voltage DC voltage. The phase shift angle obtained by the PI controller is the basic phase shift angle d of the DAB converter, and the basic phase shift angle d will participate in the calculation of the final phase shift angle of each DAB converter. [0033] The auxiliary equalization control adopts the PI controller to perform closed-loop control on the difference between the average value of the intermediate DC capacitor voltage and the intermediate DC capacitor voltage to obtain the calculated leakage inductance value of each DAB converter. The calculated leakage inductance value% Then the error between the theoretical design leakage inductance value and the actual leakage inductance value will be compensated. The error compensation can be expressed as a proportional coefficient Lki/Lkd, which will participate in the calculation of the final shift of each DAB converter: [0034] d- = 0.5 - /0.25· - y% [0035] The control system compensates for the leakage inductance error by calculating the leakage inductance parameters, and uses the compensated proportional coefficient to directly modify the basic shift ratio. The final shift ratio package of each DAB converter can be directly calculated to obtain the final shift ratio package. The phase shift adjusts the intermediate DC capacitor voltage and the transmission power of each DAB converter.
[EN US11088620B1]: Multi-level switching power converters including bypass transistors and associated methods | [EN US11088620B1]: A multi-level switching power converter includes a string of N upper transistors and a string of N lower transistors, where N is an integer greater than one. The N upper transistors are electrically coupled in series between a first power node and a switching node, and the N lower transistors are electrically coupled in series between the switching node and a reference node. The multi-level switching power converter further includes N−1 flying capacitors, an inductor, a bypass transistor, and a controller. The bypass transistor is electrically coupled between the switching node and the reference node. The controller is configured to (a) control switching of the N upper transistors and the N lower transistors and (b) cause the bypass transistor to operate in its on state in response to all of the N lower transistors operating in their respective on states. | US10734898B1 | 2020-08-04 | US201816020289A | 2018-06-27 | US201816020289A, 2018-06-27 US201762525652P, 2017-06-27 | US10734898B1: 2020-08-04 US11088620B1: 2021-08-10 | MAXIM INTEGRATED PRODUCTS | ARNOLD CORY B JERGOVIC ILIJA | H02M3/158: I H02M1/00: N H02M1/088: I | H02M3/158: I H02M1/0048: A H02M7/4837: I Y02B70/10: A H02M1/088: I | US2018097453A1 US2017244321A1 US9160232B2 US2015311822A1 US10050515B1 US10075080B1 US2016261189A1 |  | [EN US11088620B1]: 1. A multi-level switching power converter, comprising: a string of a plurality of upper transistors electrically coupled in series between a first power node and a switching node;a string of a plurality lower transistors electrically coupled in series between the switching node and a reference node;a flying capacitor connected between a node within the string of the plurality of upper transistors and a node within the string of the plurality of lower transistors;an inductor electrically coupled between the switching node and a second power node;a bypass transistor connected between the switching node and the reference node; anda controller configured to operate the switches as a DC to DC power converter by (a) control switching of the plurality of upper transistors and the plurality of lower transistors and (b) cause the bypass transistor to operate in its on state in response to all of the plurality of lower transistors operating in their respective on states. 2. The multi-level switching power converter of claim 1, wherein the controller is further configured to control switching of the plurality of upper transistors to regulate at least one of (a) magnitude of voltage at the first power node, (b) magnitude of voltage at the second power node, (c) magnitude of current flowing into the multi-level switching power converter, and (d) magnitude of current flowing out of the multi-level switching power converter. 3. The multi-level switching power converter of claim 1, wherein the controller is further configured to limit a duty cycle of the plurality of upper transistors to less than 1/N, where N is an integer equal to how many upper transistors are electrically coupled between the first power node and the switching node. 4. The multi-level switching power converter of claim 1, wherein the bypass transistor has an on-resistance that is less than a sum of respective on-resistances of the plurality of lower transistors. 5. The multi-level switching power converter of claim 1, each of the plurality of upper transistors, each of the plurality of lower transistors, and the bypass transistor being housed in a common integrated circuit package. 6. The multi-level switching power converter of claim 1, the multi-level switching power converter having a buck topology. 7. The multi-level switching power converter of claim 1, wherein the controller is further configured to cause each of the plurality of lower transistors to switch in a complementary manner with a respective one of the plurality of upper transistors. 8. The multi-level switching power converter of claim 1, the multi-level switching power converter having a boost topology. 9. The multi-level switching power converter of claim 8, wherein the controller is further configured to cause each of the plurality of upper transistors to switch in a complementary manner with a respective one of the plurality of lower transistors. 10. The multi-level switching power converter of claim 1, wherein: the plurality of upper transistors comprises: a first upper transistor electrically coupled between the first power node and a first upper node,a second upper transistor electrically coupled between the first upper node and a second upper node, anda third upper transistor electrically coupled between the second upper node and the switching node; andthe plurality of lower transistors comprises: a first lower transistor electrically coupled between the switching node and a first lower node,a second lower transistor electrically coupled between the first lower node and a second lower node, anda third lower transistor electrically coupled between the second lower node and the reference node. 11. The multi-level switching power converter of claim 1, wherein: the plurality of upper transistors comprises: a first upper transistor electrically coupled between the first power node and a first upper node, anda second upper transistor electrically coupled between the first upper node and the switching node; andthe plurality of lower transistors comprises: a first lower transistor electrically coupled between the switching node and a first lower node, anda second lower transistor electrically coupled between the first lower node and the reference node. 12. A method for operating a multi-level switching power converter, comprising: repeatedly charging and discharging at least a flying capacitor and an inductor converting one DC voltage to another DC voltage by (a) repeatedly switching at least one of a plurality of upper transistors electrically coupled in series and (b) repeatedly switching at least one of a plurality of lower transistors electrically coupled in series; andin response to all of the plurality of lower transistors operating in their respective on states, causing a bypass transistor electrically coupled in parallel with the plurality of lower transistors to operate in its on state, to provide a current path in parallel with the plurality of lower transistors. 13. The method of claim 12, further comprising transferring electric power between an input electric power source and a load. 14. The method of claim 12, wherein: the step of repeatedly switching at least one of the plurality of upper transistors comprises repeatedly switching each of the plurality of upper transistors out of phase with each other; andthe step of repeatedly switching at least one of the plurality of lower transistors comprises repeatedly switching each of the plurality of lower transistors in a complementary manner with a respective one of the plurality of upper transistors. 15. The method of claim 14, the multi-level switching power converter having a buck topology. 16. The method of claim 12, wherein: the step of repeatedly switching at least one of the plurality of lower transistors comprises repeatedly switching each of the plurality of lower transistors out of phase with each other; andthe step of repeatedly switching at least one of the plurality of upper transistors comprises repeatedly switching each of the plurality of upper transistors in a complementary manner with a respective one of the plurality of lower transistors. 17. The method of claim 16, the multi-level switching power converter have a boost topology. 18. The method of claim 12, further comprising limiting a duty cycle of the plurality of upper transistors to less than 1/N, wherein N is an integer equal to how many upper transistors are electrically coupled in series. 19. The method of claim 12, the step of causing the bypass transistor electrically coupled in parallel with the plurality of lower transistors to operate in its on state comprising switching the bypass transistor from its off state to its on state after each of the plurality of lower transistors is operating in its on state. 20. The method of claim 12, the step of causing the bypass transistor electrically coupled in parallel with the plurality of lower transistors to operate in its on state comprising switching the bypass transistor from its off state to its on state while switching one or more of the plurality of lower transistors from their respective off states to their respective on states. | [EN US11088620B1]: RELATED APPLICATIONS This application is a continuation of U.S. patent application Ser. No. 16/020,289, filed on Jun. 27, 2018, which claims benefit of priority to U.S. Provisional Patent Application Ser. No. 62/525,652, filed on Jun. 27, 2017. Each of the above-mentioned applications is incorporated herein by reference. BACKGROUND There is substantial need for switching power converters to convert high voltage to low voltage. For example, power distribution busses in enterprise-grade information technology equipment commonly operate at a relatively high voltage, such as 48 volts or 54 volts, to help minimize magnitude of current carried by these busses. Many loads in information technology equipment, however, operate at a low voltage. For instance, modern microprocessors often include a processor core that operates at a voltage of around one volt, and modern electronic memory devices typically operate at a voltage of less than two volts. Consequently, switching power converters are required in information technology equipment to convert high voltage to low voltage. As another example, automotive power distribution busses commonly operate at a nominal voltage of around 14 volts during automobile operation, and switching of automobile electrical loads may cause power distribution buss voltage to significantly exceed 14 volts for short time periods. Many automobile electrical loads, however, require a much smaller voltage, such 3.3 volts. Consequently, switching power converters are also required in automobiles to convert high voltage to low voltage. A two-level buck converter is capable of converting high voltage to low voltage. However, switching transistors in a two-level buck converter must have a high voltage rating if the two-level buck converter is to be used in high voltage applications. A transistor having a high voltage rating typically has a higher on-resistance for a given area than an otherwise identical transistor having a low voltage rating. Such high on-resistance causes significant resistive power loss at high current levels. Consequently, a two-level buck converter designed for high voltage operation will typically be less efficient at high current levels than an otherwise identical two-level buck converter designed for low-voltage operation. A multi-level buck converter can be used in place of a two-level buck converter to reduce voltage across transistors, where in this document, the term “multi-level” means three or more levels. For example, FIG. 1 illustrates a conventional four-level buck switching power converter 100 based on the Meynard topology which includes three upper transistors 102, three lower transistors 104, two flying capacitors 106, an inductor 108, an output capacitor 110, and a controller 112. In this document, specific instances of an item may be referred to by use of a numeral in parentheses (e.g., upper transistor 102(1)) while numerals without parentheses refer to any such item (e.g., upper transistors 102). Upper transistors 102 are electrically coupled in series between a power node 114 and a switching node 116, and lower transistors 104 are electrically coupled in series between switching node 116 and a reference node 118. Flying capacitor 106(1) is electrically coupled between a first upper node 122(1) and a second lower node 124(2), and flying capacitor 106(2) is electrically coupled between a second upper node 122(2) and a first lower node 124(1). Inductor 108 is electrically coupled between switching node 116 and a power node 120. An input electric power source 126 having a voltage Vin is electrically coupled between power node 114 and reference node 118, and a load 128 is electrically coupled between power node 120 and reference node 118. Controller 112 is configured to control switching of upper transistors 102 such that the upper transistors switch out of phase with each other and with a duty cycle that achieves a desired magnitude of an output voltage Vout. Controller 112 is also configured to control switching of lower transistors 104 such that each lower transistor 104 switches in a complementary manner with a respective upper transistor 102. It can be determined that maximum voltage across each upper transistor 102 and that maximum voltage across each lower transistor 104 is equal to Vin/3. Accordingly, the four-level topology of buck converter 100 enables each transistor 102 and 104 to have a significantly lower voltage rating (i.e., Vin/3) than the magnitude of input voltage Vin. BRIEF DESCRIPTION OF THE DRAWINGS FIG. 1 illustrates a conventional four-level buck switching power converter. FIG. 2 illustrates a four-level buck switching power converter including a bypass transistor, according to an embodiment. FIG. 3 shows waveforms illustrating one example of operation of an embodiment of the FIG. 2 switching power converter with a duty cycle of upper transistors being about 17%. FIG. 4 shows waveforms illustrating one example of operation of an embodiment of the FIG. 2 switching power converter with a duty cycle of upper transistors being 50%. FIG. 5 illustrates a four-level buck switching power converter like that of FIG. 2, but with lower transistors, upper transistors, and a bypass transistor housed in a common integrated circuit package, according to an embodiment. FIG. 6 illustrates a switching power converter which is like that of FIG. 2, but including two upper transistors, two lower transistors, and one flying capacitor, according to an embodiment. FIG. 7 shows waveforms illustrating one example of operation of the FIG. 6 switching power converter with a duty cycle of upper transistors being about 17%. FIG. 8 illustrates a four-level boost switching power converter including a bypass transistor, according to an embodiment. FIG. 9 shows waveforms illustrating one example of operation of the FIG. 8 switching power converter. FIG. 10 shows waveforms illustrating another example of operation of the FIG. 8 switching power converter. FIG. 11 shows waveforms illustrating yet another example of operation of the FIG. 8 switching power converter. FIG. 12 illustrates a method for operating a multi-level switching power converter, according to an embodiment. DETAILED DESCRIPTION OF THE EMBODIMENTS Applicant has determined that a conventional multi-level switching power converter may suffer from significant resistive power losses during operation at low duty cycles associated with converting high input voltage magnitude to low output voltage magnitude. For example, when conventional four-level buck converter 100 of FIG. 1 operates with a duty cycle of less than 33%, all three lower transistors 104 operate in their respective on states during three out of six sub-periods of each switching period, such that current flows through all three lower transistors for a significant portion of each switching period. The collective on-resistance of lower transistors 104 is relatively large due to their series electrical connection, and therefore, significant power is dissipated in lower transistors 104 when current of large magnitude flows through all three lower transistors 104. Accordingly, significant power is dissipated in lower transistors 104 when buck converter 100 is operating at low duty cycle and supplying an output current Iout having a large magnitude. Applicant has developed multi-level switching power converters and associated methods which at least partially overcome the problems discussed above. These multi-level switching power converters include a bypass transistor electrically coupled in parallel with the switching power converter's lower transistors, and the bypass transistor is caused to operate in its on state in response to all of the lower transistors operating in their respective on states. The bypass transistor provides a relatively low-resistance current path in parallel with the lower transistors, thereby reducing current flowing through the lower transistors and associated power dissipation in the lower transistors. In this document, a transistor is in its on state when the transistor is being controlled to be its conductive state, and a transistor is in its off state when the transistor is being controlled to be in its non-conductive state. For example, an n-channel enhancement MOSFET in its on state when a voltage above the transistor's threshold voltage is applied between the transistor's gate and source, and the transistor is in its off state when a voltage below the transistor's threshold voltage is applied between the transistor's gate and source. FIG. 2 illustrates a four-level buck switching power converter 200 including three upper transistors 202, three lower transistors 204, two flying capacitors 206, an inductor 208, an output capacitor 210, a bypass transistor 212, and a controller 214. Upper transistors 202 are electrically coupled in series between a first power node 216 and a switching node 218 to form an upper string 220. Specifically, first upper transistor 202(1) is electrically coupled between first power node 216 and a first upper node 222(1), second upper transistor 202(2) is electrically coupled between first upper node 222(1) and a second upper node 222(2), and third upper transistor 202(3) is electrically coupled between second upper node 222(2) and switching node 218. Lower transistors 204 are electrically coupled in series between switching node 218 and a reference node 224 to form a lower string 226. Specifically, first lower transistor 204(1) is electrically coupled between switching node 218 and a first lower node 228(1), second lower transistor 204(2) is electrically coupled between first lower node 228(1) and a second lower node 228(2), and third lower transistor 204(3) is electrically coupled between second lower node 228(2) and reference node 224. Although upper transistors 202, lower transistors 204, and bypass transistor 212 are shown as being n-channel enhancement MOSFETs, one or more of these transistors could be replaced with, or supplemented by, a different type of transistor, such as a p-channel enhancement MOSFET or even a bipolar junction transistor (BJT), without departing from the scope hereof. Upper transistors 202, lower transistors 204, and bypass transistor 212 can be formed of, for example, silicon, gallium nitride, and/or another semiconductor material. Each flying capacitor 206 is electrically coupled between a respective upper node 222 of upper string 220 and a respective lower node 228 of lower string 226. In particular, first flying capacitor 206(1) is electrically coupled between first upper node 222(1) and second lower node 228(2), and second flying capacitor 206(2) is electrically coupled between second upper node 222(2) and first lower node 228(1). Inductor 208 is electrically coupled between switching node 218 and a second power node 230, and output capacitor 210 is electrically coupled between second power node 230 and reference node 224. Bypass transistor 212 is electrically coupled in parallel with lower transistors 204 between switching node 218 and reference node 224. An input electric power source 232 having a voltage Vin is electrically coupled between first power node 216 and reference node 224, and a load 234 is electrically coupled between second power node 230 and reference node 224. While not required, it is anticipated that input electric power source 232 and load 234 will typically not be part of switching power converter 200. Controller 214 is configured to generate a respective upper control signal U for each upper transistor 202, to control switching of upper transistors 202 to transfer electric power from electric power source 232 to load 234. Each upper control signal U controls switching of a respective upper transistor 202. In particular, upper control signal U(1) controls switching of first upper transistor 202(1), upper control signal U(2) controls switching of second upper transistors 202(2), and upper control signal U(3) controls switching of third upper transistor 202(3). Controller 214 is also configured to generate upper control signals U such that each upper transistor 202 switches out of phase with each other upper transistor 202. For example, in certain embodiments, controller 214 generates each upper control signals U 120 degrees out of phase with each other upper control signal U, such that each upper transistor 202 switches 120 degrees out of phase with other upper transistor 202. In some embodiments, controller 214 is further configured to generate upper control signals U and thereby control switching of upper transistors 202 to regulate at least one of (a) magnitude of voltage Vin at first power node 216, (b) magnitude of voltage Vout at second power node 230, (c) magnitude of current Iin flowing into switching power converter 200, and (d) magnitude of load current Iout flowing out of switching power converter 200. Controller 214 achieves such regulation using a pulse width modulation (PWM) or a pulse frequency modulation (PFM) control technique in response to one or more of a voltage feedback signal Vfb and a current feedback signal Ifb, in certain embodiments. In some embodiments, voltage feedback signal Vfb represents magnitude of voltage Vout at second power node 230 and current feedback signal Ib represents magnitude of current I1 through inductor 208. However, voltage feedback signal Vfb and current feedback signal Ifb could be modified to represent a different voltage and current, respectively. Additionally, controller 214 could alternately be configured to achieve regulation using one or more additional or different parameters without departing from the scope hereof. Lower transistors 204 perform a freewheeling function, i.e., each lower transistor 204 provides a path for current flowing through inductor 208 when a respective upper transistor 202 switches from its on state to its off state. Accordingly, controller 214 is further configured to generate a respective lower control signal L for each lower transistor 204, to control switching of lower transistors 204 such that they perform a freewheeling function. Each lower control signal L controls switching of a respective lower transistor 204. In particular, lower control signal L(1) controls switching of first lower transistor 204(1), lower control signal L(2) controls switching of second lower transistor 204(2), and lower control signal L(3) controls switching of third lower transistor 204(3). Controller 214 is also configured to generate lower control signals L such that each lower transistor 204 switches in a complementary manner with a respective upper transistor 202. Specifically, controller 214 is configured to generate lower control signals L such that (a) first lower transistor 204(1) switches in a complementary manner with third upper transistor 202(3), (b) second lower transistor 204(2) switches in a complementary manner with second upper transistor 202(2), and (c) third lower transistor 204(3) switches in a complementary manner with first upper transistor 202(1). Controller 214 is further configured to generate a bypass control signal B to control switching of bypass transistor 212 to cause bypass transistor 212 to operate in its on state in response to all lower transistors 204 operating in their respective on states. While not required, bypass transistor 212 typically has an on-resistance, i.e., resistance of the transistor when the transistor is in its on state, that is less than a sum of respective on-resistances of lower transistors 204. In these embodiments, bypass transistor 212 provides a relatively low-resistance current path in parallel with lower transistors 204, thereby reducing current flowing through lower transistors 204 and associated power dissipation in lower transistors 204, when all lower transistors 204 are operating in their respective on states. Consequently, use of bypass transistor 212 in switching power converter 200 may enable lower transistors 204 to have a relatively high on-resistance without unduly degrading efficiency of switching power converter 200, thereby promoting low cost and small size of switching power converter 200. Each upper transistor 202 and each lower transistor 204 need only have a maximum voltage rating of Vin/3. Bypass transistor 212 need only have a maximum voltage rating of Vin/3 when duty cycle of upper transistors 202 is less than 33%. Additionally, first flying capacitor 206(1) need only have a maximum voltage of (⅔)*Vin, and second flying capacitor 206(2) need only have a maximum voltage rating of Vin/3. Flying capacitors 206 are selected, for example, to have sufficiently large capacitance values such that voltage across each flying capacitor 206 remains relatively constant, and also to have a sufficiently low equivalent series resistance (ESR) to prevent excessive heating, during anticipating operating conditions of switching power converter 200. In some embodiments, controller 214 is configured to generate bypass control signal B such that bypass transistor 212 switches from its off state to its on state while one or more of lower transistors 204 switch from their respective off states to their respective on states, such that switching of bypass transistor 212 is synchronized with switching of lower transistors 204. In some other embodiments, however, controller 214 is configured to generate bypass control signal B such that bypass transistor 212 switches at a different time than lower transistors 204. For example, in a particular embodiment, controller 214 is configured to generate bypass control signal B such that (a) bypass transistor 212 switches from its off state to its on state a first amount of time after each lower transistor 204 is operating in its on state and (b) bypass transistor 212 switches from its on state to its off state a second amount of time before one or more lower transistor 204 switches from its on state to its off state. Such offset in switching of bypass transistor 212 relative to switching of lower transistors 204 may minimize switching losses incurred during switching of bypass transistor 212. It should be appreciated that the benefits of using bypass transistor 212 are greatest at low duty cycle operation because the amount of time that first bypass transistor 212 operates in its on state is inversely proportional to upper transistor 202 duty cycle. Additionally, bypass transistor 212 will not operate in its on state if duty cycle of upper transistors is 1/N or greater, where N is the number of upper transistors 202, since all lower transistors 204 will never simultaneously be in their respective on states during this condition. Additionally, maximum voltage across bypass transistor 212 increases if duty cycle of upper transistors is 1/N or greater, thereby potentially necessitating that bypass transistor 212 has a higher voltage rating. Accordingly, in some embodiments, controller 214 is further configured to constrain duty cycle of upper transistors 202 to less than 1/N. FIG. 3 shows waveforms 300 illustrating one example of operation of switching power converter 200 with a duty cycle of upper transistors 202 being about 17%. In this example, each upper control signal U, each lower control signal L, and bypass control signal B is in it asserted state when it is logic high. Signal Vx represents voltage at switching node 218. Controller 214 generates upper control signals U such that each upper control signal is 120 degrees out of phase with each other upper control signal. Additionally, controller 214 generates lower control signals L such that each lower control signal L is asserted/de-asserted in a complementary manner with a respective upper control signal U. For example, lower control signal L(1) is de-asserted when upper control signal U(3) is asserted, and lower control signal L(1) is asserted when upper control signal U(3) is de-asserted. Controller 214 additionally asserts bypass control signal B solely when all of lower control signals L are asserted, such that bypass transistor 212 is in its on state solely when all of lower transistors 204 are in their respective on states. Consequently, bypass transistor 212 is on in each of sub-periods tsp2, tsp4, and tsp6 of period T. First flying capacitor 206(1) is charged during sub-period tsp1 and discharged during sub-period tsp3, and second flying capacitors 206(2) is charged during sub-period tsp3 and discharged during sub-period tsp5. Inductor 208 is charged during sub-periods tsp1, tsp3, and tsp5, and inductor 208 is discharged during sub-periods tsp2, tsp4, and tsp6. For comparison purposes, FIG. 4 shows waveforms 400 illustrating one example of operation of an embodiment where controller 214 permits operation at duty cycles of upper transistors 202 greater than or equal to 33%. Duty cycle is 50% in this example, and as can be observed, there is no sub-period within period T where all of lower signals L are asserted. Consequently, bypass control signal B is never asserted in this example. In certain embodiments of switching power converter 200, two or more components of the switching power converter are co-packaged. For example, FIG. 5 illustrates a four-level buck switching power converter 500 which is like switching power converter 200 of FIG. 2, but with lower transistors 202, upper transistors 204, and bypass transistor 212 housed in a common integrated circuit package 502. The transistors are not shown in FIG. 5 to promote clarity. In some embodiments, lower transistors 202, upper transistors 204, and bypass transistor 212 are formed on a common silicon substrate 504 within integrated circuit package 502. Presence of bypass transistor 212 in switching power converter 500 may enable size of silicon substrate 504 to be reduced without reducing efficiency, relative to an otherwise identical version of switching power converter 500 without bypass transistor 212. Alternately or additionally, presence of bypass transistor 212 in switching power converter 500 may enable efficiency to be increased relative to an otherwise identical version of switching power converter 500 without bypass transistor 212 by reducing resistive dissipation in lower transistors 204, in a manner analogous to that discussed above with respect to FIG. 2. In certain alternate embodiments, one or more of controller 214, flying capacitors 206, and inductor 208 are additionally housed in integrated circuit package 502. Although switching power converter 200 includes three upper transistors 202, three lower transistors 204, and two flying capacitors 206, the number of each of these elements could be varied without departing from the scope hereof. In particular, switching power converter 200 could be modified to have N upper transistors, N lower transistors, and N−1 flying capacitors, where N is an integer greater than one. For example, FIG. 6 illustrates a switching power converter 600 which is like switching power converter 200 of FIG. 2, but where N is two, such that switching power converter 600 includes two upper transistors 202, two lower transistors 204, and one flying capacitor 206. FIG. 7 shows waveforms 700 illustrating one example of operation of switching power converter 600 with duty cycle of upper transistors 202 being about 17%. Each period T only includes four sub-periods tsp1 through tsp4, instead of the six sub-periods of FIGS. 3 and 4, due switching power converter 600 including two upper transistors 202 instead of four upper transistors 202. Controller 214 asserts bypass control signal B to cause bypass transistor 212 to operate in its on state during each of sub-periods tsp2 and tsp4, corresponding to when all of the lower transistors 204 are in their respective on states. The multi-level switching power converters disclosed herein could be modified to have a boost topology, instead of a buck topology. For example, FIG. 8 illustrates a four-level boost switching power converter 800 including three upper transistors 802, three lower transistors 804, two flying capacitors 806, an inductor 808, an output capacitor 810, a bypass transistor 812, and a controller 814. Upper transistors 802 are electrically coupled in series between a first power node 816 and a switching node 818 to form an upper string 820. Specifically, first upper transistor 802(1) is electrically coupled between first power node 816 and a first upper node 822(1), second upper transistor 802(2) is electrically coupled between first upper node 822(1) and a second upper node 822(2), and third upper transistor 802(3) is electrically coupled between second upper node 822(2) and switching node 818. Lower transistors 804 are electrically coupled in series between switching node 818 and a reference node 824 to form a lower string 826. Specifically, first lower transistor 804(1) is electrically coupled between switching node 818 and a first lower node 828(1), second lower transistor 804(2) is electrically coupled between first lower node 828(1) and a second lower node 828(2), and third lower transistor 804(3) is electrically coupled between second lower node 828(2) and reference node 824. Although upper transistors 802, lower transistors 804, and bypass transistor 812 are shown as being n-channel enhancement MOSFETs, one or more of these transistors could be replaced with, or supplemented by, a different type of transistor, such as a p-channel enhancement MOSFET or even a bipolar junction transistor (BJT), without departing from the scope hereof. Each flying capacitor 806 is electrically coupled between a respective upper node 822 of upper string 820 and a respective lower node 828 of lower string 826. In particular, first flying capacitor 806(1) is electrically coupled between first upper node 822(1) and second lower node 828(2), and second flying capacitor 806(2) is electrically coupled between second upper node 822(2) and first lower node 828(1). Inductor 808 is electrically coupled between switching node 818 and a second power node 830, and output capacitor 810 is electrically coupled between first power node 816 and reference node 824. Bypass transistor 812 is electrically coupled in parallel with lower transistors 804 between switching node 818 and reference node 824. An input electric power source 832 having a voltage Vin is electrically coupled between second power node 830 and reference node 824, and a load 834 is electrically coupled between first power node 816 and reference node 824. While not required, it is anticipated that input electric power source 832 and load 834 will typically not be part of switching power converter 800. Controller 814 is configured to generate a respective lower control signal L for each lower transistor 804, to control switching of lower transistors 804. Each lower control signal L controls switching of a respective lower transistor 804 to transfer electric power from input electric power source 832 to load 834. In particular, lower control signal L(1) controls switching of first lower transistor 804(1), lower control signal L(2) controls switching of second lower transistor 804(2), and lower control signal L(3) controls switching of third lower transistor 804(3). Controller 814 is also configured to generate lower control signals L such that each lower transistor 804 switches out of phase with each other lower transistor 804. For example, in certain embodiments, controller 814 generates each lower control signals L 120 degrees out of phase with each other lower control signal L, such that each lower transistor 804 switches 120 degrees out of phase with other lower transistor 804. In some embodiments, controller 814 is further configured to generate lower control signals L and thereby control switching of lower transistors 804 to regulate at least one of (a) magnitude of voltage Vin at second power node 830, (b) magnitude of voltage Vout at first power node 816, (c) magnitude of current Lin flowing into switching power converter 800, and (d) magnitude of load current Iout flowing out of switching power converter 800. Controller 814 achieves such regulation using a PWM or a PFM control technique in response to one or more of a voltage feedback signal Vfb and a current feedback signal Ifb, in certain embodiments. In some embodiments, voltage feedback signal Vfb represents magnitude of voltage Vout at first power node 816 and current feedback signal Ifb represents magnitude of current I1 through inductor 808. However, voltage feedback signal Vfb and current feedback signal Ifb could be modified to represent a different voltage and current, respectively. Additionally, controller 814 could alternately be configured to achieve regulation using one or more additional or different parameters without departing from the scope hereof. Upper transistors 802 perform a freewheeling function, i.e., each upper transistor 802 provides a path for current flowing through inductor 808 when a respective lower transistor 804 switches from its on state to its off state. Accordingly, controller 814 is further configured to generate a respective upper control signal U for each upper transistor 802, to control switching of upper transistors 802 such that they perform a freewheeling function. Each upper control signal U controls switching of a respective upper transistor 802. In particular, upper control signal U(1) controls switching of first upper transistor 802(1), upper control signal U(2) controls switching of second upper transistors 802(2), and upper control signal U(3) controls switching of third upper transistor 802(3). Controller 814 is also configured to generate upper control signals U such that each upper transistor 802 switches in a complementary manner with a respective lower transistor 804, except when lower transistors 804 continuously operate in their respective on states, as discussed below. Specifically, controller 814 is configured to generate upper control signals U such that (a) first upper transistor 802(1) switches in a complementary manner with third lower transistor 804(3), (b) second upper transistor 802(2) switches in a complementary manner with second lower transistor 804(2), and (c) third upper transistor 802(3) switches in a complementary manner with first lower transistor 804(1). Controller 814 is further configured to generate a bypass control signal B to control switching of bypass transistor 812 to cause bypass transistor 812 to operate in its on state in response to all lower transistors 804 operating in their on state. While not required, bypass transistor 812 typically has an on-resistance that is less than a sum of respective on-resistances of lower transistors 804. In these embodiments, bypass transistor 812 provides a relatively low-resistance current path in parallel with lower transistors 804, thereby reducing current flowing through lower transistors 804 and associated power dissipation in lower transistors 804, when all lower transistors 804 are operating in their respective on states. Consequently, use of bypass transistor 812 in switching power converter 800 may enable lower transistors 804 to have a relatively high on-resistance without unduly degrading efficiency of switching power converter 800, thereby promoting low cost and small size of switching power converter 800. In some embodiments, controller 814 is configured to generate bypass control signal B such that bypass transistor 812 switches from its off state to its on state while one or more of lower transistors 804 switch from their respective off states to their respective on states, such that switching of bypass transistor 812 is synchronized with switching of lower transistors 804. In some other embodiments, however, controller 814 is configured to generate bypass control signal B such that bypass transistor 812 switches at a different time than lower transistors 804. For example, in a particular embodiment, controller 814 is configured to generate bypass control signal B such that (a) bypass transistor 812 switches from its off state to its on state a first amount of time after each lower transistor 804 is operating in its on state and (b) bypass transistor 812 switches from its on state to its off state a second amount of time before one or more lower transistor 804 switches from its on state to its off s
[ZH CN111917316B]: 基于模块化多电平换流器集中控制下子模块温度调节与平衡方法 [EN CN111917316B]: Sub-module temperature adjustment and balance method under centralized control based on modular multilevel converter | [ZH CN111917316B]: 本发明公开了基于模块化多电平换流器集中控制下子模块温度调节与平衡方法，步骤：采集各子模块散热器的温度，桥臂电流，桥臂上各子模块的电容电压以及开关函数；根据采集数据计算各子模块的平均结温，根据平均结温计算各子模块的虚拟电压偏置系数；根据各子模块的虚拟电压偏置系数计算各子模块的虚拟电容电压，根据虚拟电容电压对桥臂内子模块进行升序排序并建立子模块索引列表；通过对参考信号进行调制实时确定所需导通的子模块个数，再根据子模块索引表和桥臂电流方向，实时确定应当导通的子模块，从而达到桥臂内子模块的温度平衡。本发明既不受限于子模块个数，也不会影响变换器并网的电能质量，控制算法简单，易于理解和实施。 [EN CN111917316B]: The invention discloses a sub-module temperature adjusting and balancing method based on centralized control of a modular multilevel converter. The method comprises the steps: collecting the temperature and bridge arm current of a radiator of each sub-module, the capacitor voltage of each sub-module on a bridge arm and a switching function; calculating the average junction temperature of each sub-module according to the acquired data, and calculating the virtual voltage bias coefficient of each sub-module according to the average junction temperature; calculating the virtual capacitor voltageof each sub-module according to the virtual voltage bias coefficient of each sub-module, performing ascending sorting on the sub-modules in the bridge arm according to the virtual capacitor voltage, and establishing a sub-module index list; determining the number of the sub-modules needing to be conducted in real time by modulating the reference signal, and determining the sub-modules needing to be conducted in real time according to the sub-module index table and the bridge arm current direction, so temperature balance of the sub-modules in the bridge arm is achieved. The method is not limited by the number of sub-modules, does not affect the grid-connected power quality of the converter, is simple in control algorithm, and is easy to understand and implement. | CN111917316B | 2020-11-10 2021-07-20 | CN202010502592A | 2020-06-04 2020-06-04 | CN202010502592A, 2020-06-04 CN202010502592A, 2020-06-04 | CN111917316B: 2021-07-20 | UNIV SOUTHEAST STATE GRID JIANGSU ELECTRIC POWER CO RES INST STATE GRID CORP CHINA 东南大学 国网江苏省电力有限公司电力科学研究院 国家电网有限公司 | DENG FUJIN ZHAO JIFENG ZHANG JIANZHONG WANG QINGSONG DOU XIAOBO WU ZAIJUN CHEN SHU | H02M7/483: I H02J3/36: I H02M1/32: I H02M7/5387: I | H02J3/36: I H02M1/32: I H02M7/483: I H02M7/5387: I H02M1/327: A Y02E60/60: A | US2015288287A1 CN108155814A CN108933535A CN109742961A CN109980981A CN110289779A CN110880785A |  | [ZH CN111917316B]: 1.基于模块化多电平换流器集中控制下子模块温度调节与平衡方法，其特征在于，包 括以下步骤： ⑴采集各个子模块散热器的温度，桥臂电流，桥臂上各个子模块的电容电压以及开关 函数； ⑵根据步骤⑴采集的数据计算各个子模块的平均结温，根据平均结温计算各个子模 块的虚拟电压偏置系数； 所述虚拟电压偏置系数按下式计算： ki=Ucauave-Vref ((y1)/(Rthjhi) -Pconave) 上式中，飞为第i个子模块的虚拟电压偏置系数，υοαυα4νΕ,Τ撩Τ^Ι^Μ,Ροοηχ分别为 子模块电容电压平均值、开关器件手册中开关能耗的测试电压、桥臂内子模块的平均结温、 散热片温度、第i个子模块的热阻、桥臂内子模快的平均导通损耗； (3)根据各个子模块的虚拟电压偏置系数计算各个子模块的虚拟电容电压，根据虚拟 电容电压对桥臂内子模块进行升序排序并建立子模块索引列表； (4)通过对参考信号进行调制实时确定所需导通的子模块个数，再根据子模块索引表 和桥臂电流方向，实时确定应当导通的子模块，从而达到桥臂内子模块的温度平衡。 2 .根据权利要求1所述基于模块化多电平换流器集中控制下子模块温度调节与平衡方 法，其特征在于，在步骤⑶中，所述虚拟电容电压按下式计算： U' caui = ki+Ucaui 上式中，u' caui为第i个子模块的虚拟电容电压，ki为第i个子模块的虚拟电压偏置系数， Ucaui为第i个子模块的电容电压。 3 .根据权利要求1所述基于模块化多电平换流器集中控制下子模块温度调节与平衡方 法，其特征在于，在步骤⑷中，首先，根据有功功率控制、无功功率控制以及环流抑制控制 算法确定调制波;其次，经过调制得到桥臂上应投入的子模块个数n0n ；最后，结合桥臂内子 模块虚拟电容电压和桥臂电流方向，实时确定应当导通的子模块，当桥臂电流为正，投入虚 拟电容电压最低的n0n个子模块，当桥臂电流为负，投入虚拟电容电压最高的n0n个子模块。 [EN CN111917316B]: 1. The temperature adjustment and balance method of sub-modules based on the centralized control of modular multi-level converters is characterized by including the following steps: (1) Collect the temperature of each sub-module radiator, the current of the bridge arm, and the temperature of each sub-module on the bridge arm. Capacitor voltage and switching function; (2) Calculate the average junction temperature of each sub-module according to the data collected in step (1), and calculate the virtual voltage bias coefficient of each sub-module according to the average junction temperature; The virtual voltage bias coefficient is calculated as follows: ki=Ucauave-Vref ((y1)/(Rthjhi)-Pconave) In the above formula, Fei is the virtual voltage bias coefficient of the i-th submodule, υοαυα4νΕ,ΤteaseΤ^Ι^Μ, Pοοηχ are the average value of the capacitor voltage of the submodule, the test voltage of the switching energy consumption in the switching device manual, The average junction temperature of the sub-modules in the bridge arm, the heat sink temperature, the thermal resistance of the i-th sub-module, and the average conduction loss of the sub-modules in the bridge arm; Virtual capacitor voltage, according to the virtual capacitor voltage, sort the sub-modules in the bridge arm in ascending order and establish a sub-module index list; (4) Determine the number of sub-modules that need to be turned on in real time by modulating the reference signal, and then according to the sub-module index table And the current direction of the bridge arm, the sub-modules that should be turned on are determined in real time, so as to achieve the temperature balance of the sub-modules in the bridge arm. 2 The method for temperature adjustment and balance of sub-modules based on the centralized control of modular multilevel converters according to claim 1, characterized in that, in step (3), the virtual capacitor voltage is calculated as follows: U'caui = ki+Ucaui In the above formula, u' cauiIs the virtual capacitor voltage of the i-th sub-module, ki is the virtual voltage bias coefficient of the i-th sub-module, UcauiIs the capacitor voltage of the i-th sub-module. 3 The method for temperature adjustment and balance of sub-modules based on the centralized control of modular multilevel converters according to claim 1, characterized in that, in step (4), first, according to active power control, reactive power control and circulating current suppression control The algorithm determines the modulation wave; secondly, the number of sub-modules that should be put on the bridge arm n is obtained after modulation0n ; Finally, combining the virtual capacitor voltage of the sub-module in the bridge arm and the direction of the bridge arm current, determine the sub-module that should be turned on in real time. When the bridge arm current is positive, the lowest virtual capacitor voltage n0nSub-modules, when the bridge arm current is negative, input the highest virtual capacitor voltage n0nSub-modules. | [ZH CN111917316B]: 基于模块化多电平换流器集中控制下子模块温度调节与平衡 方法 技术领域 [0001]本发明属于多电平电力电子变换器技术领域。 背景技术 [0002]模块化多电平变换器已经成为高压直流输电技术应用中非常有前景的拓扑。与传 统的两电平和三电平电压源变换器相比，模块化多电平变换器由于每个桥臂内级联子模块 的结构不需要串联功率器件的特点，模块化多电平变换器在高压传输系统当中引起了人们 也来越多的关注。 [0003]除了效率之外，大功率变换器的可靠运行也是一个关键的指标，功率器件对变换 器的可靠性起着重要的作用。模块化多电平变换器包含许多子模块，每个子模块包括多个 功率器件。在过载、子模块长期运行导致的参数不匹配或部分冷却装置失效的情况下，可能 会导致一个或者多个子模块之间的较大的温度差异。由于在电力电子变换器中功率器件被 认为是最容易失效的，功率半导体的失效主要是由过热引起，所以子模块中功率器件的较 大的温度差异会给模块化多电平变换器的安全可靠运行造成一个巨大的威胁。 [0004]针对模块化多电平变换器子模块功率开关管的温度平衡调节控制问题，现有技术 通过改变变换器开关管的开关频率、调节无功、通过驱动信号连续脉宽调制和非连续脉宽 调制之间的切换策略、改变门极驱动电压等方法来调节子模块之间的温度，但是上述方法 会增加硬件系统和算法的复杂度，影响电能的输出质量，增大系统的运行成本。因此，需要 提出一种新的模块化多电平变换器子模块的温度平衡控制方法，一方面保证不影响电能质 量输出性能的前提下不增加系统的硬件系统和算法的复杂度，另一方面保证系统的成本不 增加的前提下实现模块化多电平变换器的安全可靠运行。 发明内容 [0005]为了解决上述背景技术提到的技术问题，本发明提出了基于模块化多电平换流器 集中控制下子模块温度调节与平衡方法。 [0006]为了实现上述技术目的，本发明的技术方案为： [0007]基于模块化多电平换流器集中控制下子模块温度调节与平衡方法，包括以下步 骤： [0008] ⑴采集各个子模块散热器的温度，桥臂电流，桥臂上各个子模块的电容电压以及 开关函数； [0009] ⑵根据步骤⑴采集的数据计算各个子模块的平均结温，根据平均结温计算各个 子模块的虚拟电压偏置系数； [0010] ⑶根据各个子模块的虚拟电压偏置系数计算各个子模块的虚拟电容电压，根据 虚拟电容电压对桥臂内子模块进行升序排序并建立子模块索引列表； [0011] (4)通过对参考信号进行调制实时确定所需导通的子模块个数，再根据子模块索 引表和桥臂电流方向，实时确定应当导通的子模块，从而达到桥臂内子模块的温度平衡。 [0012] 进一步地，在步骤⑵中，所述虚拟电压偏置系数按下式计算： [0013] ki = UcauaVe-Vref ((^1)/(%m)弋…) [0014]上式中，&amp;为第i个子模块的虚拟电压偏置系数，*uave、Vref、Tjm、Th、Rthjhi、Pconave分 别为子模块电容电压平均值、开关器件手册中开关能耗的测试电压、桥臂内子模块的平均 结温、散热片温度、第i个子模块的热阻、桥臂内子模快的平均导通损耗。 [0015] 进一步地，在步骤(3)中，所述虚拟电容电压按下式计算： [0016] U，caui = ki+Ucaui [0017]上式中，u,caui为第i个子模块的虚拟电容电压，&amp;为第i个子模块的虚拟电压偏置 系数，ucaui为第i个子模块的电容电压。 [0018] 进一步地，在步骤⑷中，首先，根据有功功率控制、无功功率控制以及环流抑制控 制算法确定调制波;其次，经过调制得到桥臂上应投入的子模块个数n0n ；最后，结合桥臂内 子模块虚拟电容电压和桥臂电流方向，实时确定应当导通的子模块，当桥臂电流为正，投入 虚拟电容电压最低的n0n个子模块，当桥臂电流为负，投入虚拟电容电压最高的n0n个子模 块。 [0019]采用上述技术方案带来的有益效果： [0020] 1、本发明对拓扑和工况的适应性广，实用价值高:现有技术中通过调节无功环流 来补偿并联变换器之间的温度差，但是这种方法仅适用于并联变换器的结构配置;现有技 术中利用冗余的子模块主动旁路加中性点偏移来调节子模块的温度，但该方法仅限于带有 并联晶闸管的子模块结构和不平衡电网条件下。相对于以上两种技术，本发明适用于任意 拓扑和任意工况下的桥臂内子模块的温度平衡。 [0021] 2、本发明算法简单，计算方便，易于理解和实施:通过引入虚拟电压偏置系数，平 衡由虚拟电压偏置系数产生的虚拟电容电压，使各自模块温度达到一致。一方面，所提出的 控制算法基于老化的功率器件，而子模块的功率器件老化速度通常非常缓慢，这意味着不 需要在每个控制周期都更新虚拟电压偏置系数，从而简化了计算并减少了计算量;另一方 面虚拟电压偏置系数与各个子模块的温度呈现明确的对应关系，虚拟电压偏置系数取值方 便，计算简单。 [0022] 3、本发明不需要对硬件电路做任何改动，没有造成系统的硬件复杂性和系统成本 的增加。 [0023] 4、本发明在保证不影响电能质量输出性能的前提下实现模块化多电平变换器的 安全可靠运行。 附图说明 [0024]图1是三相MMC及子模块拓扑结构图； [0025]图2是本发明设计的方法流程图。 具体实施方式 [0026]以下将结合附图，对本发明的技术方案进行详细说明。 [0027]本发明针对子模块功率器件热阻老化导致的子模块温度分布不均问题，提出了适 用于MMC的子模块温度调节与平衡方法，其中MMC拓扑结构由六个桥臂组成，如图1所示，每 个桥臂上包含了n个相同的子模块(Submodule，SM)以及一个桥臂电感Ls，子模块采用半桥 结构，每个子模块由两个功率开关TrT2,两个二极管DrD2和一个直流电容组成，电容电压 平衡方法为:根据桥臂参考电压与载波比较得到一个桥臂上需要投入的子模块个数为n0n， 对前述所得虚拟电容电压进行升序排序，当桥臂电流为正，投入虚拟电容电压最低的n0n个 子模块，当桥臂电流为负，投入虚拟电容电压最高的n0n个子模块。 [0028]本发明设计的基于基于模块化多电平换流器集中控制下子模块温度调节与平衡 方法，如图2所示，步骤如下： [0029]步骤1：采集各个子模块散热器的温度，桥臂电流iarm，桥臂上各个子模块的电容电 压Ucaui以及开关函数Saui。 [0030]步骤2：根据步骤1采集的数据计算各个子模块的平均结温，根据平均结温计算各 个子模块的虚拟电压偏置系数。 [0031] 在本实施例中，优选采用如下方法计算虚拟电压偏置系数： [0032]『ucauaveHef ((^^)/(忆如)Ronav) [0033]上式中，&amp;为第i个子模块的虚拟电压偏置系数，ucauave、Vref、Tjm、Th、Rthjhi、Pconave分 别为子模块电容电压平均值、开关器件手册中开关能耗的测试电压、桥臂内子模块的平均 结温、散热片温度、第i个子模块的热阻、桥臂内子模快的平均导通损耗。 [0034]步骤3：根据各个子模块的虚拟电压偏置系数计算各个子模块的虚拟电容电压，根 据虚拟电容电压对桥臂内子模块进行升序排序并建立子模块索引列表。 [0035] 在本实施例中，优选采用如下方法计算虚拟电容电压： [0036] u'caui = ki+ucaui [0037]上式中，u’caui为第i个子模块的虚拟电容电压，&amp;为第i个子模块的虚拟电压偏置 系数，ucaui为第i个子模块的电容电压。 [0038]步骤4：通过对参考信号进行调制实时确定所需导通的子模块个数，再根据子模块 索引表和桥臂电流方向，实时确定应当导通的子模块，从而达到桥臂内子模块的温度平衡。 [0039]具体地，首先，根据有功功率控制、无功功率控制以及环流抑制控制算法确定调制 波yau ；其次，经过调制得到桥臂上应投入的子模块个数n0n ；最后，结合桥臂内子模块虚拟电 容电压和桥臂电流方向，实时确定应当导通的子模块，当桥臂电流为正，投入虚拟电容电压 最低的n0n个子模块，当桥臂电流为负，投入虚拟电容电压最高的n0n个子模块。 [0040]本发明尤其适用于子模块数目众多的MMC系统，与传统的温度平衡方法相比，一方 面保证不影响电能质量输出性能的前提下不增加系统的硬件系统和算法的复杂度，另一方 面保证系统的成本不增加的前提下实现模块化多电平变换器的安全可靠运行。 [0041]实施例仅为说明本发明的技术思想，不能以此限定本发明的保护范围，凡是按照 本发明提出的技术思想，在技术方案基础上所做的任何改动，均落入本发明保护范围之内。 CN 111917316 Β [EN CN111917316B]: Technical field of sub-module temperature adjustment and balance method under centralized control of modular multilevel converter [0001] The present invention belongs to the technical field of multi-level power electronic converters. Background technique [0002] Modular multilevel converters have become a very promising topology in the application of HVDC technology. Compared with traditional two-level and three-level voltage source converters, modular multi-level converters do not require series power devices due to the structure of cascaded sub-modules in each bridge arm. Modular multi-level converters It has attracted more and more attention in the high-voltage transmission system. [0003] In addition to efficiency, the reliable operation of a high-power converter is also a key indicator, and power devices play an important role in the reliability of the converter. The modular multilevel converter contains many sub-modules, and each sub-module includes multiple power devices. In the case of overload, parameter mismatch caused by long-term operation of sub-modules, or failure of part of the cooling device, a large temperature difference between one or more sub-modules may be caused. Since power devices are considered to be the most prone to failure in power electronic converters, the failure of power semiconductors is mainly caused by overheating, so the large temperature difference of the power devices in the sub-modules will give the modular multilevel converter safety Reliable operation poses a huge threat. [0004] In view of the temperature balance adjustment control problem of the power switch tube of the modular multilevel converter sub-module, the prior art changes the switching frequency of the converter switch tube, adjusts the reactive power, and drives the signal continuous pulse width modulation and discontinuous The switching strategy between pulse width modulation, changing the gate drive voltage and other methods to adjust the temperature between the sub-modules, but the above methods will increase the complexity of the hardware system and algorithm, affect the output quality of power, and increase the operating cost of the system . Therefore, a new temperature balance control method for modular multilevel converter sub-modules needs to be proposed. On the one hand, it does not increase the complexity of the hardware system and algorithm of the system without affecting the power quality output performance. On the other hand, The safe and reliable operation of the modular multilevel converter can be realized without increasing the cost of the system. Summary of the invention [0005] In order to solve the technical problems mentioned in the above background art, the present invention proposes a temperature adjustment and balance method for sub-modules based on the centralized control of a modular multilevel converter. [0006] In order to achieve the above technical objectives, the technical solution of the present invention is: [0007] The temperature adjustment and balance method of sub-modules based on the centralized control of the modular multilevel converter includes the following steps: [0008] Collect the temperature of each sub-module radiator, the current of the bridge arm, the capacitor voltage of each sub-module on the bridge arm, and the switching function; [0009] (2) Calculate the average junction temperature of each sub-module according to the data collected in step (1), and calculate the virtual voltage bias coefficient of each sub-module according to the average junction temperature; [0010] Calculate the virtual capacitor voltage of each sub-module according to the virtual voltage bias coefficient of each sub-module, sort the sub-modules in the bridge arm in ascending order according to the virtual capacitor voltage and establish a sub-module index list; [0011] (4) Determine the number of sub-modules that need to be turned on in real time by modulating the reference signal, and then according to the sub-module search Lead the meter and the current direction of the bridge arm, and determine the sub-modules that should be turned on in real time, so as to achieve the temperature balance of the sub-modules in the bridge arm. [0012] Further, in step (2), the virtual voltage offset coefficient is calculated as follows: [0013] ki = UcauaVeVref ((^1)/(%m)Yi...) [0014]In the above formula, &amp; is the virtual voltage bias coefficient of the i-th submodule, *uave, Vref, Tjm, Th, Rthjhi, and Pconave are the average value of the capacitor voltage of the submodule, the test voltage of the switching energy consumption in the switching device manual, and the bridge The average junction temperature of the sub-module in the arm, the temperature of the heat sink, the thermal resistance of the i-th sub-module, and the average conduction loss of the sub-module in the bridge arm. [0015] Further, in step (3), the virtual capacitor voltage is calculated as follows: [0016] U,caui = ki+Ucaui [0017] In the above formula, u,cauiIs the virtual capacitor voltage of the i-th sub-module, &amp; is the virtual voltage bias coefficient of the i-th sub-module, ucauiIs the capacitor voltage of the i-th sub-module. [0018] Further, in step (4), firstly, the modulation wave is determined according to the active power control, reactive power control, and circulating current suppression control algorithm; secondly, the number of sub-modules that should be put on the bridge arm n is obtained through modulation.0n ; Finally, combining the virtual capacitor voltage of the sub-module in the bridge arm and the direction of the bridge arm current, determine the sub-module that should be turned on in real time. When the bridge arm current is positive, the lowest virtual capacitor voltage n0nSub-modules, when the bridge arm current is negative, input the highest virtual capacitor voltage n0nSub-modules. [0019] The beneficial effects brought about by the above technical solutions: [0020] 1. The present invention has wide adaptability to topology and working conditions, and has high practical value: in the prior art, the temperature difference between parallel converters is compensated by adjusting the reactive power circulating current, but this method is only suitable for parallel conversion The structure configuration of the device; in the prior art, the redundant sub-module active bypass plus neutral point offset is used to adjust the temperature of the sub-module, but this method is limited to the sub-module structure with parallel thyristors and unbalanced power grid conditions . Compared with the above two technologies, the present invention is suitable for the temperature balance of the sub-modules in the bridge arm under any topology and any working conditions. [0021] 2. The algorithm of the present invention is simple, easy to calculate, easy to understand and implement: by introducing a virtual voltage bias coefficient, the virtual capacitor voltage generated by the virtual voltage bias coefficient is balanced, so that the respective module temperatures are consistent. On the one hand, the proposed control algorithm is based on aging power devices, and the aging speed of the power devices of the sub-modules is usually very slow, which means that there is no need to update the virtual voltage bias coefficient in each control cycle, which simplifies the calculation and reduces On the other hand, the virtual voltage bias coefficient and the temperature of each sub-module show a clear correspondence relationship, the virtual voltage bias coefficient is convenient to take, and the calculation is simple. [0022] 3. The present invention does not need to make any changes to the hardware circuit, and does not cause the hardware complexity of the system and the increase of the system cost. [0023] 4. The present invention realizes the safe and reliable operation of the modular multilevel converter under the premise of ensuring that the power quality output performance is not affected. Description of the drawings [0024] FIG. 1 is a topological structure diagram of a three-phase MMC and sub-modules; [0025] FIG. 2 is a flowchart of a method designed by the present invention. Detailed ways [0026] The technical solution of the present invention will be described in detail below in conjunction with the accompanying drawings. [0027] In view of the uneven temperature distribution of the sub-modules caused by the aging of the thermal resistance of the sub-module power devices, the present invention proposes a suitable The sub-module temperature adjustment and balance method used for MMC, in which the MMC topology is composed of six bridge arms, as shown in Figure 1, each bridge arm contains n identical sub-modules (Submodule, SM) and a bridge Arm inductance Ls, The sub-module adopts a half-bridge structure, and each sub-module consists of two power switches TrT2, Two diodes DrD2It is composed of a DC capacitor, and the capacitor voltage balance method is: According to the comparison of the reference voltage of the bridge arm and the carrier, the number of sub-modules that need to be input on a bridge arm is n0n, Perform the ascending order of the virtual capacitor voltages obtained above, when the bridge arm current is positive, put in the n with the lowest virtual capacitor voltage0nSub-modules, when the bridge arm current is negative, input the highest virtual capacitor voltage n0nSub-modules. [0028] The temperature adjustment and balance method of sub-modules based on the centralized control of modular multi-level converters designed in the present invention is shown in Figure 2, and the steps are as follows: [0029] Step 1: Collect the temperature of each sub-module radiator, the bridge arm current iarm, The capacitance voltage Ucaui of each sub-module on the bridge arm and the switching function Saui. [0030] Step 2: Calculate the average junction temperature of each sub-module according to the data collected in Step 1, and calculate the virtual voltage bias coefficient of each sub-module according to the average junction temperature. [0031] In this embodiment, the following method is preferably used to calculate the virtual voltage offset coefficient: [0032]UcauaveHef ((^^)/(Reminiscence)Ronav) [0033]In the above formula, &amp; is the virtual voltage bias coefficient of the i-th submodule, ucauave, Vref, Tjm, Th, Rthjhi, and Pconave are the average value of the capacitor voltage of the submodule, the test voltage of the switching energy consumption in the switching device manual, and the bridge arm. The average junction temperature of the inner submodule, the temperature of the heat sink, the thermal resistance of the i-th submodule, and the average conduction loss of the submodule in the bridge arm. [0034] Step 3: Calculate the virtual capacitor voltage of each sub-module according to the virtual voltage bias coefficient of each sub-module, sort the sub-modules in the bridge arm in ascending order according to the virtual capacitor voltage and establish a sub-module index list. [0035] In this embodiment, the following method is preferably used to calculate the virtual capacitor voltage: [0036] u'caui = ki+ucaui [0037] In the above formula, u'cauiIs the virtual capacitor voltage of the i-th sub-module, &amp; is the virtual voltage bias coefficient of the i-th sub-module, ucauiIs the capacitor voltage of the i-th sub-module. [0038] Step 4: Determine the number of sub-modules that need to be turned on in real time by modulating the reference signal, and then determine the sub-modules that should be turned on in real time according to the sub-module index table and the direction of the bridge arm current, so as to reach the sub-modules in the bridge arm. The temperature balance of the module. [0039] Specifically, first, the modulation wave y is determined according to the active power control, the reactive power control, and the circulating current suppression control algorithm.au ; Secondly, the number of sub-modules that should be put into the bridge arm n is obtained after modulation0n ; Finally, combining the virtual capacitor voltage of the sub-module in the bridge arm and the direction of the bridge arm current, determine the sub-module that should be turned on in real time. When the bridge arm current is positive, the lowest virtual capacitor voltage n0nSub-modules, when the bridge arm current is negative, input the highest virtual capacitor voltage n0nSub-modules. [0040] The present invention is especially suitable for MMC systems with a large number of sub-modules. Compared with the traditional temperature balance method, on the one hand, it does not increase the complexity of the hardware system and algorithm of the system without affecting the power quality output performance, and on the other hand, On the one hand, the safe and reliable operation of the modular multilevel converter can be realized without increasing the cost of the system. [0041] The embodiments are only to illustrate the technical ideas of the present invention, and cannot be used to limit the scope of protection of the present invention. Any changes made on the basis of the technical solutions according to the technical ideas of the present invention shall fall into the protection of the present invention. Within range. CN 111917316 Β
[DE DE102020200927A1]: Hybrid-Mehrpegel-Leistungsumsetzer mit lnduktor zwischen Stufen [EN US2021234462A1]: Hybrid Multi-Level Power Converter with Inter-Stage Inductor | [DE DE102020200927A1]: Das vorliegende Dokument bezieht sich auf einen Leistungsumsetzer mit einem Induktor, einer ersten Stufe und einer zweiten Stufe. Die erste Stufe kann zwischen einen Eingang des Leistungsumsetzers und den Induktor gekoppelt sein und die erste Stufe kann einen ersten fliegenden Kondensator umfassen. Die zweite Stufe kann zwischen den Induktor und einen Ausgang des Leistungsumsetzers gekoppelt sein und die zweite Stufe kann einen zweiten fliegenden Kondensator umfassen. Ein zweiter Anschluss des ersten fliegenden Kondensators kann mit einem ersten Anschluss des Induktors verbunden sein und ein erster Anschluss des zweiten fliegenden Kondensators kann mit einem zweiten Anschluss des Induktors verbunden sein. [EN US2021234462A1]: The present document relates to a power converter comprising an inductor, a first stage, and a second stage. The first stage may be coupled between an input of the power converter and the inductor, and the first stage may comprise a first flying capacitor. The second stage may be coupled between the inductor and an output of the power converter, and the second stage may comprise a second flying capacitor. A second terminal of the first flying capacitor may be connected to a first terminal of the inductor, and a first terminal of the second flying capacitor may be connected to a second terminal of the inductor. | US2021234462A1 | 2021-07-29 | US202016919928A | 2020-07-02 | DE102020200927A, 2020-01-27 | DE102020200927A1: 2021-07-29 US2021234462A1: 2021-07-29 | DIALOG SEMICONDUCTOR UK LTD | CANNILLO FRANCESCO PETERSEN HOLGER | H02M3/158: I H02M3/07: I G05F1/595: I | G05F1/595: I H02M3/07: I H02M3/158: I H02M1/0095: I H02M3/1584: I H02M1/0006: A H02M1/0025: A |  |  | [DE DE102020200927A1]: Tiefsetzleistungsumsetzer, der Folgendes umfasst: - einen Induktor, - eine erste Stufe, die zwischen einen Eingang des Tiefsetzleistungsumsetzers und den Induktor gekoppelt ist, wobei die erste Stufe einen ersten fliegenden Kondensator umfasst, und - eine zweite Stufe, die zwischen den Induktor und einen Ausgang des Tiefsetzleistungsumsetzers gekoppelt ist, wobei die zweite Stufe einen zweiten fliegenden Kondensator umfasst. Tiefsetzleistungsumsetzer nach Anspruch 1, wobei - ein zweiter Anschluss des ersten fliegenden Kondensators mit einem ersten Anschluss des Induktors verbunden ist, und - ein erster Anschluss des zweiten fliegenden Kondensators mit einem zweiten Anschluss des Induktors verbunden ist. Tiefsetzleistungsumsetzer nach Anspruch 2, wobei die erste Stufe ferner einen Speicherkondensator umfasst und der Tiefsetzleistungsumsetzer dazu konfiguriert ist, abwechselnd einen ersten Anschluss des Speicherkondensators - mit dem zweiten Anschluss des ersten fliegenden Kondensators oder - mit einem ersten Anschluss des ersten fliegenden Kondensators zu koppeln. Tiefsetzleistungsumsetzer nach Anspruch 3, wobei die erste Stufe Folgendes umfasst - ein erstes Schaltelement, das zwischen den Eingang des Tiefsetzleistungsumsetzers und den ersten Anschluss des ersten fliegenden Kondensators gekoppelt ist, - ein zweites Schaltelement, das zwischen den ersten Anschluss des ersten fliegenden Kondensators und einen Zwischenknoten gekoppelt ist, - ein drittes Schaltelement, das zwischen den Zwischenknoten und den zweiten Anschluss des ersten fliegenden Kondensators gekoppelt ist, und - ein viertes Schaltelement, das zwischen den zweiten Anschluss des ersten fliegenden Kondensators und ein Referenzpotential gekoppelt ist, wobei der Speicherkondensator zwischen den Zwischenknoten und das Referenzpotential gekoppelt ist. Tiefsetzleistungsumsetzer nach Anspruch 3 oder 4, wobei die zweite Stufe Folgendes umfasst - ein fünftes Schaltelement, das zwischen den ersten Anschluss des zweiten fliegenden Kondensators und den Ausgang des Tiefsetzleistungsumsetzers gekoppelt ist, - ein sechstes Schaltelement, das zwischen den Ausgang des Tiefsetzleistungsumsetzers und einen zweiten Anschluss des zweiten fliegenden Kondensators gekoppelt ist, und - ein siebtes Schaltelement, das zwischen den zweiten Anschluss des zweiten fliegenden Kondensators und ein Referenzpotential gekoppelt ist. Tiefsetzleistungsumsetzer nach einem der Ansprüche 3 bis 5, wobei der Tiefsetzleistungsumsetzer dazu konfiguriert ist, in einem Magnetisierungszustand - einen ersten Magnetisierungsstrompfad vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers, und - einen zweiten Magnetisierungsstrompfad vom Speicherkondensator über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Tiefsetzleistungsumsetzer nach einem der Ansprüche 3 bis 6, wobei der Tiefsetzleistungsumsetzer dazu konfiguriert ist, in einem Entmagnetisierungszustand - einen Entmagnetisierungsstrompfad von einem Referenzpotential über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Tiefsetzleistungsumsetzer nach Anspruch 7, wobei der Tiefsetzleistungsumsetzer ferner dazu konfiguriert ist, im Entmagnetisierungszustand - einen ersten Strompfad von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential und - einen zweiten Strompfad vom Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Tiefsetzleistungsumsetzer nach einem der Ansprüche 3 bis 8, wobei der Tiefsetzleistungsumsetzer dazu konfiguriert ist, in einem alternativen Magnetisierungszustand - einen ersten Magnetisierungsstrompfad vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator und über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers, - einen zweiten Magnetisierungsstrompfad vom Speicherkondensator und über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers und - einen dritten Strompfad von einem Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Tiefsetzleistungsumsetzer nach einem der Ansprüche 3 bis 9, wobei der Tiefsetzleistungsumsetzer dazu konfiguriert ist, in einem alternativen Entmagnetisierungszustand - einen Entmagnetisierungsstrompfad von einem Referenzpotential über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers, und - einen Strompfad von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential herzustellen. Hochsetzleistungsumsetzer, der Folgendes umfasst: - einen Induktor, - eine erste Stufe, die zwischen einen Eingang des Hochsetzleistungsumsetzers und den Induktor gekoppelt ist, wobei die erste Stufe einen ersten fliegenden Kondensator umfasst, und - eine zweite Stufe, die zwischen den Induktor und einen Ausgang des Hochsetzleistungsumsetzers gekoppelt ist, wobei die zweite Stufe einen zweiten fliegenden Kondensator umfasst. Hochsetzleistungsumsetzer nach Anspruch 11, wobei - ein zweiter Anschluss des ersten fliegenden Kondensators mit einem ersten Anschluss des Induktors verbunden ist, und - ein erster Anschluss des zweiten fliegenden Kondensators mit einem zweiten Anschluss des Induktors gekoppelt ist. Hochsetzleistungsumsetzer nach Anspruch 12, wobei die zweite Stufe ferner einen Speicherkondensator umfasst und der Hochsetzleistungsumsetzer dazu konfiguriert ist, abwechselnd einen ersten Anschluss des Speicherkondensators - mit dem ersten Anschluss des zweiten fliegenden Kondensators oder - mit einem zweiten Anschluss des zweiten fliegenden Kondensators zu koppeln. Hochsetzleistungsumsetzer nach Anspruch 13, wobei die zweite Stufe Folgendes umfasst: - ein erstes Schaltelement, das zwischen den Ausgang des Hochsetzleistungsumsetzers und den zweiten Anschluss des zweiten fliegenden Kondensators gekoppelt ist, - ein zweites Schaltelement, das zwischen den zweiten Anschluss des zweiten fliegenden Kondensators und einen Zwischenknoten gekoppelt ist, - ein drittes Schaltelement, das zwischen den Zwischenknoten und den ersten Anschluss des zweiten fliegenden Kondensators gekoppelt ist, und - ein viertes Schaltelement, das zwischen den ersten Anschluss des zweiten fliegenden Kondensators und ein Referenzpotential gekoppelt ist, wobei der Speicherkondensator zwischen den Zwischenknoten und das Referenzpotential gekoppelt ist. Hochsetzleistungsumsetzer nach Anspruch 13 oder 14, wobei die erste Stufe Folgendes umfasst: - ein fünftes Schaltelement, das zwischen den zweiten Anschluss des ersten fliegenden Kondensators und den Eingang des Hochsetzleistungsumsetzers gekoppelt ist, - ein sechstes Schaltelement, das zwischen den Eingang des Hochsetzleistungsumsetzers und einen ersten Anschluss des ersten fliegenden Kondensators gekoppelt ist, und - ein siebtes Schaltelement, das zwischen den ersten Anschluss des ersten fliegenden Kondensators und ein Referenzpotential gekoppelt ist. Hochsetzleistungsumsetzer nach einem der Ansprüche 13 bis 15, wobei der Hochsetzleistungsumsetzer dazu konfiguriert ist, in einem Entmagnetisierungszustand - einen ersten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers herzustellen, und - einen zweiten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den Speicherkondensator zu einem Referenzpotential herzustellen. Hochsetzleistungsumsetzer nach einem der Ansprüche 13 bis 16, wobei der Hochsetzleistungsumsetzer dazu konfiguriert ist, in einem Magnetisierungszustand - einen Magnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den Induktor zu einem Referenzpotential herzustellen. Hochsetzleistungsumsetzer nach Anspruch 17, wobei der Hochsetzleistungsumsetzer ferner dazu konfiguriert ist, im Entmagnetisierungszustand - einen ersten Strompfad von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential, und - einen zweiten Strompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zum Referenzpotential herzustellen. Verfahren zum Betreiben eines Tiefsetzleistungsumsetzers mit einem Induktor, einer ersten Stufe mit einem ersten fliegenden Kondensator und einer zweiten Stufe mit einem zweiten fliegenden Kondensator, wobei das Verfahren umfasst - Koppeln der ersten Stufe zwischen einen Eingang des Tiefsetzleistungsumsetzers und den Induktor, und - Koppeln der zweiten Stufe zwischen den Induktor und einen Ausgang des Tiefsetzleistungsumsetzers. Verfahren nach Anspruch 19, wobei die erste Stufe ferner einen Speicherkondensator umfasst und das Verfahren das abwechselnde Koppeln eines ersten Anschlusses des Speicherkondensators - mit einem ersten Anschluss des ersten fliegenden Kondensators oder - mit einem zweiten Anschluss des ersten fliegenden Kondensators umfasst. Verfahren nach Anspruch 20, wobei das Verfahren in einem Magnetisierungszustand das Herstellen - eines ersten Magnetisierungsstrompfades vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers, und - eines zweiten Magnetisierungsstrompfades vom Speicherkondensator über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers umfasst. Verfahren nach Anspruch 20, wobei das Verfahren in einem Entmagnetisierungszustand das Herstellen - eines Entmagnetisierungsstrompfades von einem Referenzpotential über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers umfasst. Verfahren nach Anspruch 22, wobei das Verfahren im Entmagnetisierungszustand das Herstellen - eines ersten Strompfades von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential und - eines zweiten Strompfades vom Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers umfasst. Verfahren zum Betreiben eines Hochsetzleistungsumsetzers mit einem Induktor, einer ersten Stufe mit einem ersten fliegenden Kondensator und einer zweiten Stufe mit einem zweiten fliegenden Kondensator, wobei das Verfahren Folgendes umfasst: - Koppeln der ersten Stufe zwischen einen Eingang des Hochsetzleistungsumsetzers und den Induktor und - Koppeln der zweiten Stufe zwischen den Induktor und einen Ausgang des Hochsetzleistungsumsetzers. Verfahren nach Anspruch 24, wobei die zweite Stufe ferner einen Speicherkondensator umfasst und das Verfahren das abwechselnde Koppeln eines ersten Anschlusses des Speicherkondensators - mit dem ersten Anschluss des zweiten fliegenden Kondensators oder - mit einem zweiten Anschluss des zweiten fliegenden Kondensators umfasst. Verfahren nach Anspruch 25, wobei das Verfahren in einem Entmagnetisierungszustand das Herstellen - eines ersten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers und - eines zweiten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den Speicherkondensator zu einem Referenzpotential umfasst. Verfahren nach Anspruch 26, wobei das Verfahren in einem Magnetisierungszustand das Herstellen - eines Magnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den Induktor zu einem Referenzpotential umfasst. Verfahren nach Anspruch 27, wobei das Verfahren im Magnetisierungszustand das Herstellen - eines ersten Strompfades von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential und - eines zweiten Strompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zum Referenzpotential umfasst. [EN US2021234462A1]: 1) A buck power converter comprising an inductor,a first stage coupled between an input of the buck power converter and the inductor, wherein the first stage comprises a first flying capacitor, anda second stage coupled between the inductor and an output of the buck power converter, wherein the second stage comprises a second flying capacitor. 2) The buck power converter of claim 1, wherein a second terminal of the first flying capacitor is connected to a first terminal of the inductor, anda first terminal of the second flying capacitor is connected to a second terminal of the inductor. 3) The buck power converter of claim 2, wherein the first stage further comprises a reservoir capacitor, and the buck power converter is configured to alternately couple a first terminal of the reservoir capacitor to the second terminal of the first flying capacitor, orto a first terminal of the first flying capacitor. 4) The buck power converter of claim 3, wherein the first stage comprises a first switching element coupled between the input of the buck power converter and the first terminal of the first flying capacitor,a second switching element coupled between the first terminal of the first flying capacitor and an intermediate node,a third switching element coupled between the intermediate node and the second terminal of the first flying capacitor, anda fourth switching element coupled between the second terminal of the first flying capacitor and a reference potential,wherein the reservoir capacitor is coupled between the intermediate node and the reference potential. 5) The buck power converter of claim 3, wherein the second stage comprises a fifth switching element coupled between the first terminal of the second flying capacitor and the output of the buck power converter,a sixth switching element coupled between the output of the buck power converter and a second terminal of the second flying capacitor, anda seventh switching element coupled between the second terminal of the second flying capacitor and a reference potential. 6) The buck power converter of claim 3, wherein the buck power converter is configured to establish, in a magnetizing state, a first magnetizing current path from the input of the buck power converter, via the first flying capacitor, via the inductor, and via the second flying capacitor to the output of the buck power converter, anda second magnetizing current path from the reservoir capacitor, via the inductor, and via the second flying capacitor to the output of the buck power converter. 7) The buck power converter of claim 3, wherein the buck power converter is configured to establish, in a demagnetizing state, a demagnetizing current path from a reference potential, via the inductor to the output of the buck power converter. 8) The buck power converter of claim 7, wherein the buck power converter is further configured to establish, in the demagnetizing state, a first current path from a reference potential, via the first flying capacitor, via the reservoir capacitor, to the reference potential, anda second current path from the reference potential, via the second flying capacitor, to the output of the buck power converter. 9) The buck power converter of claim 3, wherein the buck power converter is configured to establish, in an alternative magnetizing state, a first magnetizing current path from the input of the buck power converter, via the first flying capacitor, and via the inductor to the output of the buck power converter,a second magnetizing current path from the reservoir capacitor, and via the inductor, to the output of the buck power converter, anda third current path from a reference potential, via the second flying capacitor, to the output of the buck power converter. 10) The buck power converter of claim 3, wherein the buck power converter is configured to establish, in an alternative demagnetizing state, a demagnetizing current path from a reference potential, via the inductor, and via the second flying capacitor to the output of the buck power converter, anda current path from a reference potential, via the first flying capacitor, via the reservoir capacitor, to the reference potential. 11) A boost power converter comprising an inductor,a first stage coupled between an input of the boost power converter and the inductor, wherein the first stage comprises a first flying capacitor, anda second stage coupled between the inductor and an output of the boost power converter, wherein the second stage comprises a second flying capacitor. 12) The boost power converter of claim 11, wherein a second terminal of the first flying capacitor is connected to a first terminal of the inductor, anda first terminal of the second flying capacitor is connected to a second terminal of the inductor. 13) The boost power converter of claim 12, wherein the second stage further comprises a reservoir capacitor, and the boost power converter is configured to alternately couple a first terminal of the reservoir capacitor to the first terminal of the second flying capacitor, orto a second terminal of the second flying capacitor. 14) The boost power converter of claim 13, wherein the second stage comprises a first switching element coupled between the output of the boost power converter and the second terminal of the second flying capacitor,a second switching element coupled between the second terminal of the second flying capacitor and an intermediate node,a third switching element coupled between the intermediate node and the first terminal of the second flying capacitor, anda fourth switching element coupled between the first terminal of the second flying capacitor and a reference potential,wherein the reservoir capacitor is coupled between the intermediate node and the reference potential. 15) The boost power converter of claim 13, wherein the first stage comprises a fifth switching element coupled between the second terminal of the first flying capacitor and the input of the boost power converter,a sixth switching element coupled between the input of the boost power converter and a first terminal of the first flying capacitor, anda seventh switching element coupled between the first terminal of the first flying capacitor and a reference potential. 16) The boost power converter of claim 13, wherein the boost power converter is configured to establish, in a demagnetizing state, a first demagnetizing current path from the input of the boost power converter, via the first flying capacitor, via the inductor, and via the second flying capacitor to the output of the boost power converter, anda second demagnetizing current path from the input of the boost power converter, via the first flying capacitor, via the inductor, and via the reservoir capacitor to a reference potential. 17) The boost power converter of claim 13, wherein the boost power converter is configured to establish, in a magnetizing state, a magnetizing current path from the input of the boost power converter, via the inductor, to a reference potential. 18) The boost power converter of claim 17, wherein the boost power converter is further configured to establish, in the demagnetizing state, a first current path from a reference potential, via the reservoir capacitor, via the second flying capacitor, to the reference potential, anda second current path from the input of the boost power converter, via the first flying capacitor, to the reference potential. 19) A method of operating a buck power converter comprising an inductor, a first stage with a first flying capacitor, and a second stage with a second flying capacitor, the method comprising coupling the first stage between an input of the buck power converter and the inductor, andcoupling the second stage between the inductor and an output of the buck power converter. 20) The method of claim 19, wherein the first stage further comprises a reservoir capacitor, and the method comprises alternately coupling a first terminal of the reservoir capacitor to a first terminal of the first flying capacitor, orto a second terminal of the first flying capacitor. 21) The method of claim 20, wherein the method comprises establishing, in a magnetizing state, a first magnetizing current path from the input of the buck power converter, via the first flying capacitor, via the inductor, and via the second flying capacitor to the output of the buck power converter, anda second magnetizing current path from the reservoir capacitor, via the inductor, and via the second flying capacitor to the output of the buck power converter. 22) The method of claim 20, wherein the method comprises establishing, in a demagnetizing state, a demagnetizing current path from a reference potential, via the inductor to the output of the buck power converter. 23) The method of claim 22, wherein the method comprises establishing, in the demagnetizing state, a first current path from a reference potential, via the first flying capacitor, via the reservoir capacitor, to the reference potential, anda second current path from the reference potential, via the second flying capacitor, to the output of the buck power converter. 24) A method of operating a boost power converter comprising an inductor, a first stage with a first flying capacitor, and a second stage with a second flying capacitor, the method comprising coupling the first stage between an input of the boost power converter and the inductor, andcoupling the second stage between the inductor and an output of the boost power converter. 25) The method of claim 24, wherein the second stage further comprises a reservoir capacitor, and the method comprises alternately coupling a first terminal of the reservoir capacitor to the first terminal of the second flying capacitor, orto a second terminal of the second flying capacitor. 26) The method of claim 25, wherein the method comprises establishing, in a demagnetizing state, a first demagnetizing current path from the input of the boost power converter, via the first flying capacitor, via the inductor, and via the second flying capacitor to the output of the boost power converter, anda second demagnetizing current path from the input of the boost power converter, via the first flying capacitor, via the inductor, and via the reservoir capacitor to a reference potential. 27) The method of claim 26, wherein the method comprises establishing, in a magnetizing state, a magnetizing current path from the input of the boost power converter, via the inductor, to a reference potential. 28) The method of claim 27, wherein the method comprises establishing, in the magnetizing state, a first current path from a reference potential, via the reservoir capacitor, via the second flying capacitor, to the reference potential, anda second current path from the input of the boost power converter, via the first flying capacitor, to the reference potential. | [DE DE102020200927A1]: Technisches Gebiet Das vorliegende Dokument bezieht sich auf Leistungsumsetzer. Insbesondere bezieht sich das vorliegende Dokument auf Hybrid-Mehrpegel-Leistungsumsetzer mit verbesserter Effizienz. Hintergrund Es besteht ein zunehmender Bedarf an regulierten Leistungsumsetzern mit hoher Effizienz in mehreren Marktsegmenten wie z. B. Halbleiterlaufwerken (SSDs), einer Rechenvorrichtung, Aufladungsvorrichtungen oder tragbaren integrierten Leistungsmanagementschaltungen (PMICs). Insbesondere ist es sehr erwünscht, Leistungsumsetzer mit höherer Effizienz und kleinerer Fläche als herkömmliche Tiefsetzumsetzer zu entwerfen. Innerhalb dieses Dokuments werden Hybrid-Mehrpegel-Leistungsumsetzer vorgeschlagen. Dabei gibt der Begriff „Mehrpegel“ an, dass der Leistungsumsetzer einen Induktor umfasst und dass der Leistungsumsetzer in der Lage ist, mehr als zwei verschiedene Spannungen über diesen Induktor anzulegen. Überdies betrifft das vorliegende Dokument „Hybrid“-Leistungsumsetzer, d. h. Leistungsumsetzer mit sowohl fliegenden Kondensatoren als auch Induktoren. Im Hinblick auf die Gesamtfläche des Leistungsumsetzers sind die Größen der erforderlichen Induktoren und fliegenden Kondensatoren wichtige Entwurfsparameter. Folglich ist es wichtig, die Größen der letzteren Schaltungselemente zu verringern. Überdies besteht ein Bedarf an Leistungsumsetzern, die eine Leistungsumsetzung mit einem kleinen Umsetzungsverhältnis VOUT/VIN von Eingangs- zu Ausgangsspannung durchführen, insbesondere wenn VOUT/VIN &lt; 1/4. Als weiteres Ziel ist es für die Umsetzereffizienz vorteilhaft, die Spannung über dem Induktor während des Betriebs des Leistungsumsetzers zu begrenzen. Das vorliegende Dokument geht die vorstehend erwähnten technischen Probleme an. Zusammenfassung Gemäß einem Aspekt wird ein Tiefsetzleistungsumsetzer vorgestellt. Der Tiefsetzleistungsumsetzer kann einen Induktor, eine erste Stufe und eine zweite Stufe umfassen. Die erste Stufe kann zwischen einen Eingang des Tiefsetzleistungsumsetzers und den Induktor gekoppelt sein und die erste Stufe kann einen ersten fliegenden Kondensator umfassen. Die zweite Stufe kann zwischen den Induktor und einen Ausgang des Tiefsetzleistungsumsetzers gekoppelt sein und die zweite Stufe kann einen zweiten fliegenden Kondensator umfassen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, eine Ausgangsspannung am Ausgang des Tiefsetzleistungsumsetzers zu regulieren, die kleiner ist als eine Eingangsspannung am Eingang des Tiefsetzleistungsumsetzers. Dazu kann der Tiefsetzleistungsumsetzer mehrere Schaltelemente zum Steuern der Ströme, die durch die Komponenten des Tiefsetzleistungsumsetzers fließen, umfassen. Ferner kann der Tiefsetzleistungsumsetzer eine Rückkopplungsschleife zum Vergleichen der Ausgangsspannung (oder eines Ausgangsstroms) mit einem Referenzwert und Erzeugen von jeweiligen Steuersignalen zum Steuern der mehreren Schaltelemente umfassen. Im Allgemeinen können der erste und der zweite fliegende Kondensator passive elektronische Komponenten sein, die in der Lage sind, elektrische Energie in einem elektrischen Feld zu speichern. Die Kondensatoren können verschiedene Kapazitäten aufweisen oder können dieselbe Kapazität aufweisen. Jeder Kondensator kann einen ersten Anschluss und einen zweiten Anschluss umfassen. Der Begriff „fliegend“ kann von der Tatsache stammen, dass ein Anschluss des Kondensators während des Umsetzerbetriebs mit verschiedenen Referenzspannungen verbunden wird. Das ist so, als ob der geladene Kondensator von einer Spannung zur anderen fliegt. Ein zweiter Anschluss des ersten fliegenden Kondensators kann mit einem ersten Anschluss des Induktors verbunden sein und ein erster Anschluss des zweiten fliegenden Kondensators kann mit einem zweiten Anschluss des Induktors verbunden sein. Mit anderen Worten, der erste fliegende Kondensator, der Induktor und der zweite fliegende Kondensator können eine Reihenschaltung zwischen dem Eingang des Tiefsetzleistungsumsetzers und dem Ausgang des Tiefsetzleistungsumsetzers bilden. Die erste Stufe kann einen Speicherkondensator umfassen und der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, abwechselnd einen ersten Anschluss des Speicherkondensators mit dem zweiten Anschluss des ersten fliegenden Kondensators (der mit dem Induktor verbunden sein kann) oder mit einem ersten Anschluss des ersten fliegenden Kondensators zu koppeln. Da ein zweiter Anschluss des Speicherkondensators mit einem Referenzpotential (wie z. B. Masse) verbunden sein kann, kann der Speicherkondensator einen durch den Induktor fließenden Strom im ersten Fall entladen und zu diesem beitragen, wohingegen der erste fliegende Kondensator im zweiten Fall den Speicherkondensator aufladen kann. Die erste Stufe kann ein erstes Schaltelement umfassen, das zwischen den Eingang des Tiefsetzleistungsumsetzers und den ersten Anschluss des ersten fliegenden Kondensators gekoppelt ist. Die erste Stufe kann ein zweites Schaltelement umfassen, das zwischen den ersten Anschluss des ersten fliegenden Kondensators und einen Zwischenknoten gekoppelt ist. Die erste Stufe kann ein drittes Schaltelement umfassen, das zwischen den Zwischenknoten und den zweiten Anschluss des ersten fliegenden Kondensators gekoppelt ist. Die erste Stufe kann ein viertes Schaltelement umfassen, das zwischen den zweiten Anschluss des ersten fliegenden Kondensators und ein Referenzpotential gekoppelt ist. Der Speicherkondensator kann zwischen den Zwischenknoten und das Referenzpotential gekoppelt sein. Insbesondere kann der erste Anschluss des Speicherkondensators mit dem Zwischenknoten verbunden sein und der zweite Anschluss des Speicherkondensators kann mit dem Referenzpotential verbunden sein. In diesem gesamten Dokument ist der Begriff „Referenzpotential“ in seiner breitestmöglichen Hinsicht gemeint. Insbesondere ist das Referenzpotential nicht auf Masse, d. h. ein Referenzpotential mit einer direkten physikalischen Verbindung zur Erde, begrenzt. Vielmehr kann sich der Begriff „Referenzpotential“ auf irgendeinen Referenzpunkt beziehen, zu dem und von dem elektrische Ströme fließen können oder von dem Spannungen gemessen werden können. Überdies sollte erwähnt werden, dass die in diesem Dokument erwähnten Referenzpotentiale sich nicht notwendigerweise auf denselben physikalischen Kontakt beziehen können. Stattdessen können sich die in diesem Dokument erwähnten Referenzpotentiale auf verschiedene physikalische Kontakte beziehen, obwohl manchmal auf „das“ Referenzpotential für eine leichte Darstellung Bezug genommen wird. Jedes Schaltelement kann mit irgendeiner geeigneten Vorrichtung implementiert werden, wie beispielsweise einem Metalloxid-Halbleiter-Feldeffekttransistor (MOSFET), einem Bipolartransistor mit isoliertem Gate (IGBT), einem MOS-gesteuerten Thyristor oder anderen geeigneten Leistungsvorrichtungen. Jedes Schaltelement kann ein Gate aufweisen, an das eine Ansteuerspannung oder ein Steuersignal angelegt werden kann, um das jeweilige Schaltelement einzuschalten (d. h. das Schaltelement zu schließen) oder das jeweilige Schaltelement auszuschalten (d. h. das Schaltelement zu öffnen). Die zweite Stufe kann ein fünftes Schaltelement umfassen, das zwischen den ersten Anschluss des zweiten fliegenden Kondensators und den Ausgang des Tiefsetzleistungsumsetzers gekoppelt ist. Die zweite Stufe kann ein sechstes Schaltelement umfassen, das zwischen den Ausgang des Tiefsetzleistungsumsetzers und einen zweiten Anschluss des zweiten fliegenden Kondensators gekoppelt ist. Die zweite Stufe kann ein siebtes Schaltelement umfassen, das zwischen den zweiten Anschluss des zweiten fliegenden Kondensators und ein Referenzpotential gekoppelt ist. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, in einem Magnetisierungszustand einen ersten Magnetisierungsstrompfad vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, im Magnetisierungszustand einen zweiten Magnetisierungsstrompfad vom Speicherkondensator über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Für diesen Zweck kann der Tiefsetzleistungsumsetzer dazu konfiguriert sein, im Magnetisierungszustand das erste Schaltelement, das dritte Schaltelement und das sechste Schaltelement zu schließen und die restlichen Schaltelemente zu öffnen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, in einem Entmagnetisierungszustand einen Entmagnetisierungsstrompfad von einem Referenzpotential über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, im Entmagnetisierungszustand einen ersten Strompfad von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential und einen zweiten Strompfad vom Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Für diesen Zweck kann der Tiefsetzleistungsumsetzer dazu konfiguriert sein, im Entmagnetisierungszustand das zweite Schaltelement, das vierte Schaltelement, das fünfte Schaltelement und das siebte Schaltelement zu schließen und die restlichen Schaltelemente zu öffnen. Der Tiefsetzleistungsumsetzer kann einen Ausgangskondensator umfassen, der zwischen dem Ausgang des Tiefsetzleistungsumsetzers und dem Referenzpotential verbunden ist. Der Leistungsumsetzer kann dazu konfiguriert sein, zwischen dem Magnetisierungszustand und dem Entmagnetisierungszustand umzuschalten und die Schaltelemente dementsprechend zu steuern. Der Fachmann versteht leicht, dass das Adjektiv „Magnetisierung“ hier verwendet wird, um den Zweck des Magnetisierungszustandes bzw. Magnetisierungsstrompfades zu beschreiben. Während er sich im Magnetisierungszustand befindet, kann ein Strom entlang des Magnetisierungsstrompfades fließen und kann zunehmen, was zu einer Zunahme der magnetischen Energie, die im Induktor gespeichert ist, führt. Mit anderen Worten, der Induktor kann während des Magnetisierungszustandes als „magnetisiert“ bezeichnet werden. Analog versteht der Fachmann leicht, dass das Adjektiv „Entmagnetisierung“ hier verwendet wird, um den Zweck des Entmagnetisierungszustandes bzw. des Entmagnetisierungsstrompfades zu beschreiben. Während er sich im Entmagnetisierungszustand befindet, kann ein Strom entlang des Entmagnetisierungsstrompfades fließen und kann abnehmen, was zu einer Abnahme der im Induktor gespeicherten magnetischen Energie führt. Mit anderen Worten, der Induktor kann während des Entmagnetisierungszustandes als „entmagnetisiert“ bezeichnet werden. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, in einem alternativen Magnetisierungszustand einen ersten Magnetisierungsstrompfad vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator und über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, im alternativen Magnetisierungszustand einen zweiten Magnetisierungsstrompfad vom Speicherkondensator und über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, im alternativen Magnetisierungszustand einen dritten Strompfad von einem Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, in einem alternativen Entmagnetisierungszustand einen Entmagnetisierungsstrompfad von einem Referenzpotential über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers herzustellen. Der Tiefsetzleistungsumsetzer kann dazu konfiguriert sein, im alternativen Entmagnetisierungszustand einen Strompfad von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential herzustellen. Der Leistungsumsetzer kann dazu konfiguriert sein, zwischen dem Magnetisierungszustand, dem alternativen Magnetisierungszustand, dem Entmagnetisierungszustand und dem alternativen Entmagnetisierungszustand umzuschalten und die Schaltelemente dementsprechend zu steuern. Gemäß einem anderen Aspekt wird ein Hochsetzleistungsumsetzer vorgestellt. Der Hochsetzleistungsumsetzer kann einen Induktor, eine erste Stufe, die zwischen einen Eingang des Hochsetzleistungsumsetzers und den Induktor gekoppelt ist, wobei die erste Stufe einen ersten fliegenden Kondensator umfasst, und eine zweite Stufe, die zwischen den Induktor und einen Ausgang des Hochsetzleistungsumsetzers gekoppelt ist, wobei die zweite Stufe einen zweiten fliegenden Kondensator umfasst, umfassen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, eine Ausgangsspannung am Ausgang des Hochsetzleistungsumsetzers zu regulieren, die größer ist als eine Eingangsspannung am Eingang des Hochsetzleistungsumsetzers. Dazu kann der Hochsetzleistungsumsetzer mehrere Schaltelemente zum Steuern der Ströme, die durch die Komponenten des Hochsetzleistungsumsetzers fließen, umfassen. Ferner kann der Hochsetzleistungsumsetzer eine Rückkopplungsschleife zum Vergleichen der Ausgangsspannung (oder eines Ausgangsstroms) mit einem Referenzwert und Erzeugen von jeweiligen Steuersignalen zum Steuern der mehreren Schaltelemente umfassen. Ein zweiter Anschluss des ersten fliegenden Kondensators kann mit einem ersten Anschluss des Induktors verbunden sein und ein erster Anschluss des zweiten fliegenden Kondensators kann mit einem zweiten Anschluss des Induktors verbunden sein. Die zweite Stufe kann ferner einen Speicherkondensator umfassen und der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, einen ersten Anschluss des Speicherkondensators abwechselnd mit dem ersten Anschluss des zweiten fliegenden Kondensators oder mit einem zweiten Anschluss des zweiten fliegenden Kondensators zu koppeln. Die zweite Stufe kann ein erstes Schaltelement umfassen, das zwischen den Ausgang des Hochsetzleistungsumsetzers und den zweiten Anschluss des zweiten fliegenden Kondensators gekoppelt ist. Die zweite Stufe kann ein zweites Schaltelement umfassen, das zwischen den zweiten Anschluss des zweiten fliegenden Kondensators und einen Zwischenknoten gekoppelt ist. Die zweite Stufe kann ein drittes Schaltelement umfassen, das zwischen den Zwischenknoten und den ersten Anschluss des zweiten fliegenden Kondensators gekoppelt ist. Die zweite Stufe kann ein viertes Schaltelement umfassen, das zwischen den ersten Anschluss des zweiten fliegenden Kondensators und ein Referenzpotential gekoppelt ist, wobei der Speicherkondensator zwischen den Zwischenknoten und das Referenzpotential gekoppelt ist. Die erste Stufe kann ein fünftes Schaltelement umfassen, das zwischen den zweiten Anschluss des ersten fliegenden Kondensators und den Eingang des Hochsetzleistungsumsetzers gekoppelt ist. Die erste Stufe kann ein sechstes Schaltelement umfassen, das zwischen den Eingang des Hochsetzleistungsumsetzers und einen ersten Anschluss des ersten fliegenden Kondensators gekoppelt ist. Die erste Stufe kann ein siebtes Schaltelement umfassen, das zwischen den ersten Anschluss des ersten fliegenden Kondensators und ein Referenzpotential gekoppelt ist. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, in einem Entmagnetisierungszustand einen ersten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers herzustellen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, im Entmagnetisierungszustand einen zweiten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den Speicherkondensator zu einem Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, in einem Magnetisierungszustand einen Magnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers, über den Induktor zu einem Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann ferner dazu konfiguriert sein, im Magnetisierungszustand einen ersten Strompfad von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann ferner dazu konfiguriert sein, im Magnetisierungszustand einen zweiten Strompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zum Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, in einem alternativen Entmagnetisierungszustand einen ersten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers herzustellen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, im alternativen Entmagnetisierungszustand einen zweiten Entmagnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den Induktor und über den Speicherkondensator zu einem Referenzpotential herzustellen. Überdies kann der Hochsetzleistungsumsetzer dazu konfiguriert sein, im alternativen Entmagnetisierungszustand einen Strompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zu einem Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann dazu konfiguriert sein, in einem alternativen Magnetisierungszustand einen Magnetisierungsstrompfad vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor zu einem Referenzpotential herzustellen. Der Hochsetzleistungsumsetzer kann ferner dazu konfiguriert sein, im alternativen Magnetisierungszustand einen Strompfad von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential herzustellen. Gemäß einem anderen Aspekt wird ein Verfahren zum Betreiben eines Tiefsetzleistungsumsetzers beschrieben. Das Verfahren kann Schritte umfassen, die den Merkmalen des Tiefsetzleistungsumsetzers entsprechen, die im vorliegenden Dokument beschrieben sind. Der Tiefsetzleistungsumsetzer kann einen Induktor, eine erste Stufe mit einem ersten fliegenden Kondensator und eine zweite Stufe mit einem zweiten fliegenden Kondensator umfassen. Das Verfahren kann das Koppeln der ersten Stufe zwischen einen Eingang des Tiefsetzleistungsumsetzers und den Induktor umfassen. Das Verfahren kann das Koppeln der zweiten Stufe zwischen den Induktor und einen Ausgang des Tiefsetzleistungsumsetzers umfassen. Die erste Stufe kann ferner einen Speicherkondensator umfassen. Das Verfahren kann das abwechselnde Koppeln eines ersten Anschlusses des Speicherkondensators mit einem ersten Anschluss des ersten fliegenden Kondensators oder mit einem zweiten Anschluss des ersten fliegenden Kondensators umfassen. Das Verfahren kann das Herstellen eines ersten Magnetisierungsstrompfades vom Eingang des Tiefsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers in einem Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines zweiten Magnetisierungsstrompfades vom Speicherkondensator über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers im Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines Entmagnetisierungsstrompfades von einem Referenzpotential über den Induktor zum Ausgang des Tiefsetzleistungsumsetzers in einem Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines ersten Strompfades von einem Referenzpotential über den ersten fliegenden Kondensator, über den Speicherkondensator zum Referenzpotential im Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines zweiten Strompfades vom Referenzpotential über den zweiten fliegenden Kondensator zum Ausgang des Tiefsetzleistungsumsetzers im Entmagnetisierungszustand umfassen. Gemäß einem nochmals anderen Aspekt wird ein Verfahren zum Betreiben eines Hochsetzleistungsumsetzers vorgestellt. Das Verfahren kann Schritte umfassen, die den Merkmalen des Hochsetzleistungsumsetzers entsprechen, die im vorliegenden Dokument beschrieben sind. Der Hochsetzleistungsumsetzer kann einen Induktor, eine erste Stufe mit einem ersten fliegenden Kondensator und eine zweite Stufe mit einem zweiten fliegenden Kondensator umfassen. Das Verfahren kann das Koppeln der ersten Stufe zwischen einen Eingang des Hochsetzleistungsumsetzers und den Induktor umfassen. Das Verfahren kann das Koppeln der zweiten Stufe zwischen den Induktor und einen Ausgang des Hochsetzleistungsumsetzers umfassen. Die zweite Stufe kann ferner einen Speicherkondensator umfassen und das Verfahren kann ferner das abwechselnde Koppeln eines ersten Anschlusses des Speicherkondensators mit dem ersten Anschluss des zweiten fliegenden Kondensators oder mit einem zweiten Anschluss des zweiten fliegenden Kondensators umfassen. Das Verfahren kann das Herstellen eines ersten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers in einem Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines zweiten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor und über den Speicherkondensator zu einem Referenzpotential im Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines Magnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den Induktor zu einem Referenzpotential in einem Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines ersten Strompfades von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential im Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines zweiten Strompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zum Referenzpotential im Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines ersten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den Induktor und über den zweiten fliegenden Kondensator zum Ausgang des Hochsetzleistungsumsetzers in einem alternativen Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines zweiten Entmagnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den Induktor und über den Speicherkondensator zu einem Referenzpotential im alternativen Entmagnetisierungszustand umfassen. Überdies kann das Verfahren das Herstellen eines Strompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator zu einem Referenzpotential im alternativen Entmagnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines Magnetisierungsstrompfades vom Eingang des Hochsetzleistungsumsetzers über den ersten fliegenden Kondensator, über den Induktor zu einem Referenzpotential in einem alternativen Magnetisierungszustand umfassen. Das Verfahren kann das Herstellen eines Strompfades von einem Referenzpotential über den Speicherkondensator, über den zweiten fliegenden Kondensator zum Referenzpotential im alternativen Magnetisierungszustand umfassen. Gemäß einem weiteren Aspekt wird ein Software-Programm beschrieben. Das Software-Programm kann für die Ausführung auf einem Prozessor und zum Durchführen der Verfahrensschritte, die im vorliegenden Dokument umrissen sind, wenn es durch den Prozessor ausgeführt wird, ausgelegt sein. Gemäß einem anderen Aspekt wird ein Speichermedium beschrieben. Das Speichermedium kann ein Software-Programm umfassen, das für die Ausführung auf einem Prozessor und zum Durchführen der Verfahrensschritte, die im vorliegenden Dokument umrissen sind, wenn es durch den Prozessor ausgeführt wird, ausgelegt sein. Gemäß einem weiteren Aspekt wird ein Computerprogrammprodukt beschrieben. Das Computerprogrammprodukt kann Befehle zum Durchführen der Verfahrensschritte, die im vorliegenden Dokument umrissen sind, wenn es durch den Prozessor ausgeführt wird, ausgelegt sein. Es sollte beachtet werden, dass die Verfahren und Systeme, einschließlich ihrer bevorzugten Ausführungsformen, wie im vorliegenden Dokument umrissen, eigenständig oder in Kombination mit den anderen Verfahren und Systemen, die in diesem Dokument offenbart sind, verwendet werden können. Außerdem sind die im Zusammenhang mit einem System umrissenen Merkmale auch auf ein entsprechendes Verfahren anwendbar. Ferner können alle Aspekte der Verfahren und Systeme, die im vorliegenden Dokument umrissen sind, beliebig kombiniert werden. Insbesondere können die Merkmale der Ansprüche in beliebiger Weise miteinander kombiniert werden. Im vorliegenden Dokument bezieht sich der Begriff „koppeln“ oder „gekoppelt“ auf Elemente, die miteinander in elektrischer Kommunikation stehen, ob direkt verbunden, z. B. über Drähte, oder in irgendeiner anderen Weise. Figurenliste Die vorliegende Erfindung wird beispielhaft und nicht zur Begrenzung in den Figuren der begleitenden Zeichnungen dargestellt, in denen sich gleiche Bezugszeichen auf ähnliche oder identische Elemente beziehen; es zeigen: 1 einen beispielhaften Leistungsumsetzer;2 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem Magnetisierungszustand betrieben wird;3 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem Entmagnetisierungszustand betrieben wird;4 eine Induktorstromwelligkeit für verschiedene Umsetzungsverhältnisse für einen herkömmlichen Tiefsetzleistungsumsetzer und für den vorgeschlagenen Mehrpegel-Hybrid-Leistungsumsetzer, der im Tiefsetzmodus betrieben wird;5 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem alternativen Magnetisierungszustand betrieben wird;6 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem alternativen Entmagnetisierungszustand betrieben wird;7 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Hochsetzmodus in einem Magnetisierungszustand betrieben wird;8 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Hochsetzmodus in einem Entmagnetisierungszustand betrieben wird;9 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Hochsetzmodus in einem alternativen Magnetisierungszustand betrieben wird; und10 Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Hochsetzmodus in einem alternativen Entmagnetisierungszustand betrieben wird. Ausführliche Beschreibung 1 zeigt einen beispielhaften Leistungsumsetzer 100 gemäß den Lehren des vorliegenden Dokuments. Der beispielhafte Leistungsumsetzer 100 umfasst einen Induktor 1, eine erste Stufe und eine zweite Stufe. Die erste Stufe ist zwischen einen Eingang des Leistungsumsetzers 100 und den Induktor 1 gekoppelt, ein Kondensator 2 ist mit einem ersten Anschluss des Induktors 1 verbunden und ein erster Anschluss des zweiten fliegenden Kondensators 3 ist mit einem zweiten Anschluss des Induktors 1 verbunden. Die erste Stufe des beispielhaften Leistungsumsetzers 100 umfasst ein erstes Schaltelement 11, das zwischen den Eingang des Leistungsumsetzers und den ersten Anschluss des ersten fliegenden Kondensators 2 gekoppelt ist. Sie umfasst ferner ein zweites Schaltelement 12, das zwischen den ersten Anschluss des ersten fliegenden Kondensators 2 und einen Zwischenknoten gekoppelt ist. Der Leistungsumsetzer 100 umfasst ferner ein drittes Schaltelement 13, das zwischen den Zwischenknoten und den zweiten Anschluss des ersten fliegenden Kondensators 2 gekoppelt ist, und ein viertes Schaltelement 14, das zwischen den zweiten Anschluss des ersten fliegenden Kondensators 2 und ein Referenzpotential gekoppelt ist. Ein Speicherkondensator 4 ist zwischen den Zwischenknoten und das Referenzpotential gekoppelt. Der Leistungsumsetzer 100 steuert das zweite Schaltelement 12 und das dritte Schaltelement 13, so dass ein erster Anschluss des Speicherkondensators 4 abwechselnd mit (a) dem zweiten Anschluss des ersten fliegenden Kondensators 2 oder (b) mit einem ersten Anschluss des ersten fliegenden Kondensators 2 gekoppelt wird. Mit anderen Worten, in der ersten Stufe werden der erste fliegende Kondensator CF1 und der Speicherkondensator CR abwechselnd in Reihe und parallel angeordnet und entwickeln daher eine Spannung von VIN/2 über ihnen, wobei VIN die Eingangsspannung am Eingang des Leistungsumsetzers 100 bezeichnet. Wie in 1 dargestellt, umfasst die zweite Stufe ein fünftes Schaltelement 15, das zwischen den ersten Anschluss des zweiten fliegenden Kondensators 3 und den Ausgang des Leistungsumsetzers gekoppelt ist, ein sechstes Schaltelement 16, das zwischen den Ausgang des Leistungsumsetzers und einen zweiten Anschluss des zweiten fliegenden Kondensators 3 gekoppelt ist, und ein siebtes Schaltelement 17, das zwischen den zweiten Anschluss des zweiten fliegenden Kondensators 3 und ein Referenzpotential gekoppelt ist. Überdies ist typischerweise ein Ausgangskondensator 5 zwischen dem Ausgang des Leistungsumsetzers und dem Referenzpotential verbunden. In der zweiten Stufe wird der zweite fliegende Kondensator 3 periodisch mit der Ausgangsspannung VOUT des Leistungsumsetzers verbunden, wobei daher seine mittlere Spannung bestimmt wird. Der vorgeschlagene Leistungsumsetzer 100 kann in einer Durchlassrichtung betrieben werden, die als Tiefsetzmodus bezeichnet wird, in dem der Leistungsumsetzer 100 eine Ausgangsspannung am Ausgang des Tiefsetzleistungsumsetzers reguliert, die kleiner ist als eine Eingangsspannung am Eingang des Tiefsetzleistungsumsetzers. Der Tiefsetzmodus ist unter Verwendung von jeweiligen Stromflüssen in 2, 3, 5 und 6 dargestellt. Im Tiefsetzmodus kann der vorgeschlagene Leistungsumsetzer 100 mit nur zwei Zuständen ohne den Bedarf am Regulieren der Spannung seiner fliegenden Kondensatoren 2 und 3 arbeiten. Tatsächlich werden die Spannungen über den fliegenden Kondensatoren grundsätzlich durch den Leistungsumsetzerbetrieb bestimmt, wie in der folgenden Beschreibung erörtert wird. Der Leistungsumsetzer kann beispielsweise zwischen einem Magnetisierungszustand und einem Entmagnetisierungszustand umschalten. 2 zeigt Strompfade (durch jeweilige Pfeile dargestellt), wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem Magnetisierungszustand D1 betrieben wird. Während des Magnetisierungszustandes D1 wird der Induktor magnetisiert. Die Spannung des Knotens X ist VIN/2. Das erste 11 und das dritte 13 Schaltelement sind geschlossen und das zweite 12 und das vierte 14 Schaltelement sind offen. Das Schaltelement 16 ist geschlossen und das Schaltelement 15 und 17 sind offen. Der Knoten Y liegt auf einer Spannung 2VOUT. Der Induktorstrom wird durch sowohl die Eingangsspannung VIN über den fliegenden Kondensator CF1 (auf einer Spannung von VIN/2) als auch durch den Speicherkondensator CR (auf VIN/2 aufgeladen) bezogen. Der zweite fliegende Kondensator CF2 (auf einer Spannung von VOUT) koppelt den Knoten Y vom Ausgang des Leistungsumsetzers ab. Mit anderen Worten, der erste fliegende Kondensator und der zweite fliegende Kondensator werden zwischen VIN und dem Referenzpotential während D1 in Reihe und während D2 parallel angeordnet. 3 zeigt Strompfade, wenn der beispielhafte Leistungsumsetzer in einem Tiefsetzmodus in einem Entmagnetisierungszustand D2 betrieben wird. Während des Entmagnetisierungszustandes D2 wird der Induktor durch den Verbindungsknoten X auf das Referenzpotential und den Knoten Y auf VOUT entmagnetisiert. Der erste fliegende Kondensator CF1 wird mit dem Speicherkondensator CR parallel angeordnet, da S1 und S3 offen sind, und S2 und S4 geschlossen sind. Der zweite fliegende Kondensator CF2 ist parallel zum Ausgangskondensator COUT. S5 und S7 sind geschlossen und S6 ist offen. Der Ladungsausgleich der fliegenden und Speicherkondensatoren wird während des Umsetzerbetriebs garantiert, wenn die Kondensatoren Stromflüsse mit entgegengesetzten Richtungen während der zwei Zustände D1 und D2 erfahren. Während des Magnetisierungszustandes D1 laden sich der erste fliegende Kondensator CF1 und der zweite fliegende Kondensator CF2 auf, während sich der Speicherkondensator C
[ZH CN113224960A]: 全桥型模块化多电平换流器子模块电容电压波动抑制方法 [EN CN113224960A]: Full-bridge modular multilevel converter sub-module capacitance voltage fluctuation suppression method | [ZH CN113224960A]: 本申请涉及一种全桥型MMC子模块电容电压波动抑制方法，包括：获取全桥型MMC的交流侧电流幅值，并根据交流侧电流幅值、功率因数角和全桥型MMC的子模块电容电压波动分量模型，得到理论所需环流值；获取全桥型MMC的上桥臂电流瞬时值、下桥臂电流瞬时值和直流电流瞬时值，并计算得到全桥型MMC的实际环流值；计算理论所需环流值和实际环流值的差值，根据差值生成参考电压，将参考电压注入全桥型MMC，并进行调制后在各相中产生所需环流，对各子模块电容电压波动进行抑制。上述全桥型MMC子模块电容电压波动抑制方法，可以根据实际环流值注入对应的参考电压，有利于提升子模块电容电压波动抑制效果。 [EN CN113224960A]: This application relates to a method for suppressing capacitance voltage fluctuations of a full-bridge MMC sub-module, including: obtaining the AC side current amplitude of the full-bridge MMC, and according to the AC side current amplitude, power factor angle, and sub-modules of the full-bridge MMC Capacitor voltage fluctuation component model to obtain the theoretically required circulating current value; obtain the instantaneous value of the upper bridge arm current, the instantaneous value of the lower bridge arm current and the instantaneous value of the DC current of the full-bridge MMC, and calculate the actual circulating current value of the full-bridge MMC; Calculate the difference between the theoretical required circulating current value and the actual circulating current value, generate a reference voltage according to the difference, inject the reference voltage into the full-bridge MMC, and generate the required circulating current in each phase after modulation, and fluctuate the capacitor voltage of each sub-module Suppress. The foregoing full-bridge type MMC sub-module capacitor voltage fluctuation suppression method can inject a corresponding reference voltage according to the actual circulating current value, which is beneficial to improve the sub-module capacitor voltage fluctuation suppression effect. | CN113224960A | 2021-08-06 | CN202110465599A | 2021-04-28 | CN202110465599A, 2021-04-28 | CN113224960A: 2021-08-06 | 中国南方电网有限责任公司超高压输电公司天生桥局 |  | H02M7/483: I |  |  |  | [ZH CN113224960A]: 1 .一种全桥型模块化多电平换流器子模块电容电压波动抑制方法，其特征在于，包括： 获取全桥型模块化多电平换流器的交流侧电流幅值，并根据所述交流侧电流幅值、功 率因数角和所述全桥型模块化多电平换流器的子模块电容电压波动分量模型，得到理论所 需环流值； 获取所述全桥型模块化多电平换流器的上桥臂电流瞬时值、下桥臂电流瞬时值和直流 电流瞬时值，并计算得到所述全桥型模块化多电平换流器的实际环流值； 计算所述理论所需环流值和所述实际环流值的差值，根据所述差值生成参考电压，将 所述参考电压注入所述全桥型模块化多电平换流器，并进行调制后在各相中产生所需环 流，对各子模块电容电压波动进行抑制。 2 .根据权利要求1所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于，所述获取全桥型模块化多电平换流器的交流侧电流幅值，并根据所述交流侧 电流幅值、功率因数角和所述全桥型模块化多电平换流器的子模块电容电压波动分量模 型，得到理论所需环流值之前，还包括： 根据全桥型模块化多电平换流器的特征参数，得到所述全桥型模块化多电平换流器的 子模块电容电压波动分量模型。 3 .根据权利要求2所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于，所述特征参数包括功率因数角、调制比、交流侧电流幅值、桥臂电压频率、子模 块个数、各子模块电容值和各子模块电容电压，所述根据全桥型模块化多电平换流器的特 征参数，得到所述全桥型模块化多电平换流器的子模块电容电压波动分量模型，包括： 根据调制比、桥臂电压频率、子模块个数和各子模块电容电压，得到所述全桥型模块化 多电平换流器的等效开关函数； 根据功率因数角、调制比、交流侧电流幅值和桥臂电压频率，得到所述全桥型模块化多 电平换流器的桥臂电流函数； 根据所述等效开关函数、所述桥臂电流函数、各子模块电容值和各子模块电容电压，得 到所述全桥型模块化多电平换流器的子模块电容电压波动分量模型。 4 .根据权利要求3所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于，所述等效开关函数为桥臂参考电压与所有全桥子模块电容电压和之比。 5 .根据权利要求3所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于，所述根据功率因数角、所述调制比、交流侧电流幅值和桥臂电压频率，得到所 述全桥型模块化多电平换流器的桥臂电流函数，包括： 根据功率因数角、调制比和交流侧电流幅值，得到所述全桥型模块化多电平换流器的 直流电流函数； 根据所述直流电流函数，交流侧电流幅值、桥臂电压频率和功率因数角，得到所述全桥 型模块化多电平换流器的桥臂电流函数。 6 .根据权利要求1所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于，所述获取全桥型模块化多电平换流器的交流侧电流幅值，并根据所述交流侧 电流幅值、功率因数角和所述全桥型模块化多电平换流器的子模块电容电压波动分量模 型，得到理论所需环流值，包括： 根据所述全桥型模块化多电平换流器的子模块电容电压波动分量模型，得到所述子模 块电容电压波动分量的初始纹波系数表达式； 根据所述初始纹波系数表达式，得到所述全桥型模块化多电平换流器的最佳调制比； 将所述最佳调制比代入所述初始纹波系数表达式，得到注入理论所需环流时的纹波系 数表达式； 根据所述注入理论所需环流时的波纹系数表达式,得到理论所需环流表达式； 获取所述全桥型模块化多电平换流器的交流侧电流幅值，并将采集的交流侧电流幅值 以及功率因数角代入所述理论所需环流表达式，得到理论所需环流值。 7 .根据权利要求6所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于,所述子模块电容电压波动分量包括基频波动分量，所述根据所述注入理论所 需环流时的波纹系数表达式,得到理论所需环流表达式，包括： 根据所述注入理论所需环流时的纹波系数表达式，得到基频波动分量的纹波系数，并 将所述基频波动分量的纹波系数设为零,得到理论所需环流表达式。 8 .根据权利要求7所述的全桥型模块化多电平换流器子模块电容电压波动抑制方法， 其特征在于,所述理论所需环流表达式为： 式中」2f为理论所需环流的幅值，中2f为理论所需环流的相位，I,为交流侧电流幅值，Μ 为最佳调制比，/为功率因数角。 9 .根据权利要求1-8任意一项所述的全桥型模块化多电平换流器子模块电容电压波动 抑制方法,其特征在于,所述实际环流值的表达式为； 4 - Uu + Λ + 号）/2 式中，I。为所述实际环流值,匕为所述上桥臂电流瞬时值，L为所述下桥臂电流瞬时值， Q为所述直流电流瞬时值。 10.根据权利要求「8任意一项所述的全桥型模块化多电平换流器子模块电容电压波 动抑制方法，其特征在于，所述计算所述理论所需环流值和所述实际环流值的差值,根据所 述差值生成参考电压，将所述参考电压注入所述全桥型模块化多电平换流器，并进行调制 后在各相中产生所需环流，对各子模块电容电压波动进行抑制,包括： 计算所述理论所需环流值和所述实际环流值的差值,根据所述差值生成参考电压，将 所述参考电压注入所述全桥型模块化多电平换流器，并利用最近电平逼近方法进行调制后 在各相中产生所需环流，对各子模块电容电压波动进行抑制。 [EN CN113224960A]: 1 A method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module, characterized in that it comprises: obtaining the AC side current amplitude of the full-bridge modular multilevel converter, and The AC side current amplitude, the power factor angle, and the sub-module capacitance voltage fluctuation component model of the full-bridge modular multilevel converter to obtain the theoretically required circulating current value; obtain the full-bridge modular multilevel converter The instantaneous value of the upper bridge arm current, the instantaneous value of the lower bridge arm current, and the instantaneous value of the DC current of the flat converter, and the actual circulating current value of the full-bridge modular multilevel converter is calculated; The difference between the required circulating current value and the actual circulating current value is used to generate a reference voltage based on the difference, and the reference voltage is injected into the full-bridge modular multilevel converter, and modulated in each phase Generate the required circulating current to suppress the fluctuation of the capacitor voltage of each sub-module. 2 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to claim 1, wherein said acquiring the AC side current amplitude of the full-bridge modular multilevel converter According to the AC side current amplitude, power factor angle and the sub-module capacitor voltage fluctuation component model of the full-bridge modular multilevel converter, before obtaining the theoretically required circulating current value, it also includes: The characteristic parameters of the full-bridge modular multilevel converter are obtained, and the sub-module capacitance voltage fluctuation component model of the full-bridge modular multilevel converter is obtained. 3 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to claim 2, wherein the characteristic parameters include power factor angle, modulation ratio, AC side current amplitude, bridge The arm voltage frequency, the number of sub-modules, the capacitance value of each sub-module, and the capacitance voltage of each sub-module are described according to the characteristic parameters of the full-bridge modular multilevel converter to obtain the full-bridge modular multilevel The sub-module capacitor voltage fluctuation component model of the converter includes: According to the modulation ratio, the bridge arm voltage frequency, the number of sub-modules, and the capacitor voltage of each sub-module, obtain the full-bridge modular multilevel converter, etc. Effective switching function; obtain the bridge arm current function of the full-bridge modular multilevel converter according to the power factor angle, modulation ratio, AC side current amplitude, and bridge arm voltage frequency; according to the equivalent switching function , The bridge arm current function, the capacitance value of each sub-module and the capacitance voltage of each sub-module are used to obtain the sub-module capacitance voltage fluctuation component model of the full-bridge modular multilevel converter. 4 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to claim 3, wherein the equivalent switching function is the reference voltage of the bridge arm and the capacitance voltage of all the full-bridge sub-modules And the ratio. 5 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to claim 3, characterized in that, according to the power factor angle, the modulation ratio, the AC side current amplitude and the bridge Arm voltage frequency to obtain the arm current function of the full-bridge modular multilevel converter, including: obtaining the full-bridge modular multilevel converter according to the power factor angle, modulation ratio and AC side current amplitude The DC current function of the leveling converter; according to the DC current function, the AC side current amplitude, the bridge arm voltage frequency and the power factor angle, the bridge arm current function of the full-bridge modular multilevel converter is obtained . 6 The method for suppressing capacitor voltage fluctuations in a sub-module of a full-bridge modular multilevel converter according to claim 1, wherein said acquiring the AC side current amplitude of the full-bridge modular multilevel converter According to the AC side current amplitude, power factor angle, and the sub-module capacitor voltage fluctuation component model of the full-bridge modular multilevel converter, the theoretical required circulating current value is obtained, including: According to the The capacitor voltage fluctuation component model of the sub-module of the full-bridge modular multilevel converter is obtained, and the sub-module is obtained The initial ripple coefficient expression of the voltage fluctuation component of the block capacitor; obtain the optimal modulation ratio of the full-bridge modular multilevel converter according to the initial ripple coefficient expression; and convert the optimal modulation ratio Substituting the initial ripple coefficient expression to obtain the ripple coefficient expression when injecting the theoretically required circulating current; obtaining the theoretically required circulating current expression according to the ripple coefficient expression when injecting the theoretically required circulating current; The AC side current amplitude of the full-bridge modular multilevel converter, and the collected AC side current amplitude and power factor angle are substituted into the theoretically required circulating current expression to obtain the theoretically required circulating current value. 7 The method for suppressing capacitor voltage fluctuations in a sub-module of a full-bridge modular multilevel converter according to claim 6, wherein the capacitor voltage fluctuation component of the sub-module includes a fundamental frequency fluctuation component, and the Inject the ripple coefficient expression when injecting the theoretically required circulating current to obtain the theoretically required circulating current expression, including: According to the ripple coefficient expression when injecting the theoretically required circulating current, the ripple coefficient of the fundamental frequency fluctuation component is obtained, and the The ripple coefficient of the fundamental frequency fluctuation component is set to zero, and the theoretically required circulating current expression is obtained. 8 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to claim 7, wherein the theoretically required circulating current expression is: where "2f is the theoretically required circulating current Where 2f is the phase of the theoretically required circulating current, I is the amplitude of the AC side current, M is the best modulation ratio, and / is the power factor angle. 9 The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to any one of claims 1-8, wherein the expression of the actual circulating current value is; 4 -Uu + Λ + sign)/2 where I. Is the actual circulating current value, d is the instantaneous value of the upper bridge arm current, L is the instantaneous value of the lower bridge arm current, and Q is the instantaneous value of the direct current. 10. The method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module according to any one of claims "8, wherein said calculation of said theoretical required circulating current value and said actual The difference of the circulating current value, the reference voltage is generated according to the difference, and the reference voltage is injected into the full-bridge modular multilevel converter, and after modulation, the required circulating current is generated in each phase. Sub-module capacitance voltage fluctuation suppression includes: calculating the difference between the theoretically required circulating current value and the actual circulating current value, generating a reference voltage according to the difference, and injecting the reference voltage into the full-bridge modular The multi-level converter uses the nearest level approximation method to modulate and generates the required circulating current in each phase to suppress the fluctuation of the capacitor voltage of each sub-module. | [ZH CN113224960A]: 全桥型模块化多电平换流器子模块电容电压波动抑制方法 技术领域 [0001]本申请涉及全桥型模块化多电平变流器技术领域，特别是涉及一种全桥型模块化 多电平换流器子模块电容电压波动抑制方法。 背景技术 [0002] 模块化多电平变流器(modular multilevel converter，MMC)凭借其开关器件无 动静态均压问题、易扩展、系统效率高及输出波形质量好等优势，已成为柔性直流输电中换 流器的首选拓扑。其中，全桥型MMC基于具备负电平输出能力的全桥型子模块，具备良好的 直流短路故障穿越和直流电压翻转特性，在由电网换相换流器和MMC构成的混合直流输电 系统中具有广阔的应用前景。全桥型MMC，每个桥臂含有大量级联的子模块，每个子模块均 含有一个电容，在稳态运行过程中，由于桥臂电流对子模块电容的充放电作用使得所有子 模块电容电压均处于波动状态。 [0003] 传统的全桥型MMC子模块电容电压波动抑制方法，利用全桥型MMC子模块的负电平 输出能力，在保持换流器传输容量以及直流侧电压不变的情况下，增大交流侧相电压峰值， 实现交流侧提压运行，以降低子模块电容电压波动率。然而，由于实际应用场景下，交流侧 相电压峰值的提压能力有限，传统的全桥型MMC子模块电容电压波动抑制方法，子模块电容 电压波动抑制效果并不显著。 [0004]因此，传统的全桥型MMC子模块电容电压波动抑制方法，具有子模块电容电压波动 抑制效果差的问题。 发明内容 [0005] 基于此，有必要针对上述技术问题，提供一种全桥型MMC子模块电容电压波动抑制 方法，提升子模块电容电压波动抑制效果。 [0006] 一种全桥型模块化多电平换流器子模块电容电压波动抑制方法，包括： [0007]获取全桥型模块化多电平换流器的交流侧电流幅值，并根据所述交流侧电流幅 值、功率因数角和所述全桥型模块化多电平换流器的子模块电容电压波动分量模型，得到 理论所需环流值； [0008]获取所述全桥型模块化多电平换流器的上桥臂电流瞬时值、下桥臂电流瞬时值和 直流电流瞬时值，并计算得到所述全桥型模块化多电平换流器的实际环流值； [0009]计算所述理论所需环流值和所述实际环流值的差值，根据所述差值生成参考电 压，将所述参考电压注入所述全桥型模块化多电平换流器，并进行调制后在各相中产生所 需环流，对各子模块电容电压波动进行抑制。 [0010]在其中一个实施例中，所述获取全桥型模块化多电平换流器的交流侧电流幅值， 并根据所述交流侧电流幅值、功率因数角和所述全桥型模块化多电平换流器的子模块电容 电压波动分量模型，得到理论所需环流值之前，还包括： [0011]根据全桥型模块化多电平换流器的特征参数，得到所述全桥型模块化多电平换流 器的子模块电容电压波动分量模型。 [0012]在其中一个实施例中，所述特征参数包括功率因数角、调制比、交流侧电流幅值、 桥臂电压频率、子模块个数、各子模块电容值和各子模块电容电压，所述根据全桥型模块化 多电平换流器的特征参数，得到所述全桥型模块化多电平换流器的子模块电容电压波动分 量模型，包括： [0013]根据调制比、桥臂电压频率、子模块个数和各子模块电容电压，得到所述全桥型模 块化多电平换流器的等效开关函数； [0014]根据功率因数角、调制比、交流侧电流幅值和桥臂电压频率，得到所述全桥型模块 化多电平换流器的桥臂电流函数； [0015]根据所述等效开关函数、所述桥臂电流函数、各子模块电容值和各子模块电容电 压，得到所述全桥型模块化多电平换流器的子模块电容电压波动分量模型。 [0016]在其中一个实施例中，所述等效开关函数为桥臂参考电压与所有全桥子模块电容 电压和之比。 [0017]在其中一个实施例中，所述根据功率因数角、所述调制比、交流侧电流幅值和桥臂 电压频率，得到所述全桥型模块化多电平换流器的桥臂电流函数，包括： [0018]根据功率因数角、调制比和交流侧电流幅值，得到所述全桥型模块化多电平换流 器的直流电流函数； [0019] 根据所述直流电流函数，交流侧电流幅值、桥臂电压频率和功率因数角，得到所述 全桥型模块化多电平换流器的桥臂电流函数。 [0020]在其中一个实施例中，所述获取全桥型模块化多电平换流器的交流侧电流幅值， 并根据所述交流侧电流幅值、功率因数角和所述全桥型模块化多电平换流器的子模块电容 电压波动分量模型，得到理论所需环流值，包括： [0021]根据所述全桥型模块化多电平换流器的子模块电容电压波动分量模型，得到所述 子模块电容电压波动分量的初始纹波系数表达式； [0022]根据所述初始纹波系数表达式，得到所述全桥型模块化多电平换流器的最佳调制 比； [0023]将所述最佳调制比代入所述初始纹波系数表达式，得到注入理论所需环流时的纹 波系数表达式； [0024]根据所述注入理论所需环流时的波纹系数表达式，得到理论所需环流表达式； [0025]获取所述全桥型模块化多电平换流器的交流侧电流幅值，并将采集的交流侧电流 幅值以及功率因数角代入所述理论所需环流表达式，得到理论所需环流值。 [0026]在其中一个实施例中，所述子模块电容电压波动分量包括基频波动分量，所述根 据所述注入理论所需环流时的波纹系数表达式，得到理论所需环流表达式，包括： [0027]根据所述注入理论所需环流时的纹波系数表达式，得到基频波动分量的纹波系 数，并将所述基频波动分量的纹波系数设为零，得到理论所需环流表达式。 [0028] 在其中一个实施例中，所述理论所需环流表达式为： 广二—3ίηφ [0030] 式中，%f为理论所需环流的幅值，82f为理论所需环流的相位，Is为交流侧电流幅 值,Μ为最佳调制比，◎为功率因数角。 [0031]在其中一个实施例中，所述实际环流值的表达式为； [。。32] lc =(九 + /(+ 蜀/2 [0033]式中，I。为所述实际环流值，匕为所述上桥臂电流瞬时值，L为所述下桥臂电流瞬 时值,Q为所述直流电流瞬时值。 [0034]在其中一个实施例中，所述计算所述理论所需环流值和所述实际环流值的差值， 根据所述差值生成参考电压，将所述参考电压注入所述全桥型模块化多电平换流器，并进 行调制后在各相中产生所需环流，对各子模块电容电压波动进行抑制,包括： [0035]计算所述理论所需环流值和所述实际环流值的差值，根据所述差值生成参考电 压，将所述参考电压注入所述全桥型模块化多电平换流器，并利用最近电平逼近方法进行 调制后在各相中产生所需环流，对各子模块电容电压波动进行抑制。 [0036]上述全桥型MMC子模块电容电压波动抑制方法，首先根据全桥型MMC的子模块电容 电压波动特性，得到理论所需环流值;再根据获取的电流数据，到实际环流值;最后再根据 该理论所需环流值和实际环流值的差值，生成参考电压，并将该参考电压注入该全桥型 MMC,通过调制后在各相中产生所需环流，对子模块电容电压波动进行抑制。可以根据实际 环流值注入对应的参考电压，有利于提升子模块电容电压波动抑制效果。 附图说明 [0037]图1为一实施例中全桥型MMC的基本电路拓扑； [0038]图2为一实施例中全桥型MMC桥臂参考电压与直流电压关系示意图； [0039]图3为一实施例中全桥型MMC子模块电容电压波动抑制方法的流程图； [0040]图4为另一实施例中全桥型MMC子模块电容电压波动抑制方法的流程图； [0041]图5为一实施例中根据全桥型模块化多电平换流器的特征参数，得到全桥型模块 化多电平换流器的子模块电容电压波动分量模型的流程图； [0042]图6为一实施例中根据功率因数角、调制比、交流侧电流幅值和桥臂电压频率，得 到全桥型模块化多电平换流器的桥臂电流函数的流程图； [0043]图7为一实施例中获取全桥型模块化多电平换流器的交流侧电流幅值，并根据交 流侧电流幅值、功率因数角和全桥型模块化多电平换流器的子模块电容电压波动分量模 型,得到理论所需环流值的流程图； [0044]图8为一实施例中全桥型MMC子模块电容电压纹波随功率因数角变化曲线； [0045]图9为一实施例中全桥型MMC环流注入控制框图； [0046]图10为一实施例中额定工况下未采用环流注入时全桥型MMC稳态仿真结果示意 图； [0047]图11为一实施例中额定工况下采用环流注入时全桥型MMC稳态仿真结果示意图； [0048]图12为一实施例中单位功率因数情况下未采用环流注入时全桥型MMC稳态仿真结 果示意图； [0049]图13为一实施例中单位功率因数情况下未采用环流注入时全桥型MMC稳态仿真结 果示意图。 具体实施方式 [0050]为了使本申请的目的、技术方案及优点更加清楚明白，以下结合附图及实施例，对 本申请进行进一步详细说明。应当理解，此处描述的具体实施例仅仅用以解释本申请，并不 用于限定本申请。 [0051]除非另有定义，本文所使用的所有的技术和科学术语与属于本申请的技术领域的 技术人员通常理解的含义相同。本文中在本申请的中所使用的术语只是为了描述具 体的实施例的目的，不是旨在于限制本申请。 [0052]可以理解，以下实施例中的“连接”，如果被连接的电路、模块、单元等相互之间具 有电信号或数据的传递，则应理解为“电连接”、“通信连接”等。 [0053]在此使用时，单数形式的“一”、“一个”和“所述/该”也可以包括复数形式，除非上 下文清楚指出另外的方式。还应当理解的是，术语“包括/包含”或“具有”等指定所陈述的特 征、整体、步骤、操作、组件、部分或它们的组合的存在，但是不排除存在或添加一个或更多 个其他特征、整体、步骤、操作、组件、部分或它们的组合的可能性。同时，在本中使用 的术语“和/或”包括相关所列项目的任何及所有组合。 [0054] 基于电压源换流器的柔性高压直流输电（voltage source converter high voltage direct current，VSC「HVDC）系统能够实现有功功率和无功功率解耦控制，不存在 换相失败风险，且具备黑启动能力，在大规模可再生能源汇集与输送、交流电网异步互联等 场合存在广阔的应用前景。但传统的VSC-HVDC系统广泛采用功率半导体器件直接串联的两 电平或三电平换流器，滤波器体积庞大且运行效率较低，限制了VSC-HVDC的发展。为此，德 国学者R.Marquardt提出了模块化多电平变流器（modular multilevel converter,MMC）， 相比传统的电压源换流器，MMC主要存在以下优势：1）具有模块化结构，可通过设置不同数 量模块灵活调节MMC电压等级；2）输出电平数多，谐波含量较低；3）功率半导体器件开关频 率低，效率较高；4）交流侧无需体积庞大的滤波装置;5）可设置冗余模块，可靠性较高。因 此，MMC在VSC-HVDC领域获得了较广泛的应用。近些年，国内外建设的VSC-HVDC工程几乎都 采用了MMC拓扑。 [0055]为抑制全桥型MMC子模块电容电压波动，通常可以采取以下两种方式:一是背景技 术中所提到的通过增大交流侧相电压峰值，实现交流侧提压运行，以降低子模块电容电压 波动率；二是改变全桥型MMC的拓扑结构，采用箝位双子模块和半桥子模块构成的混合型 MMC电路拓扑，在能够实现直流短路故障阻断的情况下最大程度减少功率半导体器件数量。 对于第一种波动抑制方法的缺点，此处不再赘述。对于第二种波动抑制方法，虽然能够一定 程度上抑制子模块电容电压波动，但该拓扑无法实现故障穿越。 [0056] 基于此，本申请提出一种全新的全桥型MMC子模块电容电压波动抑制方法，充分利 用全桥型MMC子模块电容电压波动特性,通过环流注入，消除无功功率产生的基频波动分 量，从而降低全桥型MMC子模块电容电压波动。 [0057]下面将结合本发明实施例中的附图，对本实发明实施例中的技术方案进行清楚、 完整地描述。如图1所示,全桥型MMC的基本电路拓扑与半桥型MMC类似，也由三相六个桥臂 构成，即每一相包含上、下两个桥臂。但全桥型MMC的每个子模块由四只功率半导体器件和 一个直流电容构成，因此，全桥子模块能够输出三种电平，当功率半导体器件ΊΊ和T4处于导 通状态时,其输出正电容电压；当功率半导体器件T2和T3处于导通状态时，其输出负电容电 压,其余情况输出零电平。如图2所示,由于全桥型MMC子模块能够输出负电平，在稳态运行 过程中其桥臂可包含负电压分量，图2中,Un为直流电压,NU。为桥臂子模块电容电压。 [0058]在一个实施例中，如图3所示，提供了一种全桥型MMC子模块电容电压波动抑制方 法,包括步骤S200至步骤S600 ο [0059]步骤S200：获取全桥型模块化多电平换流器的交流侧电流幅值，并根据交流侧电 流幅值、功率因数角和全桥型模块化多电平换流器的子模块电容电压波动分量模型，得到 理论所需环流值。 [0060]其中，功率因数角是功率因数的反余弦，而功率因数为额定有功功率和额定无功 功率的比值。获取全桥型MMC的交流侧电流幅值的方法，可以是主动获取或者被动接收。具 体的，可以基于预设频率进行交流侧电流幅值的获取动作，以得到全桥型MMC运行状态的实 时参数，再根据全桥型MMC的子模块电容电压波动分量模型，将全桥型MMC的功率因数角和 交流侧电流幅值代入子模块电容电压波动分量模型，得到理论所需环流值。 [0061]步骤S400：获取全桥型模块化多电平换流器的上桥臂电流瞬时值、下桥臂电流瞬 时值和直流电流瞬时值,并计算得到全桥型模块化多电平换流器的实际环流值。 [0062]同样的，获取全桥型模块化多电平换流器的上桥臂电流瞬时值、下桥臂电流瞬时 值和直流电流瞬时值的方式，可以是主动获取，也可以是被动接收。具体的，在全桥型MMC三 相对称运行,且三相所有全桥型子模块都相同的前提下，获取全桥型MMC三相中任意一相的 上桥臂电流瞬时值、下桥臂电流瞬时值和直流电流瞬时值，就可以得到全桥型MMC的实际环 流值。载全桥型MMC三相非对称运行时，则需分别获取各相的上桥臂电流瞬时值、下桥臂电 流瞬时值和直流电流瞬时值，进而计算得到各相的实际环流值。 [0063] 在一个实施例中，实际环流值的表达式为； [0064] lc （/u + /（ + 号·）/2 [0065]式中，I。为实际环流值,匕为上桥臂电流瞬时值，L为下桥臂电流瞬时值为直流 电流瞬时值。 [0066] 步骤S600 ：计算理论所需环流值和实际环流值的差值,根据该差值生成参考电压， 将该参考电压注入全桥型模块化多电平换流器，并进行调制后在各相中产生所需环流，对 各子模块电容电压波动进行抑制。 [0067] 其中，调制方法可以是脉宽调制方法或最近电平逼近调制方法。具体的，计算理论 所需环流值和实际环流值的差值，根据该差值生成参考电压，并将该参考电压注入全桥型 MMC的对应相中。再通过脉宽调制方法或最近电平逼近调制方法生成控制信号，控制全桥型 模块化多电平换流器中的开关器件，完成参考电压在每个桥臂子模块的调制，从而在全桥 型MMC的各相中产生所需环流，对各相子模块电容电压波动进行抑制。 [0068]上述全桥型MMC子模块电容电压波动抑制方法，首先根据全桥型MMC的子模块电容 电压波动特性，得到理论所需环流值;再根据获取的电流数据，到实际环流值;最后再根据 该理论所需环流值和实际环流值的差值，生成参考电压，并将该参考电压注入该全桥型 MMC,通过调制后在各相中产生所需环流，对子模块电容电压波动进行抑制。可以根据实际 环流值注入对应的参考电压，有利于提升子模块电容电压波动抑制效果。 [0069] 在一个实施例中,如图4所示,步骤S200之前，还包括步骤S100 ：根据全桥型模块化 多电平换流器的特征参数,得到全桥型模块化多电平换流器的子模块电容电压波动分量模 型。 [0070]其中，全桥型MMC的特征参数包括功率因数角、调制比、交流侧电流幅值、桥臂电压 频率、子模块个数、各子模块电容值和各子模块电容电压等。功率因数角为功率因数的反余 弦，可以由额定有功功率和额定无功功率得到。具体的,根据全桥型MMC的特征参数,结合全 桥型MMC的拓扑结构和工作特性，对全桥型MMC的子模块电容电压波动过程进行分析，可以 得到全桥型MMC的子模块电容电压波动分量模型。 [0071] 在一个实施例中，全桥型MMC的子模块电容电压波动分量模型为： [0072] cu = &amp; + 3 t + 卷§讥（公七一①）… 一鬻- 0）] [0073]式中，u°u为子模块电容电压瞬时值,U°为各子模块电容电压,No为直流电压％。与U° 的比值,Ν为子模块个数,C为各子模块电容值,m为调制比，I,为交流侧电流幅值，3为桥臂 电压频率，（P为功率因数角。 [0074]在一个实施例中，特征参数包括功率因数角、调制比、交流侧电流幅值、桥臂电压 频率、子模块个数、各子模块电容值和各子模块电容电压，如图5所示，步骤S100包括步骤 S110至步骤S130。 [0075]步骤S110：根据调制比、桥臂电压频率、子模块个数和各子模块电容电压，得到全 桥型模块化多电平换流器的等效开关函数。 [0076]如上文所述,全桥型MMC实质上是由多个全桥电路组成的，通过控制全桥电路上开 关器件的通断，可以改变全桥型MMC子模块的输出电平,进而影响子模块的电容电压。基于 此,全桥型MMC中各开关器件工作状态，会影响各子模块的电容电压波动情况。其中，等效开 关函数是用于表征全桥型MMC中各开关器件工作状态的函数。 [0077] 比，即: [0078] [0079] 在一个实施例中，等效开关函数为桥臂参考电压与所有全桥子模块电容电压和之 二m cos ω t) 式中，u°u为子模块电容电压瞬时值,以为交流侧电压幅值,明。为直流电压,No为直 流电压与U°的比值,Ν为子模块个数,U°为各子模块电容电压,m为调制比，3为桥臂电压 频率。 [0080]步骤S120：根据功率因数角、调制比、交流侧电流幅值和桥臂电压频率，得到全桥 型模块化多电平换流器的桥臂电流函数。 [0081]具体的，根据功率因数角、调制比、交流侧电流幅值和桥臂电压频率，结合全桥型 MMC的拓扑结构，可以得到全桥型MMC的桥臂电流函数。 [0082]步骤S130：根据等效开关函数、桥臂电流函数、各子模块电容值和各子模块电容电 压，得到全桥型模块化多电平换流器的子模块电容电压波动分量模型。 [0083]具体的，根据等效开关函数、桥臂电流函数、各子模块电容值和各子模块电容电 压，将等效开关函数和桥臂电流函数对时间积分，可以得到子模块电容电压瞬时值的表达 式，进而得到全桥型MMC子模块电容电压波动分量模型。 [0084]其中，子模块电容电压瞬时值的表达式为： [0085] ucu + Suiudt [0086]式中，u°u为子模块电容电压瞬时值,U°为各子模块电容电压,C为各子模块电容值, Su为等效开关函数,r为桥臂电流函数。 [0087] 在一个实施例中，如图6所示，步骤S120包括步骤S121和步骤S122。 [0088]步骤S121：根据功率因数角、调制比和交流侧电流幅值，得到全桥型模块化多电平 换流器的直流电流函数。 [0089]具体的，结合全桥型MMC的电路拓扑，根据功率因数角、调制比和交流侧电流幅值, 得到全桥型模块化多电平换流器的直流电流函数为： [0090] /a=—m/5 cos φ [0091]步骤S122：根据直流电流函数，交流侧电流幅值、桥臂电压频率和功率因数角，得 到全桥型模块化多电平换流器的桥臂电流函数。 [0092]具体的，根据直流电流函数，交流侧电流幅值、桥臂电压频率和功率因数角，得到 全桥型模块化多电平换流器的桥臂电流函数为： 1 [0093] iu + 2COS (st - 0) [0094] 式中，臬为桥臂电流,In为直流电流函数，I,为交流侧电流幅值，/为功率因数角， 3为桥臂电压频率。 [0095]上述实施例中，即是给出了全桥型MMC的子模块电容电压波动分量模型的建立过 程,为理论所需环流值的确定过程提供依据。 [0096] 在一个实施例中，如图7所示，步骤S200包括步骤S210至步骤S250。 [0097]步骤S210：根据全桥型模块化多电平换流器的子模块电容电压波动分量模型，得 到子模块电容电压波动分量的初始纹波系数表达式。 [0098]其中，电压纹波是指输出直流电压中的交流成分。纹波系数,是指直流电压中的交 流成分的峰峰值。具体的，根据全桥型MMC的子模块电容电压波动分量模型，去除子模块电 容电压中的直流成分，就可以得到子模块电容电压波动分量的初始纹波系数表达式。 [0099]步骤S220：根据初始纹波系数表达式,得到全桥型模块化多电平换流器的最佳调 制比。 [0100] 步骤S230：将最佳调制比代入初始纹波系数表达式,得到注入理论所需环流时的 纹波系数表达式。 [0101] 对于全桥型MMC,由于其桥臂中能够包含负电压分量，因此，其调制比可大于1。因 此，根据初始纹波系数表达式，可以分析得出其他条件一定时初始波纹系数与调制比的关 系，进而得出全桥型MMC的最佳调制比。再将最佳调制比代入初始纹波系数表达式,并假设 已注入理论所需环流，可以得到注入理论所需环流时的纹波系数表达式。 [0102] 步骤S240：根据注入理论所需环流时的波纹系数表达式，得到理论所需环流表达 式。 [0103]具体的,根据注入理论所需环流时的波纹系数表达式,结合预设条件，可以得到理 论所需环流表达式。该预设条件，可以是波动分量为极小值，也可以是波纹系数为零。 [0104]在一个实施例中，子模块电容电压波动分量包括基频波动分量，步骤S240包括:根 据注入理论所需环流时的纹波系数表达式，得到基频波动分量的纹波系数,并将基频波动 分量的纹波系数设为零，得到理论所需环流表达式。具体的，当基频波动分量的纹波系数设 为零时，全桥型MMC的基频波动分量为零，即注入理论所需环流后，可以消除全桥型MMC的基 频波动分量。 [0105] 在一个实施例中，理论所需环流表达式为： （侬=2 [0107] 式中，^f为理论所需环流的幅值，92；·为理论所需环流的相位，I,为交流侧电流幅 值,Μ为最佳调制比，0为功率因数角。 [0108]步骤S250：获取全桥型模块化多电平换流器的交流侧电流幅值，并将采集的交流 侧电流幅值以及功率因数角代入理论所需环流表达式，得到理论所需环流值。 [0109]具体的，获取全桥型MMC的交流侧电流幅值，并将该交流侧电流幅值和功率因数角 代入理论所需环流表达式,可以得到理论所需环流值。 [0110] 对应的，步骤400包括:获取全桥型MMC的上桥臂电流瞬时值、下桥臂电流瞬时值和 直流电流瞬时值，并计算得到全桥型MMC的实际环流的幅值和相位。步骤600包括:计算理论 所需环流值和实际环流值的幅值和相位差,并根据该幅值和相位差，生成参考电压,将参考 电压注入全桥型MMC,并进行调制后在各相中产生所需环流，对各子模块电容电压波动进行 抑制。 [0111]为便于理解，下面对全桥型MMC子模块电容电压波动抑制过程进行详细说明。需要 说明的是，本实施例中全桥型MMC子模块电容电压波动分量模型的建立过程，以以下假设为 前提： [0112] ⑴全桥型MMC三相对称运行，每一相的上、下桥臂对称； [0113] ⑵三相所有全桥型子模块都相同,电压在所有子模块中均匀分布； [0114] ⑶忽略桥臂等效电阻对全桥型MMC的影响。 [0115]设全桥型MMC的调制比为m,其直流电压与交流相电压的幅值分别为明。和也。由此 可得： [0117]进一步的，设全桥型MMC直流电流为：。，交流侧电流幅值为Ι,，忽略损耗的情况下， 根据功率守恒可以得到： [0118] i7dc/dc =汐s『s cos φ (2) [0119] 其中，/为全桥型MMC的功率因数角。将式⑴带入式⑵，可以得到： 3 [0120] /dc = -m/s cos 0 (3) [0121]由于三相所有全桥型子模块都相同，因此各相的子模块电容电压波动情况均相 同，下面以全桥型MMC的A相为例进行说明。定义其桥臂等效开关函数为桥臂参考电压与所 有全桥子模块电容电压和之比，即： u介 [0122] = (4) [0123]式中，Sau为A相的等效开关函数,U°为各子模块电容电压,No为直流电压％。与U°的 比值,Ν为子模块个数。一般而言,全桥型MMC桥臂二倍频环流的存在会增加换流器损耗与子 模块电容电压波动，因此，在实际系统中需对抑制二倍频环流,从而可得到其桥臂电流表达 式为： [0124] iau = £/dc +COS(3t - (p) (5) [0125]式中，iau为A相桥臂电流函数。由于全桥型MMC每个桥臂电压在桥臂所有子模块中 均匀分布，所以可通过下式计算得到任意全桥子模块电容电压瞬时值： [0126] ^-cau — Ue 十 Sauiaudt (6) [0127]式中，U°au为A相子模块电容电压瞬时值,C为各子模块电容值。 [0128] 将式⑶、(4)和⑸带入式⑹，可得： [0129] 观曲” =Ue 十 巴筌to t 十套si(3t - 0)…一翳(7) [0130]根据式(7),去除子模块电容电压中的直流成分，就可以得到子模块电容电压波动 分量的初始纹波系数表达式。由式⑺可知，全桥子模块电容电压主要包含基频和二倍频波 动分量，因此初始纹波系数包含基频纹波系数。f和二倍频波纹系数。2铲根据式⑺，计算得 到基频纹波系数ff和二倍频波纹系数。2f分别为： 「01311 e = NΜ(2-吟2 cos? 0+4sin2 审 饮、 [0132] _ mN% 2f — (9) [0133] 对于半桥型MMC,由于其调制比m始终小于1,因此，其子模块电容电压波动中基频 分量占主要部分。但对于全桥型MMC来说,情况有所不同，这主要原因在于其桥臂中能够包 含负电压分量，其调制比可大于1。另外,应用于HVDC领域的全桥型MMC在大多数情况下均运 行于单位功率因数情况下，即便交流侧存在无功功率，其功率因数一般也在0.97以上。因 此,对于全桥子模块电容电压波动来说，其幅值主要由式⑻中的(2 - m^cos2 0决定。 基于此，当全桥型MMC的调制比为1.414时,可消除其子模块电容电压大部分基频波动分量， 从而大幅度降低全桥子模块电容电压波动，减小全桥型MMC子模块电容。也即，最佳调制比Μ 为1.414。 [0134] 此外，由式⑻可知,当全桥型MMC交流侧存在无功功率时，其子模块电容电压仍包 含部分基频波动分量。MMC子模块电容电压不同频率波动分量幅值与其角频率成反比。因 此，由无功功率引起的基频波动分量能够增加全桥型MMC子模块电容电压波动，进而增加其 子模块电容。 [0135]如图8所示，为全桥型MMC子模块电容电压波动随功率因数变化曲线。其中，全桥子 模块电容电压波动分量基值如下 [0136] % = (1°) [0137] 由图可知，仅当全桥型MMC调制比为1.414,且处于单位功率因数运行工况时，其子 模块电容电压波动最小,主要包含二倍频波动。而在非单位功率因数情况下，由无功功率产 生的基频波动分量会增加全桥子模块电容电压波动幅值，即便是全桥型MMC无功功率仅占 传输有功功率25%的情况下(cos 9=0.97 ),相比单位功率因数情况,全桥子模块电容电 压纹波增加近30%。因此,全桥型MMC交流侧无功功率会极大增加其子模块电容电压纹波， 不仅导致全桥子模块电容体积增大，也会使全桥型MMC成本增加。为此，需要研究能够抑制 全桥型MMC无功功率所产生的子模块电容电压基频波动分量方法。 [0138]如前文所述，当全桥型MMC调制比为1.414时，其交流侧无功功率所产生的基频波 动分量会极大增加全桥子模块电容电压波动，从而增大子模块电容值，进而增加全桥型MMC 成本。因此，需要在非单位功率因数情况下实现由于无功功率产生的全桥子模块电容电压 基频波动分量。 [0139]与半桥型MMC类似,在不施加环流抑制策略的情况下，全桥型MMC桥臂中也会产生 二倍频环流，而全桥型MMC桥臂等效开关函数中主要包含直流和基频分量。因此，环流与桥 臂等效开关函数能够产生全桥子模块基频波动分量，通过调节环流的幅值与相位,使环流 产生的基频波动分量与无功功率产生的基频波动相互抵消，从而达到抑制全桥型MMC非单 位功率因数情况下子模块电容电压中的基频波动分量。 [0140] 假设在全桥型MMC桥臂中注入环流的幅值与相位分别为12f和Φ 2f,则根据⑸可 以得到此时全桥型MMC的A相上桥臂电流iau c为： [0141] Lau c = ¦/dc + COS((Ot - φ} + I2f COS(2wt + (11) [0142]将式(3)、(4)和(11)带入式⑹中，可以计算得到注入环流后全桥子模块电容电压 波动U°auj为： Ucau_c = £ i Saniau_cdt = ¦·_ μ iscos&lt;p t + Is stn(wt — p) — MJ2f sin(st + φ2^ —华stn(23t — ¢) + 12f 5ίη(2ωΐ + @2/·) —^^-5ίη(3ωί + 92/)] （12） [0144]由式（12）可知，在全桥型MMC桥臂中注入二倍频环流后，全桥子模块电容电压除包 含基频和二倍频波动分量外，还会产生少量的三倍频波动分量。但相比基频和二倍频波动 分量，三倍频幅值较小，因此，忽略由二倍频环流所产生三倍频波动分量。因此，根据式（12） 可得在环流注入情况下全桥子模块电容电压基频纹波系数为： [0145] 守/二生猊 口一贮芍竺里S讥3t +比（3t一0）-用传5亩（皿+ 32『）¦¦ （於） [0146] 其中，¦ ¦ ¦「表示基频纹波范数。在全桥型MMC的调制比为1.414的情况下,通过注 入环流消除由无功功率产生的基频波动分量，即令式（13）所示的全桥MMC子模块基频纹波 系数为零,得到理论所需注入环流的幅值与相位为： 72f = —5ΐηφ [0147]: 匕 （14） [0148]因此，在全桥型MMC桥臂中注入幅值和相位如式（14）所示的环流，即能消除由无功 功率产生的基频波动分量,从而使全桥型MMC子模块电容电压中主要包含二倍频波动分量。 [0149]进一步的，可以计算得到此时全桥型MMC子模块电容电压二倍频纹波系数Z c为： [0150] £2f c - Ά - ¢） +/2/5ίη（2ωί + 甲zf）¦¦ （⑸ [0151] 将式（14）带入式（15）,可以得到： [0152] (16) [0153] 根据式（16）可知,注入二倍频环流后全桥子模块电容电压二倍频波动分量与未注 入环流时相当，因此，采用本申请中的环流注入方法既能够消除由无功功率产生的基频波 动，又不会增加全桥子模块电容电压二倍频波动分量。 [0154]如图9所示，根据全桥型MMC的有功功率（P）和无功功率（Q）计算功率因数角，结合 其交流侧电流幅值计算得到理论所需环流值,再将理论所需环流值与采样得到的环流做 差，经过比例谐振控制器产生参考电压，将生成的参考电压加入到通过双闭环控制产生的 各桥臂参考电压中，通过最近电平逼近方法完成每个桥臂全桥子模块调制，从而在全桥型 MMC各相中产生所需环流，进而完成全桥型MMC非单位功率因数条件下子模块电容电压基频 纹波抑制。 [0155]为验证本发明所提出的环流注入方法的有效性，在仿真软件中搭建了 ±160kV/ 400MW的全桥型MMC仿真模型，其主电路参数如表1所示。 [0156]如表1所示的全桥型MMC主电路参数，可以计算得到其调制比为1.414。另外，根据 式（14）可以计算得到注入二倍频环流幅值约为208A。注入二倍频环流后全桥子模块电容电 压纹波可降低约30%,但所注入的二倍频环流还会产生三倍频电容电压波动分量，虽然三 倍频波动分量幅值较小，但也会增加全桥子模块电容电压波动。因此，采用所提出的环流注 入方法后，按可减少全桥子模块电容电压波动20%考虑，即在全桥子模块电容电压波动基 本相当的情况下，采用所提出的环流注入方法后,全桥型MMC子模块电容可降低约20%。即， 如表1所示,未采用环流注入的全桥型MMC子模块电容为4.5mF,采用所提出的环流注入方法 后,子模块电容为3.6mF。 [0157] 表1全桥型MMC的主电路参数 电路参数 无环流注入 环流注入 额定仃功功率 400 MW 400 MW 额定无功功率 100 Mvar 100 Mvar 直流电压 ±160 kV ±160 kV 交流线电压[0158] (mis) 277 kV 277 kV 桥臂模块个数 215 215 模块电容 4 5 mF 3.6 mF 桥臂也感 40 mH 40 mH 全桥子模块平 均电压 2.0 kV 2.0 kV [0159]如图10所示为额定工况下全桥型MMC未采用环流注入时额定工况下仿真结果。图 10(a)-(d)分别为四象限运行条件下全桥子模块电容电压波形。由仿真结果可知，当全桥型 MMC调制比为1.414时,其子模块电容电压波动以二倍频分量为主。而当全桥型MMC交流侧存 在无功功率时，其子模块电容电压波动也包含基频分量，与前文分析基本一致。根据图10 (a) - (d)可知，全桥子模块电容电压纹波约为4.6%。 [0160] 额定工况下，采用上文所述的环流注入方法,全桥型MMC四象限稳态仿真结果如图 11所示。注入环流后，全桥型MMC子模块电容电压主要包含二倍频波动分量，即由无功功率 所产生的基频波动分量被消除。如图11 (a) -(d)可知，采用所提出的环流注入方法后，全桥 型MMC子模块电容电压波动范围约为1907V〜2095V，纹波系数为4.7%。即，环流注入后，全 桥型型MMC子模块电容降低约20%。 [0161] 此外,根据式(14)可知,在单位功率因数情况下,全桥型MMC注入环流的幅值为零, 即单位功率因数情况下无需注入二倍频环流。因此，需要考虑全桥型MMC子模块电容减小后 在单位功率因数情况下其电容电压波动情况，为此，分别进行全桥型MMC单位功率因数情况 下仿真。 [0162]在单位功率因数情况下，全桥型MMC子模块电容为4.5mF时，其仿真结果如图12所 示;全桥型MMC子模块电容为3.6mF时，其仿真结果如图13所示。根据图12和图13所示的仿真 结果，在单位功率因数情况下，全桥型MMC子模块电容电压波动几乎全部为二倍频波动分 量,与前文的分析结果基本一致。另外，当全桥型MMC子模块电容为4.5mF时，其子模块电容 电压波动范围约为1940〜2060V,纹波系数约为3%,全桥子模块电容为3.6mF时，其子模块 电容电压波动范围约为1922〜2072V,纹波系数约为3.6%。虽然在单位功率因数情况下，全 桥型MMC子模块电容减小后其子模块电容电压纹波系数增大，但其纹波系数均小于额定工 况下。因此，单位功率因数情况下未采用环流注入的全桥型MMC子模块电容电压波动仍然满 足系统设计要求。 [0163] 根据以上仿真结果可知，本申请所提出的环流注入方法能够抑制由于全桥型MMC 无功功率所产生的子模块电容电压基频波动分量，可在全桥子模块电容电压波动基本相当 的情况下实现降低全桥型MMC子模块电容约20%。 [0164]以上实施例的各技术特征可以进行任意的组合，为使描述简洁，未对上述实施例 中的各个技术特征所有可能的组合都进行描述，然而，只要这些技术特征的组合不存在矛 盾，都应当认为是本记载的范围。 [0165]以上该实施例仅表达了本申请的几种实施方式，其描述较为具体和详细，但并不 能因此而理解为对发明专利范围的限制。应当指出的是，对于本领域的普通技术人员来说， 在不脱离本申请构思的前提下，还可以做出若干变形和改进，这些都属于本申请的保护范 围。因此，本申请专利的保护范围应以所附权利要求为准。 [EN CN113224960A]: Full-bridge modular multilevel converter sub-module capacitance voltage fluctuation suppression method technical field [0001] This application relates to the technical field of full-bridge modular multilevel converters, and in particular to a method for suppressing capacitance voltage fluctuations of sub-modules of full-bridge modular multilevel converters. Background technique [0002] Modular multilevel converter (MMC) has become a flexible direct current power converter due to its advantages in switching devices, such as no dynamic and static voltage equalization, easy expansion, high system efficiency, and good output waveform quality. The preferred topology of the streamer. Among them, the full-bridge MMC is based on a full-bridge sub-module with negative level output capability, and has good DC short-circuit fault ride-through and DC voltage reversal characteristics. Broad application prospects. Full-bridge MMC, each bridge arm contains a large number of cascaded sub-modules, and each sub-module contains a capacitor. During steady-state operation, the capacitor voltage of all sub-modules is caused by the charging and discharging effect of the bridge arm current on the sub-module capacitance. All are in a state of volatility. [0003] The traditional full-bridge type MMC sub-module capacitance voltage fluctuation suppression method uses the negative level output capability of the full-bridge type MMC sub-module to increase the AC voltage while keeping the converter transmission capacity and DC side voltage unchanged. The side-phase voltage peak value realizes the AC side boost operation to reduce the fluctuation rate of the sub-module capacitor voltage. However, due to the limited boosting ability of the AC side phase voltage peak in actual application scenarios, the traditional full-bridge MMC sub-module capacitor voltage fluctuation suppression method, the sub-module capacitor voltage fluctuation suppression effect is not significant. [0004] Therefore, the traditional full-bridge type MMC sub-module capacitor voltage fluctuation suppression method has the problem of poor suppression effect of the sub-module capacitor voltage fluctuation. Summary of the invention [0005] Based on this, it is necessary to provide a full-bridge type MMC sub-module capacitor voltage fluctuation suppression method to improve the suppression effect of the sub-module capacitor voltage fluctuation in response to the above technical problems. [0006] A method for suppressing capacitance voltage fluctuations of a full-bridge modular multilevel converter sub-module includes: [0007] Obtain the AC side current amplitude of the full-bridge modular multilevel converter, and according to the AC side current amplitude, power factor angle and the full-bridge modular multilevel converter Sub-module capacitor voltage fluctuation component model to obtain the theoretical required circulating current value; [0008] Obtain the instantaneous value of the upper bridge arm current, the instantaneous value of the lower bridge arm current, and the instantaneous value of the direct current of the full-bridge modular multilevel converter, and calculate the full-bridge modular multilevel The actual circulating current value of the inverter; [0009] Calculate the difference between the theoretical required circulating current value and the actual circulating current value, generate a reference voltage according to the difference, and inject the reference voltage into the full-bridge modular multilevel converter, And after modulation, the required circulating current is generated in each phase to suppress the fluctuation of the capacitor voltage of each sub-module. [0010] In one of the embodiments, the acquisition of the AC side current amplitude of the full-bridge type modular multilevel converter is based on the AC side current amplitude, the power factor angle and the full-bridge type The sub-module capacitance voltage fluctuation component model of the modular multilevel converter, before obtaining the theoretical required circulating current value, also includes: [0011] According to the characteristic parameters of the full-bridge modular multilevel converter, the full-bridge modular multilevel converter is obtained The capacitor voltage fluctuation component model of the sub-module of the converter. [0012] In one of the embodiments, the characteristic parameters include power factor angle, modulation ratio, AC side current amplitude, bridge arm voltage frequency, number of sub-modules, capacitance value of each sub-module, and capacitance voltage of each sub-module, The obtaining the sub-module capacitance voltage fluctuation component model of the full-bridge modular multilevel converter according to the characteristic parameters of the full-bridge modular multilevel converter includes: [0013] According to the modulation ratio, the bridge arm voltage frequency, the number of sub-modules and the capacitor voltage of each sub-module, the equivalent switching function of the full-bridge modular multilevel converter is obtained; [0014] According to the power factor angle, the modulation ratio, the AC side current amplitude and the bridge arm voltage frequency, the bridge arm current function of the full-bridge modular multilevel converter is obtained; [0015] According to the equivalent switching function, the bridge arm current function, the capacitance value of each sub-module, and the capacitance voltage of each sub-module, the sub-module capacitance voltage fluctuation of the full-bridge modular multilevel converter is obtained Component model. [0016] In one of the embodiments, the equivalent switching function is the ratio of the bridge arm reference voltage to the sum of the capacitor voltages of all full-bridge sub-modules. [0017] In one of the embodiments, the bridge arm of the full-bridge modular multilevel converter is obtained according to the power factor angle, the modulation ratio, the AC side current amplitude and the bridge arm voltage frequency Current functions, including: [0018] According to the power factor angle, modulation ratio and AC side current amplitude, the DC current function of the full-bridge modular multilevel converter is obtained; [0019] According to the DC current function, the AC side current amplitude, the bridge arm voltage frequency, and the power factor angle, the bridge arm current function of the full-bridge modular multilevel converter is obtained. [0020] In one of the embodiments, the acquisition of the AC side current amplitude of the full-bridge type modular multilevel converter is based on the AC side current amplitude, the power factor angle and the full-bridge type The sub-module capacitor voltage fluctuation component model of the modular multi-level converter can obtain the theoretical required circulating current value, including: [0021] According to the sub-module capacitor voltage fluctuation component model of the full-bridge modular multilevel converter, the initial ripple coefficient expression of the sub-module capacitor voltage fluctuation component is obtained; [0022] According to the initial ripple coefficient expression, the optimal modulation ratio of the full-bridge modular multilevel converter is obtained; [0023] Substituting the optimal modulation ratio into the initial ripple coefficient expression to obtain the ripple coefficient expression when the theoretically required circulating current is injected; [0024] According to the ripple coefficient expression when the theoretically required circulation is injected, the theoretically required circulation expression is obtained; [0025] Obtain the AC side current amplitude of the full-bridge modular multilevel converter, and substitute the collected AC side current amplitude and power factor angle into the theoretically required circulating current expression to obtain the theoretical result Requires circulation value. [0026] In one of the embodiments, the sub-module capacitance voltage fluctuation component includes a fundamental frequency fluctuation component, and the theoretically required circulating current expression is obtained according to the ripple coefficient expression when the theoretically required circulating current is injected, including : [0027] According to the ripple coefficient expression when the theoretically required circulating current is injected, the ripple coefficient of the fundamental frequency fluctuation component is obtained, and the ripple coefficient of the fundamental frequency fluctuation component is set to zero to obtain the theoretically required circulating current expression. [0028] In one of the embodiments, the theoretically required circulation expression is: Guang Er-3ίηφ [0030] In the formula, %f is the theoretical required circulating current amplitude, 82f is the theoretical required circulating current phase, Is is the AC side current amplitude, M is the optimal modulation ratio, and is the power factor angle. [0031] In one of the embodiments, the expression of the actual circulation value is; [. . 32] lc =(Nine + /(+ Shu/2 [0033] In the formula, I. Is the actual circulating current value, d is the instantaneous value of the upper bridge arm current, L is the instantaneous value of the lower bridge arm current, and Q is the instantaneous value of the direct current. [0034] In one of the embodiments, the calculation of the difference between the theoretical required circulating current value and the actual circulating current value, generating a reference voltage according to the difference, and injecting the reference voltage into the full-bridge type Modular multi-level converter, and after modulation, generates the required circulating current in each phase, and suppresses the fluctuation of the capacitor voltage of each sub-module, including: [0035] Calculate the difference between the theoretical required circulating current value and the actual circulating current value, generate a reference voltage according to the difference, and inject the reference voltage into the full-bridge modular multilevel converter, And use the nearest level approximation method to modulate and generate the required circulating current in each phase to suppress the fluctuation of the capacitor voltage of each sub-module. [0036] The above-mentioned full-bridge type MMC sub-module capacitance voltage fluctuation suppression method, first according to the full-bridge type MMC sub-module capacitance voltage fluctuation characteristics, the theoretical required circulating current value is obtained; and then according to the obtained current data, to the actual circulating current value; Then, according to the difference between the theoretically required circulating current value and the actual circulating current value, a reference voltage is generated, and the reference voltage is injected into the full-bridge MMC, and the required circulating current is generated in each phase after modulation, and the capacitor voltage of the sub-module is fluctuated Suppress. The corresponding reference voltage can be injected according to the actual circulating current value, which is beneficial to improve the suppression effect of the capacitor voltage fluctuation of the sub-module. Description of the drawings [0037] FIG. 1 is a basic circuit topology of a full-bridge MMC in an embodiment; [0038] FIG. 2 is a schematic diagram of the relationship between the reference voltage of the full-bridge MMC bridge arm and the DC voltage in an embodiment; [0039] FIG. 3 is a flowchart of a method for suppressing capacitance voltage fluctuations of a full-bridge MMC sub-module in an embodiment; [0040] FIG. 4 is a flowchart of a method for suppressing capacitance voltage fluctuations of a full-bridge MMC sub-module in another embodiment; [0041] FIG. 5 is a flow chart of obtaining a sub-module capacitance voltage fluctuation component model of the full-bridge modular multilevel converter according to the characteristic parameters of the full-bridge modular multilevel converter in an embodiment; [0042] FIG. 6 is a flow chart of obtaining the bridge arm current function of the full-bridge modular multilevel converter according to the power factor angle, modulation ratio, AC side current amplitude, and bridge arm voltage frequency in an embodiment; [0043] FIG. 7 is an embodiment of obtaining the AC side current amplitude of the full-bridge modular multilevel converter, and according to the AC side current amplitude, power factor angle and full-bridge modular multilevel conversion The capacitor voltage fluctuation component model of the sub-module of the current transformer, and the flow chart of the theoretical required circulating current value is obtained; [0044] FIG. 8 is a curve of the capacitance voltage ripple of the full-bridge MMC sub-module as a function of the power factor angle in an embodiment; [0045] FIG. 9 is a block diagram of a full-bridge MMC circulating current injection control block diagram in an embodiment; [0046] FIG. 10 is a schematic diagram of steady-state simulation results of a full-bridge MMC when circulating current injection is not used under rated operating conditions in an embodiment picture; [0047] FIG. 11 is a schematic diagram of steady-state simulation results of a full-bridge type MMC when circulating current injection is used under rated operating conditions in an embodiment; Schematic diagram of steady-state simulation results of type MMC; [0049] FIG. 13 is a schematic diagram of steady-state simulation results of a full-bridge MMC when circulating current injection is not used in the case of unity power factor in an embodiment. Detailed ways [0050] In order to make the purpose, technical solutions, and advantages of the application more clear, the application will be further described in detail below with reference to the accompanying drawings and embodiments. It should be understood that the specific embodiments described herein are only used to explain the present application, and are not used to limit the present application. [0051] Unless otherwise defined, all technical and scientific terms used herein have the same meaning as commonly understood by those skilled in the technical field of this application. The terminology used in the application herein is only for the purpose of describing specific embodiments, and is not intended to limit the application. [0052] It can be understood that the "connection" in the following embodiments should be understood as "electrical connection", "communication connection", etc., if the connected circuits, modules, units, etc. have electrical signals or data transfer between each other. . [0053] When used herein, the singular forms of "a", "an" and "the/the" may also include plural forms, unless the context clearly indicates otherwise. It should also be understood that the terms "including/including" or "having" and the like designate the existence of the stated features, wholes, steps, operations, components, parts or their combinations, but do not exclude the existence or addition of one or more The possibility of other features, wholes, steps, operations, components, parts or their combination. Meanwhile, the term "and/or" used in this specification includes any and all combinations of related listed items. [0054] A voltage source converter high voltage direct current (VSC "HVDC) system based on a voltage source converter can realize decoupling control of active power and reactive power, without the risk of commutation failure, and with black The start-up capability has broad application prospects in large-scale renewable energy collection and transmission, AC grid asynchronous interconnection, etc. However, traditional VSC-HVDC systems widely use two-level or three-level converters connected in series with power semiconductor devices. , The size of the filter and the low operating efficiency limit the development of VSC-HVDC. For this reason, German scholar R. Marquardt proposed a modular multilevel converter (modular multilevel converter, MMC), compared with the traditional voltage Source converter, MMC has the following advantages: 1) It has a modular structure, and the voltage level of MMC can be flexibly adjusted by setting different numbers of modules; 2) The number of output levels is large, and the harmonic content is low; 3) Power semiconductor device switch Low frequency and high ef
[EN US2020336083A1]: MODULAR MULTILEVEL CONVERTER TOPOLOGIES | [EN US2020336083A1]: A Modular Multilevel Converter (MMC) circuit for converting DC power to AC and vice versa. At each respective connection to the AC power-source/load, the MMC circuit uses one Pulse Width Modulation Insulated Gate Bipolar Transistor (PWM IGBT) to control the switching between upper and lower arms of sub-modules. The circuit eliminates the inter-phase inductors often used in MMCs, and replaces the inductors by two complementary-gated PWM IGBTs, thereby eliminating circulating current. Moreover, the multilevel converter topology disclosed herein requires less number of components including PWM IGBTs and capacitors. In fact, at least two submodules per-phase are eliminated: one submodule in the upper arm and one submodule in the lower arm. In other words, the MMC topology not only mitigates the circulating current but also eliminates at least one submodule in the upper arm and at least one submodule in the lower arm per-phase. | US2020336083A1 | 2020-10-22 | US202016855755A | 2020-04-22 | US202016855755A, 2020-04-22 US201962836904P, 2019-04-22 | US2020336083A1: 2020-10-22 | UNIV CALIFORNIA | CORZINE KEITH A DARGAHI VAHID | H02M7/483: I H02M7/5387: I | H02M7/483: I H02M7/4835: A H02M7/53871: I |  |  | [EN US2020336083A1]: 1. A Modular Multilevel Converter (MMC) circuit, comprising: an upper arm connected to a positive rail of a DC (Direct Current) voltage source;a lower arm connected to a negative rail of said DC voltage source; anda midpoint connecting said lower arm and said upper arm, wherein: said upper arm and said lower arm are respectively comprised of a plurality of serially connected submodules;said upper arm connects to said midpoint using a first Pulse-Width-Modulation Insulated-Gate Bipolar Transistor (PWM IGBT) as an upper arm connection;said lower arm connects to said midpoint using a second PWM IGBT as a lower arm connection; andsaid upper arm connection being complementary gated with respect to said lower arm connection. 2. The MMC circuit of claim 1, each submodule, in a half-bridge topology, in said plurality of serially connected submodules comprising: a capacitor;two PWM IGBTs having complementary gated switching states; anda submodule midpoint electrically connected to each of said two PWM IGBTs and a cascaded submodule in said plurality of serially connected submodules. 3. The MMC circuit of claim 2, wherein said submodule midpoint of a first upper submodule of said upper arm is electrically connected to the positive rail of the DC voltage source; andwherein a submodule non-midpoint of a first lower submodule of said lower arm is electrically connected to the negative rail of the DC voltage source. 4. The MMC circuit of claim 2, wherein each submodule in said plurality of serially connected submodules forms a half-bridge circuit. 5. The MMC circuit of claim 2, wherein each submodule in said plurality of serially connected submodules forms a full-bridge circuit. 6. The MMC circuit of claim 1, wherein said midpoint further comprises: an upper arm PWM IGBT, said upper arm PWM IGBT electrically connected to said upper arm, said upper arm PWM IGBT being gated identically to said upper arm;a lower arm PWM IGBT, said lower arm PWM IGBT electrically connected to said lower arm, said lower arm PWM IGBT being gated identically to said lower arm; anda midpoint submodule comprising: a capacitor;two midpoint PWM IGBTs having complementary gated switching states; anda submodule midpoint electrically connected to each of said two midpoint PWM IGBTs. 7. The MMC circuit of claim 6, wherein a commutation sequence of said upper arm PWM IGBT and said lower arm PWM IGBT is used based on a direction of at least one of load current or SM current.wherein said commutation sequence ensures that a blocking voltage of said midpoint of said upper arm PWM IGBT and said lower arm PWM IGBT is limited to 1 p.u. 8. The MMC circuit of claim 1, wherein a commutation sequence of said first PWM IGBT and said second PWM IGBT is used based on a direction of at least one of load current or SM current,wherein said commutation sequence ensures that a blocking voltage of said midpoint of said first PWM IGBT and said second PWM IGBT is limited to 1 p.u. 9. An integrated circuit, comprising: an upper arm plurality of serially electrically-connected submodules;a lower arm plurality of serially electrically-connected submodules, anda midpoint electrically connecting said lower arm plurality of serially electrically-connected submodules and said upper arm plurality of serially electrically-connected submodules, wherein: said upper arm plurality of serially electrically-connected submodules is electrically connected to said midpoint via a first PWM switch;said lower arm plurality of serially electrically-connected submodules is electrically connected to said midpoint via a second PWM switch; andsaid first PWM switch and said second PWM switch are complementary gated with respect to each other. 10. The integrated circuit of claim 9, wherein each submodule in said upper arm plurality of serially electrically-connected submodules and said lower arm plurality of serially electrically-connected submodules comprise: a capacitor;two PWM IGBTs having complementary gated switching states; anda submodule midpoint electrically connected to each of said two PWM IGBTs and a cascaded submodule in one of said upper arm plurality of serially electrically-connected submodules and said lower arm plurality of serially electrically-connected submodules. 11. The integrated circuit of claim 10, wherein said submodule midpoint of a first upper submodule of said upper arm plurality of serially electrically-connected submodules is electrically connected to a positive rail of a DC voltage source; andwherein a submodule non-midpoint of a first lower submodule of said lower arm plurality of serially electrically-connected submodules is electrically connected to a negative rail of said DC voltage source. 12. The integrated circuit of claim 10, wherein said submodule forms a half-bridge circuit. 13. The integrated circuit of claim 10, wherein said submodule forms a full-bridge circuit. 14. The integrated circuit of claim 10, wherein said midpoint further comprises: an upper arm PWM IGBT, said upper arm PWM IGBT electrically connected to said upper arm plurality of serially electrically-connected submodules, said upper arm PWM IGBT being gated identically to said upper arm plurality of serially electrically-connected submodules;a lower arm PWM IGBT, said lower arm PWM IGBT electrically connected to said lower arm plurality of serially electrically-connected submodules, said lower arm PWM IGBT being gated identically to said lower arm plurality of serially electrically-connected submodules; said upper arm PWM IGBT having a complementary switching pulses with respect to said lower arm PWM IGBT; anda midpoint submodule comprising: a capacitor;two midpoint PWM IGBTs having complementary gated switching states; anda submodule midpoint electrically connected to each of said two midpoint PWM IGBTs. | [EN US2020336083A1]: CROSS-REFERENCE TO RELATED APPLICATIONS This application claims priority benefit from U.S. provisional patent application No. 62/836,904, filed on Apr. 22, 2019, the entire content of which is incorporated herein by reference. BACKGROUND 1. Technical Field The present disclosure relates to DC-AC converters, and more specifically to a modular multilevel converter which is capable of converting DC to three-phase AC or three-phase AC to DC. 2. Introduction Converting Direct Current (DC) to Alternating Current (AC) electricity, and vice versa, is often done using a Modular Multilevel Converter (MMC). MMCs, such as the MMC 100 illustrated in FIG. 1, use three separate legs, each leg receiving a distinct phase of AC power 102. MMCs operate using an upper-arm and a lower-arm, where each respective arm connects to the positive 120 and negative 122 rails of a DC-voltage source 116, respectively. The MMC phase-leg is formed by connecting the upper arm (positive arm) to the lower arm (negative arm) through an inductor 104 being formed by inductors 106 with a midpoint 118. The upper and lower arms themselves are formed of cascaded submodules (SMs) 108, 110. While SM configurations can vary from application to application, in their simplest structure they are formed using a power switch-based half-bridge module and a capacitor, with the connection 112, 114 between each SM extending from a non-midpoint of a first SM to a midpoint between the power switches on a connected SM. The capacitor of each SM can be used to clamp the voltage of the power switches within each SM, with the voltage across each capacitor equaling 1 p.u., or 100% of the cell/capacitor voltage. In most MMC designs, this voltage is the same for all of the SMs. However, a drawback of this design is circulating current among the SMs. This circulating current is generated due to the capacitors' voltage difference inside the upper and lower SMs. In other words, the SMs of the upper-arm are always connected to the SMs of the lower-arm due to the circulating current that flows through a path provided by the inductor 104. The circulating current does not contribute to the converter's output power. To account for the circulating current, power switches and capacitors with higher current ratings must be used within the SMs of the MMC 100. Moreover, the circulating current increases the operating junction temperature and restrains the semiconductor devices from switching at higher pulse-width-modulation (PWM) frequencies, all resulting in power loses due to this MMC topology. SUMMARY Additional features and advantages of the disclosure will be set forth in the description which follows, and in part will be obvious from the description, or can be learned by practice of the herein disclosed principles. The features and advantages of the disclosure can be realized and obtained by means of the instruments and combinations particularly pointed out in the appended claims. These and other features of the disclosure will become more fully apparent from the following description and appended claims, or can be learned by the practice of the principles set forth herein. A Modular Multilevel Converter (MMC) circuit, configured as disclosed herein, can include: an upper arm connected to the positive rail of a DC (Direct Current) voltage source; a lower arm connected to the negative rail of the DC voltage source; and a midpoint connecting the lower arm and the upper arm, wherein: the upper arm and the lower arm are respectively comprised of plurality of serially connected submodules; the upper arm connects to the midpoint using a first Pulse-Width-Modulation Insulated-Gate Bipolar Transistor (PWM IGBT) as an upper arm connection; the lower arm connects to the midpoint using a second PWM IGBT as a lower arm connection; and the upper arm connection being complementary gated with respect to the lower arm connection. An integrated circuit, configured as disclosed herein, can include: an upper arm plurality of serially electrically-connected submodules; a lower arm plurality of serially electrically-connected submodules, and a midpoint electrically connecting the lower arm plurality of serially connected submodules and the upper arm plurality of serially connected submodules, wherein: the upper arm plurality of serially electrically-connected submodules is electrically connected to the midpoint via a first PWM switch; the lower arm plurality of serially electrically-connected submodules is electrically connected to the midpoint via a second PWM switch; and the first PWM switch and the second PWM switch are complementary gated with respect to each other. BRIEF DESCRIPTION OF THE DRAWINGS FIG. 1 illustrates an example of a conventional modular multilevel converter configuration; FIG. 2 illustrates an example submodule according to an embodiment of the invention; FIG. 3 illustrates an example bridge structure to connect the upper arm to the lower arm according to an embodiment of the invention; FIG. 4 illustrates an example MMC using the example bridge structure of FIG. 3 according to an embodiment of the invention; and FIG. 5 illustrates an example MMC with a common-SM used at the midpoint connecting the upper arm to the lower arm using two complementary gated PWM IGBTs. DETAILED DESCRIPTION Various embodiments of the disclosure are described in detail below. While specific implementations are described, it should be understood that this is done for illustration purposes only. Other components and configurations may be used without parting from the spirit and scope of the disclosure. A MMC can be used to convert DC electricity to AC and vice versa. In at least one embodiment of the disclosed invention, this conversion is accomplished by a MMC employing a series connection of modular submodules to form the converter's phase-leg, the phase leg being that portion of the MMC circuit associated with a specific phase of the AC. The SMs in the upper-arm and lower-arm of the disclosed MMC topology, in their simplest configurations, are realized by a capacitor and a half-bridge or full-bridge module. The half-bridge/full bridge modules utilize Pulse Width Modulation (PWM) Insulated Gate Bipolar Transistors (IGBTs), with an additional half-bridge structure formed by complementary switching PWM IGBTs. This additional half-bridge module is used for connecting the upper arm to the lower arm, and its power switches are configured to switch due to complementary signals on their respective PWM IGBTs. Configuring the PWM IGBTs in this manner eliminates the circulating current among the SMs which is present in the classic MMC topology illustrated in FIG. 1. In addition, utilizing this complementarily switching half-bridge module to connect the SMs of the upper arm to the SMs of the lower arm mitigates the circulating current. The elimination of circulating current within the SMs of upper arm and lower arm results in a lower operating junction temperature, and also increases switching frequency and power capabilities. The disclosed MMC topology retains the modularity feature of the SMs in the classic MMC illustrated in FIG. 1. An (n+1) level three-phase MMC as disclosed herein includes (n−1) SMs in the upper-arm and (n−1) SMs in the lower arm per-phase, thereby eliminating two of the SMs per-phase required in the classic design. Assuming an n-p.u. voltage for the DC source, the IGBTs and the capacitors in all 2×(n−1) SMs per-phase will have a consistent 1 p.u. DC voltage rating. These variations and others shall be described herein as the various embodiments are set forth. The steps and examples outlined herein are examples only, and can be implemented in any combination thereof, including combinations that exclude, add, or modify certain components. FIG. 2 illustrates an example submodule 108. In this example, the submodule 108 has two IGBTs 202 electrically connected at a midpoint 204. Each respective IGBT 202 within the submodule 108 is complementary gated, with the input pulse to the “upper” IGBT being αn 206 and the “lower” IGBT input pulse being αn 208 (the bar indicating the complementary or opposite). The SM 108 capacitor 210 has a voltage rating of 1 p.u. The SM 108 is electrically connected to other SMs through two electrical connections 212, 214, one of the electrical connections 214 extending from the midpoint 204 between the two IGBTs 202. FIG. 3 illustrates an example bridge structure 300 to connect the upper arm of SMs 306 to the lower arm of SMs 308. In this example bridge structure 300, the IGBTs 302, 304 are electrically connected at a midpoint 314 to an AC power-source/load 102. The IGBT 302 electrically connected to the upper arm of SMs 306 has input voltage pulse β, while the IGBT 304 electrically connected to the lower arm of SMs 308 has input pulse β, which is the complementary (opposite) of the input pulse β. In this example bridge structure 300, the IGBTs 302, 304 have a voltage rating of 1 p.u. FIG. 4 illustrates an example MMC 400 using the example bridge structure of FIG. 3. This example is identical to that of FIG. 1, with the exception that the bridge structure 300 of FIG. 3 is used in place of the inductor 104 of FIG. 1 along with elimination of two submodules per-phase, one submodule in upper arm and one submodule in lower arm, in the conventional MMC topology of FIG. 1. As described above, at the midpoint 312 of the bridge structure 300 is a connection to the AC power source/load 102, and as illustrated here, that AC power source/load can have multiple phases (e.g., three-phase AC power source/load). FIG. 5 illustrates an example MMC 500 with a SM 110 used at the midpoint connecting the upper arm to the lower arm. As illustrated, in this configuration 500, a submodule 110 identical to those used in the upper and lower arms is located at the midpoint connecting the upper and lower arms. Connecting this midpoint submodule 110 to the upper and lower arms are (for each arm) two PWM IGBTs 302, 304. The respective pairs of PWM IGBTs 302, 304 having complementary switching pulses with respect to each other are gated identically to the upper or lower arms, respectively, as are the PWM IGBTs within the submodule 110. The complementary switching pulses of PWM IGBTs of 302 and 304, with respect to each other, mitigates the circulating current in this topology. The output to the AC power source/load 102 is the midpoint between the two PWM IGBTs of the submodule 110. In this configuration, the common-SM between the upper and lower arms replaces the inter-phase reactors within each phase in prior art designs. Furthermore, it eliminates four submodules per-phase of the classic MMC topology: two submodules in the upper arm and two submodules in the lower arm. A Modular Multilevel Converter (MMC) circuit, configured as disclosed herein, can include: an upper arm connected to a positive rail of a DC (Direct Current) voltage source; a lower arm connected to a negative rail of the DC voltage source; and a midpoint connecting the lower arm and the upper arm, wherein: the upper arm and the lower arm are respectively comprised of plurality of serially connected submodules; the upper arm connects to the midpoint using a first Pulse-Width-Modulation Insulated-Gate Bipolar Transistor (PWM IGBT) as an upper arm connection; the lower arm connects to the midpoint using a second PWM IGBT as a lower arm connection; and the upper arm connection being complementary gated with respect to the lower arm connection. The submodules of the MMC can each respectively be formed by a half-bridge circuit or a full-bridge circuit configurations. In a half-bridge topology for SMs, each submodule in said plurality of serially connected submodules can include: a capacitor; two PWM IGBTs having complementary gated switching signals (states); and a submodule midpoint electrically connected to each of said two PWM IGBTs and a cascaded submodule in said plurality of serially connected submodules. In addition, said submodule midpoint of a first upper submodule of said upper arm can be electrically connected to the positive rail of the DC voltage source, and said submodule non-midpoint of a first lower submodule of said lower arm can be electrically connected to the negative rail of the DC voltage source. In an example embodiment, the midpoint can be a submodule, with an upper arm PWM IGBT, the upper arm PWM IGBT electrically connected to the upper arm, the upper arm PWM IGBT being gated identically to the upper arm; a lower arm PWM IGBT, the lower arm PWM IGBT electrically connected to the lower arm, the lower arm PWM IGBT being gated identically to the lower arm; the upper arm PWM IGBT gated complementary with respect to the one lower arm PWM IGBT, thereby eliminating any circulating-current; and the midpoint submodule including: a capacitor; two midpoint PWM IGBTs having complementary gated switching states; and a submodule midpoint electrically connected to each of the two midpoint PWM IGBTs. An integrated circuit, configured as disclosed herein, can include: an upper arm plurality of serially electrically-connected submodules; a lower arm plurality of serially electrically-connected submodules, and a midpoint electrically connecting the lower arm plurality of serially connected submodules and the upper arm plurality of serially connected submodules, wherein: the upper arm plurality of serially electrically-connected submodules is electrically connected to the midpoint via a first PWM switch; the lower arm plurality of serially electrically-connected submodules is electrically connected to the midpoint via a second PWM switch; and the first PWM switch and the second PWM switch are complementary gated with respect to each other. The submodules of the integrated circuit can each respectively be formed by a half-bridge circuit or a full-bridge circuit configurations. In a half-bridge topology for SMs, each submodule in said plurality of serially connected submodules can include: a capacitor; two PWM IGBTs having complementary gated switching signals (states); and a submodule midpoint electrically connected to each of said two PWM IGBTs and a cascaded submodule in said plurality of serially connected submodules. In addition, said submodule midpoint of a first upper submodule of said upper arm can be electrically connected to the positive rail of the DC voltage source, and said submodule non-midpoint of a first lower submodule of said lower arm can be electrically connected to the negative rail of the DC voltage source. In one example embodiment, the midpoint can further include an upper arm PWM IGBT, the upper arm PWM IGBT electrically connected to the upper arm plurality of serially electrically-connected submodules, the upper arm PWM IGBT being gated identically to the upper arm plurality of serially electrically-connected submodules; a lower arm PWM IGBT, the lower arm PWM IGBT electrically connected to the lower arm plurality of serially electrically-connected submodules, the lower arm PWM IGBT being gated identically to the lower arm plurality of serially electrically-connected submodules; the upper arm PWM IGBT having a complementary gated switching state with respect to the lower arm PWM IGBT, thereby eliminating circulating-current; and a midpoint submodule comprising: a capacitor; two midpoint PWM IGBTs having complementary gated switching pulses; and a submodule midpoint electrically connected to each of said two midpoint PWM IGBTs. Use of language such as “at least one of X, Y, and Z,” “at least one of X, Y, or Z,” “at least one or more of X, Y, and Z,” “at least one or more of X, Y, or Z,” “at least one or more of X, Y, and/or Z,” or “at least one of X, Y, and/or Z,” are intended to be inclusive of both a single item (e.g., just X, or just Y, or just Z) and multiple items (e.g., {X and Y}, {X and Z}, {Y and Z}, or {X, Y, and Z}). The phrase “at least one of” and similar phrases are not intended to convey a requirement that each possible item must be present, although each possible item may be present. The various embodiments described above are provided by way of illustration only and should not be construed to limit the scope of the disclosure. Various modifications and changes may be made to the principles described herein without following the example embodiments and applications illustrated and described herein, and without departing from the spirit and scope of the disclosure.
[ZH CN112615556A]: 一种多电平逆变器以及多电平逆变器的控制方法 [EN CN112615556A]: Multi-level inverter and control method of multi-level inverter | [ZH CN112615556A]: 本申请提供了一种多电平逆变器、多电平逆变器的控制方法以及不间断电源，涉及电力电子技术领域。该多电平逆变器包括换流桥臂、逆变电路和控制器。逆变电路的正输入端口连接多电平逆变器的正输入端口，逆变电路的负输入端口连接多电平逆变器的负输入端口，逆变电路的输出端连接多电平逆变器的正输出端口。换流桥臂包括上半桥臂和下半桥臂，桥臂中点连接多电平逆变器的负输出端口。控制器在逆变电路的正输出周期内控制上半桥臂断开，下半桥臂导通；在负输出周期内控制上半桥臂导通，下半桥臂断开。利用本方案可将逆变电路中使用的开关管的数量缩减一半，降低了多电平逆变器的成本。 [EN CN112615556A]: The invention provides a multi-level inverter, a control method of the multi-level inverter and an uninterruptible power supply, which relate to the technical field of power electronics. The multi-level inverter comprises a converter bridge arm, an inverter circuit and a controller. A positive input port of the inverter circuit is connected with a positive input port of the multi-level inverter, a negative input port of the inverter circuit is connected with a negative input port of the multi-level inverter, and an output end of the inverter circuit is connected with a positive output port of the multi-level inverter. The converter bridge arm comprises an upper half bridge arm and a lower half bridge arm, and the midpoint of the bridge arm is connected with the negative output port of the multi-level inverter. The controller controls the upper half bridge arm to be disconnected and the lower half bridge arm to be connected in the positive output period of the inverter circuit; and the upper half bridge arm is controlled to be conducted and the lower half bridge arm is controlled to be disconnected in a negative output period. By utilizing the scheme, the number of the switching tubes used in the inverter circuit can be reduced by half, and the cost of the multi-level inverter is reduced. | CN112615556A | 2021-04-06 | CN202011375682A | 2020-11-30 | CN202011375682A, 2020-11-30 | CN112615556A: 2021-04-06 | HUAWEI TECH CO LTD | JIANG ZHENGDONG LU MAOYONG HUANG ZHUYONG | H02M7/483: I H02J9/06: I H02M7/5387: I | H02J9/062: I H02M7/483: I H02M7/53871: I | CN103887862A CN105703656A CN106712272A CN108540003A |  | [ZH CN112615556A]: 1 .一种多电平逆变器，其特征在于，应用于单母线系统，所述多电平逆变器包括:换流 桥臂、逆变电路和控制器； 所述逆变电路的正输入端口连接所述多电平逆变器的正输入端口，所述逆变电路的负 输入端口连接所述多电平逆变器的负输入端口，所述逆变电路的输出端连接所述多电平逆 变器的正输出端口； 所述换流桥臂包括上半桥臂和下半桥臂，所述上半桥臂的第一端连接所述多电平逆变 器的正输入端口，所述上半桥臂的第二端通过桥臂中点连接所述下半桥臂的第一端，所述 下半桥臂的第二端连接所述多电平逆变器的负输入端口，所述桥臂中点连接所述多电平逆 变器的负输出端口； 所述控制器，用于在所述逆变电路的正输出周期内控制所述上半桥臂断开，下半桥臂 导通;在所述逆变电路的负输出周期内控制所述上半桥臂导通，下半桥臂断开。 2 .根据权利要求1所述的多电平逆变器，其特征在于，所述上半桥臂包括开关管M1，所 述下半桥臂包括开关管M2,所述M1和M2分别与一个二极管反并联； 所述控制器在所述逆变电路的正输出周期内控制所述M1断开，且控制所述M2闭合;在 所述逆变电路的负输出周期内，控制所述M1闭合，且控制所述M2断开。 3 .根据权利要求1所述的多电平逆变器，其特征在于，所述多电平逆变器为五电平逆变 器，所述逆变电路包括第一电容、第二电容和开关管Q1-Q4,每个所述开关管分别于一个二 极管反并联； 所述第一电容的第一端和所述Q1的第一端连接所述多电平逆变器的正输入端口，所述 第一电容的第二端通过第一节点连接所述第二电容的第一端，所述第二电容的第二端和所 述Q2的第二端连接所述多电平逆变器的负输入端口，所述第一节点连接所述Q4的第一端， 所述Q4的第二端连接所述Q3的第二端，所述Q3的第一端连接所述逆变电路的输出端； 所述Q1的第二端连接所述逆变电路的输出端和所述Q2的第一端。 4 .根据权利要求3所述的多电平逆变器，其特征在于，所述控制器用于在每个所述正输 出周期内： 先在第一预设时间内控制所述Q1关断，控制所述Q3导通，并控制所述Q2和Q4交替导通; 再在第二预设时间内控制所述Q1和Q3交替导通，控制所述Q2关断并控制所述Q4导通;然后 在每个所述正输出周期的剩余时间内控制所述Q1关断，控制所述Q3导通，并控制所述Q2和 Q4交替导通； 所述控制器还用于在每个所述负输出周期内： 先在第一预设时间内控制所述Q2关断，控制所述Q4导通，并控制所述Q1和Q3交替导通; 再在第二预设时间内控制所述Q2和Q4交替导通，控制所述Q1关断并控制所述Q3导通;然后 在每个所述负输出周期的剩余时间内控制所述Q2关断，控制所述Q4导通，并控制所述Q1和 Q3交替导通； 所述第一预设时间等于所述正输出周期的剩余时间和所述负输出周期的剩余时间。 5 .根据权利要求1所述的多电平逆变器，其特征在于，所述逆变电路包括第一支路、第 二支路和N条第三支路，所述N为大于或等于2的正整数； 所述第一支路包括开关管Q5,所述Q5的第一端连接所述逆变电路的正输入端口，所述 Q5的第二端连接所述逆变电路的输出端； 所述第二支路包括开关管Q6,所述Q6的第一端连接所述逆变电路的输出端，所述Q6的 第二端连接所述逆变电路的负输入端口； 每条所述第三支路包括开关管Q7和Q8,所述Q7的第一端连接所述第三支路的第一端， 所述Q7的第二端连接所述Q8的第二端，所述Q8的第一端连接所述第三支路的第二端； 第一条所述第三支路的第一端通过第一电容连接所述第一支路的第一端，第M条第三 支路的第一端通过第M电容连接第(M-1)条第三支路的第一端，第N条第三支路的第一端通 过第(N+1)电容连接所述第二支路的第二端,所述M=2,3,…,N； 所述N条第三支路第二端连接所述逆变电路的负输出端口； 所述逆变电路包括的各开关管分别与一个二极管反并联。 6 .根据权利要求1所述的多电平逆变器，其特征在于，所述多电平逆变器为五电平逆变 器，所述逆变电路包括第一电容、第二电容和开关管Q1-Q4,每个所述开关管分别于一个二 极管反并联； 所述第一电容的第一端和所述Q1的第一端连接所述多电平逆变器的正输入端口，所述 第一电容的第二端通过第一节点连接所述第二电容的第一端，所述第二电容的第二端和所 述Q4的第二端连接所述多电平逆变器的负输入端口，所述第一节点连接所述Q2的第二端， 所述Q2的第一端连接所述Q1的第二端和所述Q3的第一端，所述Q3的第二端连接所述Q4的第 一端和所述逆变电路的输出端。 7 .根据权利要求3所述的多电平逆变器，其特征在于，所述控制器用于在每个所述正输 出周期内： 先在第一预设时间内控制所述Q1关断、Q2导通，且控制Q3和Q4交替导通;再在第二预设 时间内控制所述Q3导通、Q4关断，且控制Q1和Q2交替导通;然后在所述正输出周期的剩余时 间内控制所述Q1关断、Q2导通,且控制Q3和Q4交替导通； 所述控制器还用于在每个所述负输出周期内： 先在所述第一预设时间内控制所述Q3导通、Q4关断，且控制Q1和Q2交替导通;再在所述 第二预设时间内控制所述Q2导通，Q1关断，且控制Q3和Q4交替导通;然后在所述负输出周期 的剩余时间内控制所述Q3导通、Q4关断，且控制Q1和Q2交替导通； 所述第一预设时间等于所述正输出周期的剩余时间和所述负输出周期的剩余时间。 8 .根据权利要求1所述的多电平逆变器，其特征在于，所述逆变电路包括N个逆变桥臂 和电容C「CN,所述N为大于或等于3的整数； 每个所述逆变桥臂上半桥臂包括开关管Q1和Q2,所述Q1的第一端连接所述逆变桥臂的 第一端，所述Q1的第二端通过所述逆变桥臂的桥臂中点连接所述Q2的第二端，所述Q2的第 一端连接所述逆变桥臂的第二端； 第一条所述逆变桥臂的第一端连接所述逆变电路的正输入端口，且通过电容C1连接第 一条所述逆变桥臂的第二端； 第M条逆变桥臂的第一端连接第(M-1)条逆变桥臂的桥臂中点，第M条逆变桥臂的第二 端通过电容CM连接第(M-1)条逆变桥臂的第二端，第N条逆变桥臂的第二端连接所述逆变电 路的负输入端口，所述M=2,3,…,N； 所述逆变电路包括的各开关管分别与一个二极管反并联。 9 .根据权利要求1-8中任意一项所述的多电平逆变器，其特征在于，所述多电平逆变器 还包括第一滤波电感和第一滤波电容； 所述第一滤波电感连接在所述逆变电路的输出端和所述多电平逆变器的正输出端口 之间;所述第一滤波电容连接在所述多电平逆变器的真输出端口和负输出端口之间。 10 .根据权利要求1-9中任意一项所述的多电平逆变器，其特征在于，所述多电平逆变 器还包括AC-DC电路； 所述AC-DC电路的正输入端口用于连接交输入，所述AC-DC电路的负输入端口用于连接 所述桥臂中点，所述AC-DC电路的正输出端口连接所述逆变电路的正输入端口，所述DC-DC 电路的负输出端口连接所述逆变电路的负输入端口； 所述AC-DC电路用于将所述交流输入提供的交流电变换为直流电后传输给所述逆变电 路。 11 .根据权利要求10所述的多电平逆变器，其特征在于，所述AC-DC电路的结构沿所述 换流桥臂与所述逆变电路对称。 12 .根据权利要求10或11所述的多电平逆变器，其特征在于，所述控制器还用于控制所 述AC-DC电路的工作状态。 13 .一种多电平逆变器的控制方法，其特征在于，所述多电平逆变器应用于单母线系 统，所述方法包括： 在多电平逆变器的逆变电路的正输出周期内，控制所述多电平逆变器的负输出端的电 位为所述逆变电路的负输入端口的电位； 在所述逆变电路的负输出周期内，控制所述多电平逆变器的负输出端的电位为所述逆 变电路的正输入端口的电位。 14 .根据权利要求13所述的控制方法，其特征在于，所述多电平逆变器还包括换流桥 臂，所述换流桥臂包括上半桥臂和下半桥臂，所述上半桥臂的第一端连接所述逆变电路的 正输入端口，所述上半桥臂的第二端通过桥臂中点连接所述下半桥臂的第一端，所述下半 桥臂的第二端连接所述逆变电路的负输入端口，所述桥臂中点连接所述多电平逆变器的负 输出端口；所述在多电平逆变器的逆变电路的正输出周期内，控制所述多电平逆变器的负 输出端的电位为所述逆变电路的负输入端口的电位，具体包括： 在所述逆变电路的正输出周期内控制所述上半桥臂断开，下半桥臂导通； 所述在所述逆变电路的负输出周期内，控制所述多电平逆变器的负输出端的电位为所 述逆变电路的正输入端口的电位，具体包括： 在所述逆变电路的负输出周期内控制所述上半桥臂导通，下半桥臂断开。 15 .一种不间断电源，其特征在于，所述不间断电源包括权利要求1-9中任一项所述的 多电平逆变器，所述多电平逆变器的输出端连接负载，所述不间断电源还包括:整流器、旁 路电路和电池； 所述旁路电路的第一端连接所述整流器的输入端，所述旁路电路的第二端连接所述多 电平逆变器的输出端； 所述整流器的输入端连接交流电源； 所述整流器，用于将所述交流电源提供的交流电转换为直流电后传输至所述电池和所 述多电平逆变器； 所述旁路电路，用于在启用时使所述交流电源直接为所述负载供电； 所述电池，用于当所述整流器停止工作时，向所述多电平逆变器输出直流电。 16 .根据权利要求15所述的不间断电源，其特征在于，所述整流器与所述多电平逆变器 集成在一起，所述整流器包括AC-DC电路； 所述AC-DC电路与所述逆变电路沿所述换流桥臂对称； 所述AC-DC电路的正输入端口用于连接所述交流电源，所述AC-DC电路的负输入端口用 于连接所述桥臂中点，所述AC-DC电路的正输出端口连接所述逆变电路的正输入端口，所述 DC-DC电路的负输出端口连接所述逆变电路的负输入端口； 所述AC-DC电路用于将所述交流电源提供的交流电变换为直流电后传输给所述逆变电 路。 [EN CN112615556A]: 1 A multi-level inverter, characterized in that it is applied to a single bus system, the multi-level inverter includes: a converter bridge arm, an inverter circuit, and a controller; the positive input of the inverter circuit The port is connected to the positive input port of the multi-level inverter, the negative input port of the inverter circuit is connected to the negative input port of the multi-level inverter, and the output terminal of the inverter circuit is connected to the multi-level inverter. The positive output port of the level inverter; the converter bridge arm includes an upper half bridge arm and a lower half bridge arm, and the first end of the upper half bridge arm is connected to the positive input port of the multi-level inverter , The second end of the upper half bridge arm is connected to the first end of the lower half bridge arm through the midpoint of the bridge arm, and the second end of the lower half bridge arm is connected to the negative input of the multi-level inverter Port, the midpoint of the bridge arm is connected to the negative output port of the multi-level inverter; the controller is used to control the upper half bridge arm to be disconnected during the positive output period of the inverter circuit, The lower half of the bridge arm is turned on; the upper half of the bridge arm is controlled to be turned on and the lower half of the bridge arm is turned off during the negative output period of the inverter circuit. 2 The multi-level inverter according to claim 1, wherein the upper half of the bridge arm includes a switch tube M1, the lower half of the bridge arm includes a switch tube M2, and the M1 and M2 are respectively connected to a diode Anti-parallel; the controller controls the M1 to open during the positive output period of the inverter circuit, and controls the M2 to close; during the negative output period of the inverter circuit, controls the M1 to close, And control the M2 to turn off. 3 The multi-level inverter according to claim 1, wherein the multi-level inverter is a five-level inverter, and the inverter circuit includes a first capacitor, a second capacitor, and a switch Tubes Q1-Q4, each of the switch tubes is connected in anti-parallel with a diode; the first end of the first capacitor and the first end of the Q1 are connected to the positive input port of the multilevel inverter, so The second end of the first capacitor is connected to the first end of the second capacitor through a first node, and the second end of the second capacitor and the second end of the Q2 are connected to the multilevel inverter. Negative input port, the first node is connected to the first terminal of Q4, the second terminal of Q4 is connected to the second terminal of Q3, and the first terminal of Q3 is connected to the output terminal of the inverter circuit ; The second end of the Q1 is connected to the output end of the inverter circuit and the first end of the Q2. 4 The multi-level inverter according to claim 3, wherein the controller is configured to: in each positive output period: first control the Q1 to be turned off within a first preset time, and control The Q3 is turned on, and the Q2 and Q4 are controlled to be turned on alternately; then within a second preset time, the Q1 and Q3 are controlled to be turned on alternately, and the Q2 is controlled to turn off and the Q4 is controlled to turn on; then During the remaining time of each positive output period, control the Q1 to turn off, control the Q3 to turn on, and control the Q2 and Q4 to alternately turn on; In the output period: first control the Q2 to be turned off within the first preset time, control the Q4 to turn on, and control the Q1 and Q3 to be turned on alternately; and then control the Q2 and Q2 within the second preset time Q4 is turned on alternately, controlling said Q1 to turn off and controlling said Q3 to turn on; and then controlling said Q2 to turn off during the remaining time of each negative output cycle, controlling said Q4 to turn on, and controlling said Q1 and Q3 are turned on alternately; the first preset time is equal to the remaining time of the positive output period and the remaining time of the negative output period. 5 The multi-level inverter according to claim 1, wherein the inverter circuit includes a first branch, a second branch, and N third branches, and the N is greater than or equal to 2. The first branch includes a switch tube Q5, the first end of Q5 is connected to the positive input port of the inverter circuit, and the second end of Q5 is connected to the output terminal of the inverter circuit; The second branch includes a switch tube Q6, a first end of the Q6 is connected to the output end of the inverter circuit, and a second end of the Q6 is connected to the negative input port of the inverter circuit; each of the The third branch includes switch tubes Q7 and Q8, the first end of Q7 is connected to the first end of the third branch, the second end of Q7 is connected to the second end of Q8, and the The first end is connected to the second end of the third branch; the first end of the first third branch is connected to the first end of the first branch through a first capacitor, the M-th third branch The first end of the circuit is connected to the first end of the (M-1)th third branch through the M-th capacitor, and the first end of the Nth third branch is connected to the second end through the (N+1)th capacitor. The second end of the branch, the M=2,3,...,N; the second ends of the N third branches are connected to the negative output port of the inverter circuit; the switches included in the inverter circuit The tubes are connected in anti-parallel with a diode respectively. 6 The multi-level inverter according to claim 1, wherein the multi-level inverter is a five-level inverter, and the inverter circuit includes a first capacitor, a second capacitor, and a switch Tubes Q1-Q4, each of the switch tubes is connected in anti-parallel with a diode; the first end of the first capacitor and the first end of the Q1 are connected to the positive input port of the multilevel inverter, so The second end of the first capacitor is connected to the first end of the second capacitor through a first node, and the second end of the second capacitor and the second end of the Q4 are connected to the multilevel inverter. Negative input port, the first node is connected to the second end of Q2, the first end of Q2 is connected to the second end of Q1 and the first end of Q3, and the second end of Q3 is connected to The first terminal of Q4 and the output terminal of the inverter circuit. 7 The multi-level inverter according to claim 3, wherein the controller is configured to: in each positive output period: first control the Q1 to be turned off and Q2 within a first preset time Turn on, and control Q3 and Q4 to turn on alternately; then control Q3 to turn on, Q4 to turn off, and control Q1 and Q2 to turn on alternately within a second preset time; then in the remaining time of the positive output cycle The Q1 is controlled to be turned off, Q2 is turned on, and Q3 and Q4 are controlled to be turned on alternately; the controller is also used to: in each negative output period: The Q3 is turned on, Q4 is turned off, and Q1 and Q2 are controlled to be turned on alternately; then within the second preset time, the Q2 is turned on, Q1 is turned off, and Q3 and Q4 are controlled to be turned on alternately; In the remaining time of the negative output period, the Q3 is controlled to be turned on, Q4 is turned off, and Q1 and Q2 are controlled to be alternately turned on; the first preset time is equal to the remaining time of the positive output period and the negative output The remaining time of the cycle. 8 The multi-level inverter according to claim 1, wherein the inverter circuit includes N inverter bridge arms and a capacitor C "CNThe N is an integer greater than or equal to 3; the upper half of each inverter bridge arm includes switch tubes Q1 and Q2, and the first end of the Q1 is connected to the first end of the inverter bridge arm, The second end of the Q1 is connected to the second end of the Q2 through the midpoint of the inverter bridge arm, and the first end of the Q2 is connected to the second end of the inverter bridge arm; The first end of the inverter bridge arm is connected to the positive input port of the inverter circuit, and the second end of the first inverter bridge arm is connected through a capacitor C1; the first end of the Mth inverter bridge arm is The terminal is connected to the midpoint of the (M-1)th inverter bridge arm, and the second terminal of the Mth inverter bridge arm passes through the capacitor CMConnect the second end of the (M-1)th inverter bridge arm, and connect the second end of the Nth inverter bridge arm to the negative input port of the inverter circuit, the M=2,3,...,N ; Each switch tube included in the inverter circuit is connected in anti-parallel with a diode. 9 The multi-level inverter according to any one of claims 1-8, wherein the multi-level inverter It also includes a first filter inductor and a first filter capacitor; the first filter inductor is connected between the output terminal of the inverter circuit and the positive output port of the multilevel inverter; the first filter capacitor It is connected between the true output port and the negative output port of the multi-level inverter. 10 The multi-level inverter according to any one of claims 1-9, wherein the multi-level inverter further comprises an AC-DC circuit; the positive input port of the AC-DC circuit Used to connect the AC input, the negative input port of the AC-DC circuit is used to connect the midpoint of the bridge arm, the positive output port of the AC-DC circuit is connected to the positive input port of the inverter circuit, and the DC -The negative output port of the DC circuit is connected to the negative input port of the inverter circuit; the AC-DC circuit is used to convert the alternating current provided by the alternating current input into direct current and transmit it to the inverter circuit. 11 The multi-level inverter according to claim 10, wherein the structure of the AC-DC circuit is symmetrical with the inverter circuit along the commutation bridge arm. 12 The multi-level inverter according to claim 10 or 11, wherein the controller is also used to control the working state of the AC-DC circuit. 13 A control method of a multi-level inverter, characterized in that the multi-level inverter is applied to a single bus system, the method comprising: in the positive output of the inverter circuit of the multi-level inverter In the period, control the potential of the negative output terminal of the multi-level inverter to be the potential of the negative input port of the inverter circuit; in the negative output period of the inverter circuit, control the multi-level inverter The potential of the negative output terminal of the inverter is the potential of the positive input terminal of the inverter circuit. 14 The control method according to claim 13, wherein the multi-level inverter further comprises a converter bridge arm, the converter bridge arm includes an upper half bridge arm and a lower half bridge arm, and the upper The first end of the half bridge arm is connected to the positive input port of the inverter circuit, the second end of the upper half bridge arm is connected to the first end of the lower half bridge arm through the midpoint of the bridge arm, and the lower half bridge arm The second end of the arm is connected to the negative input port of the inverter circuit, and the midpoint of the bridge arm is connected to the negative output port of the multi-level inverter; In the positive output period, controlling the potential of the negative output terminal of the multi-level inverter to the potential of the negative input port of the inverter circuit specifically includes: controlling the upper voltage during the positive output period of the inverter circuit The half-bridge arm is disconnected and the lower half-bridge arm is turned on; said controlling the potential of the negative output terminal of the multi-level inverter to be the positive input of the inverter circuit during the negative output period of the inverter circuit The potential of the port specifically includes: controlling the upper half bridge arm to turn on and the lower half bridge arm to turn off during the negative output period of the inverter circuit. 15 An uninterruptible power supply, wherein the uninterruptible power supply comprises the multi-level inverter according to any one of claims 1-9, and the output end of the multi-level inverter is connected to a load, The uninterruptible power supply further includes: a rectifier, a bypass circuit, and a battery; a first end of the bypass circuit is connected to the input end of the rectifier, and a second end of the bypass circuit is connected to the multi-level inverter The output terminal of the rectifier; the input terminal of the rectifier is connected to an AC power source; the rectifier is used to convert the AC power provided by the AC power source into DC power and transmit it to the battery and the multi-level inverter; The bypass circuit is used to make the AC power supply directly supply power to the load when it is activated; The battery is used to output direct current to the multi-level inverter when the rectifier stops working. 16 The uninterruptible power supply according to claim 15, wherein the rectifier is integrated with the multi-level inverter, and the rectifier includes an AC-DC circuit; the AC-DC circuit and the The inverter circuit is symmetrical along the converter bridge arm; the positive input port of the AC-DC circuit is used to connect to the AC power source, and the negative input port of the AC-DC circuit is used to connect to the midpoint of the bridge arm, The positive output port of the AC-DC circuit is connected to the positive input port of the inverter circuit, and the negative output port of the DC-DC circuit is connected to the negative input port of the inverter circuit; the AC-DC circuit is used for The AC power provided by the AC power source is converted into DC power and then transmitted to the inverter circuit. | [ZH CN112615556A]: 一种多电平逆变器以及多电平逆变器的控制方法 技术领域 [0001] 本申请涉及电力电子技术领域，尤其涉及一种多电平逆变器、多电平逆变器的控 制方法以及不间断电源。 背景技术 [0002] 逆变器（Inverter）为一种将直流电（Direct Current，DC）转换为交流电 （Alternating Current，AC）的变压器，广泛应用于不间断电源、光伏发电系统以及电动车 辆等场景中。逆变器的输入端连接直流电源，输出端可以连接交流负载或进行交流并网，逆 变器一般包括逆变电路和谐振电路，逆变电路用于将直流电转换为交流电，谐振电路用于 将交流电转换为波形近似正弦曲线的交流输出。 [0003] 随着逆变器技术的不断发展，多电平逆变器的应用日渐广泛。多电平逆变器能够 降低每个功率器件承受的电压压降，所以可以使用低耐压规格的器件实现高压大功率输 出，电平数的增加意味着改善了逆变器的输出电压波形和减小了输出波形的畸变，仅使用 较低的开关频率就可以实现以高开关频率工作的两电平逆变器的功能，还降低了功率器件 的损耗，提升了逆变器的效率。 [0004] 一并参见图1和图2,其中图1为逆变电路采用T型连接的三电平逆变器的示意图， 图2为逆变电路采用I型连接的示意图。 [0005]当三电平逆变器将直流输入转换为单相交流输出时，以上两种拓扑的逆变电路10 使用四个可控开关管。但随着逆变器电平数的增加，逆变电路使用的可控开关管的数量也 会相应增加。 [0006] 一并参见图3和图4,其中图3为现有技术的一种二极管箝位型五电平逆变器的示 意图，图4为现有技术的一种飞跨电容型五电平逆变电路的示意图。 [0007]增加电平数后，以上两种拓扑的逆变电路10需要使用八个可控开关管，相较于三 电平逆变电路翻倍，以此类推，随着电平数从三开始逐渐增加，逆变电路中的可控开关管数 量以翻倍的方式增加，致驱动信号复杂，增大了控制难度，同时使用的二极管（图3方式）或 电容（图4方式）大量增加，提高了多电平逆变器的成本。 发明内容 [0008]为了解决上述技术问题，本申请提供了一种多电平逆变器、多电平逆变器的控制 方法以及不间断电源，减少了多电平逆变器使用的可控开关管的数量，降低了多电平逆变 器的成本。 [0009] 第一方面，本申请提供了一种多电平逆变器，该多电平逆变器可应用于单母线系 统，多电平逆变器包括换流桥臂、逆变电路和控制器。其中，逆变电路的正输入端口连接多 电平逆变器的正输入端口，逆变电路的负输入端口连接多电平逆变器的负输入端口，逆变 电路的输出端连接多电平逆变器的正输出端口。换流桥臂包括上半桥臂和下半桥臂，上半 桥臂的第一端连接多电平逆变器的正输入端口，上半桥臂的第二端通过桥臂中点连接下半 桥臂的第一端，下半桥臂的第二端连接多电平逆变器的负输入端口，桥臂中点连接多电平 逆变器的负输出端口。控制器在逆变电路的正输出周期内控制上半桥臂断开，下半桥臂导 通;在逆变电路的负输出周期内控制上半桥臂导通，下半桥臂断开。 [0010]该多电平逆变器的换流桥臂在逆变电路的正、负输出周期切换工作状态，进而改 变负输出端的电位参考点，具体为：当换流桥臂的上半桥臂断开且下半桥臂导通时，多电平 逆变器的负输出端的电位参考点为逆变电路的负输入端口；当换流桥臂的上半桥臂导通且 下半桥臂断开时，多电平逆变器的负输出端的电位参考点为逆变电路的正输入端口。进而 通过改变电位的参考点，增加多电平逆变器输出的电平的数量，例如当多电平逆变器需要 输出五电平时，逆变电路仅需使用三电平拓扑，当多电平逆变器需要输出七电平时，逆变电 路仅需使用五电平拓扑，由此可见，利用本方案可将逆变电路所需的开关管的数量缩减一 半，降低了多电平逆变器的成本。 [0011]多电平逆变器的逆变电路和换流桥臂中使用的开关管可以为:绝缘栅双极型晶体 管Qnsulated Gate Bipolar Transistor，IGBT）、金属氧化物半导体场效应晶体管（Metal Oxide Semiconductor Filed Effect Transistor，MOSFET，以下简称MOS管）、碳化硅场效 应管（Silicon Carbide Metal Oxide Semiconductor，SiC MOSFET）等中的一种或多种的 组合。 [0012]结合第一方面，在第一种可能的实现方式中，换流桥臂的上半桥臂包括开关管M1， 换流桥臂的下半桥臂包括开关管M2，M1和M2分别与一个二极管反并联。控制器在逆变电路 的正输出周期内控制M1断开，且控制M2闭合，此时逆变电路的负输出端口的电位参考点为 多电平逆变器的负输入端口；控制器在逆变电路的负输出周期内，控制M1闭合，且控制M2断 开，此时逆变电路的负输出端口的电位参考点为多电平逆变器的正输入端口。 [0013]结合第一方面，在第二种可能的实现方式中，多电平逆变器为五电平逆变器，逆变 电路包括第一电容、第二电容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一 电容的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容的第二端通过第一 节点连接第二电容的第一端，第二电容的第二端和Q2的第二端连接多电平逆变器的负输入 端口，第一节点连接Q4的第一端，Q4的第二端连接Q3的第二端，Q3的第一端连接逆变电路的 输出端。Q1的第二端连接逆变电路的输出端和Q2的第一端。 [0014]结合第一方面，在第三种可能的实现方式中，控制器用于在每个正输出周期内： [0015]先在第一预设时间内控制Q1关断，控制Q3导通，并控制所述Q2和Q4交替导通;再在 第二预设时间内控制所述Q1和Q3交替导通，控制所述Q2关断并控制所述Q4导通；然后在每 个所述正输出周期的剩余时间内控制所述Q1关断，控制所述Q3导通，并控制所述Q2和Q4交 替导通； [0016]所述控制器还用于在每个所述负输出周期内： [0017]先在第一预设时间内控制所述Q2关断，控制所述Q4导通，并控制所述Q1和Q3交替 导通;再在第二预设时间内控制所述Q2和Q4交替导通，控制所述Q1关断并控制所述Q3导通; 然后在每个所述正输出周期的剩余时间内控制所述Q2关断，控制所述Q4导通，并控制所述 Q1和Q3交替导通。 [0018]其中，第一预设时间等于剩余时间。 [0019]结合第一方面，在第四种可能的实现方式中，该多电平逆变器的逆变电路包括第 一支路、第二支路和N条第三支路,N为大于或等于2的正整数。其中，第一支路包括开关管 Q5,Q5的第一端连接逆变电路的正输入端口小5的第二端连接逆变电路的输出端。第二支路 包括开关管Q6，Q6的第一端连接逆变电路的输出端，Q6的第二端连接逆变电路的负输入端 口。每条第三支路包括开关管Q7和Q8，Q7的第一端连接第三支路的第一端，Q7的第二端连接 Q8的第二端，Q8的第一端连接第三支路的第二端。 [0020]第一条第三支路的第一端通过第一电容连接第一支路的第一端，第M条第三支路 的第一端通过第M电容连接第(M-1)条第三支路的第一端，第N条第三支路的第一端通过第 (N+1)电容连接第二支路的第二端,M=2,3,…,N0N条第三支路第二端连接逆变电路的负输 出端口。逆变电路包括的各开关管分别与一个二极管反并联。 [0021]结合第一方面，在第五种可能的实现方式中，多电平逆变器为五电平逆变器，逆变 电路包括第一电容、第二电容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一 电容的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容的第二端通过第一 节点连接第二电容的第一端，第二电容的第二端和Q4的第二端连接多电平逆变器的负输入 端口，第一节点连接Q2的第二端，Q2的第一端连接Q1的第二端和Q3的第一端，Q3的第二端连 接Q4的第一端和逆变电路的输出端。 [0022]结合第一方面，在第六种可能的实现方式中，控制器用于在每个正输出周期内： [0023]先在第一预设时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0024] 再在第二预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0025] 然后在正输出周期的剩余时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0026] 控制器还用于在每个负输出周期内： [0027]先在第一预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0028] 再在所述第二预设时间内控制Q2导通，Q1关断，且控制Q3和Q4交替导通； [0029] 然后在负输出周期的剩余时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0030]第一预设时间等于正输出周期的剩余时间和负输出周期的剩余时间。 [0031]结合第一方面，在第七种可能的实现方式中，逆变电路包括N个逆变桥臂和电容 C「Cn,N大于或等于3。 [0032]每个逆变桥臂上半桥臂包括开关管Q1和Q2,Q1的第一端连接逆变桥臂的第一端， Q1的第二端通过逆变桥臂的桥臂中点连接Q2的第二端，Q2的第一端连接逆变桥臂的第二 端； [0033]第一条逆变桥臂的第一端连接逆变电路的正输入端口，且通过电容C1连接第一条 逆变桥臂的第二端； [0034]第M条逆变桥臂的第一端连接第(M-1)条逆变桥臂的桥臂中点，第M条逆变桥臂的 第二端通过电容Cm连接第(M-1)条逆变桥臂的第二端，第N条逆变桥臂的第二端连接逆变电 路的负输入端口出=2,3,…,N。 [0035]逆变电路包括的各开关管分别与一个二极管反并联。 [0036]结合第一方面，在第八种可能的实现方式中，多电平逆变器还包括第一滤波电感 和第一滤波电容。第一滤波电感连接在逆变电路的输出端和多电平逆变器的正输出端口之 间;第一滤波电容连接在多电平逆变器的真输出端口和负输出端口之间。 [0037]第一滤波电感和第一滤波电容形成的谐振电路用于将逆变电路的输出转换为波 形近似正弦曲线的交流电。 [0038]结合第一方面，在第九种可能的实现方式中，多电平逆变器还包括AC-DC电路;ACDC电路的正输入端口用于连接交输入，AC-DC电路的负输入端口用于连接桥臂中点，AC-DC 电路的正输出端口连接逆变电路的正输入端口，DC-DC电路的负输出端口连接逆变电路的 负输入端口。AC-DC电路用于将交流输入提供的交流电变换为直流电后传输给所述逆变电 路。 [0039]结合第一方面，在第十种可能的实现方式中，AC-DC电路的结构沿换流桥臂与逆变 电路对称。利用该AC-DC电路，还可以使换流桥臂实现工频电流的抵消，进而减小换流桥臂 的开关管的损耗，提升效率。 [0040]结合第一方面，在第十一种可能的实现方式中，控制器还用于控制AC-DC电路的工 作状态。 [0041] 第二方面，本申请还提供了一种多电平逆变器的控制方法，用于控制多电平逆变 器，该多电平逆变器应用于单母线系统，该方法包括以下步骤： [0042]在多电平逆变器的逆变电路的正输出周期内，控制多电平逆变器的负输出端的电 位为逆变电路的负输入端口的电位； [0043]在逆变电路的负输出周期内，控制多电平逆变器的负输出端的电位为逆变电路的 正输入端口的电位。 [0044]该方法通过改变电位参考点，在逆变电路输出的原有电平数量的基础上，额外增 加了两个电平。使得多电平逆变器可以采用输出电平数较少的拓扑输出更多的电平数，因 此可以将逆变电路所需的开关管的数量缩减一半，同时减少了需要使用的电容，降低了多 电平逆变器的体积以及成本。 [0045]结合第二方面，在第一种可能的实现方式中，多电平逆变器还包括换流桥臂，换流 桥臂包括上半桥臂和下半桥臂，上半桥臂的第一端连接逆变电路的正输入端口，上半桥臂 的第二端通过桥臂中点连接下半桥臂的第一端，下半桥臂的第二端连接逆变电路的负输入 端口，桥臂中点连接多电平逆变器的负输出端口。 [0046]在多电平逆变器的逆变电路的正输出周期内，控制多电平逆变器的负输出端的电 位为逆变电路的负输入端口的电位，具体包括： [0047]在逆变电路的正输出周期内控制上半桥臂断开，下半桥臂导通。 [0048]在逆变电路的负输出周期内，控制多电平逆变器的负输出端的电位为逆变电路的 正输入端口的电位，具体包括： [0049]在逆变电路的负输出周期内控制上半桥臂导通，下半桥臂断开。 [0050]结合第二方面，在第二种可能的实现方式中，多电平逆变器为五电平逆变器，逆变 电路包括第一电容、第二电容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一 电容的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容的第二端通过第一 节点连接第二电容的第一端，第二电容的第二端和Q2的第二端连接多电平逆变器的负输入 端口，第一节点连接Q4的第一端，Q4的第二端连接Q3的第二端，Q3的第一端连接逆变电路的 输出端。Q1的第二端连接逆变电路的输出端和Q2的第一端，此时该方法包括以下步骤： [0051] 在每个正输出周期内： [0052]先在第一预设时间内控制Q1关断，控制Q3导通，并控制所述Q2和Q4交替导通；再在 第二预设时间内控制所述Q1和Q3交替导通，控制所述Q2关断并控制所述Q4导通；然后在每 个所述正输出周期的剩余时间内控制所述Q1关断，控制所述Q3导通，并控制所述Q2和Q4交 替导通； [0053]在每个所述负输出周期内： [0054] 先在第一预设时间内控制所述Q2关断，控制所述Q4导通，并控制所述Q1和Q3交替 导通;再在第二预设时间内控制所述Q2和Q4交替导通，控制所述Q1关断并控制所述Q3导通; 然后在每个所述正输出周期的剩余时间内控制所述Q2关断，控制所述Q4导通，并控制所述 Q1和Q3交替导通。 [0055]其中，第一预设时间等于剩余时间。 [0056]结合第二方面，在第三种可能的实现方式中，多电平逆变器为五电平逆变器，逆变 电路包括第一电容、第二电容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一 电容的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容的第二端通过第一 节点连接第二电容的第一端，第二电容的第二端和Q4的第二端连接多电平逆变器的负输入 端口，第一节点连接Q2的第二端，Q2的第一端连接Q1的第二端和Q3的第一端，Q3的第二端连 接Q4的第一端和逆变电路的输出端，此时该方法包括以下步骤： [0057] 在每个正输出周期内： [0058]先在第一预设时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0059] 再在第二预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0060] 然后在正输出周期的剩余时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0061]在每个负输出周期内： [0062]先在第一预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0063] 再在所述第二预设时间内控制Q2导通，Q1关断，且控制Q3和Q4交替导通； [0064] 然后在负输出周期的剩余时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0065]第一预设时间等于正输出周期的剩余时间和负输出周期的剩余时间。 [0066] 第三方面，本申请还提供了一种不间断电源(Uninterruptible Power Supply， UPS)，该不间断电源包括以上实现方式提供的多电平逆变器，还包括整流器、旁路电路和电 池。旁路电路的第一端连接整流器的输入端，旁路电路的第二端连接多电平逆变器的输出 端。整流器的输入端连接交流电源;整流器将交流电源提供的交流电转换为直流电后传输 至电池和多电平逆变器。旁路电路用于在启用时使交流电源直接为负载供电。电池用于当 整流器停止工作时，向多电平逆变器输出直流电。 [0067]利用该多电平逆变器，通过改变电位的参考点，增加多电平逆变器输出的电平的 数量，因此可将逆变电路中使用的开关管的数量缩减一半，降低了多电平逆变器的体积以 及成本，进而降低了不间断电源的体积以及成本。 [0068]结合第三方面，在第一种可能的实现方式中，整流器与多电平逆变器集成在一起， 整流器包括AC-DC电路。AC-DC电路与逆变电路沿换流桥臂对称。AC-DC电路的正输入端口用 于连接交流电源，AC-DC电路的负输入端口连接换流桥臂的桥臂中点，AC-DC电路的正输出 端口连接逆变电路的正输入端口，DC-DC电路的负输出端口连接逆变电路的负输入端口。 AC-DC电路用于将交流电源提供的交流电变换为直流电后传输给逆变电路。 [0069]利用与逆变电路对称的AC-DC电路，还可以使换流桥臂实现工频电流的抵消，进而 减小换流桥臂的开关管的损耗，提升效率。 附图说明 [0070]图1为现有技术提供的逆变电路采用T型连接的三电平逆变器的示意图; [0071]图2为现有技术提供的逆变电路采用I型连接的三电平逆变器的示意图； [0072]图3为现有技术的一种二极管箝位型五电平逆变器的示意图； [0073]图4为现有技术的一种飞跨电容型五电平逆变电路的示意图； [0074]图5为本申请提供的一种示例性的不间断电源的示意图； [0075]图6为本申请实施例提供的一种多电平逆变器的示意图； [0076]图7为本申请实施例提供的另一种多电平逆变器的示意图； [0077]图8为本申请实施例提供的一种五电平逆变器的示意图； [0078]图9为本申请实施例提供的控制信号的时序示意图； [0079]图10A为本申请实施例提供的五电平逆变器工作状态图一； [0080]图10B为本申请实施例提供的五电平逆变器工作状态图二； [0081]图10C为本申请实施例提供的五电平逆变器工作状态图三； [0082]图10D为本申请实施例提供的五电平逆变器工作状态图四； [0083]图10E为本申请实施例提供的五电平逆变器工作状态图五； [0084]图10F为本申请实施例提供的五电平逆变器工作状态图六； [0085]图10G为本申请实施例提供的五电平逆变器工作状态图七； [0086]图10H为本申请实施例提供的五电平逆变器工作状态图八； [0087]图11为本申请实施例提供的另一种多电平逆变器的示意图； [0088]图12为本申请实施例提供的另一种五电平逆变器的示意图； [0089]图13A为本申请实施例提供的另一种五电平逆变器的示意图一； [0090]图13B为本申请实施例提供的另一种五电平逆变器的示意图二； [0091]图13C为本申请实施例提供的另一种五电平逆变器的示意图三； [0092]图13D为本申请实施例提供的另一种五电平逆变器的示意图四； [0093]图13E为本申请实施例提供的另一种五电平逆变器的示意图五； [0094]图13F为本申请实施例提供的另一种五电平逆变器的示意图六； [0095]图13G为本申请实施例提供的另一种五电平逆变器的示意图七； [0096]图13H为本申请实施例提供的另一种五电平逆变器的示意图八； [0097]图13I为本申请实施例提供的另一种五电平逆变器的示意图九； [0098]图13J为本申请实施例提供的另一种五电平逆变器的示意图十； [0099]图13K为本申请实施例提供的另一种五电平逆变器的示意图十一； [0100]图13L为本申请实施例提供的另一种五电平逆变器的示意图十二； [0101]图13M为本申请实施例提供的另一种五电平逆变器的示意图十三； [0102]图13N为本申请实施例提供的另一种五电平逆变器的示意图十四； [0103]图13O为本申请实施例提供的另一种五电平逆变器的示意图十五； [0104]图13P为本申请实施例提供的另一种五电平逆变器的示意图十六； [0105]图14为本申请实施例提供的又一种多电平逆变器的示意图； [0106]图15A为本申请实施例提供的再一种多电平逆变器的示意图； [0107]图15B为本申请实施例提供的另一种多电平逆变器的示意图； [0108]图16为本申请实施例提供的一种多电平逆变器的控制方法的示意图； [0109]图17为本申请实施例提供的另一种多电平逆变器的控制方法的示意图； [0110]图18为本申请实施例提供的一种不间断电源的示意图。 具体实施方式 [0111]为了使本领域技术人员更好地理解本申请实施例提供的技术方案，下面首先介绍 本申请提供的多电平逆变器的应用场景。 [0112]应用于不间断电源、光伏发电系统以及电动车辆等场景中的多电平逆变器，为了 输出波形近似正弦曲线的交流电，其电平数量一般为三、五、七及以上的奇数，以实现正、负 输出半周期内控制信号的对称性。 [0113] 下面以该多电平逆变器应用在不间断电源(Uninterruptible Power Supply， UPS)为例进行说明。 [0114]参见图5,该图为本申请提供的一种示例性的不间断电源的示意图。 [0115] 不间断电源100具体包括:整流器101、多电平逆变器102、电池103和旁路电路104。 [0116] 其中，整流器101用于将电源200提供的交流电转换为直流电后传输至电池103,以 为电池103充电，还将交流电转换为直流电后传输至多电平逆变器102。 [0117]多电平逆变器102将获取的直流电转换为交流电后为不间断电源的负载300供电。 [0118] 电池103用于当整流器101停止工作时向多电平逆变器102输出直流电。 [0119]旁路电路104的一端连接整流器101的输入端，另一端连接逆变器102的输出端。 [0120]旁路电路104用于在启用时使电源200直接为负载300供电。 [0121] 具体的，不间断电源100通过控制主路开关S1、电池开关S2和旁路开关S3的状态以 改变工作状态，下面具体说明。 [0122] 当电源200正常供电且UPS无故障时，UPS的主路工作，即主路开关S1闭合，电池开 关S2和旁路开关S3均断开。此时电源200输入UPS的交流电经过整流器101和多电平逆变器 102给负载300供电，并且通过整流器101给电池103充电，UPS能够向负载300输出稳定的电 压。 [0123] 当电源200输入故障、需要电源200停止供电或整流器101故障时，由UPS的电池103 向负载30供电。此时电池开关S2闭合，主路开关S1和旁路开关S3均断开，多电平逆变器102 将电池103提供的直流电转换为交流电后为负载300供电。 [0124] 当多电平逆变器102故障时，旁路电路104需要启动工作，此时旁路开关S3导通，主 路开关S1和电池开关S2均闭合，电源200直接向负载300供电。 [0125] 在另一些可能的实方式中，多电平逆变器102前一级还包括DC-DC电路，DC-DC电路 用于对直流电进行直流变换，例如DC-DC电路为升压(Boost)电路，用于将直流电进行升压 后再传输至多电平逆变器102。 [0126] 多电平逆变器102中每个功率器件(即多电平逆变器包括的可控开关管)承受的电 压压降相较于传统的两电平逆变器更低，因此可以使用具备低耐压规格的器件实现高压大 功率输出。增加多电平逆变器的电平数量，能够改善输出电压波形，减小输出波形的畸变， 可以还降低功率器件的开关频率与损耗。但是当多电平逆变器的电平数量由三开始逐渐增 加时，多电平逆变器所需的功率器件的数量以翻倍的方式增加，大大增大了多电平逆变器 体积、控制复杂程度以及成本。 [0127] 为了解决以上问题，本申请提供了一种多电平逆变器、多电平逆变器的控制方法 以及不间断电源，该多电平逆变器应用单母线的系统，利用换流桥臂改变系统的参考点来 实现多电平的输出，进而减少多电平逆变电路使用的开关器件的数量，降低了多电平逆变 器的成本，下面结合实施例具体说明。 [0128]本申请说明中的“第一”、“第二”等用词仅用于描述目的，而不能理解为指示或暗 示相对重要性或者隐含指明所指示的技术特征的数量。 [0129]在本申请中，除非另有明确的规定和限定，术语“连接”应做广义理解，例如，“连 接”可以是固定连接，也可以是可拆卸连接，或成一体;可以是直接连接，也可以通过中间媒 介或器件进行间接连接。 [0130]目前三电平逆变器的实现方案较为成熟，且使用的开关管数量为四，数量较少，本 申请实施例旨在降低更高电平数量的逆变器使用的开关管的数量，即本申请以下实施例提 供的多电平逆变器指电平数量大于或等于五的逆变器，以下不再赘述，下面结合附图具体 说明。 [0131]参见图6,该图为本申请实施例提供的一种多电平逆变器的示意图。 [0132] 该多电平逆变器包括逆变电路10、换流桥臂20和控制器40。 [0133] 其中，逆变电路10的正输入端口连接多电平逆变器的正输入端口（图中对应BUS +），逆变电路10的负输入端口连接多电平逆变器的负输入端口（图中对应BUS-），逆变电路 的输出端连接多电平逆变器的正输出端口。 [0134]换流桥臂20包括上半桥臂和下半桥臂，上半桥臂的第一端连接多电平逆变器的正 输入端口，上半桥臂的第二端通过桥臂中点连接下半桥臂的第一端，下半桥臂的第二端连 接多电平逆变器的负输入端口，桥臂中点连接多电平逆变器的负输出端口。 [0135]控制器40在逆变电路10的正输出周期内，控制上半桥臂断开且控制下半桥臂导 通，此时负输出端口通过下半桥臂连接多电平逆变器的负输入端口，即此时逆变电路10的 负输出端口的电位参考点为多电平逆变器的负输入端口，多电平逆变器的输出电压可以表 示为（Vout+-VBUS-）。 [0136]控制器在逆变电路10的负输出周期内，控制上半桥臂导通且控制下半桥臂关闭， 此时负输出端口通过上半桥臂连接多电平逆变器的正输入端口，即此时逆变电路10的负输 出端口的电位参考点为多电平逆变器的正输入端口，多电平逆变器的输出电压可以表示为 （Vout+-VBUS+）。 [0137]因此通过改变电位参考点，在逆变电路10输出的电平数量的基础上，额外增加了 两个电平。当逆变电路10使用图1或图2所示的三电平拓扑时，多电平逆变器能够实现五电 平输出，当逆变电路10使用图3或图4所示的五电平拓扑时，多电平逆变器能够实现七电平 输出，以此类推，多电平逆变器可以采用输出电平数较少的拓扑输出更多的电平数，因此可 以将逆变电路10所需的开关管的数量缩减一半，同时减少了需要使用的电容，降低了多电 平逆变器的体积以及成本。 [0138] 控制器可以为专用集成电路（Application Specific Integrated Circuit， ASIC)、可编程逻辑器件(Programmable Logic Device,PLD)、数字信号处理器(Digital Signal Processor，DSP)或其组合。上述PLD可以是复杂可编程逻辑器件(Complex Programmable Logic Device，CPLD)、现场可编程逻辑门阵列(Field-programmable Gate Array，FPGA)、通用阵列逻辑(Generic Array Logic，GAL)或其任意组合，本申请实施例对 此不作具体限定。 [0139]逆变电路301中包括开关管，本申请实施例不具体限定可控开关管的类型，例如可 以为绝缘栅双极型晶体管、金属氧化物半导体场效应晶体管、碳化硅场效应管等中的一种 或多种的组合。 [0140]控制器可以向开关管发送控制信号以控制可控开关管的工作状态。在一些实施例 中，该控制信号为脉冲宽度调制(Pulse Width Modulation，PWM)信号。 [0141]在一些实施例中，上半桥臂包括第一开关管M1，下半桥臂包括第二开关管M2。其 中，M1和M2分别与一个二管反并联。该二极管可以为开关管的寄生二极管(又称体二极管)， 或者单独设置的二极管，本申请实施例对此不做具体限定。 [0142] M1的第一端连接上半桥臂的第一端，M1的第二端通过桥臂中点连接M2的第一端， M2的第二端连接下半桥臂的第二端，以M1和M2为MOS管且具体为NMOS管为例，则第一端为M1 和M2的漏极，第二端为M1和M2的源极。 [0143] 控制器在逆变电路10的正输出周期内控制M1断开，以使上半桥臂断开，且控制M2 闭合，以使下半桥臂导通。控制器在逆变电路10的负输出周期内，控制M1闭合，以使上半桥 臂导通，且控制M2断开，以使下半桥臂断开。 [0144]参见图7,该图为本申请实施例提供的另一种多电平逆变器的示意图。 [0145]图示多电平逆变器与图6的区别在于，还包括了谐振电路30。谐振电路30具体包括 第一滤波电感L1和第一滤波电容C1。 [0146]其中，L1连接在逆变电路10的输出端和多电平逆变器的正输出端口之间，C1连接 在多电平逆变器的正输出端口和负输出端口之间。 [0147]谐振电路30用于将逆变电路10的输出转换为波形近似正弦曲线的交流电。 [0148]下面结合具体的实现方式说明该多电平逆变器的工作原理。 [0149]首先以五电平逆变器为例进行说明。 [0150] 参见图8,该图为本申请实施例提供的一种五电平逆变器的示意图。 [0151] 该五电平逆变器的逆变电路具体包括第一电容C1、第二电容C2和开关管Q1-Q4。其 中，每个开关管分别于一个二极管反并联。二极管可以为开关管的体二极管，或单独设置的 二极管，本申请实施例不做具体限定。 [0152] 第一电容C1的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容C1 的第二端通过第一节点连接第二电容C2的第一端。 [0153] 第二电容C2的第二端和Q2的第二端连接多电平逆变器的负输入端口，第一节点连 接Q4的第一端，Q4的第二端连接Q3的第二端，Q3的第一端连接逆变电路10的输出端。 [0154] Q1的第二端连接逆变电路10的输出端和Q2的第一端。 [0155] 以开关管Q1-Q4具体为NMOS管为例，Q1-Q4的第一端为漏极，Q1-Q4的第二端为源 极。 [0156] 控制器用于对开关管Q1-Q4和换流桥臂的开关管M1、M2进行控制，下面具体说明。 [0157] 其中C1两端电压为BUS2,C2两端电压为BUS1,一般使用的C1和C2型号相同，电容值 相同，因此通常BUS1和BUS2相同。 [0158]参见图9,该图为本申请实施例提供的控制信号的时序示意图。 [0159] 一并参见图10A-10B所示的五电平逆变器的工作状态图。 [0160]为了方便理解，图9所示的时序图中未直接示意出各开关管的控制信号设置了死 区时间（Dead time），本申请实施例对死区时间的具体长度不做限定，可根据实际应用的开 关管的规格确定。死区时间时五电平逆变器的工作状态示意图依次参见图10B、D、F和H所 示。以上工作状态图中仅示出了开关管的通断状态，用于进行续流的二极管未示出。 [0161] 控制器在每个正输出周期内： [0162] 控制器控制M1断开，且控制M2闭合； [0163]先在第一预设时间（时间长度等于零时刻至t2时刻的长度）内控制Q1关断，控制Q3 导通，并控制Q2和Q4交替导通； [0164]再在第二预设时间（时间长度等于t2时刻至t4时刻的长度）内控制Q1和Q3交替导 通，控制Q2关断并控制Q4导通； [0165]然后在每个正输出周期的剩余时间（时间长度等于t4时刻至t5时刻的长度）内控 制Q1关断，控制Q3导通，并控制Q2和Q4交替导通。 [0166] 控制器还用于在每个负输出周期内： [0167] 控制器在逆变电路10的负输出周期内控制M1闭合，且控制M2断开； [0168]先在第一预设时间内控制Q2关断，控制Q4导通，并控制Q1和Q3交替导通； [0169] 再在第二预设时间内控制Q2和Q4交替导通，控制Q1关断并控制Q3导通； [0170] 然后在每个正输出周期的剩余时间内控制Q2关断，控制Q4导通，并控制Q1和Q3交 替导通。 [0171]下面以正输出周期为例进行说明，负输出周期的情况类似，本实施例不再赘述： [0172] 在0-t1内，Q1关断，Q3导通，Q2处于关断状态，Q4处于导通状态，此时五电平逆变器 的工作状态如图10A，C1和C2处于充电状态，C1的两端电压为BUS2，C2的两端电压为BUS1，同 时L和Co进行充电，Co的充电电压为BUS1，续流回路如图中虚线所示。 [0173] 然后Q1和Q2维持关断，Q3维持导通，Q4在Q2导通前先切换为关断状态，此过程对应 图10B，持续时间为开关管Q4的死区时间。 [0174] 然后Q1维持关断，Q3维持导通，Q2切换为关闭状态，此过程对应图10C，L和Co释放 能量，续流回路如图中虚线所示。 [0175] 然后Q1和Q2维持关断，Q3维持导通，Q2在Q4导通前先切换为关闭状态，此过程对应 图10D，提前时间为开关管Q2的死区时间。 [0176]以上过程完成了一个第一控制周期，包括“储能时间-死区时间-续流时间-死区时 间“，在0-t2的时间内重复完成以上的第一控制周期，即实现了正输出周期内输出电压由0 提升至BUS1的过程。 [0177]同理，在t4-t5的时间内重复完成以上的第一控制周期，即实现了正输出周期的剩 余时间内输出电压由BUS1下降至0的过程。 [0178] 在t2-t3内，维持Q2关断且Q4导通，先控制Q1导通，Q3关断，此时C1和C2处于充电状 态，同时L和Co进行充电，续流回路如图10E中虚线所示，Co的充电电压为BUS1+BUS2。 [0179] 然后Q1在Q3切换为导通前先切换为关断状态，此过程对应图10F,持续时间为Q1的 死区时间。 [0180] 然后维持Q1关断、Q2关断且Q4导通，Q3切换为导通，此时利用Q2的反并联二极管进 行续流，续流回路如图10G中虚线所示。 [0181] 然后Q3在Q1切换为导通前先切换为关断状态，此过程对应图10H，持续时间为Q3的 死区时间。 [0182]以上过程完成了一个第二控制周期，包括“储能时间-死区时间-续流时间-死区时 间“，在t2-t4的时间内重复完成以上的第二控制周期，即实现了正输出周期内输出电压处 于BUS1至BUS1+BUS2的过程。 [0183]综上所述，该五电平逆变器的换流桥臂在逆变电路的正、负输出周期进行工作状 态的切换，改变了负输出端的电位参考点，进而增加多电平逆变器输出的电平的数量，使得 五电平逆变器的逆变电路仅需使用三电平逆变电路的拓扑，使用的开关管的数量缩减一 半，降低了多电平逆变器的成本。 [0184]基于以上实施例提供的五电平逆变器实现方式，本申请实施例还提供了一种多电 平逆变器，能够实现七电平及以上数量的电平输出，下面结合附图具体说明。 [0185]参见图11，该图为本申请实施例提供的另一种多电平逆变器的示意图。 [0186]图示多电平逆变器的逆变电路10包括第一支路、第二支路和N条第三支路。 [0187] 其中，N为大于或等于3的整数。 [0188]第一支路包括开关管Q5，Q5的第一端连接逆变电路10的正输入端口小5的第二端 连接逆变电路的输出端。 [0189]第二支路包括开关管Q6，Q6的第一端连接逆变电路10的输出端，Q6的第二端连接 逆变电路的负输入端口。 [0190] N条第三支路的电路结构相同。每条第三支路包括开关管Q7和Q8，Q7的第一端连接 第三支路的第一端，Q7的第二端连接Q8的第二端，Q8的第一端连接第三支路的第二端。 [0191]第一条第三支路的第一端通过第一电容^连接第一支路的第一端，第M条第三支 路的第一端通过第M电容连接第(M-1)条第三支路的第一端，第N条第三支路的第一端通过 第(N+1)电容％+1连接第二支路的第二端,M=2,3,…,N。 [0192] N条第三支路第二端连接逆变电路10的负输出端口。 [0193]以上第一支路、第二支路和第三支路中包括的开关管均分别与一个二极管反并 联，该二极管可以为开关管的体二极管，或单独设置的二极管，本申请实施例不做具体限 定。 [0194]该多电平逆变器的换流桥臂在逆变电路10的正、负输出周期进行工作状态的切 换，进而改变负输出端的电位参考点，具体为：当换流桥臂的上半桥臂断开且下半桥臂导通 时，多电平逆变器的负输出端的电位参考点为逆变电路的负输入端口；当换流桥臂的上半 桥臂导通且下半桥臂断开时，多电平逆变器的负输出端的电位参考点为逆变电路的正输入 端口。通过改变电位的参考点，增加多电平逆变器输出的电平的数量，可将逆变电路中使用 的开关管的数量缩减一半，降低了多电平逆变器的成本。 [0195]下面结合附图说明另一种五电平逆变器的实现方式。 [0196] 参见图12,该图为本申请实施例提供的另一种五电平逆变器的示意图。 [0197] 一并参见图13A至图13P所示的五电平逆变器的工作状态图。 [0198]以上工作状态图中仅示出了开关管的通断状态，用于进行续流的二极管未示出。 [0199] 死区时间时五电平逆变器的工作状态示意图依次参见图13B、D、F、H、J、L、N和P所 示。 [0200] 该五电平逆变器的逆变电路包括第一电容C1、第二电容C2和开关管Q1-Q4,每个开 关管分别于一个二极管反并联。 [0201] 第一电容C1的第一端和Q1的第一端连接多电平逆变器的正输入端口，第一电容C1 的第二端通过第一节点连接第二电容C2的第一端，第二电容C2的第二端和Q4的第二端连接 多电平逆变器的负输入端口。 [0202] 第一节点连接Q2的第二端，Q2的第一端连接Q1的第二端和Q3的第一端，Q3的第二 端连接Q4的第一端和逆变电路的输出端。 [0203]控制器具体用于在每个正输出周期内： [0204]先在第一预设时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0205] 再在第二预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0206] 然后在正输出周期的剩余时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通。 [0207] 控制器还用于在每个负输出周期内： [0208]先在第一预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0209] 再在第二预设时间内控制Q2导通，Q1关断，且控制Q3和Q4交替导通； [0210] 然后在负输出周期的剩余时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通。 [0211]其中，第一预设时间等于正输出周期的剩余时间和负输出周期的剩余时间。 [0212]下面结合工作状态图具体进行说明。 [0213] 控制器在每个正输出周期内： [0214] 控制器控制M1断开，且控制M2闭合； [0215] 先控制Q1和Q4关闭，Q2和Q3导通，此时五电平逆变器的工作状态参见图13A所示， C1和C2处于充电状态，C1的两端电压为BUS2，C2的两端电压为BUS1，同时L和Co进行充电，Co 的充电电压为BUS1，续流回路如图中虚线所示。 [0216] 然后在Q4导通前先控制Q3关断，此过程对应图13B，持续时间为开关管Q3的死区时 间。 [0217] 接着Q1和Q3维持关断，Q2维持导通，控制Q4切换为导通状态，此时L和Co释放能量， 续流回路如图13C中虚线所示。 [0218] 然后Q1和Q3维持关断，Q2维持导通，控制Q4在Q3导通前关断，此过程对应图13D，提 前时间为Q4的死区时间。 [0219]以上过程完成了一个第一控制周期，包括“储能时间-死区时间-续流时间-死区时 间”，在第一预设时间内重复完成以上的第一控制周期，即实现了正输出周期内输出电压由 0提升至BUS1的过程。 [0220]同理，在正输出周期的剩余时间内重复完成以上的第一控制周期，即实现了正输 出周期的剩余时间内输出电压由BUS1下降至0的过程。 [0221] 在第二预设时间内，控制器先控制Q1和Q3闭合，Q2和Q4断开，此时C1和C2处于充电 状态，C1的两端电压为BUS2，C2的两端电压为BUS1，同时L和Co进行充电，Co的充电电压为 BUS1+BUS2，续流回路如图13E中虚线所示。 [0222] 接着控制器控制Q2和Q4维持断开，控制Q3维持闭合，且控制Q1在Q2闭合之前断开， 此过程对应图13F,Q1提前断开的时间为Q1的死区时间。 [0223] 然后控制器控制Q1和Q4维持断开，控制Q3维持闭合，且控制Q2切换为闭合状态，此 时L和Co进行放电，续流回路参见图13G，利用Q4的反并联二极管进行续流。 [0224] 接着控制器控制Q1和Q4维持断开，控制Q3维持闭合，且控制Q2在Q1闭合之前断开， 此过程对应于图13H，Q2提前断开的时间为Q2的死区时间。 [0225]以上过程完成了一个第二控制周期，包括“储能时间-死区时间-续流时间-死区时 间”，在正输出周期的第二预设时间内重复完成以上的第二控制周期，即实现了正输出周期 内输出电压处于BUS1至BUS1+BUS2的过程。 [0226]下面说明负输出周期内的控制过程。 [0227] 控制器控制M1闭合，且控制M2断开。 [0228] 控制器先控制Q1和Q4断开，控制Q2和Q3导通，此时五电平逆变器的工作状态如图 13I所示，C1和C2处于充电状态，C1的两端电压为-BUS2,C2的两端电压为-BUS1,同时L和Co 进行充电，Co的充电电压为-BUS1,续流回路如图中虚线所示。 [0229] 其中-BUS1-BUS2 = BUS-。 [0230] 然后Q1和Q4维持关断，Q3维持导通，Q2在Q1切换为导通状态前先切换为关断状态， 此过程对应图13J,Q2提前关断的时间为Q2的死区时间。 [0231] 接着Q2和Q4维持关断，Q3维持导通，Q1切换为导通状态，此时L和C。释放能量，续流 回路如图13K中虚线所示。 [0232] 然后Q2和Q4维持关断，Q3维持导通，Q1在Q2切换为导通状态之间先切换为关断状 态，此过程对应图13L,Q1提前关断的时间为Q1的死区时间。 [0233]以上过程完成了一个第三控制周期，包括“储能时间-死区时间-续流时间-死区时 间”，在负输出周期的第一预设时间内重复完成以上的第三控制周期，即实现了负输出周期 内输出电压由0降低至-BUS1的过程。 [0234]同理，在负输出周期的剩余时间内重复完成以上的第三控制周期，即实现了负输 出周期剩余时间内输出电压由-BUS1上升至0的过程。 [0235] 在负输出周期的第二预设时间内，控制器先控制Q1和Q3断开，再控制Q2和Q4闭合， 此时C1和C2处于充电状态，C1的两端电压为-BUS2,C2的两端电压为-BUS1,同时L和C。进行 充电，续流回路如图13M中虚线所示，C。的充电电压为-BUS1-BUS2。 [0236] 接着控制器控制Q1和Q3维持断开，控制Q2维持闭合，控制Q4在Q3切换为导通状态 之前先切换为关断状态，此过程对应图13N,Q4提前关断的时间为Q4的死区时间。 [0237] 然后控制器控制Q1和Q4维持断开，控制Q2维持闭合且控制Q3切换为导通状态，此 时L和C。释放能量，续流回路如图13O中虚线所示，利用Q1的反并联二极管进行续流。 [0238] 接着控制器控制Q1和Q4维持断开，控制Q2维持闭合，且控制Q3在Q4切换为导通状 态之前提前关断，Q3提前关断的时间为Q3的死区时间。 [0239]以上过程完成了一个第四控制周期，包括“储能时间-死区时间-续流时间-死区时 间”，在负输出周期的第二预设时间内重复完成以上的第四控制周期，即实现了负输出周期 内输出电压处于-BUS1至-BUS1-BUS2内的过程。 [0240]综上所述，该五电平逆变器的换流桥臂在逆变电路的正、负输出周期进行工作状 态的切换，改变了负输出端的电位参考点，进而增加多电平逆变器输出的电平的数量，使得 五电平逆变器的逆变电路仅需使用三电平逆变电路的拓扑，使用的开关管的数量缩减一 半，降低了多电平逆变器的成本。 [0241]下面结合附图说明另一种能够实现七电平及以上数量的电平输出的多电平逆变 器。 [0242]参见图14,该图为本申请实施例提供的又一种多电平逆变器的示意图。 [0243]该多电平逆变器的逆变电路10包括N个逆变桥臂和电容C「CN。 [0244] 其中，N为大于或等于3的整数。 [0245]每个逆变桥臂的电路结构相同。 [0246]每个逆变桥臂上半桥臂包括开关管Q1和Q2，Q1的第一端连接逆变桥臂的第一端， Q1的第二端通过逆变桥臂的桥臂中点连接Q2的第二端，Q2的第一端连接逆变桥臂的第二 端。 [0247]第一条逆变桥臂的第一端连接逆变电路的正输入端口，且通过电容C1连接第一条 逆变桥臂的第二端。 [0248]第M条逆变桥臂的第一端连接第(M-1)条逆变桥臂的桥臂中点，第M条逆变桥臂的 第二端通过电容CM连接第(M-1)条逆变桥臂的第二端，第N条逆变桥臂的第二端连接逆变电 路的负输入端口。 [0249] 其中，M=2,3,…，N。 [0250]逆变电路包括的各开关管分别与一个二极管反并联。 [0251]该多电平逆变器的换流桥臂在逆变电路的正、负输出周期进行工作状态的切换， 进而改变负输出端的电位参考点，具体为：当换流桥臂的上半桥臂断开且下半桥臂导通时， 多电平逆变器的负输出端的电位参考点为逆变电路的负输入端口；当换流桥臂的上半桥臂 导通且下半桥臂断开时，多电平逆变器的负输出端的电位参考点为逆变电路的正输入端 口。进而通过改变电位的参考点，增加多电平逆变器输出的电平的数量，例如当多电平逆变 器需要输出五电平时，逆变电路仅需使用三电平拓扑，当多电平逆变器需要输出七电平时， 逆变电路仅需使用五电平拓扑，由此可见，利用本方案可将逆变电路中使用的开关管的数 量缩减一半，降低了多电平逆变器的成本。 [0252]当本申请实施例提供的多电平逆变器应用于不间断电源时，逆变电路的输入端连 接直流输入，参见图5对应的说明，当电源正常供电且UPS无故障时，该直流输入由前级的整 流电路将交流电转换为直流电后提供，因此在一些实施例中，多电平逆变器还可以与前级 的整流电路集成在一起，即多电平逆变器还可以包括AC-DC电路，此时集成形成了AC-DC-AC 变换器,下面结合附图具体说明。 [0253]参见图15A,该图为本申请实施例提供的再一种多电平逆变器的示意图。 [0254]图示多电平逆变器与图7所示的区别在于还包括AC-DC电路40。 [0255] AC-DC电路40的正输入端用于连接交流输入，AC-DC电路40的负输入端用于连接换 流桥臂的桥臂中点。AC-DC电路40的正输出端口连接逆变电路10的正输入端口,AC-DC电路 40的负输出端口连接逆变电路10的负输入端口。 [0256] AC-DC电路40用于将交流输入提供的交流电变换为直流电后传输给逆变电路10。 [0257] 在一些实施例中，AC-DC电路的结构沿换流桥臂20与逆变电路10对称，可以使换流 桥臂实现工频电流的抵消，进而减小换流桥臂的开关管的损耗，提升效率。 [0258] 下面以五电平逆变器为例，结合AC-DC电路40的具体实现方式进行说明。 [0259]参见图15B，该图为本申请实施例提供的另一种多电平逆变器的示意图。 [0260] AC-DC电路40包括开关管M3-M6、第二滤波电感L2和第二滤波电容Ci。 [0261]开关管M3-M6分别与一个二极管反并联，该二极管可以为开关管的体二极管，或单 独设置的二极管，本申请实施例不做具体限定。 [0262] 其中，AC-DC电路40的正输入端口通过第二滤波电感L2连接M3的第二端，M3的第一 端连接逆变电路10的正输入端口制3的第二端连接M4的第一端和M5的第一端，M4的第二端 连接DC-DC电路40的负输入端口和桥臂中点，M5的第二端连接M6的第二端，M6的第一端连接 逆变电路10的电容中点。 [0263] 第二滤波电容Ci连接在AC-DC电路40的正输入端口和负输入端口之间。 [0264]利用该AC-DC电路，还可以使换流桥臂实现工频电流的抵消，进而减小换流桥臂的 开关管的损耗，提升效率。 [0265]基于以上实施例提供的多电平逆变器，本申请实施例还提供了一种多电平逆变器 的控制方法，下面结合附图具体说明。 [0266]参见图16,该图为本申请实施例提供的一种多电平逆变器的控制方法的流程图。 [0267]该方法包括以下步骤： [0268] S1401：在多电平逆变器的逆变电路的正输出周期内，控制多电平逆变器的负输出 端的电位为逆变电路的负输入端口的电位。 [0269]多电平逆变器的负输入端口的电位用VBUS.表示，多电平逆变器的正输出端口的电 位用Vout+表示，则此时多电平逆变器的输出电压可以表示为(Vout+-VBUS-)。 [0270] S1402：在逆变电路的负输出周期内，控制多电平逆变器的负输出端的电位为逆变 电路的正输入端口的电位。 [0271]多电平逆变器的正输入端口的电位用VBUS+表示，多电平逆变器的正输出端口的电 位用Vout+表示，则此时多电平逆变器的输出电压可以表示为(Vout+-VBUS+)。 [0272]通过改变电位参考点，在逆变电路输出的原有电平数量的基础上，额外增加了两 个电平。使得多电平逆变器可以采用输出电平数较少的拓扑输出更多的电平数，因此可以 将逆变电路所需的开关管的数量缩减一半，同时减少了需要使用的电容，降低了多电平逆 变器的体积以及成本。 [0273]下面结合多电平逆变器的具体实现方式进行说明。 [0274]多电平逆变器包括换流桥臂，换流桥臂包括上半桥臂和下半桥臂。上半桥臂的第 一端连接逆变电路的正输入端口，上半桥臂的第二端通过桥臂中点连接下半桥臂的第一 端，下半桥臂的第二端连接逆变电路的负输入端口，桥臂中点连接多电平逆变器的负输出 端口。 [0275]参见图17,该图为本申请实施例提供的另一种多电平逆变器的控制方法的示意 图。 [0276] 该方法包括以下步骤： [0277] S1501：在逆变电路的正输出周期内控制上半桥臂断开，下半桥臂导通。 [0278] 此时负输出端口通过下半桥臂连接多电平逆变器的负输入端口，即此时逆变电路 的负输出端口的电位参考点为多电平逆变器的负输入端口，多电平逆变器的输出电压可以 表示为(V°ut+-VBUS，。 [0279] S1502：在逆变电路的负输出周期内控制上半桥臂导通，下半桥臂断开。 [0280] 此时负输出端口通过上半桥臂连接多电平逆变器的正输入端口，即此时逆变电路 的负输出端口的电位参考点为多电平逆变器的正输入端口，多电平逆变器的输出电压可以 表示为(V°ut+-VBUS+)。 [0281] 在一些实施例中，多电平逆变器为五电平逆变器，逆变电路包括第一电容、第二电 容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一电容的第一端和Q1的第一端 连接多电平逆变器的正输入端口，第一电容的第二端通过第一节点连接第二电容的第一 端，第二电容的第二端和Q2的第二端连接多电平逆变器的负输入端口，第一节点连接Q4的 第一端，Q4的第二端连接Q3的第二端，Q3的第一端连接逆变电路的输出端。Q1的第二端连接 逆变电路的输出端和Q2的第一端。 [0282] 此时该方法还包括以下步骤： [0283] 在每个正输出周期内： [0284] 先在第一预设时间内控制Q1关断，控制Q3导通，并控制所述Q2和Q4交替导通； [0285] 再在第二预设时间内控制Q1和Q3交替导通，控制所述Q2关断并控制Q4导通； [0286] 然后在每个正输出周期的剩余时间内控制Q1关断，控制Q3导通，并控制Q2和Q4交 替导通。 [0287]在每个所述负输出周期内： [0288]先在第一预设时间内控制Q2关断，控制Q4导通，并控制Q1和Q3交替导通;再在第二 预设时间内控制Q2和Q4交替导通，控制Q1关断并控制Q3导通； [0289] 然后在每个正输出周期的剩余时间内控制Q2关断，控制Q4导通，并控制Q1和Q3交 替导通。 [0290]其中，第一预设时间等于剩余时间。 [0291] 在另一些实施例中，多电平逆变器为五电平逆变器，逆变电路包括第一电容、第二 电容和开关管Q1-Q4,每个开关管分别于一个二极管反并联。第一电容的第一端和Q1的第一 端连接多电平逆变器的正输入端口，第一电容的第二端通过第一节点连接第二电容的第一 端，第二电容的第二端和Q4的第二端连接多电平逆变器的负输入端口，第一节点连接Q2的 第二端，Q2的第一端连接Q1的第二端和Q3的第一端，Q3的第二端连接Q4的第一端和逆变电 路的输出端。 [0292] 此时该方法还包括以下步骤： [0293]在每个正输出周期内： [0294]先在第一预设时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0295] 再在第二预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0296] 然后在正输出周期的剩余时间内控制Q1关断、Q2导通，且控制Q3和Q4交替导通； [0297]在每个负输出周期内： [0298]先在第一预设时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0299] 再在所述第二预设时间内控制Q2导通，Q1关断，且控制Q3和Q4交替导通； [0300] 然后在负输出周期的剩余时间内控制Q3导通、Q4关断，且控制Q1和Q2交替导通； [0301]第一预设时间等于正输出周期的剩余时间和负输出周期的剩余时间。 [0302]该方法通过控制换流桥臂在逆变电路的正、负输出周期切换工作状态，进而改变 负输出端的电位参考点，具体为：当换流桥臂的上半桥臂断开且下半桥臂导通时，多电平逆 变器的负输出端的电位参考点为逆变电路的负输入端口；当换流桥臂的上半桥臂导通且下 半桥臂断开时，多电平逆变器的负输出端的电位参考点为逆变电路的正输入端口，可将逆 变电路所需的开关管的数量缩减一半，降低了多电平逆变器的成本。 [0303]基于以上实施例提供的多电平逆变器，本申请实施例还提供了一种不间断电源， 下面结合附图具体说明。 [0304] 参见图18,该图为本申请实施例提供的一种不间断电源的示意图。 [0305] 该不间断电源100包括整流器101、多电平逆变器102、电池103和旁路电路104。 [0306]旁路电路104的第一端通过主路开关S1连接整流器101的输入端和交流电源，旁路 电路104的第二端连接多电平逆变器102的输出端。 [0307] 电池103通过电池开关S2连接多电平逆变器102的输入端。 [0308]旁路电路104设置有旁路开关S3。 [0309] 不间断电源100的控制器通过控制主路开关S1、电池开关S2和旁路开关S3的状态 以改变工作状态，下面具体说明。 [0310] 当交流电源正常供电且UPS无故障时，UPS的主路工作，即主路开关S1闭合，电池开 关S2和旁路开关S3均断开。 [0311] 此时交流电源输入的交流电经过整流器101和多电平逆变器102给负载供电，并且 通过整流器101给电池103充电，UPS能够向负载300输出稳定的电压。 [0312]当交流电源故障，或者需要交流电源停止供电，或者整流器101故障时，由UPS的电 池103向负载供电。此时整流器101停止工作，电池开关S2闭合，主路开关S1和旁路开关S3均 断开，多电平逆变器102将电池103提供的直流电转换为交流电后为负载供电。 [0313] 当多电平逆变器102故障时，旁路电路104需要启动工作，此时旁路开关S3导通，主 路开关S1和电池开关S2均闭合，交流电源直接向负载供电。 [0314] 关于多电平逆变器102的具体实现方式可以参见以上实施例中的相关说明，本申 请实施例在此不再赘述。 [0315] 不间断电源100的控制器可以与多电平逆变器102的控制器集成在一起。 [0316]该不间断电源的多电平逆变器包括换流桥臂，换流桥臂在逆变电路的正、负输出 周期进行工作状态的切换，进而改变负输出端的电位参考点，具体为：当换流桥臂的上半桥 臂断开且下半桥臂导通时，多电平逆变器的负输出端的电位参考点为逆变电路的负输入端 口；当换流桥臂的上半桥臂导通且下半桥臂断开时，多电平逆变器的负输出端的电位参考 点为逆变电路的正输入端口。通过改变电位的参考点，增加多电平逆变器输出的电平的数 量，例如当多电平逆变器需要输出五电平时，逆变电路仅需使用三电平拓扑，当多电平逆变 器需要输出七电平时，逆变电路仅需使用五电平拓扑。 [0317]利用该多电平逆变器，可将逆变电路中使用的开关管的数量缩减一半，降低了多 电平逆变器的体积以及成本，进而降低了不间断电源的体积以及成本。 [0318] 在一些实施例中，整流器与多电平逆变器集成在一起，整流器包括AC-DC电路。 [0319] AC-DC电路的正输入端口用于连接交流电源，AC-DC电路的负输入端口用于连接桥 臂中点，AC - DC电路的正输出端口连接逆变电路的正输入端口，AC - DC电路的负输出端口连 接逆变电路的负输入端口。AC-DC电路用于将交流电源提供的交流电变换为直流电后传输 给逆变电路。 [0320] AC-DC电路与逆变电路沿换流桥臂对称。进而可以使换流桥臂实现工频电流的抵 消，进而减小换流桥臂的开关管的损耗，提升效率。 [0321]应当理解，在本申请中，”至少一个（项）”是指一个或者多个，“多个”是指两个或两 个以上。“和/或”，用于描述关联对象的关联关系，表示可以存在三种关系，例如，A和/或B” 可以表示：只存在A，只存在B以及同时存在A和B三种情况，其中A，B可以是单数或者复数。字 符7”一般表示前后关联对象是一种“或”的关系。“以下至少一项（个）”或其类似表达，是指 这些项中的任意组合，包括单项（个）或复数项（个）的任意组合。例如，a，b或c中的至少一项 （个），可以表示:a，b，c，“a和b”，“a和c”，“b和c”，或a和b和c”，其中a，b，c可以是单个，也可 以是多个。 [0322]本中的各个实施例均采用递进的方式描述，各个实施例之间相同相似的部 分互相参见即可，每个实施例重点说明的都是与其他实施例的不同之处。另外，还可以根据 实际的需要选择其中的部分或者全部单元和模块来实现本实施例方案的目的。本领域普通 技术人员在不付出创造性劳动的情况下，即可以理解并实施。 [0323]以上所述仅是本申请的具体实施方式，应当指出，对于本技术领域的普通技术人 员来说，在不脱离本申请原理的前提下，还可以做出若干改进和润饰，这些改进和润饰也应 视为本申请的保护范围。 [EN CN112615556A]: A multi-level inverter and a control method of the multi-level inverter Technical field [0001] This application relates to the field of power electronics technology, and in particular to a multi-level inverter, a control method of the multi-level inverter, and an uninterruptible power supply. Background technique [0002] An inverter (Inverter) is a transformer that converts direct current (DC) into alternating current (AC), and is widely used in scenarios such as uninterruptible power supplies, photovoltaic power generation systems, and electric vehicles. The input end of the inverter is connected to a DC power supply, and the output end can be connected to an AC load or AC grid-connected. The inverter generally includes an inverter circuit and a resonance circuit. The inverter circuit is used to convert DC power into AC power. The alternating current is converted into an alternating current output with a waveform similar to a sine curve. [0003] With the continuous development of inverter technology, the application of multi-level inverters has become increasingly widespread. Multi-level inverters can reduce the voltage drop of each power device, so devices with low withstand voltage specifications can be used to achieve high-voltage and high-power output. The increase in the number of levels means that the output voltage waveform of the inverter is improved. The distortion of the output waveform is reduced, and the function of a two-level inverter operating at a high switching frequency can be realized only by using a lower switching frequency, and the loss of power devices is also reduced, and the efficiency of the inverter is improved. [0004] Refer to FIGS. 1 and 2 together, where FIG. 1 is a schematic diagram of a three-level inverter with a T-type connection for the inverter circuit, and FIG. 2 is a schematic diagram of an I-type connection for the inverter circuit. [0005] When the three-level inverter converts the DC input into the single-phase AC output, the inverter circuit 10 of the above two topologies uses four controllable switch tubes. However, as the number of inverter levels increases, the number of controllable switch tubes used in the inverter circuit will increase accordingly. [0006] Refer to FIGS. 3 and 4 together, in which FIG. 3 is a schematic diagram of a diode clamped five-level inverter in the prior art, and FIG. 4 is a flying capacitor type five-level inverter in the prior art. Schematic diagram of the flat inverter circuit. [0007] After increasing the number of levels, the inverter circuit 10 of the above two topologies needs to use eight controllable switching tubes, which is doubled compared to the three-level inverter circuit, and so on, as the number of levels increases from three It began to increase gradually. The number of controllable switches in the inverter circuit doubled, resulting in complex drive signals and increased control difficulty. At the same time, the number of diodes (method in Figure 3) or capacitors (method in Figure 4) increased greatly. , Increasing the cost of multi-level inverters. Summary of the invention [0008] In order to solve the above technical problems, the present application provides a multi-level inverter, a control method of the multi-level inverter, and an uninterruptible power supply, which reduces the controllable switch tubes used by the multi-level inverter. The number of inverters reduces the cost of multi-level inverters. [0009] In the first aspect, the present application provides a multi-level inverter, which can be applied to a single bus system. The multi-level inverter includes a converter bridge arm, an inverter circuit, and Controller. Among them, the positive input port of the inverter circuit is connected to the positive input port of the multi-level inverter, the negative input port of the inverter circuit is connected to the negative input port of the multi-level inverter, and the output terminal of the inverter circuit is connected to the multi-level inverter. The positive output port of the inverter. The converter bridge arm includes an upper half bridge arm and a lower half bridge arm. The first end of the upper half bridge arm is connected to the positive input port of the multilevel inverter, and the second end of the upper half bridge arm is connected to the lower half bridge arm through the midpoint of the bridge arm. half The first end of the bridge arm and the second end of the lower half bridge arm are connected to the negative input port of the multilevel inverter, and the midpoint of the bridge arm is connected to the negative output port of the multilevel inverter. The controller controls the upper half of the bridge arm to be turned off and the lower half of the bridge arm in the positive output period of the inverter circuit; in the negative output period of the inverter circuit, the controller controls the upper half of the bridge arm to be turned on and the lower half of the bridge arm to be turned off. [0010] The commutation bridge arm of the multi-level inverter switches the working state during the positive and negative output cycles of the inverter circuit, thereby changing the potential reference point of the negative output terminal, specifically: when the upper half bridge of the commutation bridge arm When the arm is disconnected and the lower half of the bridge is turned on, the potential reference point of the negative output terminal of the multi-level inverter is the negative input port of the inverter circuit; when the upper half of the commutation bridge is turned on and the lower half of the bridge is turned on When the arm is disconnected, the potential reference point of the negative output terminal of the multi-level inverter is the positive input port of the inverter circuit. Furthermore, by changing the reference point of the potential, the number of levels output by the multi-level inverter is increased. For example, when the multi-level inverter needs to output five levels, the inverter circuit only needs to use a three-level topology. When the flat inverter needs to output seven levels, the inverter circuit only needs to use the five-level topology. It can be seen that the number of switching tubes required by the inverter circuit can be reduced by half by using this solution, and the multi-level inverter is reduced. The cost of the device. [0011] The switching tubes used in the inverter circuit and the commutation bridge arm of the multi-level inverter can be: insulated gate bipolar transistor Qnsulated Gate Bipolar Transistor, IGBT), metal oxide semiconductor field effect transistor (Metal Oxide One or more combinations of Semiconductor Filed Effect Transistor, MOSFET, hereinafter referred to as MOS tube), Silicon Carbide Metal Oxide Semiconductor (SiC MOSFET), etc. [0012] With reference to the first aspect, in a first possible implementation manner, the upper half of the converter bridge arm includes switching tubes M1, and the lower half of the converter bridge arm includes switchi
[EN AU2021102724A4]: A METHOD FOR MODULAR MULTILEVEL CONVERTER (INVERTER) OPEN-CIRCUIT FAULT IDENTIFICATION AND POSITIONING | [EN AU2021102724A4]: A METHOD FOR MODULAR MULTILEVEL CONVERTER (INVERTER) OPEN CIRCUIT FAULT IDENTIFICATION AND POSITIONING Aspects of the present disclosure relate to method (100) for identifying and positioning open 5 circuit faults of multilevel inverter. The Modular Multilevel Converter (MMC) is a power electronic structure used for high voltage adjustable speed drives applications as well as power transmission applications and high-voltage direct current. MMC structure presents many advantages such as modularity, the absence of a high voltage DC bus and very low switching frequency. An ESO based fault detection and location (114) method (100) is 10 proposed, which features a low computation burden and relatively quick fault detection and location (114). In this method the voltage difference (106) between the ESO and theoretical voltages is used for setting (108) plurality of sampling points against the output current. From these sampling points the information is acquired (110). The proposed fault diagnosis strategy features a low computation burden and relatively fast speed in fault detection and 15 location (114) as it uses machine learning models based on multivariate gaussian distribution. (FIG. 1 will be the reference figure) - 13 - aippiican name: rage i 01 100 acquiring theoretical full ann voltage by a 102 calculator acquiring ESO full arm voltage by an ESO 104 calculating the difference between the theoretical full am voltage and ESO full arm voltage setting plurality of sampling point 108 acquiring current sampling information 110 identifying the open-eircuit fault 112 finding the location of the open-circuit fault using f' 114 a fault detection and location (FDL) method FIG. 1 Flow diagram of method for identifying and positioning open-circuit faults of multilevel inverter. | AU2021102724A4 | 2021-07-15 | AU2021102724A | 2021-05-21 | AU2021102724A, 2021-05-21 | AU2021102724A4: 2021-07-15 | ANKAIAH BURRI MR H ANANDA M MR KUMAR MAHESH MR N LATHA MS OOMMEN SUJO MS V DIVYA B MS | OOMMEN SUJO ANKAIAH BURRI KUMAR MAHESH H ANANDA M N LATHA V DIVYA B | G01R31/27: I G01R31/28: I G01R31/317: I | G01R31/27: I G01R31/2812: I G01R31/31706: I
[ZH CN113437877A]: 一种DC-DC变换器及其控制策略 [EN CN113437877A]: A DC-DC converter and its control strategy | [ZH CN113437877A]: 一种DC‑DC变换器及其控制策略，结合MMC和ISOP‑DAB结构的优缺点，采用一种基于MMC和级联H桥的结构用于中低压直流配电网。该结构的中压侧通过MMC承受中压电平的电压，提高了设备的可靠性。低压侧通过多个级联的H桥串联在交流侧，以适应低压总线电压和更大的电流。模块化组合方案可以有效地增加功率容量，减轻功率管的应力，增强系统的冗余性；在每个模块的调制信号之间采用交错相移控制策略，减小系统电流纹波和滤波器组件的设计参数。本发明中压侧基本控制方案采用相等的CPS‑PWM控制和不相等的CPS‑PWM控制，可以有效改善直流变换器的输电特性。 [EN CN113437877A]: A DC-DC converter and its control strategy, combining the advantages and disadvantages of the MMC and ISOP-DAB structures, adopts a structure based on MMC and cascaded H-bridges for medium and low voltage DC distribution networks. The medium voltage side of the structure bears the voltage of the medium voltage level through the MMC, which improves the reliability of the equipment. The low-voltage side is connected in series with the AC side through multiple cascaded H-bridges to adapt to the low-voltage bus voltage and larger current. The modular combination scheme can effectively increase the power capacity, reduce the stress of the power tube, and enhance the redundancy of the system; the interleaved phase shift control strategy is adopted between the modulation signals of each module to reduce the system current ripple and filter components Design parameters. The basic control scheme of the medium voltage side of the present invention adopts equal CPS-PWM control and unequal CPS-PWM control, which can effectively improve the transmission characteristics of the DC converter. | CN113437877A | 2021-09-24 | CN202110731482A | 2021-06-29 | CN202110731482A, 2021-06-29 | CN113437877A: 2021-09-24 | 西安西电电力系统有限公司 西安交通大学 |  | H02M3/335: I H02M1/32: I H02M7/483: I |  |  |  | [ZH CN113437877A]: 1 .一种DC-DC变换器，其特征在于，包括m个变压器，所述变压器的中压侧与MMC连接，低 压侧与m个级联的H桥连接；所述MMC包括两个并联的臂对，每个臂对由上下两个桥臂串联而 成，每个桥臂包括n个中压侧直流变换器子模块，所述m个H桥的输入端串联，输出端并联。 2 .根据权利要求1所述的一种DC-DC变换器，其特征在于，MMC输出端口和m个变压器之 间连接有辅助电感l3。 3 .根据权利要求1所述的一种基于新型DC-DC变换器，其特征在于，所述多个中压侧直 流变换器子模块间采用交错工作方式。 4 .根据权利要求1所述的一种DC-DC变换器，其特征在于，所述子模块为半桥子模块。 5 .根据权利要求1所述的一种DC-DC变换器，其特征在于，所述桥臂中包括一个与子模 块串联的缓冲电感。 6 .根据权利要求1所述的一种DC-DC变换器，其特征在于，所述H桥的输出端并联有电 容。 7 .权利要求1所述的变换器的控制策略，其特征在于，包括以下步骤： 步骤1，根据中压侧电压等级和开关器件的耐压能力，确定MMC一个桥臂的半桥子模块 的数目N，选择中压侧半桥子模块IGBT的器件型号； 步骤2,将中压侧每一相中的上、下桥臂组成一个臂对，给中压侧两个臂对设置相位相 反的调制波，对于一个开关周期，每一个载波控制一个子模块的触发，根据一个臂对内子模 块的数目设置载波数目； 步骤3,根据中压侧交流等效电压波形谐波畸变率大小、DC-DC变换器的功率传输能力 大小、功率传输效率以及器件可以耐受的额定电压或额定电压/电流变化率的要求，确定中 压侧交流等效电压波形为等距阶梯波还是不等距阶梯波，若中压侧交流等效电压波形为等 距阶梯波，则又等距载波移相控制产生等距阶梯波;若中压侧交流等效电压波形为不等距 阶梯波，则采用不等距载波移相控制产生不等距阶梯波，确定同一臂对中子模块的投切顺 序，进而确定载波与子模块的对应关系，对于中压侧一个桥臂有N个子模块的DC-DC变换器， 中压侧交流等效输出电压的电平数是2N+1。 8 .根据权利要求7所述的控制策略，其特征在于，采样低压侧输出电压的电压值，与标 准值作差，通过PI调节器产生信号，将该信号反馈给臂对的调制波，对中压侧的开关特性进 行调制，实现负反馈作用。 [EN CN113437877A]: 1 A DC-DC converter, characterized by comprising m transformers, the medium voltage side of the transformer is connected to the MMC, and the low voltage side is connected to m cascaded H bridges; the MMC includes two parallel arms Yes, each arm pair is formed by connecting two upper and lower bridge arms in series, and each bridge arm includes n medium-voltage side DC converter sub-modules. The input ends of the m H bridges are connected in series and the output ends are connected in parallel. 2 A DC-DC converter according to claim 1, wherein an auxiliary inductor l is connected between the MMC output port and the m transformers.3。 3 The new-type DC-DC converter according to claim 1, wherein the multiple medium voltage side DC converter sub-modules adopt an interleaved working mode. 4 The DC-DC converter according to claim 1, wherein the sub-module is a half-bridge sub-module. 5 The DC-DC converter according to claim 1, wherein the bridge arm includes a snubber inductor connected in series with the sub-module. 6 The DC-DC converter according to claim 1, wherein the output terminal of the H-bridge is connected in parallel with a capacitor. 7 The control strategy of the converter according to claim 1, characterized by comprising the following steps: Step 1. Determine the number of half-bridge sub-modules of one leg of the MMC according to the voltage level of the medium voltage side and the withstand voltage capability of the switching device N, select the device model of the half-bridge sub-module IGBT on the medium voltage side; Step 2, compose the upper and lower bridge arms in each phase of the medium voltage side into an arm pair, and set the two arm pairs on the medium voltage side with opposite phase modulation For a switching cycle, each carrier controls the triggering of a sub-module, and the number of carriers is set according to the number of sub-modules in an arm pair; Step 3, according to the magnitude of the harmonic distortion rate of the AC equivalent voltage waveform on the medium voltage side, DC-DC The power transmission capacity of the converter, the power transmission efficiency and the requirements of the rated voltage or the rated voltage/current change rate that the device can withstand, determine whether the AC equivalent voltage waveform of the medium voltage side is an equidistant step wave or an unequal step wave. If the AC equivalent voltage waveform on the medium voltage side is an equidistant stepped wave, the equidistant carrier phase shift control generates an equidistant stepped wave; if the medium voltage side AC equivalent voltage waveform is an unequal distance stepped wave, use unequal distance Carrier phase shift control generates unequal-distance step waves to determine the switching sequence of the same arm to the neutron modules, and then determine the corresponding relationship between the carrier and the submodules. For a DC-DC converter with N submodules in one bridge arm on the medium voltage side , The number of levels of the AC equivalent output voltage on the medium voltage side is 2N+1. 8 The control strategy according to claim 7, characterized in that the voltage value of the output voltage of the low-voltage side is sampled, the difference is made with the standard value, a signal is generated by the PI regulator, and the signal is fed back to the modulation wave of the arm pair, and the centering The switching characteristics of the voltage side are modulated to achieve negative feedback. | [ZH CN113437877A]: 一种DC-DC变换器及其控制策略 技术领域 [0001]本发明属于低压直流配网用DC/DC变换器控制与调制领域，特别涉及一种基于模 块化多电平变换器和级联H桥的MVDC新型DC-DC变换器。 背景技术 [0002] 随着经济的发展，资源短缺问题和环境恶化的压力已经开始突出。因此，绿色和可 持续能源的大规模开发势在必行。水，风，光和地热等新的可再生能源的应用是实现环境保 护和可持续经济发展的唯一途径。对于可持续的分布式能源，直流配电系统可以更好地获 取和吸收电能。 [0003] 直流电源转换技术已成为业界研究的热点，在当前适用于高压和大功率应用的直 流变换器拓扑中，基于输入串联输出并联ISOP结构的直流变换器拓扑是研究最多，最成熟 的拓扑。整个直流变换器由独立的DC/DC变换器组成。一方面，每个变换器在输入侧串联连 接，以承受中压直流输入侧的高电平电压。另一方面，通过输出侧的并联连接，它可以在低 压侧平均分配巨大的功率和电流。DC/DC变换器最常用的拓扑是双有源桥DAB变换器，它具 有DC-DC电压转换和双向能量传输的功能。变换器的两侧通过高频变换器HFT进行电隔离。 具有这种结构的DC变换器的主要问题是，能量在总线与总线之间传输时，需具备较大功率 容量，单个变换器容量有限且存在功率开关电压应力的限制，不能满足系统功率需求。 发明内容 [0004]为了解决现有技术中存在的问题，本发明的目的是提供一种基于模块化多电平变 换器和级联H桥的MVDC新型DC-DC变换器及其控制策略，实现直流变换器结构及其控制策略 的可行性。 [0005]为了实现上述目的，本发明采用的技术方案是，一种DC-DC变换器，包括m个变压 器，所述变压器的中压侧与MMC连接，低压侧与m个级联的H桥连接；所述MMC包括两个并联的 臂对，每个臂对由上下两个桥臂串联而成，每个桥臂包括n个中压侧直流变换器子模块，所 述m个H桥的输入端串联，输出端并联。 [0006] 进一步的，MMC的输出端口和m个变压器之间连接有辅助电感。 [0007]进一步的，多个中压侧直流变换器子模块间采用交错工作方式。 [0008]进一步的，子模块为半桥子模块。 [0009]进一步的，桥臂中包括一个与子模块串联的缓冲电感。 [0010]进一步的，H桥的输出端并联有电容。 [0011]上述的变换器的控制策略，包括以下步骤： [0012]步骤1，根据中压侧电压等级和开关器件的耐压能力，确定MMC一个桥臂的半桥子 模块的数目N，选择中压侧半桥子模块IGBT的器件型号； [0013]步骤2,将中压侧每一相中的上、下桥臂组成一个臂对，给中压侧两个臂对设置相 位相反的调制波，对于一个开关周期，每一个载波控制一个子模块的触发，根据一个臂对内 子模块的数目设置载波数目； [0014]步骤3,根据中压侧交流等效电压波形谐波畸变率大小、该DC-DC变换器的功率传 输能力大小、功率传输效率以及器件可以耐受的额定电压或额定电压/电流变化率的要求， 确定中压侧交流等效电压波形为等距阶梯波还是不等距阶梯波，等距载波移相控制产生等 距阶梯波，不等距载波移相控制产生不等距阶梯波，从而确定采用等距载波移相控制还是 不等距载波移相控制，确定同一臂对中子模块的投切顺序，进而确定载波与子模块的对应 关系，对于中压侧一个桥臂有N个子模块的DC-DC变换器，中压侧交流等效输出电压的电平 数是2N+1。 [0015] 进一步的，采样低压侧输出电压的电压值，与标准值作差，通过PI调节器产生信 号，将该信号反馈给臂对的调制波，对中压侧的开关特性进行调制，实现负反馈作用。 [0016]与现有技术相比，本发明至少具有以下有益效果： [0017]当能量在不同的母线之间传输时，需要一个大的功率容量。单个变流器的容量和 功率开关的电压应力是有限的，不能满足系统的功率需求。将多个10-100kW功率等级变换 器通过模块化组合形式以输出并联OP结构实现扩容，可以有效提升功率容量，降低功率管 应力，增强系统冗余能力。若各模块调制信号间采用交错移相控制方式，还能进一步减小系 统电流纹波和滤波元件的设计参数。 [0018]对于低压侧单个直流变换器模块，运行时的功率较低，有利于高频功率开关器件 的使用，从而减小隔离变压器的体积，降低成本；而多个直流变换器模块的串、并联组合，使 得提高整个组合直流变换器的功率等级实现更为简单，有利于变换器的扩容；多个直流变 换器模块间采用交错工作方式，可以减小输出纹波，进而减小变换器中滤波器的容量、体 积，提高动态响应速度；由于所有模块同时出现故障的概率很低，故而整个直流组合变换器 系统的可靠性相对较高；同时，方便引入一定的冗余模块来进一步提高系统的可靠性。 [0019] 采用一种基于MMC和级联H桥的结构用于中低压直流配电网。该结构的中压侧通过 MMC承受中压电平的电压，提高了设备的可靠性。低压侧通过多个级联的H桥串联在交流侧， 以适应低压总线电压和更大的电流。 [0020]本发明提供的控制策略，通过使用载波移相控制，调节子模块的投切顺序以及开 关时序，从而调节中压侧交流输出等效电压，以改变传输功率的能力，提升能量传输效率， 提高控制灵活性。 附图说明 [0021] [0022] 图； [0023] [0024] [0025] [0026] [0027] 图1为本发明的基于MMC和H桥混合结构的直流变换器拓扑； 图2为中压侧采用CPS-PWM控制的基于MMC和H桥混合结构的直流变换器拓扑示意 图3为拓扑结构等效电路； 图4为单相MMC； 图5为相等的CPS-PWM控制下，SM的载波、参考波形和投切顺序的配置； 图6为不相等的CPS-PWM控制下，SM的载波、参考波形和投切顺序的配置; 图7为中压侧和低压侧的交流等效输出电压的配置。 具体实施方式 [0028]下面结合附图和具体实施方式对本发明做进一步说明。 [0029]如图1所示，基于模块化多电平变换器(MMC)和级联H桥的DC-DC变换器结构，用于 中低压直流配电网，中压侧采用MMC端口，低压侧采用级联H桥结构，中压侧由两个臂对并联 组成，每个臂对由上下两个桥臂串联而成，每个桥臂由n个半桥子模块和缓冲电感构成，中 压侧的输出端口经过辅助电感L3和m个变压器连接，变压器与低压侧H桥连接，低压侧由m个 H桥采用输入串联输出并联结构级联而成。该结构的中压侧通过MMC承受中压电平的电压， 提高了设备的可靠性。低压侧通过多个级联的H桥串联在交流侧，以适应低压总线电压和更 大的电流。该结构的中压侧通过MMC承受中压电平的电压，提高了设备的可靠性。低压侧通 过多个级联的H桥串联在交流侧，以适应低压总线电压和更大的电流。 [0030]图2为图1的特殊情况，子模块数目为4，低压侧端口数目为2。如图2所示，基于MMC 的中压侧采用载波移相脉冲宽度调制(CPS-PWM)方法产生阶梯波形进行功率传输。如果中 压侧和输出端口1之间的相位位移与中压侧和输出端口2之间的相位位移相同，则输出端口 之间不存在能量交换，中压侧无法向低压侧传输功率，在此状态下变换器无法工作，故输出 端口1与输出端口2之间需有一定的相位位移。基于MMC的输入侧和基于级联H桥的一个输出 端口组成了DC-DC变换器，MMC由两个不同的桥臂对组成，分别表示为A桥臂对和B桥臂对。每 个桥臂对包含两个不同的桥臂，一个桥臂上有4个子模块SM，直流侧分为两部分，每部分的 电压值为Vdc/2，Vdc为中压侧直流输入电压，其中直流侧的中点电位为零。 [0031]图2的拓扑结构等效电路如图3所示，通过采用CPS-PWM控制，中压侧的交流等效输 出波形为九级阶梯波，低压侧的交流等效输出波形为方波。通过调整中压侧交流电压VAB和 低压侧交流电压VCD或VEF之间的相位位移，可以控制功率传输的大小和方向，VEF为低压侧输 入交流等效电压。 [0032]忽略缓冲电感Lupper - a、缓冲电感Lupper - b、缓冲电感Llowei、Llower . b两端的电压，MMC 在中压侧的输出电压丫“主要由上臂电压Vupper和下臂电压Vlower共同决定。通过采用CPS-PWM 控制，交流输出阶梯波形的基本特性取决于子模块SM的投切顺序。 [0033] 本发明提供的控制策略，包括载波等距的CPS-PWM控制和载波不等距的CPS-PWM控 制。通过使用载波移相控制，调节子模块的投切顺序以及开关时序，从而调节中压侧交流输 出等效电压，以改变传输功率的能力，提升能量传输效率，提高控制灵活性。 [0034]图6显示了调制波，载波和子模块投切序列之间的配置，对于MMC单相，上臂和下臂 的参考波形是反相的。然而，上臂和下臂之间的相移为零。上臂和下臂之间的子模块投切顺 序也不同。 [0035]交流等效输出电压为九级阶梯波形，整个CPS-PWM控制的子模块投切从下臂开始， 投入顺序从sm5到sm8,上臂的投入从smm」sm4开始。假设所有的电容电压都很平衡，电容电 压表示为VC,那么MMC的最大输出电压和最小输出电压分别为2Vc和-2Vc,可以得出MMC在中 压侧的输出电压Vh1=VA-VB,载波之间的相移角是相等的,VA为A桥臂对参考电压，VB为B桥臂 对参考电压。 [0036]不同输出电压水平之间的时隙始终保持一致，为了减少总谐波失真(THD),应该增 加最高输出电压水平的时隙，由于子模块的投切顺序保持不变，SM8和SM1的载波之间的相移 角扩大，而其他载波之间的相移角减少并保持不变，根据该DC-DC变换器的结构特点，可以 得出关于低压侧输出电压Vh2: Vh2 = VCD+VEF。 [0037]根据中压侧交流等效电压波形谐波畸变率大小、该DC-DC变换器的功率传输能力 大小、功率传输效率以及器件可以耐受的额定电压或额定电压/电流变化率的要求，来确定 中压侧交流等效电压波形为等距阶梯波还是不等距阶梯波，从而确定采用等距载波移相控 制还是不等距载波移相控制，等距载波移相控制产生等距阶梯波，不等距载波移相控制产 生不等距阶梯波。载波等距时子模块的载波配置，参考波形和投入顺序如图5所示。图5中， VA为A桥臂对参考电压，VB为B桥臂对参考电压，采用脉冲宽度调制，三角波为载波，正弦波为 调制波，正弦波调制波与不同的三角波载波之间的相互比较会产生对应的高低电平，从而 决定半桥子模块的开通与关断，每一个载波对应一个子模块的触发。 [0038] A相子模块的插入顺序依次为：SM5-SM6-SM7-SM8-SM1-SM2-SM3-SM4 ； B相 的插入顺序依次为：SM1-SM2-SM3-SM4-SM5-SM6-SM7-SM8。 [0039]为了降低总谐波失真THD，增加最高输出电压电平的时隙，则采用载波不等距控 制，图6展示了在载波不等距的CPS-PWM控制下的具体配置以及子模块的投入顺序。调整载 波距离，正弦波调制波与不同的三角波载波之间的相互比较会产生对应的高低电平，从而 决定半桥子模块的开通与关断，每一个载波对应一个子模块的触发。 [0040] A相子模块的插入顺序依次为：SM5-SM6-SM7-SM8-SM1-SM2-SM3-SM4 ； B相 的插入顺序依次为：SM1-SM2-SM3-SM4-SM5-SM6-SM7-SM8。 [0041]同时，在图7中清楚地示出了中压侧上的交流等效输出电压Vh1和低压侧上的交流 等效输出电压Vh2的配置，中压侧上的交流等效输出电压Vh1根据图5所示的相等的CPS-PWM 的控制得到。从图7可以看出中压侧交流输出等效波形是多电平阶梯波，由中压侧高电压产 生的电压变化率显著降低。 [EN CN113437877A]: A DC-DC converter and its control strategy technical field [0001] The present invention belongs to the field of DC/DC converter control and modulation for low-voltage DC distribution networks, and particularly relates to a new MVDC DC-DC converter based on a modular multilevel converter and a cascaded H-bridge. Background technique [0002] With the development of the economy, the problem of resource shortage and the pressure of environmental degradation have begun to become prominent. Therefore, large-scale development of green and sustainable energy is imperative. The application of new renewable energy such as water, wind, light and geothermal is the only way to realize environmental protection and sustainable economic development. For sustainable distributed energy, the DC power distribution system can better obtain and absorb electrical energy. [0003] DC power conversion technology has become a hot research topic in the industry. Among the current DC converter topologies suitable for high-voltage and high-power applications, the DC converter topology based on the input series output parallel ISOP structure is the most studied and the most mature topology. . The entire DC converter is composed of an independent DC/DC converter. On the one hand, each converter is connected in series on the input side to withstand the high-level voltage on the medium voltage DC input side. On the other hand, through the parallel connection on the output side, it can evenly distribute huge power and current on the low-voltage side. The most commonly used topology of DC/DC converters is the dual active bridge DAB converter, which has the functions of DC-DC voltage conversion and bidirectional energy transmission. The two sides of the converter are electrically isolated by the high frequency converter HFT. The main problem of the DC converter with this structure is that when energy is transmitted between the bus and the bus, a large power capacity is required. The capacity of a single converter is limited and the voltage stress of the power switch is limited, which cannot meet the power demand of the system. Summary of the invention [0004] In order to solve the problems in the prior art, the purpose of the present invention is to provide a new MVDC DC-DC converter based on a modular multilevel converter and a cascaded H-bridge and its control strategy to achieve DC conversion The feasibility of the structure of the device and its control strategy. [0005] In order to achieve the above objective, the technical solution adopted by the present invention is a DC-DC converter including m transformers, the medium voltage side of the transformer is connected with the MMC, and the low voltage side is connected with m cascaded H bridges. Connection; the MMC includes two parallel arm pairs, each arm pair is formed by connecting two upper and lower bridge arms in series, each bridge arm includes n medium voltage side DC converter sub-modules, the m H bridge The input terminals are connected in series and the output terminals are connected in parallel. [0006] Further, auxiliary inductors are connected between the output port of the MMC and the m transformers. [0007] Further, a plurality of medium voltage side DC converter sub-modules adopt an interleaved working mode. [0008] Further, the sub-module is a half-bridge sub-module. [0009] Further, the bridge arm includes a snubber inductor connected in series with the sub-module. [0010] Further, the output terminal of the H-bridge is connected in parallel with a capacitor. [0011] The above-mentioned converter control strategy includes the following steps: [0012] Step 1. Determine the number N of half-bridge sub-modules of one leg of the MMC according to the voltage level of the medium-voltage side and the withstand voltage capability of the switching device, and select the device model of the half-bridge sub-module IGBT of the medium-voltage side; [0013] Step 2, the upper and lower bridge arms in each phase of the medium voltage side are formed into an arm pair, and the two arm pairs on the medium voltage side are set with opposite phase modulation waves. For one switching cycle, each carrier controls one Triggering of sub-modules, according to an arm-to-inside The number of sub-modules sets the number of carriers; [0014] Step 3, according to the magnitude of the harmonic distortion rate of the medium voltage side AC equivalent voltage waveform, the power transmission capacity of the DC-DC converter, the power transmission efficiency, and the rated voltage or rated voltage/current change that the device can withstand Rate requirements, determine whether the AC equivalent voltage waveform of the medium voltage side is equidistant step wave or unequal step wave, equidistant carrier phase shift control produces equidistant step wave, unequal distance carrier phase shift control produces unequal step wave , So as to determine whether to use equidistant carrier phase shift control or unequal distance carrier phase shift control, determine the switching sequence of the same arm to the neutron module, and then determine the correspondence between the carrier and the submodule. For a bridge arm on the medium voltage side, there is N For the DC-DC converter of each sub-module, the number of levels of the AC equivalent output voltage on the medium voltage side is 2N+1. [0015] Further, the voltage value of the output voltage of the low voltage side is sampled and the difference is made with the standard value, a signal is generated by the PI regulator, and the signal is fed back to the modulation wave of the arm pair to modulate the switching characteristics of the medium voltage side to achieve Negative feedback effect. [0016] Compared with the prior art, the present invention has at least the following beneficial effects: [0017] When energy is transferred between different buses, a large power capacity is required. The capacity of a single converter and the voltage stress of the power switch are limited and cannot meet the power requirements of the system. Multiple 10-100kW power grade converters can be expanded in the form of output parallel OP structure through modular combination, which can effectively increase power capacity, reduce power tube stress, and enhance system redundancy. If the interleaved phase-shifting control method is adopted between the modulation signals of each module, the system current ripple and the design parameters of the filter components can be further reduced. [0018] For a single DC converter module on the low-voltage side, the power during operation is lower, which is conducive to the use of high-frequency power switching devices, thereby reducing the volume of the isolation transformer and reducing the cost; and the series of multiple DC converter modules, The parallel combination makes it easier to improve the power level of the entire combined DC converter, which is conducive to the expansion of the converter; the interleaving operation mode between multiple DC converter modules can reduce the output ripple and thereby reduce the converter. The capacity and volume of the filter improve the dynamic response speed; since the probability of failure of all modules at the same time is very low, the reliability of the entire DC combined converter system is relatively high; at the same time, it is convenient to introduce certain redundant modules to further improve the system Reliability. [0019] A structure based on MMC and cascaded H bridges is used for medium and low voltage DC power distribution networks. The medium voltage side of the structure bears the voltage of the medium voltage level through the MMC, which improves the reliability of the equipment. The low-voltage side is connected in series with the AC side through multiple cascaded H-bridges to adapt to the low-voltage bus voltage and larger current. [0020] The control strategy provided by the present invention adjusts the switching sequence and switching timing of the sub-modules by using carrier phase shift control, thereby adjusting the medium voltage side AC output equivalent voltage to change the transmission power capability and improve energy transmission efficiency , Improve control flexibility. BRIEF DESCRIPTION OF THE DRAWINGS [0021] [0022] Figure; [0023] [0024] [0025] [0026] [0027] Figure 1 is the DC converter topology based on the MMC and H-bridge hybrid structure of the present invention; Figure 2 is the medium voltage The topological diagram of the DC converter based on the mixed structure of MMC and H-bridge with CPS-PWM control on the side. 3 is the equivalent circuit of the topology; Figure 4 is the single-phase MMC; Figure 5 is the carrier, SM carrier, Configuration of reference waveform and switching sequence; Figure 6 shows the configuration of SM carrier, reference waveform and switching sequence under unequal CPS-PWM control; Figure 7 shows the configuration of the AC equivalent output voltage on the medium voltage side and the low voltage side. Detailed ways [0028] The present invention will be further described below in conjunction with the drawings and specific embodiments. [0029] As shown in Figure 1, the DC-DC converter structure based on modular multilevel converters (MMC) and cascaded H-bridges is used in medium and low voltage DC distribution networks. The medium voltage side uses MMC ports, and the low voltage The side adopts a cascaded H-bridge structure. The medium voltage side is composed of two arm pairs in parallel. Each arm pair is composed of two upper and lower bridge arms in series. Each bridge arm is composed of n half-bridge sub-modules and snubber inductors. The output port on the voltage side passes through the auxiliary inductor L3It is connected with m transformers, the transformer is connected with the low-voltage side H bridge, and the low-voltage side is formed by cascading m H bridges with input series and output parallel structure. The medium voltage side of the structure bears the voltage of the medium voltage level through the MMC, which improves the reliability of the device. The low-voltage side is connected in series with the AC side through multiple cascaded H-bridges to adapt to the low-voltage bus voltage and larger current. The medium voltage side of the structure bears the voltage of the medium voltage level through the MMC, which improves the reliability of the equipment. The low-voltage side is connected in series with the AC side through multiple cascaded H-bridges to adapt to the low-voltage bus voltage and larger current. [0030] Figure 2 is a special case of Figure 1, the number of sub-modules is 4, and the number of low-voltage side ports is 2. As shown in Figure 2, the MMC-based medium voltage side adopts the carrier phase-shifted pulse width modulation (CPS-PWM) method to generate stepped waveforms for power transmission. If the phase shift between the medium voltage side and the output port 1 is the same as the phase shift between the medium voltage side and the output port 2, there is no energy exchange between the output ports, and the medium voltage side cannot transmit power to the low voltage side. The converter cannot work in the state, so a certain phase shift is required between output port 1 and output port 2. The input side based on the MMC and an output port based on the cascaded H-bridge form a DC-DC converter. The MMC is composed of two different bridge arm pairs, denoted as A bridge arm pair and B bridge arm pair, respectively. Each bridge arm pair contains two different bridge arms. There are 4 sub-modules SM on one bridge arm. The DC side is divided into two parts, and the voltage value of each part is Vdc/2, VdcIt is the DC input voltage on the medium voltage side, and the midpoint potential on the DC side is zero. [0031] The equivalent circuit of the topology structure of FIG. 2 is shown in FIG. 3. By adopting CPS-PWM control, the AC equivalent output waveform on the medium voltage side is a nine-level step wave, and the AC equivalent output waveform on the low voltage side is a square wave. . By adjusting the AC voltage V on the medium voltage sideABAnd low-voltage side AC voltage VCDOr VEFThe phase shift between the two can control the size and direction of power transmission, VEFInput AC equivalent voltage for the low-voltage side. [0032]Ignore snubber inductance Lupper-a, snubber inductance Lupper-b, snubber inductance Llowei, LlowThe voltage across er. b, the output voltage of MMC on the medium voltage side, is mainly determined by the upper arm voltage VupperAnd lower arm voltage Vlowerdecided together. By adopting CPS-PWM control, the basic characteristics of the AC output ladder waveform depends on the switching sequence of the sub-module SM. [0033] The control strategy provided by the present invention includes CPS-PWM control with equidistant carriers and CPS-PWM control with unequal carriers. By using the carrier phase shift control, the switching sequence and switching timing of the sub-modules are adjusted to adjust the equivalent AC output voltage of the medium voltage side to change the transmission power capacity, improve energy transmission efficiency, and increase control flexibility. [0034] FIG. 6 shows the configuration between the modulation wave, the carrier and the switching sequence of the sub-modules. For MMC single-phase, the reference waveforms of the upper arm and the lower arm are inverted. However, the phase shift between the upper arm and the lower arm is zero. The switching sequence of the sub-modules between the upper arm and the lower arm is also different. [0035] The AC equivalent output voltage is a nine-level stepped waveform, the switching of the entire CPS-PWM controlled sub-module starts from the lower arm, and the sequence of switching starts from sm5To sm8, The input of the upper arm is from smm"sm4Start. Assuming that all capacitor voltages are balanced, the capacitor voltage is expressed as VC, Then the maximum output voltage and minimum output voltage of MMC are 2V respectivelycAnd -2Vc, The output voltage V of MMC on the medium voltage side can be obtainedh1=VA-VB, The phase shift angle between the carriers is equal, VAIs the reference voltage of A bridge arm pair, VBIt is the reference voltage of the B bridge arm pair. [0036] The time slots between different output voltage levels are always consistent. In order to reduce the total harmonic distortion (THD), the time slot with the highest output voltage level should be increased. Since the switching sequence of the sub-modules remains unchanged, the SM8The phase shift angle between the carrier and SM1 is enlarged, while the phase shift angle between other carriers is reduced and remains unchanged. According to the structural characteristics of the DC-DC converter, it can be Get the output voltage V on the low-voltage sideh2: Vh2 = VCD+VEF。 [0037] According to the harmonic distortion rate of the AC equivalent voltage waveform of the medium voltage side, the power transmission capacity of the DC-DC converter, the power transmission efficiency, and the requirements of the rated voltage or rated voltage/current change rate that the device can withstand , To determine whether the medium voltage side AC equivalent voltage waveform is equidistant stepped wave or unequal-distance stepped wave, so as to determine whether to use equidistant carrier phase shift control or unequal distance carrier phase shift control, and equidistant carrier phase shift control produces equidistant carrier phase shift control. Step wave, unequal interval carrier phase shift control produces unequal interval step wave. When the carriers are equidistant, the carrier configuration of the sub-modules, the reference waveforms and the order of putting them on are shown in Figure 5. In Figure 5, VAIs the reference voltage of A bridge arm pair, VBFor the reference voltage of the B bridge arm, pulse width modulation is used. The triangle wave is the carrier wave, and the sine wave is the modulation wave. The comparison between the sine wave modulated wave and different triangular wave carriers will generate the corresponding high and low levels, thereby determining the half bridge. When the module is turned on and off, each carrier corresponds to the trigger of a sub-module. [0038] The order of insertion of phase A sub-modules is: SM5-SM6-SM7-SM8-SM1-SM2-SM3-SM4; the order of insertion of phase B is: SM1-SM2-SM3-SM4-SM5-SM6-SM7 -SM8. [0039] In order to reduce the total harmonic distortion THD and increase the time slot with the highest output voltage level, the carrier unequal distance control is adopted. Figure 6 shows the specific configuration and sub-modules under the CPS-PWM control with unequal carrier carriers. The order of input. Adjust the carrier distance. The comparison between the sine wave modulated wave and the different triangular wave carriers will generate the corresponding high and low levels, thereby determining the turn-on and turn-off of the half-bridge sub-module. Each carrier corresponds to the trigger of a sub-module. [0040] The order of insertion of phase A sub-modules is: SM5-SM6-SM7-SM8-SM1-SM2-SM3-SM4; the order of insertion of phase B is: SM1-SM2-SM3-SM4-SM5-SM6-SM7 -SM8. [0041] At the same time, FIG. 7 clearly shows the AC equivalent output voltage V on the medium voltage side.h1And the AC equivalent output voltage V on the low-voltage sideh2Configuration, AC equivalent output voltage V on the medium voltage sideh1Obtained according to the equivalent CPS-PWM control shown in Figure 5. It can be seen from Figure 7 that the equivalent waveform of the AC output on the medium voltage side is a multi-level stepped wave, and the voltage change rate generated by the high voltage on the medium voltage side is significantly reduced.
[EN US2021170887A1]: MODULE-BASED ENERGY SYSTEMS HAVING CONVERTER-SOURCE MODULES AND METHODS RELATED THERETO [FR WO2020205574A1]: SYSTÈMES D'ÉNERGIE FAISANT APPEL À DES MODULES APTES À DES CONFIGURATIONS EN CASCADE ET INTERCONNECTÉES, ET PROCÉDÉS ASSOCIÉS | [EN US2021170887A1]: Module-based energy systems are provided having multiple converter-source modules. The converter-source modules can each include an energy source and a converter. The systems can further include control circuitry for the modules. The modules can be arranged in various ways to provide single phase AC, multi-phase AC, and/or DC outputs. Each module can be independently monitored and controlled. [FR WO2020205574A1]: L'invention concerne des systèmes d'énergie faisant appel à des modules ayant de multiples modules de source-convertisseur. Les modules de source de convertisseur peuvent chacun comprendre une source d'énergie et un convertisseur. Les systèmes peuvent en outre comprendre des circuits de commande pour les modules. Les modules peuvent être agencés de diverses manières pour fournir des sorties c.a. à phase unique, c.a. multi-phase et/ou c.c. Chaque module peut être surveillé et commandé indépendamment. | US2020307395A1 | 2020-10-20 2020-10-01 | US202016832529A | 2020-03-27 2020-03-27 | US202016832529A, 2020-03-27 US201962906007P, 2019-09-25 US201962826238P, 2019-03-29 US201962826158P, 2019-03-29 US202016832529A, 2020-03-27 US201962906007P, 2019-09-25 US201962826238P, 2019-03-29 US201962826158P, 2019-03-29 | US10807481B1: 2020-10-20 US10807482B1: 2020-10-20 US2020313445A1: 2020-10-01 WO2020205511A1: 2020-10-08 WO2020205574A1: 2020-10-08 US2021170886A1: 2021-06-10 US2021170887A1: 2021-06-10 | TAE TECH INC | SLEPCHENKOV MIKHAIL NADERI ROOZBEH | B60L50/60: I B60L1/00: I B60L50/51: I H02J7/00: I H02J7/14: I H02J1/10: I H02J1/00: I H02J3/00: I H02J3/38: I H02J3/28: I H02J3/34: I H02M7/49: I | B60L3/003: I B60L3/12: I B60L15/007: I H02J7/0013: I H02J7/0014: I H02M1/32: I H02M7/53871: I H02J2207/20: A H02J2310/48: A Y02T10/64: A Y02T10/70: A Y02T10/92: A B60L1/00: I B60L2210/40: A B60L50/51: I B60L50/66: I B60L58/18: I H02J7/1423: I H02J7/1492: I H02J7/00712: I | US2010121511A1 US2011187184A1 US2011198936A1 US2003231518A1 US9621073B1 US2010001587A1 US2011005580A1 US2011083733A1 US2015002099A1 US2004027104A1 CA2762473A1 US2013057198A1 US2017288407A1 US2018043789A1 US2013155736A1 US2016272134A1 US2005045392A1 US2019109891A1 WO2019183553A1 | DE102020100600A1 DE102020100600 102020100600 | [EN US2021170887A1]: 1-20. (canceled) 21. A module-based energy system, comprising: an array of N converter-source modules, wherein N is 2 or greater,wherein each of the N converter-source modules is connected in series,wherein each of the N converter-source modules comprises: a first energy source; an energy buffer coupled with the first energy source; and a converter coupled with the first energy source and the energy buffer, wherein the converter comprises a plurality of switches configured to select an output voltage of the module, andwherein the array includes a first output terminal of a first converter-source module and a second output terminal of an Nth converter-source module. 22. The system of claim 21, further comprising a plurality of local control devices, each of the plurality of local control devices communicatively coupled with one or more of the N converter-source modules, wherein the local control device is configured to generate a plurality of switching signals for the plurality of switches. 23. The system of claim 22, further comprising a master control device communicatively coupled with the plurality of local control devices 24. The system of claim 21, further comprising a load connected between the first and second output terminals. 25. The system of claim 24, wherein the load is one of a DC load or a single-phase AC load. 26. A module-based energy system, comprising: M arrays of converter-source modules, wherein M is 2 or greater,wherein each of the M arrays comprises N converter-source modules, wherein N is 2 or greater,wherein each of the N converter-source modules is connected in series in each of the M arrays,wherein each of the N converter-source modules comprises: a first energy source; an energy buffer coupled with the first energy source; and a converter coupled with the first energy source and the energy buffer, wherein the converter comprises a plurality of switches configured to select an output voltage of the module,wherein each of the M arrays includes an individual output terminal of a first converter-source module, andwherein an Nth converter-source module of each of the M arrays is connected to a common output terminal. 27. The system of claim 26, further comprising a plurality of local control devices, each of the plurality of local control devices communicatively coupled with one or more of the N converter-source modules of each of the M arrays, wherein the local control device is configured to generate a plurality of switching signals for the plurality of switches. 28. The system of claim 27, further comprising a master control device communicatively coupled with the plurality of local control devices 29. The system of claim 26, wherein the M arrays includes first and second arrays. 30. The system of claim 29, further comprising a load connected between the individual output terminals of the first and second arrays. 31. The system of claim 30, wherein the common output terminal is coupled to a neutral of the load. 32. The system of claim 29 further comprising a load connected between the common output terminal and a joint coupling of the individual output terminals of the first and second arrays. 33. The system of claim 30, wherein the load is one of a DC load or a single-phase AC load. 34. The system of claim 36, wherein the M arrays includes first, second and third arrays. 35. The system of claim 34, further comprising a three-phase load connected between the individual output terminals of the first, second and third arrays. 36. The system of claim 35, wherein the common output terminal is coupled to a neutral of the load. 37. The system of claim 34, further comprising a DC or single phase AC load connected between the common output terminal and a joint coupling of the individual output terminals of the first, second and third arrays. | [EN US2021170887A1]: CROSS-REFERENCE TO RELATED APPLICATIONS This application is a continuation of U.S. patent application Ser. No. 16/832,529, filed Mar. 27, 2020, which claims the benefit of and priority to U.S. Provisional Application Serial No. 62/826,158, filed Mar. 29, 2019, U.S. Provisional Application Ser. No. 62/826,238, filed Mar. 29, 2019, and U.S. Provisional Application Ser. No. 62/906,007, filed Sep. 25, 2019, all of which are incorporated by reference herein for all purposes. FIELD The subject matter described herein relates generally to module-based energy systems and modules for use therein, and systems, devices, and methods that facilitate the interconnection and control of modules in module-based energy systems. BACKGROUND Energy systems having multiple energy sources or sinks are commonplace in many industries. One example is the automobile industry. Today's automotive technology, as evolved over the past century, is characterized, amongst many things, by an interplay of motors, mechanical elements, and electronics. These are the key components that impact vehicle performance and driver experience. Motors are of the combustion or electric type and one usually finds one motor per car, exceptions being cars with hybrid drivetrains, featuring a combination of a combustion engine with one or two electric motors, or performance oriented electric vehicles that are outfitted with two motors. In almost all cases the rotational energy from the motor(s) is delivered via a set of highly sophisticated mechanical elements, such as clutches, transmissions, differentials, drive shafts, torque tubes, couplers, etc. These parts control to a large degree torque conversion and power distribution to the wheels and are key elements to define the performance of the car. They also impact road handling. Over the years individual car manufacturers have highly optimized these mechanical parts to provide better performance, higher fuel efficiency and ultimately differentiation in the market place. On the control side, apart from driver comforts such as entertainment, navigation and human machine interface elements, there are typically only a few clusters of specialty electronics hardware and embedded software that control/optimize motors, clutch/transmission operation and road holding/handling. An EV comprises various electrical systems that are related to the drivetrain including, among others, the battery, the charger and motor control. A short inventory of the present capabilities and shortcomings of these electrical systems are described below. Conventional Battery Design High voltage battery packs are typically organized in a serial chain of lower voltage battery modules. Each such module is further comprised of a serially connected set of individual cells and a simple embedded battery management system to regulate basic cell related characteristics, such as state of charge and voltage. Electronics with more sophisticated capabilities or some form of smart interconnectedness are absent. As a consequence, any monitoring or control function is handled by a separate system, which, if at all present elsewhere in the car, lacks the ability to monitor individual cell health, state of charge, temperature and other performance impacting metrics. There is also no ability to adjust power draw per individual cell in any form. Some of the major consequences are: (1) the weakest cell constrains the overall performance of the entire battery pack, (2) failure of any cell or module leads to a need for replacement of the entire pack, (3) battery reliability and safety are considerably reduced, (4) battery life is limited, (5) thermal management is difficult, (6) battery packs always operate below maximum capabilities, (7) sudden inrush into the battery packs of regenerative braking derived electric power cannot be readily stored in the batteries and will require dissipation via a dump resistor. Conventional Charger Design Charging circuits are typically realized in separate on-board systems. They stage power coming from outside the EV in the form of an AC signal or a DC signal, convert it to DC and feed it to the battery pack(s). Charging systems monitor voltage and current and typically supply a steady constant feed. Given the design of the battery packs and typical charging circuits, there is little ability to tailor charging flows to individual battery modules based on cell health, performance characteristics, temperature, etc. Charging cycles are also typically long as the charging systems and battery packs lack the circuitry to allow for pulsed charging or other techniques that would optimize the charge transfer or total charge achievable. Conventional Motor Control Design Conventional controls contain DC to DC conversion stages to adjust battery pack voltage levels to the bus voltage of the EV's electrical system. Motors, in turn, are then driven by simple two-level multiphase converters that provide the required AC signal(s) to the electric motor. Each motor is traditionally controlled by a separate controller, which drives the motor in a 3-phase design. Dual motor EVs would require two controllers, while EVs using four in-wheel motors would require 4 individual controllers. The conventional controller design also lacks the ability to drive next generation motors, such as switch reluctance motors (SRM), characterized by higher numbers of pole pieces. Adaptation would require higher phase designs, making the systems more complex and ultimately fail to address electric noise and driving performance, such as high torque ripple and acoustical noise. Many of these deficiencies apply not only to automobiles but other motor driven vehicles, and also to stationary applications to a certain extent. For these and other reasons, needs exist for improved systems, devices, and methods for energy systems for the vehicular industry and elsewhere. SUMMARY Example embodiments of systems, devices, and methods are provided herein for module-based energy systems widely relevant to many applications. In many of these embodiments, a module-based energy system includes multiple modules, where each module includes at least an energy source and a converter. More complex configurations of each module are also disclosed. The modules of the system can be connected together in different arrangements of varying complexities to perform functions specific to the particular technological application to which the system is applied. The system can be configured to monitor status information, at least one operating characteristic, or other parameter of each module repeatedly during use of the system, assess the state of each module based on that monitored status information, operating characteristic, or other parameter, and control each module independently in an effort to achieve and/or maintain one or more desired targets, such as electrical performance, thermal performance, lifespan, and others. This control can occur to facilitate energy provision from the system (e.g., discharging) and/or energy consumption (e.g., charging). Numerous example applications of these systems, devices, and methods are described. In many example embodiments, the at least one energy source of the module can include a capacitor (such as an ultra-capacitor or super-capacitor), a battery, and a fuel-cell. In many example embodiments, the system can include at least two converter-source modules connected in a one-dimensional array or in a multi-dimensional array. At least two one-dimensional arrays can be connected together, for example, at different rows and columns directly or by one or more additional converter-source modules. In such configurations, an output voltage of any shape and frequency can be generated at the outputs of the module-based energy system as a superposition of output voltages of individual converter-source modules. The various interconnected architectures of the example embodiments enable inter-phase power management within a single module-based energy system (e.g., a battery pack) and inter-system power management between multiple module-based energy systems (e.g., battery packs), as well as connection of auxiliary loads to the system(s), and maintenance of uniform distribution of energy provided to those loads from all converter-source modules of such systems. The various interconnected architectures of the example embodiments also enable the control of power sharing among converter-source modules. Such control enables, for example, regulation of parameters like State of Charge of the energy sources of the converter-source modules to be balanced, in real time and continually during cycling, as well as at rest, which fosters utilization of the full capacity of each energy source regardless of possible differences in their capacities. In addition, such control can be used to balance the temperature of the energy sources of the converter-source modules. Temperature balancing, for example, can increase the power capability of the system (e.g., a battery pack) and provide more uniform aging of the energy sources regardless of their physical location within the system and differences in their thermal resistivity. Other systems, devices, methods, features and advantages of the subject matter described herein will be or will become apparent to one with skill in the art upon examination of the following figures and detailed description. It is intended that all such additional systems, methods, features and advantages be included within this description, be within the scope of the subject matter described herein, and be protected by the accompanying claims. In no way should the features of the example embodiments be construed as limiting the appended claims, absent express recitation of those features in the claims. BRIEF DESCRIPTION OF FIGURES The details of the subject matter set forth herein, both as to its structure and operation, may be apparent by study of the accompanying figures, in which like reference numerals refer to like parts. The components in the figures are not necessarily to scale, emphasis instead being placed upon illustrating the principles of the subject matter. Moreover, all illustrations are intended to convey concepts, where relative sizes, shapes and other detailed attributes may be illustrated schematically rather than literally or precisely. FIGS. 1A, 1B and 1C are block diagrams depicting example embodiments of a module-based energy system. FIG. 2 is a block diagram depicting an example embodiment of a converter-source module (ConSource V1) with a local control device (LCD) interconnected to a master control device (MCD), according to embodiments of the present disclosure. FIG. 3 is a block diagram depicting another example embodiment of a converter-source module (ConSource V2) with an LCD interconnected to an MCD, according to embodiments of the present disclosure. FIG. 4 is a block diagram depicting another example embodiment of a converter-source module (ConSource V3) with an LCD interconnected to an MCD and optional auxiliary loads, according to embodiments of the present disclosure. FIG. 5A is a schematic depicting an example embodiment of a converter (Converter V1) shown in FIG. 2, according to embodiments of the present disclosure. FIG. 5B is a schematic depicting an example embodiment of a converter (Converter V2) shown in FIGS. 2 and 3, according to embodiments of the present disclosure. FIGS. 6A, 6B and 6C are diagrams depicting example embodiments of energy storage elements for use as an energy source shown in FIGS. 1, 2 and 3, according to embodiments of the present disclosure. FIGS. 7A, 7B and 7C are schematics depicting of example embodiments for use as the energy buffer shown in FIGS. 1, 2 and 3, according to embodiments of the present disclosure. FIGS. 8A, 8B, 8C, 8D, 8E, and 8F are diagrams depicting example embodiments for use as energy source 2 shown in FIG. 3, according to embodiments of the present disclosure. FIG. 9 is a graph depicting the output voltage from an example converter according to embodiments of the present disclosure. FIG. 10 is a graph depicting the output voltage from an example module-based energy storage system having six example converter-source modules, according to embodiments of the present disclosure. FIG. 11 is a block diagram depicting an example embodiment of power flow management for the example converter-source module (ConSource V2) shown in FIG. 3, according to embodiments of the present disclosure. FIGS. 12A and 12B are graphs depicting example waveforms of a converter-source (ConSource V2) module shown in FIG. 3, in which the converter V2 provides a secondary function of reduction of a second order current harmonic. FIG. 13 is a block diagram depicting an example embodiment of power flow management for the converter-source (ConSource V3) module shown in FIG. 4, according to embodiments of the present disclosure. FIGS. 14A, 14B, 14C, and 14D are graphs depicting an example embodiment of pulse width modulation applicable to example embodiments of module-based energy systems. FIG. 15 is a schematic depicting an example one-dimensional array of connected example converter-source modules, according to example embodiments of the present disclosure. FIG. 16 is a schematic depicting an example two-dimensional array of connected example converter-source modules, according to example embodiments of the present disclosure. FIG. 17 is a schematic depicting another example two-dimensional array of connected example converter-source modules, according to example embodiments of the present disclosure. FIG. 18 is a schematic depicting an example system having multiple example converter-source modules connected in a three-dimensional array, according to example embodiments of the present disclosure. FIG. 19 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, according to example embodiments of the present disclosure. FIG. 20 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, according to example embodiments of the present disclosure. FIG. 21 is a schematic depicting an example system having multiple example converter-source modules connected in a multi-dimensional array, according to example embodiments of the present disclosure. FIG. 22 is a schematic depicting an example system having multiple example converter-source modules connected in a three-dimensional array, and connected to an electrical motor, according to example embodiments of the present disclosure. FIG. 23 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to an electrical motor, according to example embodiments of the present disclosure. FIG. 24 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to an electrical motor and auxiliary loads, according to example embodiments of the present disclosure. FIG. 25 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to an electrical motor and auxiliary loads, according to example embodiments of the present disclosure. FIG. 26 is a schematic depicting another example system having multiple example converter-source modules connected in a six-dimensional array, and connected to a six-phase electrical motor and auxiliary loads, according to example embodiments of the present disclosure. FIG. 27 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to two three-phase electrical motors and auxiliary loads, according to example embodiments of the present disclosure. FIG. 28 is a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to a three-phase open-winding electrical motor and auxiliary loads, according to example embodiments of the present disclosure. FIG. 29 illustrates a schematic depicting another example system having multiple example converter-source modules connected in a three-dimensional array, and connected to two three-phase open-winding electrical motor and auxiliary loads, according to example embodiments of the present disclosure. FIG. 30 is a schematic depicting an example embodiment of a single-phase balancing controller, for use with example embodiments of the present disclosure. FIG. 31 depicts a phasor diagram of voltage sharing control for an example single-phase system, for use with example embodiments of the present disclosure. FIG. 32 depicts a schematic depicting an example embodiment of a single-phase balancing controller, for use with example embodiments of the present disclosure. FIGS. 33A and 33B depict phasor diagrams of voltage sharing control for a three-phase structure for (A) intra-phase balancing only and (B) intra-phase and inter-phase balancing. FIGS. 34A and 34B depict phasor diagrams of voltage sharing control for a three-phase structure with common modules with intra-phase and inter-phase balancing through (A) common modules and (B) common modules and neutral point shift. FIGS. 35A and 35B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for four-phase systems with (A) neutral point shift and (B) common modules and neutral point shift. FIGS. 36A and 36B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for five-phase systems with (A) neutral point shift and (B) common modules and neutral point shift. FIGS. 37A and 37B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for six-phase systems with (A) neutral point shift and (B) common modules and neutral point shift. FIGS. 38A and 38B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for an example system shown in FIG. 27 through (A) common modules and (B) common modules and neutral point shift. FIGS. 39A and 39B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for systems shown in FIG. 28 through (A) common modules and (B) common modules and neutral point shift. FIGS. 40A and 40B depict phasor diagrams of voltage sharing control with intra-phase and inter-phase balancing for systems shown in FIG. 29 through (A) common modules and (B) common modules and neutral point shift. FIGS. 41 and 42 are block diagrams depicting example embodiments of a converter-source module. FIGS. 43A and 43B are schematic diagrams depicting example embodiments of a components of a converter-source module mounted on one or more substrates. DETAILED DESCRIPTION Before the present subject matter is described in detail, it is to be understood that this disclosure is not limited to the particular embodiments described, as such may, of course, vary. It is also to be understood that the terminology used herein is for the purpose of describing particular embodiments only, and is not intended to be limiting, since the scope of the present disclosure will be limited only by the appended claims. Example embodiments of module-based energy systems are described herein, as are: example embodiments of devices, circuitry, software, and components within such systems; example embodiments of methods of operating and using such systems; and example embodiments of applications (e.g., apparatuses, machines, grids, locales, structures, environments, etc.) in which such systems can be implemented or incorporated or with which such systems can be utilized. In many cases, these applications can be classified as a mobile application or a stationary application. Examples of Applications Mobile applications are generally ones where a module-based energy system is located on or within an entity, and stores and provides electrical energy for conversion into motive force by a motor to move or assist in moving that entity. Examples of mobile entities with which the embodiments disclosed herein can be used include, but are not limited to, electric and/or hybrid entities that move over or under land, over or under sea, above and out of contact with land or sea (e.g., flying or hovering in the air), or through outer space. Examples of mobile entities with which the embodiments disclosed herein can be used include, but are not limited to, vehicles, trains, ships, vessels, aircraft, and spacecraft. Examples of mobile vehicles with which the embodiments disclosed herein can be used include, but are not limited to, those having only one wheel or track, those having only two-wheels or tracks, those having only three wheels or tracks, those having only four wheels or tracks, and those having five or more wheels or tracks. Examples of mobile entities with which the embodiments disclosed herein can be used include, but are not limited to, a car, a bus, a truck, a motorcycle, a scooter, an industrial vehicle, a mining vehicle, a flying vehicle (e.g., a plane, a helicopter, a drone, etc.), a maritime vessel (e.g., commercial shipping vessels, ships, yachts, boats or other watercraft), a submarine, a locomotive or rail-based vehicle (e.g., a train, etc.), a military vehicle, a spacecraft, and a satellite. Stationary applications are generally applications other than mobile applications. Generally, in stationary applications the module-based energy system resides in a static location while providing electrical energy for consumption by one or more other entities. Examples of stationary applications in or with which the embodiments disclosed herein can be used include, but are not limited to: energy systems for use by or within one or more residential structures or locales, energy systems for use by or within one or more industrial structures or locales, energy systems for use by or within one or more commercial structures or locales, energy systems for use by or within one or more governmental structures or locales (including both military and non-military uses), and systems that convert solar power, wind, geothermal energy, fossil fuels, or nuclear reactions into electricity for storage. Examples of stationary applications in or with which the embodiments disclosed herein can be used include, but are not limited to: energy systems for charging the mobile applications described above (e.g., a charging station). Other examples of stationary applications in or with which the embodiments disclosed herein can be used include, but are not limited to: a data center storage system, a power grid, or a micro-grid. A stationary energy system can be used in either a storage or non-storage role. In describing embodiments herein, reference may be made to a particular mobile application (e.g., an electric vehicle (EV)) or stationary application (e.g., grid). Such references are made for ease of explanation and do not mean that a particular embodiment is limited for use to only that particular mobile or stationary application. Embodiments of systems providing power to a motor can be used in both mobile and stationary applications. While certain configurations may be more suitable to some applications over others, all example embodiments disclosed herein are capable of use in both mobile and stationary applications unless otherwise noted. Example Embodiments of Module-Based Energy Systems FIG. 1A depicts an example embodiment of a module-based energy system 100. Here, system 100 includes control circuitry 102 communicatively coupled with N converter-source modules 108-1 through 108-N, over communication paths or links 106-1 through 106-N, respectively. In these embodiments, any number of two or more converter-source modules can be used (e.g., N is greater than or equal to two). The converter-source modules 108, referred to herein as “ConSource” modules, can be connected to each other in a variety of manners as will be described in more detail with respect to FIGS. 15-29. For ease of illustration, in FIGS. 1A-1C, the ConSource modules are shown connected in series, or as a one dimensional array, where the Nth ConSource module is coupled to a load 101. Load 101 is the electrical load to which system 100 outputs power when used to provide power. Load 101 can be any type of load including, but not limited to, a motor or a grid. For charging, the ConSource modules can be coupled with a charging source (not shown) either in addition to, or instead of, load 101. As will be described in greater detail herein, system 100 can be configured to supply multiple loads 101, including both primary and auxiliary loads. In the embodiment of FIG. 1A, control circuitry 102 is configured to control one or more ConSource modules 108 based on status information received from the same or different one or more of the ConSource modules. Control can also be based on one or more other factors, such as requirements of load 101. In many embodiments, the aspect that is controlled is the output power of each ConSource module over time; however other aspects can be controlled as an alternative to or in addition to output power. In many embodiments, status information of every ConSource module in system 100 will be communicated to control circuitry 102, from which control circuitry 102 will independently control every ConSource module 108-1 . . . 108-N. Other variations are possible. For example, control of a particular ConSource module (or subset of ConSource modules) can be based on status information of that particular ConSource module (or subset of ConSource modules), based on status information of a different ConSource module that is not the particular ConSource module (or subset of ConSource modules), based on status information of all ConSource modules other than the particular ConSource module (or subset of ConSource modules), based on status information of that particular ConSource module (or subset of ConSource modules) and status information of at least one other ConSource module that is not that particular ConSource module (or subset of ConSource modules), or based on status information of all ConSource modules in system 100. As will be described herein, the status information can be information about one or more aspects of each ConSource module. The status information can be an operating characteristic or other parameter. Types of status information include, but are not limited to, the following aspects of a ConSource module or components thereof: State of Charge (SOC) (e.g., the level of charge of an energy source relative to its capacity, such as a fraction or percent), State of Health (SOH) (e.g., a figure of merit of the condition of an energy source compared to its ideal conditions), capacity, temperature, voltage, current, or the presence of absence of a fault. Each ConSource module 108-1 . . . 108-N includes one or more sensors or other measuring elements for collecting sensed or measured signals or data that constitute status information, or can be converted into status information. A separate sensor is not needed to collect each type of status information, as more than one type of status information can be sensed or measured with a single sensor, or otherwise algorithmically determined without the need for additional sensors. FIG. 1B depicts another example embodiment of system 100. Here, control circuitry 102 is implemented as a master control device 112 communicatively coupled with N different local control devices 114-1 through 114-N over communication paths or links 115-1 through 115-N, respectively. Each local control device 114-1 through 114-N is communicatively coupled with one converter-source module 108-1 through 108-N over communication paths or links 116-1 through 116-N, respectively, such that there is a 1:1 relationship between local control devices 114 and converter-source modules 108. FIG. 1C depicts another example embodiment of system 100. Here, master control device 112 is communicatively coupled with M different local control devices 114-1 through 114-M over communication paths or links 115-1 through 115-M, respectively. Local control devices 114 can be coupled with and control two or more converter-source modules 108. In the example shown here, each local control device 114 is communicatively coupled with two converter-source modules 108, such that M local control devices 114-1 through 114-M are coupled with 2M converter-source modules 108-1 through 108-2M over communication paths or links 116-1 through 116-2M, respectively. Communication paths or links 106, 115, and 116 can each be wired or wireless communication paths or links that communicate data or information bidirectionally, in parallel or series fashion. Data can be communicated in a standard or custom format. In automotive applications, communication paths or links 115 can be configured to communicate data according to FlexRay or CAN protocols. In the embodiments described with respect to FIGS. 1B and 1C, the local control devices 114 receive the status information from each ConSource module, or determine the status information from sensed or measured signals or data received from each ConSource module, and communicate that information to master control device 112. In some embodiments local control devices 114 communicate the measured or sensed data to master control device 112, which then algorithmically determines the status information on the basis of that raw data. Master control device 112 can then use the status information of the ConSource modules 108 to make control determinations accordingly. The control determinations may take the form of instructions, commands, or other information (such as a modulation index described below) that can be interpreted or utilized by local control devices 114 to either maintain or adjust the operation or contribution of the ConSource modules. For example, master control device 112 may receive status information indicating one or more of the following conditions that a particular ConSource module (or component thereof) is operating in with respect to one or more other ConSource modules in system 100: with a relatively lower SOC, with a relatively lower SOH, with a relatively lower capacity, with a relatively lower voltage, with a relatively lower current, with a relatively higher temperature, or with a fault. In such an example, master control device 112 can output control information that causes the power output of that particular ConSource module to be reduced (or in some cases, raised depending on the condition). In this manner, the power output of a ConSource module that is operating with, e.g., a higher temperature, can be reduced so as to cause the temperature of that ConSource module to converge towards the temperature of one or more other ConSource modules. In other embodiments, the determination of whether to adjust the operation of a particular ConSource module can be made by comparison of the status information to predetermined thresholds, limits, or conditions, and not necessarily by comparison to statuses of other ConSource modules. The predetermined thresholds, limits, or conditions can be static thresholds, limits, or conditions, such as those set by the manufacturer that do not change during use. The predetermined thresholds, limits, or conditions can be dynamic thresholds, limits, or conditions, that are permitted to change, or that do change, during use. For example, master control device 112 can adjust the operation of a ConSource module if the status information for t
[ZH CN113285620A]: 一种多交流端口模块化多电平换流器及其控制方法 [EN CN113285620A]: Modularized multi-level converter with multiple AC ports and control method thereof | [ZH CN113285620A]: 本发明公开了一种多交流端口模块化多电平换流器及其控制方法，包括：模块化多电平换流器；以及与所述模块化多电平换流器串联的多端口柔性互联模块。本发明可实现多交流线路和直流电网在同一个换流站的站内互联以及对于交流线路潮流的主动控制；本发明和现有常用的交直流换流站组网结构相比，采用无变压器式结构，采用多条交流线路同时馈入的方式以及交直流电网互联的方式，在功率密度、换流站体积、建设成本、供电可靠性、供电系统运行效率等方面具备巨大优势；本发明中的利用多端柔性互联模块实现多交流线路的柔性互联，具备模块化的特点，通过增加互联模块中第一单相换流器的数量，可经济、高效、方便的实现交流线路的端口拓展。 [EN CN113285620A]: The invention discloses a modular multilevel converter with multiple AC ports and a control method thereof, including: a modular multilevel converter; and a multiport flexible converter connected in series with the modular multilevel converter Interconnect module. The invention can realize the interconnection of multiple AC lines and DC power grids in the same converter station and the active control of the power flow of the AC lines; compared with the existing common AC and DC converter station network structure, the invention adopts a transformerless type The structure adopts the simultaneous feeding of multiple AC lines and the interconnection of AC and DC power grids, and has huge advantages in terms of power density, converter station volume, construction cost, power supply reliability, and power supply system operating efficiency; The use of multi-terminal flexible interconnection modules to realize the flexible interconnection of multiple AC lines has the characteristics of modularity. By increasing the number of the first single-phase converters in the interconnection modules, the port expansion of the AC lines can be realized economically, efficiently and conveniently. | CN113285620A | 2021-08-20 | CN202110714164A | 2021-06-25 | CN202110714164A, 2021-06-25 | CN113285620A: 2021-08-20 | 上海交通大学 |  | H02M7/483: I H02J3/02: I H02J3/06: I H02J3/36: I H02J3/38: I |  |  |  | [ZH CN113285620A]: 1 .一种多交流端口模块化多电平换流器，其特性在于，包括： 模块化多电平换流器；以及， 与所述模块化多电平换流器串联的多端口柔性互联模块。 2 .如权利要求1所述的多交流端口模块化多电平换流器，其特征在于:所述模块化多电 平换流器包括中高压级电压源型换流器。 3 .如权利要求1所述的多交流端口模块化多电平换流器，其特征在于:所述多端口柔性 互联模块包括多个并联在公共连接母线上的第一单相换流器，每个单相换流器的交流输出 端口均与相应的交流线路相连。 4 .如权利要求1或2所述的多交流端口模块化多电平换流器，其特征在于：所述模块化 多电平换流器子模块拓扑包括半桥型子模块拓扑、全桥型子模块拓扑、箝位型双子模块拓 扑，或者多种结构混联的拓扑。 5 .如权利要求3所述的多交流端口模块化多电平换流器，其特征在于:所述公共连接母 线包括中低压直流母线，与所述中低压直流母线相连的公共连接电容为其提供电压。 6 .如权利要求1、3、5任一所述的多交流端口模块化多电平换流器，其特征在于:所述多 端口柔性互联模块根据是否包含第二单相换流器以及包含的第二单相换流器与所述模块 化多电平换流器上、下桥臂的接线方式的不同，分为三种方案，包括， 方案1:所述多端口柔性互联模块不包含所述第二单相换流器，模块化多电平换流器的 上、下桥臂的交流输出端口分别与所述多端口柔性互联模块的公共直流母线的正、负极相 连； 方案2：所述多端口柔性互联模块中包含一个与所述第一单相换流器同样并联在公共 直流母线两端的所述第二单相换流器，模块化多电平换流器的交流端口与所述第二单相换 流器的交流输出端口相连； 方案3：所述多端口柔性互联模块包含与交流线路数量匹配的第一单相换流器以及两 个第二单相换流器，所述第一单相换流器以及两个第二单相换流器并联在公共直流母线两 端，所述的两个第二单相换流器的交流输出端口分别与所述模块化多电平换流器的上、下 桥臂的交流输出端口相连。 7 .如权利要求6所述的多交流端口模块化多电平换流器，其特征在于:所述第一单相变 流器和第二单相变流器包括电压源型单相变流器。 8 .如权利要求7所述的多交流端口模块化多电平换流器，其特征在于:所述多端口柔性 互联模块中的第一单相变流器或者第二单相变流器的拓扑包括两电平半桥型变流器、三电 平半桥型变流器或者是能进行功率双向流动单相桥型变流器。 9 .如权利要求8所述的多交流端口模块化多电平换流器，其特征在于:所述多端柔性互 联模块中的单相换流器端口输出电压中包括相同大小的直流成分和根据需求控制得到的 不同的交流成分； 所述单相换流器输出端口电压的直流成分为所述公共连接母线电压值的一半。 10 .一种应用于如权利要求1所述的多交流端口模块化多电平换流器的控制方法，其特 征在于：包括，交流线路潮流控制、模块化多电平换流器控制和公共直流母线电压平衡控 制。 11 .如权利要求10所述的多交流端口模块化多电平换流器的控制方法，其特征在于:还 包括， 所述多端柔性互联模块和所述模块化多电平换流器通过协同控制，将多条交流线路与 直流电网柔性进行互联，并调节多条线路上的潮流分布； 当所述多段柔性互联模块互联了 η条交流线路时，对各条交流线路上的潮流Ρ】〜P。和Q] 〜Qn以及直流侧负载功率Pl进行控制，其中一条交流线路的有功功率将通过系统的能量平 衡自动调节，仅对所述线路上的无功功率进行控制,将所述交流线路定义为交流线路1; 在所述控制中，锁相环锁定的三相交流分量为所述定无功功率控制的所述交流线路1 的三相节点电压，通过实时输出的电网电压的相位，将三相交流a-b-c坐标系下的电压电流 通过Park变换转换至d-q坐标系中进行有功无功分量的解耦控制。 12 .如权利要求10或11所述的多交流端口模块化多电平换流器的控制方法，其特征在 于:所述交流线路潮流控制包括， 以交流线路1为基准，列写线路1节点电压V]j到线路k的节点电压Vkj的动态方程并将其 转换至d-q坐标系下得到如下方程： Lk —7~ + = -匕d + % + ①£*&amp; + Λ -γ- + /iMl -①卬 at '或 di. dLfi Lk 房 + /3&amp; = AU,㈣-匕g + 〃一叫q +Lt-^ + IiqR}+ 叫几 其中，“、％山21^、1Μ、工、（1、几分别为线路1与线路卜节点电压电流的＜1”轴分量， 小人、1^^分别为线路1与线路卜上的电感与等效电阻，3表示电网角频率，八”11^、八以^ 为等效电压八412=4111102的（17轴分量,11皿.为与交流线路1相连的第一单相变流器输出 电压中的交流成分,u°kj为与交流线路k相连的第一单相变流器输出电压中的交流成分,j = CK J a,b,c。 13 .如权利要求12所述的多交流端口模块化多电平换流器的控制方法，其特征在于:还 包括， 利用PI控制器对所述线路k上的电流进行闭环控制，具体控制方程如下所示： =左Μ （% - %） + J （% - Q ）3 + 噎-嗑-+ *人 △u；喇=左-q）+£.J（4 -/初）山+ &amp; -% + -①l3d 其中，上标*代表各自分量的参考值,kpk和分别为线路k的潮流控制环PI调节器的比 例与积分系数,匕（1川山a1^川1^为前馈项，3 LJ、a L Jq、ω LJkd、a LJkq为前馈解耦项； 所述交流线路潮流控制环的线路电流的d轴分量参考值和q轴分量参考值4根据交 流线路k的有功功率参考值耳和无功功率参考值0；计算得到： E=./v；，4）=彳£4+%/；〃 w o =.fa，G=3 （匕4-匕） 14.如权利要求10或11所述的多交流端口模块化多电平换流器的控制方法，其特征在 于:所述模块化多电平换流器控制包括， 当多交流端口型模块化多电平换流器中的MIM中仅包含一个第二单相换流器时，建立 MMC交流端口与上、下桥臂的电流的数学模型，并进行Park将其转换至与交流线路1同步旋 转的d-q坐标系下得到： “号+叫% ,dl 其中，“小心门疝院分别为^^交流端口处的电压气和电流匕的十口轴分量，“小AVq 分别为MMC等效电压A Vj= （%-Upj） /2的d-q轴分量,Upj、％分别为MMC的上、下桥臂等效电 压,7、风分别为MMC桥臂电感L和桥臂电阻R的一半,j=a,b,c； 利用PI控制器对MMC交流侧电流i°j进行闭环控制，具体控制方程如下所示： 'A吸=一匕）+ kJ 一 匕）出 + U0d + ① '△匕*=叽（&amp; 一/以）+ %“&amp; 7京族+。叫一叫几 其中，上标*代表各自分量的参考值,kp。和分别为MMC电流内环控制中PI调节器的比 例和积分调节系数,U°d、U°q为MMC交流端口电压扰动抑制项，用于增强控制环的抗干扰能 力，3 Lod、3 Loq为前馈解耦项； 所述MMC的有功电流参考值心、无功电流参考值总、无功功率参考值0：的计算表达式 如下： '2/3 …/ 。尸一豆一 3 3 &amp; =彳（匕 匕/旧）=一5，，10 15 .如权利要求14所述的多交流端口模块化多电平换流器的控制方法，其特征在于:还 包括， 当多交流端口型模块化多电平换流器中的MIM中不包含第二单相变换器或包含两个第 二单相变换器时,MMC交流端口处的电流兀为各条交流线路的电流之和为： 立。 16 .如权利要求14所述的多交流端口模块化多电平换流器的控制方法，其特征在于:还 包括， 当所述MIM采用方案2的结构时，所述MMC的上桥臂的调制波心和下桥臂的调制波心包 括的计算表达式如下所示： “二=寸一△匕—物历 - * J亦 A 11 Pj =^~ + Avj~ U^JB 当所述MIM采用方案1的结构时,所述MMC的上桥臂的调制波％,和下桥臂的调制波“；包 括的计算表达式如下所示： Αν「”阚 u . = _^^-+八忆一彳疗 pj 2 1 ”项 当所述ΜΙΜ采用方案3的结构时，所述MMC的上桥臂的调制波心和下桥臂的调制波吟包 括的计算表达式如下所示： ~ Ucsmlj ~ 一鸣 &amp; j =寸 + Δν; + %明-UdW -吗 其中，“我为用于控制MIM能量平衡以及MMC上、下桥臂能量平衡而在MMC桥臂中注入的 基频环流。 17.如权利要求10或11所述的多交流端口模块化多电平换流器的控制方法，其特征在 于:所述公共直流母线电压平衡控制包括， 当所述MIM采用方案1的拓扑，控制方程如下： “tAfa —[% （嗑—曦α）+J3化;一嗑Μ川力叽+ Μ] 4 乙1 的二%I （匕:* —%力）+ J3（匕:*—匕知助）阳丸+ Uclb Ucl fi = [% ink -匕MM ） + J 尢1 （匕Μ* - ）出]Mg + Uclc 其中，Vlinka、Vlinkb、Vlinkc为三相公共直流母线电压，心八2、为前馈的三相参考 电压,kpi、kji分别为该方案中的比例积分控制器的比例环节增益系数和积分环节增益系 数； 参考电压为： ,=叽+匕—如 U西=J/ - A吃应+仁皿也北 其中为与交流线路1相连的第一单相换流器j相调制参考电压，。以为与交流线路k 相连的第一单相换流器j相调制参考电压,V。。1m皿η为第一单相换流器和第二单相换流器共 有的直流分量参考值，该参考值大于零且小于公共直流母线电压匕* ； 当所述MIM采用方案2的拓扑，控制方程如下： “二,=[%（K* -嗑G + J胞（嗫阳,（一骁） ，“Mb = [32（%欣-匕山11b）十，£式匕;欣-匕的）山卜（-覆） =伏/&gt;2（匕* -%*c） + [ %（匕欣—匕*）阳・（一忆） 其中，kp2、&amp;2分别为比例积分控制器的比例环节增益系数和积分环节增益系数,前馈项 为0; 各第一单相换流器和第二单相换流器的调制参考电压为： 7/* =?/ t i j j commOfi,dc =山仃-A%® +匕皿Μ如 U* .=κ* ,+U / e.wy efimmnrt.de 当所述MIM采用方案3的拓扑，控制方程如下: =及3闻* —嗑J+卜,式％. -噎 =[%（%* -%他）+此式匕「曦加小阪 =[左03 （ % -嗑ic ） + J ^13 （ ^ί«ί - ^Hic ] *lcirc 其中，1^3、&amp;3分别为该方案中的比例积分控制器的比例环节增益系数和积分环节增益 系数； 各第一单相换流器和第二单相换流器的调制参考电压为： Ui/ = Μ1 + 嚷”,20C 困一clj + 丫common ,dc 〈 u：=以* — + P , U* — * p 其中，“二，为与MMC上桥臂相连的第二单相换流器的三相参考电压j相交流参考电压。 18.如权利要求17所述的多交流端口模块化多电平换流器的控制方法，其特征在于:所 述第一单相换流器和第二单相换流器的交流等效电压的分配方式所需满足的基本条件方 程包括， 当所述MIM采用方案1的拓扑，所述第一单相换流器输出电压的等效交流分量与线路电 流满足下列关系： -----1 ----a . U fl — Uek = Uc\k（k = 2,3,.../） ‘Re o/（之沅* ）；= ο . *=ι3 其中，万5为与交流线路1相连的第一单相换流器输出电压交流分量的矢量表达，万为 所述多交流端口型模块化多电平换流器的与交流线路k相连的第一单相换流器输出电压交 流分量的矢量表达，沅”为交流线路k进行目标潮流控制时，所需的交流线路1和交流线路k 之间的串联等效电压交流分量的矢量表达，7；为线路k上的交流电流矢量的共辗表达,Vunk 为多交流端口型模块化多电平换流器的MIM中的公共直流母线间的电压大小，：。为所述多 交流端口型模块化多电平换流器的直流侧流出MMC的电流,η为所述多交流端口型模块化多 电平换流器的交流侧互联的交流线路数量； 当所述ΜΙΜ采用方案2的拓扑，所述各第一单相换流器、第二单相换流器线路电流满足 下列基本条件： ,-------* -------1- -------¥ （Λι —= = 2?3 … V 」一 * 一 * Rea/（Z 沅**/欣—J ο） — 0 、 hl 其中，沅皿为与MMC相连的第二单相换流器等效也压交流分量的矢量表达，无为流入 MMC交流端口的交流也流矢量的共辗表达； 当所述MIM采用方案3的拓扑，所述各第一单相换流器、第二单相换流器线路也流以及 注入的基频环流满足下列基本条件： U c\ —UCk =U 爪k（左=27 3,…用） * 弋 * _, τ* （Ue5ftll + U亡刖2 卜/口 / _F F \ τ* Re al）: U小♦/无 I匚师1—U以理之卜/隙尸 =0 火=ι 2 其中，友海、讥强为与MMC上、下桥臂相连的第二单相换流器等效电压交流分量的矢量 表达，五为各交流线路电流矢量和的共辗表达，为注入的基频环流的共辗表达。 19 .如权利要求18所述的多交流端口模块化多电平换流器的控制方法，其特征在于:所 述第一单相换流器和第二单相换流器的交流等效电压的分配方式中瓦】的选取包括， 所述多端柔性互联模块在配网馈线上串联等效电压的分配方式为： Uc\ =Uctk/2 对于MIM采用方案1的情况，办=沅为与线路1串联的单相换流器输出电压的前馈 项； 所述守门的选取满足各第一单相换流器和第二单相换流器输出电压的交流分量幅值的 最大值最小： 当所述MIM采用方案1的拓扑，所述a的选取满足max ｛反左信=1,2,…,叫｝取到最小 值； 当所述MIM采用方案2的拓扑，所述办的选取满足max｛a*（左=1,2,…,叽仇,,小｝取到 最小值； 当所述MIM采用方案3的拓扑，所述炉”的选取满足 max｛MM 左 1,2,...,n）\,\Ucsini\,U 的⑷）取至撮小值。 20 .如权利要求18或19所述的多交流端口模块化多电平换流器的控制方法，其特征在 于:所述多交流端口型模块化多电平换流器串联在馈线上的电压的过压保护策略包括， 在所述多端柔性互联模块中的第一单相换流器的交流输出端口间并联一个保护装置； 所述保护装置由金属氧化物限压器和晶闸管旁路开关并联组成，所述金属氧化物限压 器将电压限制在保护水平，所述晶闸管旁路开关通过将第一单相换流器的交流输出端口旁 路； 所述晶闸管旁路开关由反并联晶闸管、阻容回路以及静态电阻并联后再与一个饱和电 抗器串联构成。 21 .如权利要求20所述的多交流端口模块化多电平换流器的控制方法，其特征在于:所 述多交流端口型模块化多电平换流器的启动策略包括， 第一阶段:不控充电阶段，交流线路1串联限流电阻并网，所有开关闭锁，交流电网电流 经各开关的续流二极管对多交流端口型模块化多电平换流器内的电容进行充电； 第二阶段:受控充电阶段，在所述第一阶段不控充电完成后，各电容电压尚未达到参考 值，通过开关轮流投切的方式使得回路中的充电电容个数一定，将多交流端口型模块化多 电平换流器内电容电压进一步提升； 第三阶段:斜坡升压阶段，在所述第二阶段充电结束后，投入电压控制环并给定采用斜 坡变化的参考电压，将各电容电压充电至参考值； 第四阶段:交流线路投入阶段，在充电完成后，其余各条交流线路配合各自的线路电流 控制环和与之相连的第一单相换流器的参考给定输出实现软投入。 [EN CN113285620A]: 1 A multi-AC port modular multi-level converter, characterized by comprising: a modular multi-level converter; and, a multi-port flexible interconnection module connected in series with the modular multi-level converter . 2 The multi-AC port modular multi-level converter according to claim 1, characterized in that: the modular multi-level converter comprises a medium and high voltage voltage source type converter. 3 The multi-AC port modular multi-level converter according to claim 1, wherein the multi-port flexible interconnection module comprises a plurality of first single-phase converters connected in parallel on a common connection bus, each The AC output ports of the single-phase converters are all connected to the corresponding AC lines. 4 The multi-AC port modular multi-level converter according to claim 1 or 2, characterized in that: the sub-module topology of the modular multi-level converter includes a half-bridge type sub-module topology, a full-bridge type Sub-module topology, clamp-type dual-sub-module topology, or multiple-structure hybrid topology. 5 The multi-AC port modular multi-level converter according to claim 3, characterized in that: the common connection bus includes a medium and low voltage DC bus, and a common connection capacitor connected to the medium and low voltage DC bus provides it with Voltage. 6 The multi-AC port modular multi-level converter according to any one of claims 1, 3, and 5, characterized in that: the multi-port flexible interconnection module includes a second single-phase converter and the included The second single-phase converter and the upper and lower bridge arms of the modular multilevel converter are divided into three schemes, including: Scheme 1: The multi-port flexible interconnection module does not include all In the second single-phase converter, the AC output ports of the upper and lower arms of the modular multilevel converter are respectively connected to the positive and negative poles of the common DC bus of the multi-port flexible interconnection module; Solution 2: The multi-port flexible interconnection module includes a second single-phase converter connected at both ends of a common DC bus in parallel with the first single-phase converter, and the AC port of the modular multi-level converter is connected to the second single-phase converter. The AC output port of the second single-phase converter is connected; Solution 3: The multi-port flexible interconnection module includes a first single-phase converter and two second single-phase converters matching the number of AC lines, so The first single-phase converter and the two second single-phase converters are connected in parallel at both ends of the common DC bus, and the AC output ports of the two second single-phase converters are connected to the modular multi-phase converter respectively. The AC output ports of the upper and lower bridge arms of the flat converter are connected. 7 The multi-AC port modular multilevel converter of claim 6, wherein: the first single-phase converter and the second single-phase converter comprise voltage source single-phase converters . 8 The multi-AC port modular multi-level converter according to claim 7, wherein: the topology of the first single-phase converter or the second single-phase converter in the multi-port flexible interconnection module Including two-level half-bridge converters, three-level half-bridge converters or single-phase bridge converters capable of bidirectional power flow. 9 The multi-AC port modular multi-level converter according to claim 8, characterized in that: the output voltage of the single-phase converter port in the multi-terminal flexible interconnection module includes DC components of the same size and according to requirements Different AC components obtained by control; the DC component of the voltage at the output port of the single-phase converter is half of the value of the voltage of the common connection bus. 10 A control method applied to the multi-AC port modular multi-level converter as claimed in claim 1, characterized in that it includes AC line power flow control, modular multi-level converter control and public DC Bus voltage balance control. 11 The control method of a multi-AC port modular multi-level converter as claimed in claim 10, characterized in that: also Including, the multi-terminal flexible interconnection module and the modular multi-level converter flexibly interconnect multiple AC lines with the DC grid through coordinated control, and adjust the power flow distribution on the multiple lines; when the multi-segment flexible When the interconnection module interconnects n AC lines, the power flow on each AC line is P]~P. And Q] ~Qn and the DC side load power Pl are controlled, the active power of one of the AC lines will be automatically adjusted through the energy balance of the system, and only the reactive power on the line will be controlled, and the AC line will be defined as AC line 1; In the control, the three-phase AC component locked by the phase-locked loop is the three-phase node voltage of the AC line 1 controlled by the constant reactive power, and the three-phase AC abc coordinate is calculated by the phase of the grid voltage output in real time The voltage and current under the system are converted to the dq coordinate system through Park transformation for decoupling control of active and reactive components. 12 The control method of a modular multilevel converter with multiple AC ports as claimed in claim 10 or 11, characterized in that: the power flow control of the AC line comprises, taking AC line 1 as a reference, and writing the line 1 node voltage The dynamic equation of the node voltage Vkj from V]j to line k and convert it to the dq coordinate system to obtain the following equation: Lk -7~ + = -d +% + 1£*&amp; + Λ -γ- + /iMl -at'or di. dLfi Lk Room + /3&amp; = AU, (Iv)-dagger g + one bid q + Lt-^ + IiqR}+ Call a few of them, ",%Mountain21^, 1Μ, work,（1. Which is the &lt;1" axis component of the voltage and current of the line 1 and the line BU respectively, the villain and 1^^ are the inductance and equivalent resistance on the line 1 and the line BU respectively, 3 represents the angular frequency of the power grid, and 8"11^, eight with ^ as the equivalent voltage eight 412=4111102 (17 axis component, 11 dishes. It is the AC component in the output voltage of the first single-phase converter connected to the AC line 1, u°kj is the AC line The AC component in the output voltage of the first single-phase converter connected to k, j = CK J a,b,c. 13 The control method of a multi-AC-port modular multi-level converter according to claim 12, characterized in that it further comprises: using a PI controller to perform closed-loop control of the current on the line k, and the specific control equation is as follows Shown: =Left Μ (%-%) + J (%-Q) 3 + choking-Nibble-+ *person u; La = left-q) + £.J (4 -/early) mountain + &amp;- % + -1l3d Among them, the superscript * represents the reference value of the respective components, kpk and the proportional and integral coefficients of the PI regulator of the power flow control loop of line k, d（1Chuanshan a1^Chuan1^ Is the feedforward term, 3 LJ, a L Jq, ω LJkd, a LJkq are the feedforward decoupling terms; the reference value of the d-axis component and the q-axis component of the line current of the AC line power flow control loop 4 According to AC The active power reference value ear and the reactive power reference value 0 of line k are calculated: E=./v;, 4)=NS£4+%/; w o =.fa, G=3 (dagger 4-dagger) 14. The control method of a multi-AC port modular multi-level converter according to claim 10 or 11, characterized in that: the control of the modular multi-level converter comprises: When the MIM of the multi-ac port type modular multi-level converter contains only one second single-phase converter, establish a mathematical model of the current between the MMC AC port and the upper and lower arms, and perform Park to convert it Convert to the dq coordinate system that rotates synchronously with AC line 1 to get: "Number + called %,dl where, "Be careful of the ten-axis components of the voltage and current at the AC port, "small AVq is the dq axis component of the MMC equivalent voltage A Vj= (%-Upj) /2, Upj and% are the equivalent voltages of the upper and lower arms of the MMC respectively, 7 and wind are the MMC leg inductance L and the bridge respectively Half of the arm resistance R, j=a,b,c; The PI controller is used to control the MMC AC side current i°j in a closed loop. The specific control equation is as follows:'A suction = a dagger + kJ a dagger) out + U0d + 1'dagger*=grumble(&amp;one/by)+ %"&amp; 7 Jing nationality+. Call a number of them, the superscript * represents the reference value of each component, kp. And are the proportional and integral adjustment coefficients of the PI regulator in the MMC current inner loop control, U°d, U°q are the MMC AC port voltage disturbance suppression items, used to enhance the anti-interference ability of the control loop, 3 Lod, 3 Loq It is the feedforward decoupling term; the calculation expressions of the active current reference value of the MMC, the total reactive current reference value, and the reactive power reference value 0: are as follows: '2/3 .../. Corpse one bean one 3 3 &amp; = NS (dagger/old) = a 5,, 10 15 The control method of a multi-AC-port modular multi-level converter according to claim 14, characterized in that it further comprises: when the MIM in the multi-AC port-type modular multi-level converter does not include the first When two single-phase converters or two second single-phase converters are included, the current at the AC port of the MMC is the sum of the currents of the various AC lines: Li. 16 The control method of a multi-AC-port modular multi-level converter according to claim 14, characterized in that it further comprises, when the MIM adopts the structure of scheme 2, the modulation of the upper arm of the MMC The calculation expressions included in the wave center and the modulated wave center of the lower bridge arm are as follows: "Two = Cun Yi Dagger-Physical Calendar -* J also A 11Pj =^~ + Avj~ U^JB When the MIM adopts the structure of Scheme 1, the modulation wave% of the upper bridge arm of the MMC, and the modulation wave of the lower bridge arm "; the calculation expressions included are as follows: Αν""Kanu. = _^^-+Ba Yi Yi Yu treatment pj 2 1 When the MIM adopts the structure of Scheme 3, the calculation expressions included in the modulation wave center of the upper bridge arm and the modulation wave Yin of the lower bridge arm of the MMC are as follows: ~ Ucsmlj ~ Yiming &amp; j = inch + Δν; +% Ming-UdW -? Among them, "I inject the fundamental frequency circulating current in the MMC bridge arm to control the energy balance of the MIM and the energy balance of the upper and lower arms of the MMC. 17. The control method of a multi-AC port modular multi-level converter according to claim 10 or 11, characterized in that: the common DC bus voltage balance control comprises, when the MIM adopts the topology of scheme 1, The governing equation is as follows: "tAfa -[% (Nibble-Xiα)+J3change;OneΜChuan Liji+ Μ] 4 The second %I of B1 (dagger: * -% strength) + J3 (dagger: *-dagger Zhisuke) Yang Wan+ Uclb Ucl fi = [% ink -MM) + J especially1 (M*-)]Mg + Uclc Among them, Vlinka, Vlinkb, and Vlinkc are the three-phase public DC bus voltages, and core 2 is the feedforward three-phase reference voltage, and kpi and kji are the proportional link gain coefficient and integral link gain of the proportional-integral controller in the scheme. Coefficient; The reference voltage is:, = grumble + dagger-such as U West = J/-A Chiying + Renmin Yebei where is the j-phase modulation reference voltage of the first single-phase converter connected to AC line 1. It is assumed that the first single-phase inverter connected to the AC line k modulates the reference voltage, V, in phase j. .1mΗ is the reference value of the DC component shared by the first single-phase converter and the second single-phase converter, and the reference value is greater than zero and less than the common DC bus voltage d*; when the MIM adopts the topology of scheme 2, the control The equation is as follows: "Two,=[%(K* -G + J cell (Whistleyang, (one small)," Mb = [32(%Happy-aggershan11b) Ten, £-style dagger; Xin-dagger) Shanbu (-cover) = volt/&gt;2 (dagger* -%*c) + [% (dagger-dagger*) Yang·(A remembrance) Among them, kp2 and &amp;2 are the proportional link gain coefficient and the integral link gain coefficient of the proportional integral controller respectively, and the feedforward term is 0; The modulation reference voltage of each of the first single-phase inverter and the second single-phase inverter is: 7/* =?/ tijj commOfi,dc = Shanding-A%® + dagger Μlike U* .=κ* ,+U / e.wy efimmnrt.de When the MIM adopts the topology of Scheme 3, the control equation is as follows: = And 3 Wen*-NibbleJ + predict, type %. -Choke=[%(%* -%he)+this type dagger "Xi Jia Kosaka=[Left 03 (%-ic) + J ^13 (^ί «Ί - ^Hic] *lcirc Among them, 1^3 and &amp;3 are the proportional link gain coefficient and the integral link gain coefficient of the proportional integral controller in this scheme; the modulation reference voltage of each first single-phase converter and second single-phase converter is : Ui/ = Μ1 + yell", 20C sleepy one clj + ya common, dc u: =by* - + P, U* - * p Among them, "two, is the three-phase reference voltage j-phase AC reference voltage of the second single-phase converter connected to the upper arm of the MMC. 18. The control method of the multi-AC port modular multi-level converter of claim 17, wherein: the AC equivalent voltage of the first single-phase converter and the second single-phase converter The basic condition equations that must be met by the distribution mode of the MIM include that when the MIM adopts the topology of scheme 1, the equivalent AC component of the output voltage of the first single-phase converter and the line current satisfy the following relationship: -----1 ----a. U fl - Uek = Uc\k (k = 2,3,.../)'Re o/(Zhiyuan* ); = ο. *=ι3 Among them, Wan 5 is the first order connected to AC line 1 The vector expression of the AC component of the output voltage of the phase converter is the vector expression of the AC component of the output voltage of the first single-phase converter connected to the AC line k of the multi-AC port type modular multilevel converter, When "Yuan" is AC line k for target power flow control, the required AC line 1 and AC line k The vector expression of the AC component of the series equivalent voltage, 7; is the common expression of the AC current vector on the line k, Vunk is the common DC bus in the MIM of the multi-AC port type modular multi-level converter The voltage size:. Is the current flowing out of the MMC on the DC side of the multiple AC port type modular multilevel converter, and η is the number of AC lines interconnected on the AC side of the multiple AC port type modular multilevel converter; The MIMO adopts the topology of scheme 2, and the line current of each of the first single-phase converter and the second single-phase converter meets the following basic conditions: ,-------* -------1 --------¥ (Λι -= = 2?3... V "one * one * Rea/(Z Yuan**/Happy-J ο) - 0, hl Among them, Yuan is the vector expression of the equivalent voltage AC component of the second single-phase converter connected to the MMC, and nothing flows into the MMC AC port. The common expression of the flow vector; When the MIM adopts the topology of scheme 3, the circuits of the first single-phase converter and the second single-phase converter also flow and the injected fundamental frequency circulating current meets the following basic conditions: U c\ -UCk =U claw k (left=27 3,...use) * Yi* _, τ* (Ue5ftll + UDie2 predict/mouth/ _FF \ τ* Re al): U Small /No I Master1-U Yili Zhibu/Xiao Zhan=0 Fire=ι 2 Among them, Youhai and Xiqiang are the second single-phase exchanges connected to the upper and lower arms of the MMC The vector expression of the AC component of the equivalent voltage of the current transformer, five is the common expression of the vector sum of each AC line current, and the common expression of the injected fundamental frequency circulating current. 19 The control method of a modular multilevel converter with multiple AC ports as claimed in claim 18, characterized in that: the AC equivalent voltage of the first single-phase converter and the second single-phase converter is equal to The selection of "Watts in the distribution method" includes the following: Uc\ =Uctk/2 For the case where MIM adopts scheme 1, do=yuan is the feedforward term of the output voltage of the single-phase converter connected in series with line 1; The maximum value of the AC component amplitude of the output voltage of the phase converter is the smallest: When the MIM adopts the topology of scheme 1, the selection of a satisfies max {anti-left letter=1,2,..., called} to take the minimum value ; When the MIM adopts the topology of scheme 2, the selection of the office satisfies max{a*(left=1,2,...,Hatred,,small} to the minimum value; when the MIM adopts the topology of scheme 3 , The selection of "furnace" satisfies max{MM left1,2,...,n)\,\Ucsin of i\,U) is taken to a small value. 20 The control method of the multi-AC port modular multi-level converter according to claim 18 or 19, characterized in that: the multi-AC port type modular multi-level converter is connected in series with the voltage of the feeder The overvoltage protection strategy includes: connecting a protection device in parallel between the AC output ports of the first single-phase converter in the multi-terminal flexible interconnection module; the protection device is composed of a metal oxide voltage limiter and a thyristor bypass switch in parallel , The metal oxide voltage limiter limits the voltage to the protection level, the thyristor bypass switch bypasses the AC output port of the first single-phase converter; the thyristor bypass switch is composed of anti-parallel thyristors and resistors The capacitive loop and static resistance are connected in parallel and then connected in series with a saturated reactor. 21 The control method of the multi-AC-port modular multi-level converter according to claim 20, characterized in that: the start-up strategy of the multi-AC port-type modular multi-level converter includes, the first stage: In the uncontrolled charging phase, the AC line 1 is connected to the grid in series with a current-limiting resistor, all on and off are locked, and the AC grid current charges the capacitors in the multi-AC port type modular multi-level converter through the freewheeling diodes of each switch; Stage: Controlled charging stage. After the first stage of uncontrolled charging is completed, the voltage of each capacitor has not yet reached the reference value. The number of charging capacitors in the loop is made to be constant through the switch in turn, and the multiple AC port type The capacitor voltage in the modular multi-level converter is further increased; The third stage: ramp-up stage, after the second stage of charging is completed, the voltage control loop is put into The voltage is charged to the reference value; The fourth stage: the AC line input stage, after the charging is completed, the remaining AC lines cooperate with their respective line current control loops and the reference given output of the first single-phase converter connected to it to achieve Soft investment. | [ZH CN113285620A]: 一种多交流端口模块化多电平换流器及其控制方法 技术领域 [0001] 本发明涉及中高压交直流混合电网、交直流换流站组网结构和电力电子的技术领 域，尤其涉及一种多交流端口模块化多电平换流器及其控制方法。 背景技术 [0002]交直流混合电网凭借着其在供电容量、供电可靠性、电能质量和系统灵活性等方 面的优势，正逐步成为国内外研究的热点。交直流换流站是连接直流电网和交流电网连接 的纽带，电力电子换流器则作为交直流换流站中的核心设备，通常为电压源型换流器 (voltage source converter,VSC)，可分为两电平拓扑、三电平拓扑和模块化多电平拓扑， 两电平和三电平拓扑的换流器结构简单，技术较为成熟，但在中高压场合下需要大量IGBT 串联使用，由此带来均压问题，目前能解决该问题的只有ABB一家公司；同时，为了得到较好 的动态特性与谐波特性，两电平和三电平换流器需要高频投切，导致开关损耗较大;模块化 多电平换流器(MMC)拓扑结构采用子模块级联的方式，降低对于器件耐压等级的要求，在制 造难度、开关损耗、波形质量以及故障处理能力上都具备显著优势，因此更适合于中高压场 合的应用。此外，交直流换流站的组网结构会对系统成本、供电可靠性、保护配置以及控制 灵活性等诸多方面产生影响，而提供一种方法可以实现多交流线路功能的基础上满足低成 本、高功率密度等应用需求是亟待解决的问题。 发明内容 [0003] 本部分的目的在于概述本发明的实施例的一些方面以及简要介绍一些较佳实施 例。在本部分以及本申请的摘要和发明名称中可能会做些简化或省略以避免使本部 分、摘要和发明名称的目的模糊，而这种简化或省略不能用于限制本发明的范围。 [0004] 鉴于上述现有存在的问题，提出了本发明。 [0005]因此，本发明解决的技术问题是:现有的交直流换流站组网结构只能实现单一交 流线路的馈入，不具备多交流线路互联和交直流线路的主动潮流解耦控制功能。 [0006]为解决上述技术问题，本发明提供如下技术方案:模块化多电平换流器；以及，与 所述模块化多电平换流器串联的多端口柔性互联模块。 [0007]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 模块化多电平换流器包括中高压级电压源型换流器。 [0008]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 多端口柔性互联模块包括多个并联在公共连接母线上的第一单相换流器，每个单相换流器 的交流输出端口均与相应的交流线路相连。 [0009]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 模块化多电平换流器子模块拓扑包括半桥型子模块拓扑、全桥型子模块拓扑、箝位型双子 模块拓扑，或者多种结构混联的拓扑。 [0010]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 公共连接母线包括中低压直流母线，与所述中低压直流母线相连的公共连接电容为其提供 电压。 [0011]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 多端口柔性互联模块根据是否包含第二单相换流器以及包含的第二单相换流器与所述模 块化多电平换流器上、下桥臂的接线方式的不同，分为三种方案，包括，方案1：所述多端口 柔性互联模块不包含所述第二单相换流器，模块化多电平换流器的上、下桥臂的交流输出 端口分别与所述多端口柔性互联模块的公共直流母线的正、负极相连;方案2：所述多端口 柔性互联模块中包含一个与所述第一单相换流器同样并联在公共直流母线两端的所述第 二单相换流器，模块化多电平换流器的交流端口与所述第二单相换流器的交流输出端口相 连;方案3：所述多端口柔性互联模块包含与交流线路数量匹配的第一单相换流器以及两个 第二单相换流器，所述第一单相换流器以及两个第二单相换流器并联在公共直流母线两 端，所述的两个第二单相换流器的交流输出端口分别与所述模块化多电平换流器的上、下 桥臂的交流输出端口相连。 [0012]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 第一单相变流器和第二单相变流器包括电压源型单相变流器。 [0013]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 多端口柔性互联模块中的第一单相变流器或者第二单相变流器的拓扑包括两电平半桥型 变流器、三电平半桥型变流器或者是能进行功率双向流动单相桥型变流器。 [0014]作为本发明所述的多交流端口模块化多电平换流器的一种优选方案，其中：所述 多端柔性互联模块中的单相换流器端口输出电压中包括相同大小的直流成分和根据需求 控制得到的不同的交流成分;所述单相换流器输出端口电压的直流成分为所述公共连接母 线电压值的一半。 [0015]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：包括，交流线路潮流控制、模块化多电平换流器控制和公共直流母线电压平衡控制。 [0016]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：还包括，所述多端柔性互联模块和所述模块化多电平换流器通过协同控制，将多条交流 线路与直流电网柔性进行互联，并调节多条线路上的潮流分布；当所述多段柔性互联模块 互联了n条交流线路时，对各条交流线路上的潮流P1~Pn和Q1~Qn以及直流侧负载功率PL进 行控制，其中一条交流线路的有功功率将通过系统的能量平衡自动调节，仅对所述线路上 的无功功率进行控制，将所述交流线路定义为交流线路1；在所述控制中，锁相环锁定的三 相交流分量为所述定无功功率控制的所述交流线路1的三相节点电压，通过实时输出的电 网电压的相位，将三相交流a-b-c坐标系下的电压电流通过Park变换转换至d-q坐标系中进 行有功无功分量的解耦控制。 [0017]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述交流线路潮流控制包括，以交流线路1为基准，列写线路1节点电压V]j到线路k的节 点电压vkj的动态方程并将其转换至d-q坐标系下得到如下方程： 九4 = △&amp;图一匕+噎+* L +乙U+儿用一 出乙儿 rc…ί 力 力’ I % άΙΧί! L* —Τ- + /勿&amp; = AUc¦*g -匕g + 匕g — ⑦ £*4d + 4 —7— + 4凡 + 3£¦/必 、 H ί \λ 匕 [0019]其中，匕小丫山松1^a1^、1Μ、工、％、几分别为线路1与线路卜节点电压电流的＜1”轴 分量,小人小风分别为线路1与线路1＜上的电感与等效电阻，3表示电网角频率，AJkd、A U°ikd为等效电压AUcikj = Uci「Uckj的d-q轴分量,ΙΙ。”为与交流线路1相连的第一单相变流器 输出电压中的交流成分,u°kj为与交流线路k相连的第一单相变流器输出电压中的交流成 分，j =a, b, c。 [0020]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：还包括，利用PI控制器对所述线路k上的电流进行闭环控制，具体控制方程如下所示： ί=图（1 -^d） + &amp; JCC - IQdt + 匕d —噎—①LJkq + a）Ltltq [0021] { ； [0022]其中，上标*代表各自分量的参考值,和分别为线路k的潮流控制环PI调节器 的比例与积分系数,匕小丫箱搂1^51^为前馈项，a LJ、a LJiq、ω LkIkd. ω 为前馈解耦 项； [0023]所述交流线路潮流控制环的线路电流的d轴分量参考值兀和q轴分量参考值4根 据交流线路k的有功功率参考值月和无功功率参考值0；计算得到： [0024] 夕=/(©◎ = /(%/; + %/展) 。;=/(@/展)=3%-) [0025]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述模块化多电平换流器控制包括，当多交流端口型模块化多电平换流器中的MIM中仅 包含一个第二单相换流器时，建立MMC交流端口与上、下桥臂的电流的数学模型，并进行 Park将其转换至与交流线路1同步旋转的d-q坐标系下得到： [0026] 就 4d+/〃=。5一 △匕一冲£。却 [0027]其中，%、*、1。（1、尢分别为皿（：交流端口处的电压11。押电流q的（1^轴分量，Δ νr AVq分别为MMC等效电压AVj= （%时?/2的（1”轴分量,%、%分别为皿（；的上、下桥臂 等效电压,7、风分别为MMC桥臂电感L和桥臂电阻R的一半,j=a,b,c； [0028]利用PI控制器对MMC交流侧电流q进行闭环控制，具体控制方程如下所示： A%=-，：）+ %/（&amp; -乙）北 + 几 + 山蜀 [0029]〈 . △匕=噎（&amp; - &amp; ） + Ko f （hg - &amp; 技 + U 叫- aLnIod [0030]其中，上标*代表各自分量的参考值,kp。和分别为MMC电流内环控制中PI调节器 的比例和积分调节系数,U。d、U。q为MMC交流端口电压扰动抑制项，用于增强控制环的抗干扰 能力，sLoKd、37晨为前馈解耦项;所述MMC的有功电流参考值/：、无功电流参考值仆、无 功功率参考值0：的计算表达式如下： [0031] —2/3E- =兀+力展 =/（匕 %/%） = -彳匕Jig [0032]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：还包括，当多交流端口型模块化多电平换流器中的MIM中不包含第二单相变换器或包含 两个第二单相变换器时,MMC交流端口处的电流兀为各条交流线路的电流之和为： [0033] 2 %。 £=1 [0034]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：还包括，当所述MIM采用方案2的结构时，所述MMC的上桥臂的调制波心和下桥臂的调制 波心包括的计算表达式如下所示： . * _ Ο亦 a μ0 =亍一 Δν/一%物 [0035] 4 * 3c a llpj = 可 + 一凡物 [0036]当所述ΜΙΜ采用方案1的结构时，所述MMC的上桥臂的调制波心和下桥臂的调制波 心包括的计算表达式如下所示： de ~ _ Λ ν upJ - 2 5知诙 [0037], 嗅=吐”+Z1%通 [0038]当所述MIM采用方案3的结构时，所述MMC的上桥臂的调制波心和下桥臂的调制波 吟包括的计算表达式如下所示: [0039] 双；=?一^vj~ 四一忆通一鸣 双；=容+ A, + %明-%诙-噂 [0040] 其中，“我为用于控制MIM能量平衡以及MMC上、下桥臂能量平衡而在MMC桥臂中注 入的基频环流。 [0041]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述公共直流母线电压平衡控制包括,当所述MIM采用方案1的拓扑，控制方程如下： 匕# =[图（嗫—%*°）+-%血）阳叽 +Q [0042] ，Uci 的=[%（%：一 ^linkb^ + J 总（嗑A — Kinkb ）附叽 + Uc\b u*iΛ = IkpG；植-%J + J尢i（曦—嗑J沟叽+ [0043] 其中，Vlinka、Vlinkb、Vlinkc为三相公共直流母线电压，心.、 u*lb ' U；ic为前馈的三 相参考电压,kpi,kji分别为该方案中的比例积分控制器的比例环节增益系数和积分环节增 益系数； [0044] 参考也压为： U* -η +P [0045] { * * * \uc,=^-^^vcom^dc [0046]其中，U]为与交流线路1相连的第一单相换流器j相调制参考电压，U以为与交流 线路k相连的第一单相换流器j相调制参考电压,、。丽皿也为第一单相换流器和第二单相换 流器共有的直流分量参考值，该参考值大于零且小于公共直流母线电压匕L； [0047] 当所述MIM采用方案2的拓扑，控制方程如下: [0048] %工=也式峨-嗑0） + J&amp;2（嘘-曦1的.（F） 心心=瓦2（嗫一曦Q +J尢2（嗫-%;1）町（一骁） 产二Μ =[%（%：* -%*J +J左式嗑—%此）阳・（一3） [0049]其中，kp2、kj2分别为比例积分控制器的比例环节增益系数和积分环节增益系数, 前馈项为0; [0050] [0051] [0052] [0053] 各第一单相换流器和第二单相换流器的调制参考电压为: U\.=u..+V , C】j cl j fummoti^ac “ 4与二 + ^common,de u；.=力 +V , gy 叫 esmj common 当所述MIM采用方案3的拓扑，控制方程如下： ^cstn2a 二氏3 （嗑点一端履）+ J自（嗑it — V值而）出卜口旧 = \.^p^link ~ ^linkb ) +j 左式%: 一 %kb )dt]«ie*b =[J（峨-嗑J+J自（峨-嗑J阳乙 [0054]其中，斗3、&amp;3分别为该方案中的比例积分控制器的比例环节增益系数和积分环节 增益系数； [0055]各第一单相换流器和第二单相换流器的调制参考电压为: ^U\. =u\. + V Hcl j el j common ^dc [0056] &lt; U函—e] j 灯+ 丫^口皿皿白明也U . . — U i + P 月csm 1 j csm 1 j common,acIJ . — U r +P x、 楸 2 j csm 2 / com mon ,ac [0057] 其中，Μ;u为与MMC上桥臂相连的第二单相换流器的三相参考电压j相交流参考电 压。 [0058]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述第一单相换流器和第二单相换流器的交流等效电压的分配方式所需满足的基本条 件方程包括，当所述MIM采用方案1的拓扑，所述第一单相换流器输出电压的等效交流分量 与线路电流满足下列关系： [0059] U ci —Uck = U = 2,3,---5^) ‘Re 山(之 Uck ·Λ - = 0 , K=1 3 [0060] 其中，打c为与交流线路1相连的第一单相换流器输出电压交流分量的矢量表达, 守淮为所述多交流端口型模块化多电平换流器的与交流线路k相连的第一单相换流器输出 电压交流分量的矢量表达，沅“为交流线路k进行目标潮流控制时，所需的交流线路1和交 流线路k之间的串联等效电压交流分量的矢量表达，元为线路k上的交流电流矢量的共辗表 达,立Η为多交流端口型模块化多电平换流器的中的公共直流母线间的电压大小，：。为 所述多交流端口型模块化多电平换流器的直流侧流出MMC的电流,η为所述多交流端口型模 块化多电平换流器的交流侧互联的交流线路数量； [0061]当所述ΜΙΜ采用方案2的拓扑，所述各第一单相换流器、第二单相换流器线路电流 满足下列基本条件： [0062] U—Uck - Uc\k(k - 2,3,...,«) —万丽1：) = 0 I [0063]其中，万「,,”为与MMC相连的第二单相换流器等效电压交流分量的矢量表达，了：为 流入MMC交流端口的交流电流矢量的共辗表达； [0064]当所述ΜΙΜ采用方案3的拓扑，所述各第一单相换流器、第二单相换流器线路电流 以及注入的基频环流满足下列基本条件： , —» —k U C\ —Uck = U c\k（k = 2；3，.一,/7） [0065] * Re Η J _r ^Uck9lk — hl + U ).7； —U cj附 2 =0 [0066] 其中，沅加、沅源为与MMC上、下桥臂相连的第二单相换流器等效电压交流分量 的矢量表达，£为各交流线路电流矢量和的共猴表达，了工为注入的基频环流的共辗表达。 [0067]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述第一单相换流器和第二单相换流器的交流等效电压的分配方式中守门的选取包括, 所述多端柔性互联模块在配网馈线上串联等效电压的分配方式为： [0068]沅¦=沅/2 [0069] 对于MIM采用方案1的情况，沅i -历/2为与线路1串联的单相换流器输出电压的 前馈项;所述的选取满足各第一单相换流器和第二单相换流器输出电压的交流分量幅 值的最大值最小：当所述Μ I Μ采用方案1的拓扑，所述j7”的选取满足 左= 1,2,...,*)¦}取到最小值；当所述MIM采用方案2的拓扑，所述办的选取满足 max {¦小伏= 1,2,…*)1,1%,取到最小值;当所述MIM采用方案3的拓扑，所述a的选取满 足 max{¦UcM 左二 1,2,…，耳)¦,¦U 6Ml\,U 8M 21)取到最小值。 [0070]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中：所述多交流端口型模块化多电平换流器串联在馈线上的电压的过压保护策略包括，在 所述多端柔性互联模块中的第一单相换流器的交流输出端口间并联一个保护装置;所述保 护装置由金属氧化物限压器和晶闸管旁路开关并联组成，所述金属氧化物限压器将电压限 制在保护水平，所述晶闸管旁路开关通过将第一单相换流器的交流输出端口旁路;所述晶 闸管旁路开关由反并联晶闸管、阻容回路以及静态电阻并联后再与一个饱和电抗器串联构 成。 [0071]作为本发明所述的多交流端口模块化多电平换流器控制方法的一种优选方案，其 中:所述多交流端口型模块化多电平换流器的启动策略包括,第一阶段:不控充电阶段，交 流线路1串联限流电阻并网,所有开关闭锁，交流电网电流经各开关的续流二极管对多交流 端口型模块化多电平换流器内的电容进行充电；第二阶段:受控充电阶段，在所述第一阶段 不控充电完成后，各电容电压尚未达到参考值,通过开关轮流投切的方式使得回路中的充 电电容个数一定，将多交流端口型模块化多电平换流器内电容电压进一步提升;第三阶段: 斜坡升压阶段，在所述第二阶段充电结束后，投入电压控制环并给定采用斜坡变化的参考 电压，将各电容电压充电至参考值;第四阶段:交流线路投入阶段,在充电完成后，其余各条 交流线路配合各自的线路电流控制环和与之相连的第一单相换流器的参考给定输出实现 软投入。 [0072]本发明的有益效果:本发明创新性的在模块化多电平换流器的基础上引入多端口 柔性互联模块(MIM)，提供了多个交流线路馈入端口，实现多交流线路和直流电网在同一个 换流站的站内互联;通过调节与交流线路相连的第一单相换流器的输出电压交流分量的幅 值和相位，可实现对于交流线路潮流的主动控制;本发明和现有常用的交直流换流站组网 结构相比，采用无变压器式结构,采用多条交流线路同时馈入的方式以及交直流电网互联 的方式，在功率密度、换流站体积、建设成本、供电可靠性、供电系统运行效率等方面具备巨 大优势;本发明中的利用多端柔性互联模块实现多交流线路的柔性互联，具备模块化的特 点，通过增加互联模块中第一单相换流器的数量，可经济、高效、方便的实现交流线路的端 □拓展。 附图说明 [0073]为了更清楚地说明本发明实施例的技术方案，下面将对实施例描述中所需要使用 的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本发明的一些实施例，对于本 领域普通技术人员来讲，在不付出创造性劳动性的前提下，还可以根据这些附图获得其它 的附图。其中： [0074]图1为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的交直流换流站的四种典型组网结构的系统示意图； [0075]图2为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的电压源型换流器和电压源型单相换流器的典型拓扑举例示意图； [0076]图3为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的模块化多电平换流器的子模块的一些典型拓扑举例示意图； [0077]图4为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的不包含第二单相换流器的拓扑结构及其互联多交流线路的系统接线示意图； [0078]图5为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的仅包含单个第二单相换流器的拓扑结构及其互联多交流线路的系统接线示意图； [0079]图6为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的包含两个第二单相换流器的拓扑结构及其互联多交流线路的系统接线示意图； [0080]图7为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的采用单个所述多交流端口型模块化多电平换流为核心设备的多线路多电压等级交直 流电网柔性互联系统示意图； [0081]图8为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的采用多个所述多交流端口型模块化多电平换流为核心设备的多线路多电压等级交直 流电网柔性互联系统示意图； [0082]图9为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制方 法的单相换流器的过电压保护方式接线图及保护装置内部示意图； [0083]图10为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的采用如图5所示结构，并且多端口柔性互联装置第一单相换流器、第二单相换流器和 模块化多电平换流器的子模块均采用两电平半桥型换流器拓扑实现两条交流线路互联的 换流站拓扑结构及系统接线示意图； [0084]图11为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的采用如图5所示结构，并且多端口柔性互联装置第一单相换流器、第二单相换流器和 模块化多电平换流器的子模块均采用两电平半桥型换流器拓扑实现两条交流线路互联的 换流站的控制框图； [0085]图12为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的第一种工况仿真下的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和 装置内子模块电容电压波形图； [0086]图13为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的第二种工况仿真下的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和 装置内子模块电容电压波形图； [0087]图14为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的第三种工况仿真下的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和 装置内子模块电容电压波形图； [0088]图15为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的第四种工况仿真下的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和 装置内子模块电容电压波形图； [0089]图16为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的采用如图5所示结构，并且多端口柔性互联装置第一单相换流器、第二单相换流器和 模块化多电平换流器的子模块均采用两电平半桥型换流器拓扑实现三条交流线路互联的 换流站拓扑结构及系统接线示意图； [0090]图17为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的采用如图5所示结构，并且多端口柔性互联装置第一单相换流器、第二单相换流器和 模块化多电平换流器的子模块均采用两电平半桥型换流器拓扑实现三条交流线路互联的 换流站的控制框图； [0091]图18为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的仿真中的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和装置内子模 块电容电压波形图； [0092]图19为本发明一个实施例提供的一种多交流端口模块化多电平换流器及其控制 方法的另一个仿真中的直流线路有功功率、各交流线路潮流、线路电流、直流侧电流和装置 内子模块电容电压波形图。 具体实施方式 [0093]为使本发明的上述目的、特征和优点能够更加明显易懂，下面结合附图对 本发明的具体实施方式做详细的说明，显然所描述的实施例是本发明的一部分实施例，而 不是全部实施例。基于本发明中的实施例，本领域普通人员在没有做出创造性劳动前提下 所获得的所有其他实施例，都应当属于本发明的保护的范围。 [0094]在下面的描述中阐述了很多具体细节以便于充分理解本发明，但是本发明还可以 采用其他不同于在此描述的其它方式来实施，本领域技术人员可以在不违背本发明内涵的 情况下做类似推广，因此本发明不受下面公开的具体实施例的限制。 [0095]其次，此处所称的“一个实施例”或“实施例”是指可包含于本发明至少一个实现方 式中的特定特征、结构或特性。在本中不同地方出现的“在一个实施例中“并非均指 同一个实施例，也不是单独的或选择性的与其他实施例互相排斥的实施例。 [0096]本发明结合示意图进行详细描述，在详述本发明实施例时，为便于说明，表示器件 结构的剖面图会不依一般比例作局部放大，而且所述示意图只是示例，其在此不应限制本 发明保护的范围。此外，在实际制作中应包含长度、宽度及深度的三维空间尺寸。 [0097]同时在本发明的描述中，需要说明的是，术语中的“上、下、内和外”等指示的方位 或位置关系为基于附图所示的方位或位置关系，仅是为了便于描述本发明和简化描述，而 不是指示或暗示所指的装置或元件必须具有特定的方位、以特定的方位构造和操作，因此 不能理解为对本发明的限制。此外，术语“第一、第二或第三”仅用于描述目的，而不能理解 为指示或暗示相对重要性。 [0098]本发明中除非另有明确的规定和限定，术语“安装、相连、连接“应做广义理解，例 如:可以是固定连接、可拆卸连接或一体式连接；同样可以是机械连接、电连接或直接连接， 也可以通过中间媒介间接相连，也可以是两个元件内部的连通。对于本领域的普通技术人 员而言，可以具体情况理解上述术语在本发明中的具体含义。 [0099] 实施例1 [0100]交直流换流站的组网结构会对系统成本、供电可靠性、保护配置以及控制灵活性 等诸多方面产生影响。根据交直流换流站接线方式的不同，其组网结构可分为4类，如图1 (a) -(d)所示，分别为:单交流线路+单换流站+单直流母线，多交流线路+单换流站+单直流 母线，多交流线路+多换流站+多直流母线以及混合型。以下，将这4种结构分别简称为方案 a-d，现有供电网络的组网结构都可纳为方案a-c；方案a中由于直流电网能量由单一交流母 线供给，其供电可靠性一般，并且供电范围较小；方案b在方案a的基础上引入多条交流线 路，构成多端辐射型供电网络，各条交流线路间互为备用，提高了供电可靠性，但增加了备 用线路成本，同时存在电磁环网与无功环流问题;方案c中每条交流线路均通过换流站接入 直流母线，每条直流母线可分段运行，也可实现柔性互联运行，该方案具备极大的灵活性和 较高的供电可靠性，但成本较高；而方案d将多端交流线路直接馈入换流站，利用协调控制 手段实现线路潮流的灵活调节与线路间的功率互济，不但有效解决了方案b的无功环流问 题，而且在满足方案c柔性互联需求的同时，在成本以及功率密度上也远优于方案c。 [0101]因此，本发明在方案d的基础上提出一种适用于中高压交直流混合电网的多交流 端口型模块化多电平换流器及其控制方式，在实现多交流线路功能的基础上满足低成本、 高功率密度等应用需求。 [0102]参照图1〜9,为本发明的一个实施例，提供了一种多交流端口模块化多电平换流 器及其控制方法，包括： [0103]模块化多电平换流器；以及 [0104]与模块化多电平换流器串联的多端口柔性互联模块。 [0105]具体的，本发明提出一种适用于中高压交直流混合电网的具备主动潮流控制能力 的多端口模块化多电平换流器，在同一换流站站内实现了多端交流线路与中高压直流电网 的换流；多交流端口型模块化多电平换流器包括一个模块化多电平换流器(Modular Multilevel Converter ,MMC)以及与之串联的一个多端口柔性互联模块(Multi-port interconnector module,MIM)。 [0106] 其中，多交流端口型模块化多电平换流器中的MMC为中高压级电压源型换流器，具 备有功功率双向流动功能，有功功率既可以从交流侧流向直流侧，也可以从直流侧流向交 流侧。多交流端口型模块化多电平换流器中的MIM包括多个并联在公共连接母线上的第一 单相换流器，每个单相换流器的交流输出端口均与相应的交流线路相连，其中，公共连接母 线为中低压直流母线，与之相连的公共连接电容为其提供电压支撑;通过改变第一单相换 流器输出电压中交流分量的幅值与相位，可主动实现与之相连的交流线路潮流的灵活调 节。以下将与交流线路串联的第一单相换流器输出电压中的交流分量称为串联等效电压。 [0107] 进一步的，如图3所示,MMC子模块拓扑可选用半桥型子模块拓扑、全桥型子模块拓 扑、箝位型双子模块拓扑，或者采用其他可行结构以及多种结构混联的拓扑。 [0108] 更进一步的,ΜΙΜ按照是否包含第二单相换流器以及包含的第二单相换流器与MMC 上、下桥臂的接线方式的不同，可分为三种方案，分别如图4、5、6所示;该三种方案均可实现 多交流线路与直流电网间的柔性互联;具体的，在方案1中,ΜΙΜ不包含第二单相换流器,MMC 的上、下桥臂的交流输出端口分别与ΜΙΜ的公共直流母线的正、负极相连，通过调节与基准 线路相连的第一单相变换器的输出电压来维持ΜΙΜ能量的平衡，从而保证公共直流母线电 压的稳定;在方案2中，ΜΙΜ中包含一个与第一单相换流器同样并联在公共直流母线两端的 第二单相换流器,MMC的交流端口与第二单相换流器的交流输出端口相连,除了采用方案1 中的方法还可通过调节第二单相换流器的交流输出电压的幅值与相位，实现ΜΙΜ吸收与发 出有功功率的平衡;在方案3中，ΜΙΜ包含与交流线路数量匹配的第一单相换流器以及两个 第二单相换流器，它们均并联在公共直流母线两端，两个第二单相换流器的交流输出端口 分别与MMC的上、下桥臂的交流输出端口相连,在该方案下不仅可以通过采用方案1中的方 法或者调节第二单相换流器中输出电压中交流分量的幅值与相位，还可利用MMC桥臂上的 环流与第二单相换流器中的直流分量进行功率交换，从而实现ΜΙΜ的能量平衡以维持公共 直流母线电压的稳定，进而保证整个系统安全稳定的运行。 [0109] 其中，第一单相变流器和第二单相变流器均为电压源型单相变流器;ΜΙΜ中的第一 单相变流器或者第二单相变流器的拓扑可以是两电平半桥型变流器,也可以是三电平半桥 型变流器，或者其他可实现功率双向流动的单相桥型变流器。 [0110]另外，本发明提供一种应用于多交流端口模块化多电平换流器的控制方法,包括: 交流线路潮流控制、模块化多电平换流器控制和公共直流母线电压平衡控制。 [0111]具体的，多交流端口型模块化多电平换流器通过多端柔性互联模块和MMC的协同 控制，实现了多条交流线路与直流电网的柔性互联，同时可灵活调节多条线路上的潮流分 布以满足直流侧负载的用电需求;当多段柔性互联模块互联了η条交流线路时，根据系统潮 流控制的需求，需对各条交流线路上的潮流Pi〜Ρη和5〜Qn以及直流侧负载功率Pl进行控 制，但考虑到线路损耗和器件损耗等因素，其中一条交流线路的有功功率将通过系统的能 量平衡自动调节，因此仅需对该线路上的无功功率进行控制；下面,将上述交流线路称为交 流线路1,其他交流线路分别称为交流线路k(k = 2,. . . ,η)。 [0112]在多端口模块化多电平换流器的控制中，锁相环锁定的三相交流分量为定无功功 率控制的交流线路1的三相节点电压，通过实时输出的电网电压的相位，将三相交流a-b-c 坐标系下的电压电流通过Park变换转换至d-q坐标系中进行有功无功分量的解耦控制。 [0113] 更加具体的，对上述的交流线路潮流控制、MMC控制和公共连接母线电压平衡控制 这三部分控制分别讲述： [0114] (1)交流线路潮流控制的控制目标为交流线路1的无功功率达到参考值0：、交流 线路k的有功功率达到参考值r以及交流线路k的无功功率达到参考值0；；针对线路潮流 控制，以交流线路1为基准，列写线路1节点电压V]j到线路k的节点电压ν%.的动态方程并将 其转换至d-q坐标系下可得到如下方程： Lk + 4/4=AUcl*d -匕d + % + ①£*&amp; + Λ -γ- + /iMl -3卬 1g r 力'或 [0115] dlkc!怎 4-^+ΛΛ = △ &amp;网—几+ 〃- + 4若+儿用+叫儿 、 VX＞ £*L-t L [0116]其中，匕小丫山松1^a1^、1Μ、1山、11«1、11«1分别为线路1与线路卜节点电压电流的＜1”轴 分量,小人小风分别为线路1与线路1＜上的电感与等效电阻，3表示电网角频率，Αν*、A U°ikd为等效电压AUcikj = Uci「Uckj的d-q轴分量,Α”为与交流线路1相连的第一单相变流器 输出电压中的交流成分,u°kj为与交流线路k相连的第一单相变流器输出电压中的交流成 CK J 分，（j=a,b,c）。 [0117]其中，线路潮流控制在d-q坐标系下进行，其输出为AUdkd和AUdkd，经Park逆变换 后可得线路1与线路k间第一换流器的三相等效电压差AUcikj。由于上式存在LidIiJdt+ 1凡、%（11山/讹+1山人、1^”（1/讹+h（^、11^11„/讹+41^微分环节，若将其纳入潮流控制环的 前馈扰动消除环节中，会一定程度的降低控制环的性能。因此，在设计控制环时将该微分项 忽略，利用PI控制器对线路k上的电流进行闭环控制，具体控制方程如下所示： [0118] = kpkQ kd - D + ^ik / - + 匕d —嗑—8LJkq + ©4，% =%（/L - Q ） + kik j （Cg - Λ, + [0119]其中，上标*代表各自分量的参考值,和分别为线路k的潮流控制环PI调节器 的比例与积分系数,丫、％山川1^为前馈项，提高潮流控制控制环对线路节点电压的抗干 扰能力，a LJ、a L Jq、ω LJkd、a LJkq为前馈解耦项，可实现d轴有功功率控制与q轴无功 功率控制的解耦。 [0120]由于线路目标潮流与线路节点电压、电流之间存在下列关系，因此交流线路潮流 控制环的线路电流的d轴分量参考值几和q轴分量参考值可根据交流线路k的有功功率 参考值耳和无功功率参考值。；计算得到： 兄* = /（/浸4）=j（匕儿+匕花） [0121] ¦ * ； Q； = fU；d，I；q） = [0122] ⑵多交流端口型模块化多电平换流器中的MMC的控制目标为MMC直流侧的定功率 控制达到参考值月和交流线路1的定无功功率控制达到参考值0：；按照MMC控制环节的不 同，MMC控制可由外环有功功率控制、外环无功功率控制、内环电流控制、电容电压平衡控 制、二倍频环流抑制和调制这六部分组成，当采用上述方案3中的拓扑结构时,MMC控制还包 含基频环流注入控制;本发明中多交流端口型模块化多电平换流器的三种方案中的电容电 压平衡控制以及二倍频环流抑制功能与常规MMC一致。 [0123]若多交流端口型模块化多电平换流器中的MIM中仅包含一个第二单相换流器，即 考虑上述方案2的拓扑结构;针对MMC控制，建立其MMC交流端口与上、下桥臂的电流的数学 模型,并进行Park将其转换至与交流线路1同步旋转的d-q坐标系下可得： [0124] 票+ &amp;/向=U向一Δ/+οΕ。/。。 d/ 常+/〃=%-△/却 [0125]其中，%、*、1。（1、尢分别为皿（：交流端口处的电压11。押电流q的（1^轴分量，Δ νr AVq分别为MMC等效电压AVj= （%时?/2的（1”轴分量,%、%分别为皿（；的上、下桥臂 等效电压;％、风分别为MMC桥臂电感L和桥臂电阻R的一半，（j=a,b,c）。 [0126]多交流端口型模块化多电平换流器中的MMC电流内环控制在d-q坐标系下进行，其 输出为A Vd和Δ Vq,经Park逆变换后可得MMC等效电压Δ 由于上式存在与由京/讹+坛匕和 LodI。q/dt+RoI。q微分环节,为保证控制环的性能将其忽略；利用PI控制器对MMC交流侧电流 兀进行闭环控制，具体控制方程如下所示： =%（&amp; -%）+却&amp; +砒。&amp; [0127] &lt; ； [A 匕=%（&amp; - 〃）+ W J （Q —覆）山 + 豳一山蜀 [0128]其中，上标*代表各自分量的参考值,kp。和分别为MMC电流内环控制中PI调节器 的比例和积分调节系数,U。d、U。q为MMC交流端口电压扰动抑制项，用于增强控制环的抗干扰 能力，371疝3%晨为前馈解耦项，可实现d轴有功功率控制与q轴无功功率控制的解耦。 [0129]若多交流端口型模块化多电平换流器中的MIM中不包含第二单相变换器或包含两 个第二单相变换器时，即上述的方案1和方案3,则上述MMC控制中MMC交流端口电压u°j等效 为MIM公共连接母线上的等效交流电压,MMC交流端口处的电流兀为各条交流线路的电流之 和。 i-l [0130]由于PLL锁相环以交流线路1上的节点电压为基准，则MMC的有功电流参考值勤由 直流侧负载白和无功电流参考值〃计算给定,而/以则由交流线路2〜η上的q轴电流参考值 /〜0和交流线路1的无功功率参考值。：共同给出，其计算表达式如下： '_2M-£X 4 [0131] 卡=2 =3匕/「匕兀）=彳嗑兀 [0132] 若多交流端口型模块化多电平换流器中的ΜΙΜ采用方案2的结构，该方案中的MMC 调制与常规MMC调制一致,MMC的上桥臂的调制波和下桥臂的调制波均包括由MMC内环 电流控制产生的交流端口处的等效电压AVj、MMC直流侧电压的一半3/2以及用于MMC的桥 臂上二倍频环流抑制的二倍频交流电压巴,具体计算表达式如下所示： [0133] * _ 〃 Λ 〃方=;--△匕一风物 * — % A 以g=亏+△匕一吃烟 [0134]若多交流端口型模块化多电平换流器中的MIM采用方案1的结构，该方案中由于 MMC上、下桥臂分别与MIM的正负极直流母线相连，因此这两个桥臂的交流输出端口处存在 着公共直流母线电压Vunk的直流偏置，将其均分到MMC上、下桥臂的调制中，即： zJ - Ude -曦_ _ A _u upj — 9 “颂 [0135] J — U&amp;- %”* , A v “ uPj ----2--- “物 [0136]若多交流端口型模块化多电平换流器中的MIM采用方案3的结构,该方案中存在两 个第二单相换流器,若两个第二单相换流器输出电压的交直流分量完全一致，则该方案可 转变成方案2；若两个第二单相换流器输出电压的交流分量为0,并且其中一个直流分量为 0 ,另一个直流分量为Link，则该方案可转变成方案1 ；此外，方案3中的两个单相换流器输出 电压中的交直流分量可根据能量平衡的需求在一定范围内自由变化;考虑到方案3中的控 制自由度较高，则控制两个单相换流器的直流分量一致,为使得MMC桥臂上的环流能对MIM 的能量平衡起到调节作用，两个单相换流器输出电压的交流分量不一致，与MMC上桥臂相连 的第二单相换流器的输出电压的交流分量为Ucsmij，与MMC下桥臂相连的第二单相换流器的 输出电压的交流分量为气间；为使得MMC上、下桥臂的能量平衡，将其纳入MMC的桥臂调制参 考波中，计算表达式如下所示： [0137] 评;=与—A、一评j —知物一鸣 源;=~~ +八,+源的2' 一 %诙一评了 [0138] 其中为用于控制MIM能量平衡以及MMC上、下桥臂能量平衡而在MMC桥臂中注 入的基频环流；由于MIM中两个第二单相换流器输出电压Lsmii和Ucsm2i的不一致，该分量会 影响原有MMC上、下桥臂能量的平衡，因此注入的基频环流不仅会影响MIM吸收的能量，会对 MMC上、下桥臂起到能量搬迁的作用；综上,该基频环流注入控制策略与第三部分相应的MIM 平衡控制策略协同作用，共同使得MIM和MMC上、下桥臂的能量平衡，从而维持系统的稳定。 [0139] 若多交流端口型模块化多电平换流器中的MIM采用方案3的结构,为保证MIM和MMC 装置的能量平衡，需注入一定的基频环流。由于MIM中两个第二单相换流器输出电压Ucsmij和 U°sm2i相对于MMC的交流端口等效电压A %较小,希望注入的环流尽可能扩大该多端口型模 块化多电平换流器对于交流线路潮流的调节范围，因此该环流的相位滞后于MMC等效电压 /2,以使得其对MMC原始上、下桥臂能量搬迁的作用尽可能小，此时该环流在MMC桥臂电感 上产生的电压与MMC等效电压A Vj同相位;对MMC等效电压A Vj进行Park变换将其转换至与 线路1同步旋转的d-q坐标系下，利用d-q变换之后d-q轴分量可求得MMC等效电压Δ Vj的相 位,在控制中利用MMC内环电流控制输出的MMC等效电压A%参考值进行计算,具体计算表达 式如下: [0140] O=arcsin( [0141]其中，Αν；、Αν；分别为MMC内环电流控制输出的三相MMC等效电压参考值八力转换 至d轴和q轴分量的参考值；由于注入的基频环流滞后于MMC等效电压参考值/2,该环流分 量在MMC等效电压参考值A,定向的d-q同步旋转坐标系中只存在q轴分量，此时其对上、下 桥臂的能量搬迁较小。 [0142]综上，上述针对多交流端口型模块化多电平换流器中的三种方案下的MMC控制以 及调制分别提出了一种解决思路，当然也可采用其他可行的控制和调制方案；如对于方案 3,与MMC相连的第二单相换流器可采用二倍频调制方式,与之对应的在MMC桥臂上注入二倍 频环流使得MIM能量平衡,在此基础上注入基频环流使得MMC上、下桥臂能量的平衡。 [0143] ⑶公共直流母线电压平衡控制环的控制目标为公共直流母线电压稳定在参考值 峨；公共直流母线电压平衡控制环的控制在a-b-c坐标系下进行，其输出为用于进行MIM能 量平衡的第一单相换流器或者第二单相换流器的参考电压，利用比例积分控制器对a-b-c 三相的公共直流母线电压进行控制。 [0144]若多交流端口型模块化多电平换流器中的MIM采用方案1的拓扑,该方案不包含第 二单相换流器，公共直流母线电压平衡控制环的输出为与线路1相连的第一单相换流器的 参考电压4，为充分发挥该单相换流器对于MIM平衡控制的作用，其j相交流电压参考值 ”,与线路1的j相电流k同向，控制方程如下，（j=a,b,c）： 以=[%（嚷-+房（匕-%麻）阳叽+© [0145] Uel Jb =[左卬（%）1 -嗑*。）+ link ~ + %力 Ucifi = [%（匕**- 九和）+ j1尢1（%1tl %Ac）沟 [0146]其中，V]inka、Vlinkb、Vlinkc为三相公共直流母线电压，三种方案下采用的“1、 比*、汉1均为前馈的三相参考电压，可按照本发明下述的任意一种第一单相换流器等效电 压分配方式计算给定,kpi、kji分别为该方案中的比例积分控制器的比例环节增益系数和积 分环节增益系数。 [0147]若多交流端口型模块化多电平换流器中的MIM采用方案1的拓扑，在交流线路k的 潮流控制环输出得到j相参考电压以及公共直流母线平衡控制环输出交流线路1相连 的第一单相换流器的j相交流参考电压”;心后，与各条交流线路相连的第一单相换流器的 参考电压为： [0148] ' * ' \ ' U西=Q应+曦me,必 ［0149］其中，U］为与交流线路1相连的第一单相换流器j相调制参考电压，为与交流 线路k相连的第一单相换流器j相调制参考电压,、。丽皿也为第一单相换流器和第二单相换 流器共有的直流分量参考值，该参考值大于零且小于公共直流母线电压或… ［0150］若多交流端口型模块化多电平换流器中的MIM采用方案2的拓扑,该方案包含一个 第二单相换流器,公共直流母线电压平衡控制环的输出为与MMC交流端口相连的第二单相 换流器的j相参考电压”二时，为充分发挥该第二单相换流器对于MIM的能量调节作用，其j相 交流电压参考值以句与MMC交流端口的j相电流i°j反向，控制方程如下，(j=a,b,c)： [0151] “L =氏2化+ J先2K* Ucst»b =%户2（% - %ί＞） +［尢2（% -嗫她）威卜㈠岫） 二=氏2化1* —嗑*,） + ］先2化Li — %和）威卜（一3） ［0152］其中，kp2、kj2分别为该方案中的比例积分控制器的比例环节增益系数和积分环节 增益系数，与上述方案1的公共直流母线电压平衡控制不同，方案2中的前馈项为0。 ［0153］若多交流端口型模块化多电平换流器中的MIM采用方案2的拓扑，在交流线路k的 潮流控制环控制得到j相参考电压△况;出以及公共直流母线平衡控制环输出与MMC交流端口 相连的第二单相换流器的j相交流参考电压”;必后，各第一单相换流器和第二单相换流器 的调制参考电压为： [0154] j —汉匚]j + camman yde u；的 =工点」一+匕…叫加 U* =u + * csmj 心叫 common ydc ［0155］若多交流端口型模块化多电平换流器中的MIM采用方案3的拓扑,该方案包含两个 第二单相换流器，在上述部分已经阐述该第二单相换流器的输出电压不同对于MMC控制以 及调制的影响，此外,ΜΙΜ中公共直流母线电压平衡控制也会因此发生一定的改变。 ［0156］若多交流端口型模块化多电平换流器中的ΜΙΜ采用方案3的拓扑,当交流线路的潮 流处在一定范围内时,ΜΙΜ装置能够通过第一、第二单相换流器与各交流线路电压间的能量 交互实现能量平衡时，控制与MMC上、下桥臂相连的两个第二单相换流器的输出电压一致, 其各相相位与各条交流线路电流之和的相位£力一致；当交流线路的潮流超过一定范围 时,ΜΙΜ装置无法通过第一单相换流器和第二单相换流器与各交流线路电压间的能量交互 实现能量平衡，此时需要在MMC桥臂上采用基频环流注入的方式使得ΜΙΜ能量平衡，公共直 流母线电压平衡控制的输出为与MMC下桥臂相连的第二单相换流器的交流参考电压二2,， 为充分发挥注入的基频环流对于ΜΙΜ的能量调节作用，控制第二单相换流器的j相交流电压 参考值匕金与注入的基频环流的j相电流irj同向，控制方程如下，(j = a,b,c)： ［0157］ “csm2a =［左户3 （%* 一 ）+ J ◎ （%* 一 嗑M ）力］ “csm2b =1^ρ3（匕Mk -匕） + J 尢3（匕M* 一 ）附%rt1 Ucsm1c = t^p3 （ ^link ~ ^linic + J 匕3 （ %* 一 嗑ic ）力］%k [0158]其中，斗3、&amp;3分别为该方案中的比例积分控制器的比例环节增益系数和积分环节 增益系数。 [0159]若多交流端口型模块化多电平换流器中的MIM采用方案3的拓扑，在交流线路k的 潮流控制环控制得到j相参考电压公匕均以及公共直流母线平衡控制环输出与MMC交流端口 相连的第二单相换流器的j相交流参考电压以，四后，各第一单相换流器和第二单相换流器 的调制参考电压为： C\ J - clj + ,de r U函=«d - A%% + Κ.ί1ΠΙΠΙί,η,^ [0160] &lt; * * 。皿1/ =切的叮+ 匕。mm。4 。二阳=心哈+匕™m°“0c [0161] 其中，匕叫为与MMC上桥臂相连的第二单相换流器的三相参考电压j相交流参考电 压，可按照本发明下述开环计算方式给定。 [0162]上述针对多交流端口型模块化多电平换流器中的MIM三种方案的公共直流母线平 衡控制方案分别提出了一种解决思路，当然也可采用其他可行平衡控制方案。 [0163] 本发明根据上述三种方案控制与调制策略的基本思想，提供了三种方案下多交流 端口型模块化多电平换流器的第一单相换流器和第二单相换流器的交流等效电压的多种 分配方式;根据第二方面对于三种方案控制和调制思想的阐述，各第一单相换流器和第二 单相换流器的参考电压中的直流分量一致，均为V。。1mMl μ [0164]若多交流端口型模块化多电平换流器中的MIM采用方案1的拓扑，即互联模块中不 包含第二单相换流器，各第一单相换流器分别跟与之相连的交流线路发生能量交互，为使 得MIM的能量平衡,第一单相换流器输出电压的等效交流分量与线路电流必须满足下列关 系： ----* ---* ---► Uc\ -Uck 二 4=23 …/) [0165] ，五―匕凶9 = 0 、 *=1 3 [0166]其中，交流线路1的节点电压为整个控制系统的基准电压，线路1为定无功功率交 流线路，万5为与交流线路1相连的第一单相换流器输出电压交流分量的矢量表达，万小为 多交流端口型模块化多电平换流器的与交流线路k相连的第一单相换流器输出电压交流分 量的矢量表达，U处为交流线路k进行目标潮流控制时，所需的交流线路1和交流线路k之间 的串联等效电压交流分量的矢量表达，元为线路k上的交流电流矢量的共辗表达,VIM为多 交流端口型模块化多电平换流器的MIM中的公共直流母线间的电压大小，为多交流端口 型模块化多电平换流器的直流侧流出MMC的电流,n为多交流端口型模块化多电平换流器的 交流侧互联的交流线路数量。 [0167] 若多交流端口型模块化多电平换流器中的ΜΙΜ采用方案1的拓扑，其ΜΙΜ中第一单 相换流器的交流等效电压的多种分配方式为任何一组满足上述方程组的解 [0168] 进一步的，各第一单相换流器等效电压交流分量的最优分配方法为万s的选取满 足各第一单相变流器输出电压的交流分量的幅值最小，即max｛方小(左=1,2,…,外¦｝，从而 获得最大的交流线路潮流的调节范围。 [0169]若多交流端口型模块化多电平换流器中的MIM采用方案2的拓扑,即互联模块中包 含一个第二单相换流器。各第一单相换流器、第二单相换流器线路电流必须满足下列基本 条件以实现线路潮流的稳定控制： ,-* —k —t Ud —Uck = U (k = 2,3,...,n) Re〉:Uck*^k — Uem)—0 [0171]其中，万「,”为与MMC相连的第二单相换流器等效电压交流分量的矢量表达，了：为 流入MMC交流端口的交流电流矢量的共辗表达。 [0172]若多交流端口型模块化多电平换流器中的MIM采用方案2的拓扑,ΜΙΜ中第一单相 换流器的等效电压交流分量的多种分配方式为任何一组满足上述方程组的解 ｛U&amp;(&amp; =1,2,...,凡),U的｝ ο [0173] 更进一步的，与线路1相连的第一单相换流器等效电压交流分量的一种分配方式 为选取沅其他第一单相换流器的交流输出电压参考值则通过公式 水分别计算得到，该方法的特点在于其计算简单。各第一单相换流器等效电 压交流分量的最优分配方法为打4的选取满足各第一单相变流器和第二单相换流器输出电 压的交流分量的幅值最小，即max ｛¦ίΛ* (左=L 最小，从而获得最大的交流 线路潮流的调节范围。 [0174]若多交流端口型模块化多电平换流器中的ΜΙΜ采用方案3的拓扑,即互联模块中包 含两个第二单相换流器，各第一单相换流器、第二单相换流器线路电流以及注入的基频环 流必须满足下列基本条件以实现线路潮流的稳定控制： ------&gt; -----F ----» Um =2,3,…，界) [0176] 其中，行海、沅顼2为与MMC上、下桥臂相连的第二单相换流器等效电压交流分量 的矢量表达，元为各交流线路电流矢量和的共辗表达，71为注入的基频环流的共辗表达。 [0177]若多交流端口型模块化多电平换流器中的MIM采用方案3的拓扑,ΜΙΜ中第一单相 换流器的等效电压交流分量的多种分配方式为任何一组满足上述方程组的解 {U °* （左=1,2,…, U csm 2,/ eir } ο [0178] 进一步的，各第一单相换流器等效电压交流分量的一种分配方式为选取 t/d ，特点在于其简便性。 [0179]更进一步的，各第一单相换流器和第二单相换流器的等效电压交流分量的选取与 注入环流的选取密切相关，为充分保证整个装置对于交流线路潮流的调节能力和MMC上、下 桥臂的能量平衡，等效电压最优分配方法为万”的选取满足各第一单相变流器和第二单相 换流器输出电压的交流分量幅值的最大值最小，即 max {仇Μ左= 1,2,…,叫,¦沅博¦万岫2¦}最小,在此基础上使得注入的环流分量尽可能小。 [0180]综上，针对多交流端口型模块化多电平换流器的三种方案： [0181]优选的，多交流端口型模块化多电平换流器的MIM中的各第一单相变流器和第二 单相换流器的输出电压的直流成分相同，也可使得各自的直流成分不完全相同并采用相应 的控制以及调制策略； [0182] 优选的，各单相变流器的输出电压的直流成分可以是公共直流母线电压的一半， 目的是为了充分发挥其交流分量的调制能力，也可采用其他大于零小于公共直流母线电压 大小的任意直流分量； [0183]优选的，多交流端口型模块化多电平换流器的方案3中的第二单相换流器输出电 压完全一致时，方案3可等效于方案2的拓扑结构；多交流端口型模块化多电平换流器的方 案3中，与MMC上桥臂相连的第二单相换流器输出电压中的交流分量定为零、直流分量定为 公共直流母线电压以及与MMC下桥臂相连的第二单相换流器输出电压中的交、直流分量均 定为零时,方案3可等效于方案1的拓扑结构。 [0184]本发明还提供了一种采用多交流型端口型模块化多电平换流器进行多端交流线 路和中高压直流电网间的柔性互联系统，如图7、8所示,多交流线路型柔性互联系统的核心 设备为多交流端口型模块化多电平换流器，系统还包括交流线路、直流线路、交流负载、直 流负载和储能设备等。 [0185]多交流型端口型模块化多电平换流器安装于多条交流线路和中高压直流电网的 汇集处，各条交流线路和本发明中的MIM相连，中高压直流电网与本发明中的MMC直流侧相 连;各条交流线路可接入交流负载，可经过AC/DC变换器接入直流负载或者储能设备，可以 经降压变压器接入低压交流系统,还可以经升压变压器接入高压交流系统；中高压直流电 网可接入大容量光伏相连，也可经过降压变换器接入低压直流电网，还可经过升压变换器 接入高压直流输电系统。 [0186]优选的，多交流线路型柔性互联系统可以包含一个多交流端口型模块化多电平换 流器，如图7所示;也可包含多个多交流端口型模块化多电平换流器，如图8所示；当多交流 线路型柔性互联系统包括两个及以上的多交流端口型模块化多电平换流器时，各个多交流 端口型模块化多电平换流器安装于各自区域中多条交流线路和中高压直流电网的汇集处, 通过MMC直流侧中高压直流线路利用DC/DC变换器将多个区域互联，形成拓扑结构更复杂、 供电可靠性更高的环状或者网状结构。 [0187]进一步的，本发明提供一种多交流端口型模块化多电平换流器中单相换流器的过 压保护方法，具体方法如图9所示，该保护方法通过并联在多交流端口型模块化多电平换流 器中的单相变流器的保护装置实现，保护装置包括一个金属氧化物限压器(Metal-oxide Varistors,MOV)和一个与之并联的晶闸管旁路开关，晶闸管旁路开关由静态电阻、阻容回 路、反并联晶闸管三者并联后再与一个饱和电抗器串联组成。 [0188] MOV可将单相换流器的输出电压限制在安全保护范围内，当第一单相换流器的输 出电压超过安全稳定运行范围时，晶闸管旁路开关通过将第一单相变流器相应的开关旁 路，实现过压保护。 [0189]更进一步的，本发明提供一种多交流端口型模块化多电平换流器的启动方法，多 交流端口型模块化多电平换流器的启动方法可以分别四个阶段： [0190]第一阶段为不控充电阶段，交流线路1串联限流电阻并网，所有开关闭锁，交流电 网电流经各开关的续流二极管对多交流端口型模块化多电平换流器内的电容进行充电； [0191]第二阶段为受控充电阶段，在第一阶段不控充电完成后，各电容电压尚未达到参 考值，通过开关轮流投切的方式使得回路中的充电电容个数一定，将多交流端口型模块化 多电平换流器内电容电压进一步提升； [0192]第三阶段为斜坡升压阶段，在第二阶段充电结束后，投入电压控制环并给定采用 斜坡变化的参考电压，将各电容电压充电至参考值;电压控制环MMC常用的电压控制外环以 及本发明第二方面的公共直流母线电压控制环，当多交流端口型模块化多电平换流器内电 容电压充电完成时将MMC的电压控制外环切换至本发明第二方面的定功率控制外环； [0193]第四阶段为交流线路投入阶段，在上述三个阶段充电完成后，其余各条交流线路 配合各自的线路电流控制环和与之相连的第一单相换流器的参考给定输出实现软投入。 [0194]更进一步的，本发明提供一种适用于多交流端口型模块化多电平换流器的控制系 统，多交流端口型模块化多电平换流器的控制系统可以采用集中式控制架构，也可以采用 分布式控制架构或者混合式架构；集中式控制架构，即交流线路潮流控制、MMC内相关控制 和公共直流母线电压平衡控制均在同一个控制器内部实现，其特点在于结构简单、设备少; 分布式控制架构，则将各个控制环节进行分类，分别置于多个同一级别的控制器中，如各交 流潮流控制、MMC内相关控制和公共直流母线电压平衡控制分别处在三个不同的控制器中， 这些同级控制器之间独立运行，其特点在于配置灵活、计算快速;此外，还可采用集中式控 制和分布式控制相结合的分层式混合控制架构，将系统内部各个控制根据一定的逻辑关系 置于多个不同级别的控制器中，如各交流线路潮流控制和MMC功率外环控制以及电流内环 控制处在一级控制器中，而第一单相换流器的参考电压计算和公共直流母线电压平衡控制 等则分别处于多个二级控制器中，不同级别的控制器间存在信息通讯，而同级别的控制器 间不存在信息通讯。控制器为具备实现控制能力的硬件设备，如基于现场可编程逻辑门阵 列芯片的控制器和基于数字信号处理芯片的控制器等。 [0195]总的来说，参照图4〜6,本发明提供了一种适用于中高压交直流混合电网的具备 主动潮流控制能力的多交流端口型模块化多电平换流器，多交流端口型模块化多电平换流 器包括模块化多电平换流器(MMC)以及与之相连的多端口柔性互联模块(MIM)。 [0196]模块化多电平换流器为中高压级电压源型换流器，其采用模块化级联的形式，在 制造难度、开关损耗、波形质量等方面具备显著优势;此外，它具备有功功率的双向流动功 能，可以从直流系统中吸收有功，也可以为直流系统提供有功。多端口柔性互联模块包括多 个彼此互相并联在同一公共直流母线上的第一单相变流器，第一单相变流器的输出端口与 交流线路相连;通过调节与线路相连的第一单相换流器输出电压中交流分量的幅值相位， 可实现交流线路潮流的主动控制。此外，根据多端口柔性互联模块与模块化多电平换流器 连接方式的不同,如图4〜6所示,多端口柔性互联模块还可以包括一个或者两个与第一单 相换流器并联的第二单相换流器。当多端柔性互联模块不包含第二单相换流器时，模块化 多电平换流器上、下桥臂的交流端口分别与多端柔性互联模块中的公共直流母线的正、负 极相连，如图4所示；当多端柔性互联模块包含一个第二单相换流器时，所包含的第二单相 换流器的输出端口与模块化多电平换流器的交流输出端口相连，如图5所示；当多端柔性互 联模块包含两个第二单相换流器时，所包含的两个第二单相换流器的输出端口分别与模块 化多电平换流器上、下桥臂的交流端口相连，如图6所示;在图4所示的拓扑结构中，通过改 变与交流线路1相连的第一单相换流器输出电压中的交流分量以及模块化多电平换流器的 调制策略实现多端柔性互联模块的能量平衡;在图5和图6所示的拓扑结构中，通过改变第 二单相换流器输出电压中的交流分量以及模块化多电平换流器的调制策略实现系统的稳 定。 [0197]本发明创新性的在模块化多电平换流器的基础上引入多端口柔性互联模块 (MIM),提供了多个交流线路馈入端口，实现多交流线路和直流电网在同一个换流站的站内 互联，通过调节与交流线路相连的第一单相换流器的输出电压交流分量的幅值和相位，可 实现对于交流线路潮流的主动控制;本发明和现有常用的交直流换流站组网结构相比，即 图2中的方案a-c,采用无变压器式结构，采用多条交流线路同时馈入的方式以及交直流电 网互联的方式，在功率密度、换流站体积、建设成本、供电可靠性、供电系统运行效率等方面 具备巨大优势;本发明中的利用多端柔性互联模块实现多交流线路的柔性互联，具备模块 化的特点，通过增加互联模块中第一单相换流器的数量，可经济、高效、方便的实现交流线 路的端口拓展。 [0198] 实施例2 [0199] 参照图10〜19为本发明另一个实施例，为对本方法中采用的技术效果加以验证说 明，本实施例结合具体两种实施例对多交流端口型模块化多电平换流器进行具体说明并针 对上述实施例进行仿真，以对潮流控制和能量平衡的有效性和可行性进行验证，以科学论 证的手段验证本方法所具有的真实效果。 [0200]结合具体两种实施例对多交流端口型模块化多电平换流器进行具体说明： [0201] ⑴在第一个实施例中，如图10所示，本发明使用多交流端口型模块化多电平换流 器来实现两条交流线路与中高压直流电网互联;交流端口型模块化多电平换流器包括采用 两电平半桥型换流器的模块化多电平换流器和与之相连的多端口柔性互联模块。在该实施 例中，多端口柔性互联模块包括两个第一单相换流器和一个第二单相换流器，它们均为两 电平半桥型逆变器且彼此共享同一公共直流母线;两个第一单相换流器分别与两条交流线 路相连，而第二单相换流器与模块化多电平换流器的交流端口相连;通过调节与线路相连 的第一单相换流器的交流输出电压和与模块化多电平换流器相连的第二单相换流器的交 流输出电压，在实现多端柔性互联模块内部能量平衡的基础上实现交流线路上潮流的主动 控制。 [0202]对于图10所示的多交流端口型模块化多电平换流器来实现的双交流线路互联系 统，两端口型模块化多电平换流器能量平衡的表现为两端柔性互联装置中公共直流母线间 电容电压以及模块化多电平换流器中电容电压的稳定，即要求流入上述装置的有功功率恒 为零，即： 1—» -* —» f* ―► Re«/（i7Cl + ί7c2 — Ucxm = 0 Uο*ϊο -Udc*idc -0 [0204]其中，上述方程中的第一行表示流入多端柔性互联模块的有功功率为零,方程的 第二行表示流入模块化多电平换流器的有功功率为零；万〃、万c分别为与交流线路1、2相 连的第一单相换流器输出电压中交流分量的矢量表达；亍；、7；分别为交流线路1、2上的交 流电流矢量的共猴表达；万*为与模块化多电平换流器相连的第二单相换流器输出电压 的交流分量的矢量表达；云为流入模块化多电平换流器的交流端口的交流电流矢量的共辗 表达;明。为模块化多电平换流器的直流侧电压；Q为模块化多电平换流器的直流侧流出的 电流;通过调节守皿的幅值跟相位以及模块化多电平换流器的子模块的调制度，使得上述 方程成立，即实现该实施例中的两端口型模块化多电平换流器各部分装置的能量平衡。 [0205] ⑵在第一个实施例中，如图16所示，使用多交流端口型模块化多电平换流器来实 现三条交流线路与中高压直流电网互联;交流端口型模块化多电平换流器包括采用两电平 半桥型换流器的模块化多电平换流器和与之相连的多端口柔性互联模块。在该实施例中， 多端口柔性互联模块包括三个第一单相换流器和一个第二单相换流器，它们均为两电平半 桥型逆变器且彼此共享同一公共直流母线；三个第一单相换流器分别与三条交流线路相 连，而第二单相换流器与模块化多电平换流器的交流端口相连。该实施例中，实现多端口柔 性交流互联装置的内部能量平衡的原理与⑴所说的相同。 [0206] 以下采用MATLAB/Simulink软件针对上述实施例进行仿真，以对潮流控制和能量 平衡的有效性和可行性进行验证,仿真参数如表1所示。 [0207]表1：仿真参数表。 参数 数值 线路额定视在功率 Sn=1MV . A 线路1电压 γ,,. =lO.5kV,0=O°llme.rms ' 1 线路1阻抗 Li = 35mH,R] = 0.55Q 线路2电压 V91. =10.5kV,9 =-3° 线路2阻抗 L2 = 35mH,R2 = 0.55Q 线路3电压 =10.5kV,9 =-6°llme.rms ' 3 线路3阻抗 L3 = 35mH,R3 = 0.55Q MIM公共连接电容 C. . =4mF,V-। = 2500V link ' link MMC子模块电容 C = 2mF,Vc=1750V MMC子模块个数 12（单个桥臂） 开关频率 1kHz [0209]仿真实例一： [0210]在实施方案一中，由多交流端口型模块化多电平换流器进行两条交流线路与直流 电网互联的系统接线示意图如图10所示,相应的控制方法如图11所示；该两交流端口型模 块化多电平换流器包含三个半桥型换流器，其中与交流线路相连的两个半桥型变换流器通 过线路潮流控制控制线路2上的有功功率跟无功功率;与模块化多电平换流器相连的半桥 型换流器则通过公共直流母线电压控制保证公共连接电容电压的稳定;交流线路1上的无 功功率和模块化多电平换流器直流侧的功率能通过模块化多电平换流器的外环功率控制 进行调节。 [0211]在实施方案一中，仿真设定了四种不同的运行工况以验证多交流端口型模块化多 电平换流器的主动潮流控制的有效性;此外,考虑到计算的简便性，第一单相换流器的交流 输出电压采取平均分配的方式，即%ι=%η/2以下标幺值的基准值均为模块化多电平换流 器的额定视在功率Sn=2MV · A。 [0212] 表2：四种不同的运行工况实验参数表。 Ρ P . u . Qjp.u. P2/p.u. Q2/p.u. 工况1 0.8 0.3 0.4 0.2 工况2 0.3 -0.2 0.2 -0.2 工况3 -0.3 -0.1 -0.15 -0.2 工况4 -0.8 0.3 -0.4 0.3 [0214] 工况1中，直流线路重载运行，有功功率从交流侧流向直流侧，两条交流线路平均 分配有功功率;工况2中,直流线路轻载运行，有功功率从交流侧流向直流侧，线路2承担更 多的有功功率;工况3中，直流线路轻载运行，有功功率从直流侧流向交流侧,两条交流线路 平均分配有功功率;工况4中，中高压直流线路重载运行，有功功率从直流侧流向交流侧,线 路2吸收更多有功功率。 [0215]图12〜15分别为实施方案一中从工况一到工况四的仿真结果，每幅图包含8幅波 形图，按先后顺序依次为MMC直流侧有功功率Pl波形图,线路1有功功率Ρ1和无功功率5波形 图，线路2有功功率P2和无功功率Q?波形图，三相公共直流母线电压Vunk abc波形图三相MMC 子模块电容电压Vcapacitor abc波形图（MMC上桥臂），线路1三相电流i必卜波形图，线路2三相电 CdpdCl LO± d DC IdOC 流i2abe波形图和流出MMC的直流电流J波形图。 [0216]仿真波形结果表明，多交流端口型模块化多电平换流器在实施方案一中能在保证 系统稳定运行的同时，可实现交流线路潮流和MMC直流侧功率的主动控制。 [0217]仿真实例二： [0218]实施方案二中，由多交流端口型模块化多电平换流器进行三条交流线路与中高压 直流电网互联的系统接线示意图如图16所示，相应的控制方法如图17所示；该三交流端口 型模块化多电平换流器包含五个半桥型换流器，其中与交流线路相连的三个半桥型变换流 器通过线路潮流控制控制线路2、3上的有功功率跟无功功率;与模块化多电平换流器相连 的两个半桥型换流器则通过公共直流母线电压控制保证公共连接电容电压的稳定;交流线 路1上的无功功率和模块化多电平换流器直流侧的功率能通过模块化多电平换流器的外环 功率控制进行调节。 [0219]与上述实施方案不同，实施方案二中的第一单相换流器的交流输出电压的分配方 法采用本发明提及的最优分配方式:各单相换流器的交流输出电压幅值的最大值最小，即 max {a* （左=1,2,…，叫，讥焉}最小,在此基础上使得注入的环流分量尽可能小，由此得 到与线路1相连的第一单相换流器的交流输出电压参考值守。 [0220]在实施方案二中，设定的仿真工况如下：中高压直流线路重载运行,有功功率从交 流侧流向直流侧,三条交流线路平均分配有功功率；具体的,Pl = 0 . 45p. u. , Q] = 0.2p. u., P? =0.15p.u. ,Q2 = 0.2p.u. ,P3 = 0.15p.u. ,Q2 = 0.2p.u.；以上标幺值的基准值均为模块化多 电平换流器的额定视在功率Sn=3MV · A。 [0221]图18〜19为实施方案二的仿真结果，总共包含10幅波形图，按先后顺序依次为MMC 直流侧有功功率Pl波形图，线路1有功功率P]和无功功率波形图，线路2有功功率P2和无功 功率波形图，线路3有功功率P3和无功功率Q3波形图，三相公共直流母线电压Vlink abc波形 图，三相MMC子模块电容电压Vcapacitor abc波形图（《贬上桥臂），线路1三相电流i必卜波形图，线 路2三相电流i2abe波形图，线路3三相电流i3abe波形图和流出MMC的直流电流J波形图。 [0222]仿真波形结果表明，多交流端口型模块化多电平换流器在互联三条交流线路和中 高压直流线路的基础上，仍能在保证系统稳定运行的同时，实现交流线路潮流和MMC直流侧 功率的主动控制，同时表明多交流端口型模块化多电平换流器具备端口拓展的能力。 [0223]应说明的是，以上实施例仅用以说明本发明的技术方案而非限制，尽管参照较佳 实施例对本发明进行了详细说明，本领域的普通技术人员应当理解，可以对本发明的技术 方案进行修改或者等同替换，而不脱离本发明技术方案的精神和范围，其均应涵盖在本发 明的权利要求范围当中。 [EN CN113285620A]: A multi-AC port modular multi-level converter and its control method technical field [0001] The present invention relates to the technical field of medium and high voltage AC/DC hybrid power grids, AC/DC converter station networking structure and power electronics, and more particularly to a multi-AC port modular multilevel converter and its control method. Background technique [0002] With its advantages in power supply capacity, power supply reliability, power quality, and system flexibility, AC/DC hybrid power grids are gradually becoming a research hotspot at home and abroad. The AC-DC converter station is the link between the DC grid and the AC grid, and the power electronic converter is the core equipment in the AC-DC converter station, usually a voltage source converter (VSC). It is divided into two-level topology, three-level topology and modular multi-level topology. The converters of two-level and three-level topology are simple in structure and relatively mature in technology. This brings about the problem of voltage equalization. At present, only ABB can solve this problem. At the same time, in order to obtain better dynamic characteristics and harmonic characteristics, two-level and three-level converters need to be switched at high frequencies, resulting in switching losses. Larger; Modular multilevel converter (MMC) topology adopts sub-module cascading mode, which reduces the requirements for device withstand voltage level, and has significant manufacturing difficulty, switching loss, waveform quality and fault handling capabilities Advantages, so it is more suitable for applications in medium and high pressure situations. In addition, the network structure of the AC/DC converter station will have an impact on many aspects such as system cost, power supply reliability, protection configuration, and control flex
[ZH CN113346780A]: 一种多频率三端口模块化多电平换流器 [EN CN113346780A]: A multi-frequency three-port modular multi-level converter | [ZH CN113346780A]: 本发明公开了一种多频率三端口模块化多电平换流器，包括第一三相交流系统、第二三相交流系统、第一辅助桥臂系统、第二辅助桥臂系统、上主桥臂系统及下主桥臂系统，其中，第一三相交流系统的输出端依次经第一辅助桥臂系统及第二辅助桥臂系统与第二三相交流系统相连接，上主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统之间的线路相连接，下主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统之间的线路相连接，上主桥臂系统的另一端与直流系统的正极相连接，下主桥臂系统的另一端与直流系统的负极相连接，该换流器具有高度模块化设计、易于扩展、输出电压波形质量和功率特性良好的优点。 [EN CN113346780A]: The invention discloses a multi-frequency three-port modular multilevel converter, which includes a first three-phase AC system, a second three-phase AC system, a first auxiliary bridge arm system, a second auxiliary bridge arm system, and an upper main The bridge arm system and the lower main bridge arm system, wherein the output end of the first three-phase AC system is connected to the second three-phase AC system through the first auxiliary bridge arm system and the second auxiliary bridge arm system in turn, and the upper main bridge arm One end of the system is connected to the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system, and one end of the lower main bridge arm system is connected to the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system. Connection, the other end of the upper main bridge arm system is connected to the positive pole of the DC system, and the other end of the lower main bridge arm system is connected to the negative pole of the DC system. The converter has a highly modular design, easy to expand, and output voltage waveforms. The advantages of good quality and power characteristics. | CN113346780A | 2021-09-03 | CN202110593691A | 2021-05-28 | CN202110593691A, 2021-05-28 | CN113346780A: 2021-09-03 | 西安交通大学 |  | H02M7/483: I H02J3/36: I |  |  |  | [ZH CN113346780A]: 1 .一种多频率三端口模块化多电平换流器，其特征在于，包括第一三相交流系统、第二 三相交流系统、第一辅助桥臂系统、第二辅助桥臂系统、上主桥臂系统及下主桥臂系统，其 中，第一三相交流系统的输出端依次经第一辅助桥臂系统及第二辅助桥臂系统与第二三相 交流系统相连接，上主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统之间的线 路相连接，下主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统之间的线路相连 接，上主桥臂系统的另一端与直流系统的正极相连接，下主桥臂系统的另一端与直流系统 的负极相连接。 2 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，第一三相交 流系统与第二三相交流系统的频率及幅值不同。 3 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，第一三相交 流系统的输出电压和电流分别为Vsu、Vsv、Vsw和iu、iv、iw；第二三相交流系统的输出电压和电 流分别为Vsa、Vsb、Vsc和ia、ib、i。； 上主桥臂系统包括上主桥臂px、py、pz；下主桥臂系统包括下主桥臂nx、ny、nz；第一辅 助桥臂系统包括第一辅助桥臂ux、vy、wz；第二辅助桥臂系统包括第二辅助桥臂ax、by、cz； 上主桥臂px、下主桥臂nx、第一辅助桥臂ux、第二辅助桥臂ax及第一三相交流系统中a 相与第二三相交流系统中a相之间的线路连接于节点X； 上主桥臂py、下主桥臂ny、第一辅助桥臂uy、第二辅助桥臂ay及第一三相交流系统中b 相与第二三相交流系统中b相之间的线路连接于节点Y； 上主桥臂pz、下主桥臂nz、第一辅助桥臂uz、第二辅助桥臂az及第一三相交流系统中c 相与第二三相交流系统中c相之间的线路连接于节点Z； 上主桥臂及下主桥臂均由第一电感L、第一等效电阻R以及2n个第一半桥子模块串联而 成； 第一辅助桥臂及第二辅助桥臂均由第二电感Ls,l、第二等效电阻Rs,l以及n/2个第二H桥 子模块串联而成。 4 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，上主桥臂及 下主桥臂对于第一三相交流系统及第二三相交流系统采用定有功功率/无功功率或定有功 功率/交流电压控制、恒压恒频控制、虚拟同步机控制、定直流电压/交流电压或定直流电 压/无功功率控制。 5 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，上主桥臂系 统及下主桥臂系统对于直流系统采用定直流电压、定直流电流或定有功功率控制。 6 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，第一辅助桥 臂系统对第一三相交流系统采用电流定向的定直流电压控制;第二辅助桥臂系统对第二三 相交流系统采用电流定向的定直流电压控制。 7 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，针对换流器 的外环控制，分别在输入侧和输出侧的控制策略中引入无功功率分配系数&amp;及内，通过调节 无功功率分配系数&amp;和内的大小实现无功功率在上主桥臂系统、下主桥臂系统、第一辅助桥 臂系统及第二辅助桥臂系统之间进行分配和辅助桥臂之间的合理分配。 8 .根据权利要求1所述的多频率三端口模块化多电平换流器，其特征在于，换流器的环 流抑制策略采用基于负序二倍频派克变换的前馈解耦控制技术，提取第一三相交流系统及 第二三相交流系统的系统频率产生的环流分量，抑制内部环流中的2次谐波分量。 [EN CN113346780A]: 1 A multi-frequency three-port modular multi-level converter, characterized in that it comprises a first three-phase AC system, a second three-phase AC system, a first auxiliary bridge arm system, a second auxiliary bridge arm system, and upper The main bridge arm system and the lower main bridge arm system, wherein the output end of the first three-phase AC system is connected to the second three-phase AC system via the first auxiliary bridge arm system and the second auxiliary bridge arm system in turn, and the upper main bridge One end of the arm system is connected to the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system, and one end of the lower main bridge arm system is connected to the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system The other end of the upper main bridge arm system is connected with the positive pole of the DC system, and the other end of the lower main bridge arm system is connected with the negative pole of the DC system. 2 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the frequency and amplitude of the first three-phase AC system and the second three-phase AC system are different. 3 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the output voltage and current of the first three-phase AC system are Vsu, Vsv, VswAnd iu, Iv, Iw; The output voltage and current of the second three-phase AC system are Vsa, Vsb, Vsc and ia, ib, i respectively. ; The upper main bridge arm system includes upper main bridge arms px, py, pz; the lower main bridge arm system includes lower main bridge arms nx, ny, nz; the first auxiliary bridge arm system includes first auxiliary bridge arms ux, vy, wz ; The second auxiliary bridge arm system includes the second auxiliary bridge arms ax, by, cz; the upper main bridge arm px, the lower main bridge arm nx, the first auxiliary bridge arm ux, the second auxiliary bridge arm ax and the first three-phase AC The line between phase a in the system and phase a in the second three-phase AC system is connected to node X; the upper main bridge arm py, the lower main bridge arm ny, the first auxiliary bridge arm uy, the second auxiliary bridge arm ay, and the first The line between phase b in a three-phase AC system and phase b in the second three-phase AC system is connected to node Y; upper main bridge arm pz, lower main bridge arm nz, first auxiliary bridge arm uz, and second auxiliary bridge Arm az and the line between phase c in the first three-phase AC system and phase c in the second three-phase AC system are connected to node Z; both the upper main bridge arm and the lower main bridge arm are formed by the first inductor L, the first, etc. Effective resistance R and 2n first half-bridge sub-modules are connected in series; the first auxiliary bridge arm and the second auxiliary bridge arm are both formed by the second inductor Ls,l, the second equivalent resistance Rs, l and n/2 second H bridge sub-modules are connected in series. 4 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the upper main bridge arm and the lower main bridge arm adopt fixed values for the first three-phase AC system and the second three-phase AC system. Active power/reactive power or constant active power/AC voltage control, constant voltage and constant frequency control, virtual synchronous machine control, constant DC voltage/AC voltage or constant DC voltage/reactive power control. 5 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the upper main bridge arm system and the lower main bridge arm system adopt constant DC voltage, constant DC current or constant active power for the DC system. Power Control. 6 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the first auxiliary bridge arm system adopts current-oriented constant DC voltage control for the first three-phase AC system; the second auxiliary The bridge arm system adopts current-oriented constant DC voltage control for the second three-phase AC system. 7 The multi-frequency three-port modular multi-level converter according to claim 1, characterized in that, for the outer loop control of the converter, reactive power distribution is introduced in the control strategy of the input side and the output side respectively Coefficient &amp; and inner, by adjusting the size of reactive power distribution coefficient &amp; and inner, the reactive power can be carried out among the upper main bridge arm system, lower main bridge arm system, first auxiliary bridge arm system and second auxiliary bridge arm system Reasonable distribution between distribution and auxiliary bridge arms. 8 The multi-frequency three-port modular multi-level converter according to claim 1, wherein the circulating current suppression strategy of the converter adopts a feedforward decoupling control technology based on negative sequence double frequency Parker transform, extracting The first three-phase AC system and The circulating current component generated by the system frequency of the second three-phase AC system suppresses the second harmonic component in the internal circulating current. | [ZH CN113346780A]: 一种多频率三端口模块化多电平换流器 技术领域 [0001]本发明涉及一种换流器，具体涉及一种多频率三端口模块化多电平换流器。 背景技术 [0002]随着高比例新能源的接入、能源终端消费的再电气化和电力电子变频技术的进 步，电力系统趋于多频率发展。因此，高电压大功率多端口变流器的应用前景非常广泛，在 异步联网、海上风电、远距离分频输电、海洋油气开采及未来海底输配电系统建设等方面都 具有非常重要的作用。 [0003]两端口变频器拓扑有较多类型，可作为三端口换流器设计参考。模块化多电平变 流器(Modular Multilevel Converter ,MMC)的研究较充分，技术较成熟，已在国内外多项 工程中得到实际应用，采用背靠背式MMC(BTB-MMC)可以实现交-直-交变频功能。模块化多 电平矩阵式变流器(Modular Multilevel Matrix Converter,M3C)功率密度大，冗余度高， 无需中间直流环节，实现直接功率变换。但较多的桥臂数使得M3c环流通道众多，且其连接 的两侧系统之间耦合程度高，控制策略复杂。六边形模块化多电平交交变流器(Hexverter) 仅采用6个桥臂即可直接连接两个不同频率的系统，但其拓扑决定了内部环流通道仅有一 条，不增加补偿设备两侧则需满足无功功率和环流的强约束关系，使得Hexverter系统的控 制策略难于实现。丫型模块化多电平交交变流器(YMMC)只需6个等效桥臂，结构简单对称，不 存在环流。但主桥臂同时承受两侧系统的电流，需要更大功率的IGBT器件，在大电流场景下 经济性不足。 [0004] 将背靠背MMC的直流母线引出，可实现低频-直流-工频三端口换流器功能。但传统 基于半桥子模块的MMC不具备直流故障阻断能力，因此当三端口换流器的直流侧发生短路 故障时，只能依靠交流侧断路器切除整个换流器实现故障隔离，故障恢复特性差。采用全桥 子模块或钳位双子模块替换全部或部分半桥模块以实现直流故障阻断也是一种有效的方 法，但成本显著提高。采用子模块混合式MMC需要在故障电流清除能力与投资成本之间综合 考量，均衡配置子模块类型。 发明内容 [0005]本发明的目的在于克服上述现有技术的缺点，提供了一种多频率三端口模块化多 电平换流器，该换流器具有高度模块化设计、易于扩展、输出电压波形质量和功率特性良好 的优点。 [0006]为达到上述目的，本发明所述的多频率三端口模块化多电平换流器包括第一三相 交流系统、第二三相交流系统、第一辅助桥臂系统、第二辅助桥臂系统、上主桥臂系统及下 主桥臂系统，其中，第一三相交流系统的输出端依次经第一辅助桥臂系统及第二辅助桥臂 系统与第二三相交流系统相连接，上主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥 臂系统之间的线路相连接，下主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统 之间的线路相连接，上主桥臂系统的另一端与直流系统的正极相连接，下主桥臂系统的另 一端与直流系统的负极相连接。 [0007]第一三相交流系统与第二三相交流系统的频率及幅值不同。 [0008] 第一三相交流系统的输出电压和电流分别为Vsu、Vsv、Vsw和iu、iv、iw；第二三相交流 系统的输出电压和电流分别为Vsa、Vsb、Vsc和ia、ib、ic； [0009]上主桥臂系统包括上主桥臂px、py、pz；下主桥臂系统包括下主桥臂nx、ny、nz；第 一辅助桥臂系统包括第一辅助桥臂ux、vy、wz；第二辅助桥臂系统包括第二辅助桥臂ax、by、 cz； [0010]上主桥臂px、下主桥臂nx、第一辅助桥臂ux、第二辅助桥臂ax及第一三相交流系统 中a相与第二三相交流系统中a相之间的线路连接于节点X； [0011]上主桥臂py、下主桥臂ny、第一辅助桥臂uy、第二辅助桥臂ay及第一三相交流系统 中b相与第二三相交流系统中b相之间的线路连接于节点Y； [0012]上主桥臂pz、下主桥臂nz、第一辅助桥臂uz、第二辅助桥臂az及第一三相交流系统 中c相与第二三相交流系统中c相之间的线路连接于节点Z。 [0013]上主桥臂及下主桥臂均由第一电感L、第一等效电阻R以及2n个第一半桥子模块串 联而成； [0014]第一辅助桥臂及第二辅助桥臂均由第二电感Ls l、第二等效电阻Rs l以及n/2个第 二H桥子模块串联而成。 [0015]上主桥臂及下主桥臂对于第一三相交流系统及第二三相交流系统采用定有功功 率/无功功率或定有功功率/交流电压控制、恒压恒频控制、虚拟同步机控制、定直流电压/ 交流电压或定直流电压/无功功率控制。 [0016]上主桥臂系统及下主桥臂系统对于直流系统采用定直流电压、定直流电流或定有 功功率控制。 [0017]第一辅助桥臂系统对第一三相交流系统采用电流定向的定直流电压控制;第二辅 助桥臂系统对第二三相交流系统采用电流定向的定直流电压控制。 [0018]针对换流器的外环控制，分别在输入侧和输出侧的控制策略中引入无功功率分配 系数&amp;及&amp;，通过调节无功功率分配系数&amp;和仁的大小实现无功功率在上主桥臂系统、下主 桥臂系统、第一辅助桥臂系统及第二辅助桥臂系统之间进行分配和辅助桥臂之间的合理分 配。 [0019]换流器的环流抑制策略采用基于负序二倍频派克变换的前馈解耦控制技术，提取 第一三相交流系统及第二三相交流系统的系统频率产生的环流分量，抑制内部环流中的2 次谐波分量。 [0020]本发明具有以下有益效果： [0021]本发明所述的多频率三端口模块化多电平换流器在具体操作时，将两个相同或不 同频率及幅值的三相交流系统与直流系统直接相联，同时通过直流侧与直流电网相联，实 现交流频率1-交流频率2-直流不同频率的系统之间能量交换，具有高度模块化设计、易于 扩展、输出电压波形质量和功率特性良好的优点，可广泛适用于高电压、大功率、多频率电 力变换应用场合。同时需要说明的是，本发明直接实现交流频率-交流频率-直流的功率变 换和频率控制，不存在无功约束问题，可以输出更高直流电压，具有直流故障自清除功能， 在混合多频率电力系统具有广阔的应用前景以及竞争优势。 附图说明 [0022] 图1为MFTP-MMC的主电路模型图； [0023] 图2为MFTP-MMC单相等效电路图； [0024] 图3为MFTP-MMC输入侧单相等效电路图； [0025] 图4为MFTP-MMC输出侧单相等效电路图； [0026] 图5为MFTP-MMC功率分配策略框图； [0027]图6为MFTP-MMC输入、输出侧前馈解耦闭环控制策略框图； [0028] 图7为MFTP-MMC环流抑制策略框图； [0029] 图8为MFTP-MMC稳态运行时桥臂调制波示意图； [0030] 图9a为&amp; = 1«2=1时MFTP-MMC的分频侧电压电流波形图； [0031]图9b为&amp; = 1«2=1时MFTP-MMC的分频侧输入有功功率和无功功率波形图； [0032] 图9c为&amp; = 1«2=1时MFTP-MMC的工频侧电压电流波形图； [0033] 图9d为&amp; = 1«2=1时MFTP-MMC的工频侧输出有功功率和无功功率图； [0034] 图96为&amp; = 1«2=1时MFTP-MMC的主桥臂和辅助桥臂直流电压波形图； [0035] 图9f为&amp; = 1«2=1时MFTP-MMC的直流侧输出功率波形图。 具体实施方式 [0036]为了使本技术领域的人员更好地理解本发明方案，下面将结合本发明实施例中的 附图，对本发明实施例中的技术方案进行清楚、完整地描述，显然，所描述的实施例仅仅是 本发明一部分的实施例，不是全部的实施例，而并非要限制本发明公开的范围。此外，在以 下说明中，省略了对公知结构和技术的描述，以避免不必要的混淆本发明公开的概念。基于 本发明中的实施例，本领域普通技术人员在没有做出创造性劳动前提下所获得的所有其他 实施例，都应当属于本发明保护的范围。 [0037]在附图中示出了根据本发明公开实施例的结构示意图。这些图并非是按比例绘制 的，其中为了清楚表达的目的，放大了某些细节，并且可能省略了某些细节。图中所示出的 各种区域、层的形状及它们之间的相对大小、位置关系仅是示例性的，实际中可能由于制造 公差或技术限制而有所偏差，并且本领域技术人员根据实际所需可以另外设计具有不同形 状、大小、相对位置的区域/层。 [0038]参考图1,本发明所述的多频率三端口模块化多电平换流器包括第一三相交流系 统、第二三相交流系统、第一辅助桥臂系统、第二辅助桥臂系统、上主桥臂系统及下主桥臂 系统，其中，第一三相交流系统的输出端依次经第一辅助桥臂系统及第二辅助桥臂系统与 第二三相交流系统相连接，上主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统 之间的线路相连接，下主桥臂系统的一端与第一辅助桥臂系统和第二辅助桥臂系统之间的 线路相连接，上主桥臂系统的另一端与直流系统的正极相连接，下主桥臂系统的另一端与 直流系统的负极相连接。 [0039]第一三相交流系统与第二三相交流系统的频率及幅值不同，第一三相交流系统的 输出电压和电流分别为Vsu、Vsv、Vsw和iu、iv、iw；第二三相交流系统的输出电压和电流分别为 Vsa、Vsb、Vsc和ia、ib、ic；上主桥臂系统包括上主桥臂px、py、pz；下主桥臂系统包括下主桥臂 nx、ny、nz；第一辅助桥臂系统包括第一辅助桥臂ux、vy、wz；第二辅助桥臂系统包括第二辅 助桥臂ax、by、cz；上主桥臂px、下主桥臂nx、第一辅助桥臂ux、第二辅助桥臂ax及第一三相 交流系统中a相与第二三相交流系统中a相之间的线路连接于节点X；上主桥臂py、下主桥臂 ny、第一辅助桥臂uy、第二辅助桥臂ay及第一三相交流系统中b相与第二三相交流系统中b 相之间的线路连接于节点Y;上主桥臂pz、下主桥臂nz、第一辅助桥臂uz、第二辅助桥臂az及 第一三相交流系统中c相与第二三相交流系统中c相之间的线路连接于节点Z,上主桥臂及 下主桥臂均由第一电感L、第一等效电阻R以及2n个第一半桥子模块串联而成;第一辅助桥 臂及第二辅助桥臂均由第二电感Ls」、第二等效电阻Ιζ,ι以及n/2个第二Η桥子模块串联而 成。 [0040]上主桥臂及下主桥臂对于第一三相交流系统及第二三相交流系统采用定有功功 率/无功功率或定有功功率/交流电压控制、恒压恒频控制、虚拟同步机控制、定直流电压/ 交流电压或定直流电压/无功功率控制；上主桥臂系统及下主桥臂系统对于直流系统采用 定直流电压、定直流电流或定有功功率控制；第一辅助桥臂系统对第一三相交流系统采用 电流定向的定直流电压控制;第二辅助桥臂系统对第二三相交流系统采用电流定向的定直 流电压控制;针对换流器的外环控制，分别在输入侧和输出侧的控制策略中引入无功功率 分配系数&amp;及k2,通过调节无功功率分配系数&amp;和k2的大小实现无功功率在上主桥臂系统、 下主桥臂系统、第一辅助桥臂系统及第二辅助桥臂系统之间进行分配和辅助桥臂之间的合 理分配;换流器的环流抑制策略采用基于负序二倍频派克变换的前馈解耦控制技术，提取 第一三相交流系统及第二三相交流系统的系统频率产生的环流分量，抑制内部环流中的2 次谐波分量。 [0041] 参考图1,本发明所述的多频率三端口模块化多电平换流器（MFTP-MMC系统）的等 效电路模型如图1所示。 [0042]系统输入侧电压的中性点定义为Ο1点,输出侧电压的中性点定义为Ο?点，直流线路 的中性点定义为N点，根据基尔霍夫电路定理，由图1给出MFTP-MMC系统的回路电压方程和 节点电流方程为： [0043] [0044] 力 匕=4£ + 4比+匕+限+喙。, at 匕=勺：+ &amp; £ + % + 喂 + % 或 %，= R儿 u 寸+ (1) %=一氏/一乙于+ Vax+v^ + vno at 匕=-隼亡-乙%+忆+嗫+%¾ at [0045] [0046] di I 出:T yxN=Ri +L^x* p dt -勺+- di“，n = R%+l 请- -Y +yp 您2 ⑶ . diV N = Ri + L-2 9 dt -勺+- 公2 Q =一如初一£ ~τ~ at +匕- % 心=也一吟 +曦- 一以 2 ⑷ +匕- %2 [0048] [0047] 对式⑶及式⑷分别进行两式相加和相减，得： [0049] [0050] %+匕-嗫—p ----------------it 2 a-----------Λ =N--1-- 2 2 df [0051] 若令 [0055] [0056] [0057] [0058] [0059] [0052] [0053] [0054] f V -V厂 一** 华 产妫一工一2V -V 喙 二^_妍」 2V -V 物） - 2 [/ _ xp xn产 conun j 一 c- 2V +V y _ .呼 冲 ,* cotmn _y 2V +v— r炉 2'cnjmn g 一 八- 2 ._ % +^cir λ 一 个- 2i +1, _ 叩 yn协J 2.—'印十噎“的/ - 2 则该式⑹及式⑺可表示为： 匕N = 2 (…J+ 2 dt 物 ,限 η力一 dt 物」 (9) 嗫=g&amp;·一幻 + g df 叫 匕ΎΙΛΗΙΗ X -号=&amp;+£ 2 - di .Cir.x _y v—上=RL +L2 加」 dj Cir_.Fdt do) ^COfHtH _ 工 — %=Ri-+ L 2 -- di cir _zdt (8) 当第一三相交流系统和第二三相交流系统均为三相对称系统时,则有: g=嗫。[=%启=0 （11） 首先，采用等功率变换，从abc到αΒΟ的变换矩阵为Tabc/呐： 1 _ 1-5 _1 ~2 ^- 0 走2 —且 (12) 1 1 1 [0060] 从αΒΟ到abc的变换矩阵为TaWabc： 1 0 1 [0061] T = E/ abc/a/ΪΟ V 3 .12 正2 1 / (13) _ 1_ 2 Ύ 1万 [0062] 将等功率变换矩阵Tabc/现左乘式⑴、式⑵、式⑸及式（6），三相三线制情形，零 序分量被忽略，得系统在印坐标系下的交流侧电压方程和电流方程为： [0063] V 匕*二凡*产 + 4花-十匕月十 (14) [0064] V didi, itV!p =-鸟％ - Ll 正+ 匕严 + /N (15) [0065] 限=;(八)+丁(小)鼠=2% %)+2力) + %_α+ %_产 (16) [0066] : 乙+乙=% + %&gt; (17)*户+ j加=1Ιβ + '佻？ [0067] 式(14)-式(17)中，Vsa、VsB和isa、isB为输入侧电压和电流的αΒ分量;VqVib和九、 %为输出侧电压和电流的吨分量;VqVib为输入侧辅助桥臂电压的印分量;V2N2B为输出 侧辅助桥臂电压的αΒ分量；iap,iep和ί.η、η为上主桥臂电流、下主桥臂电流的理分量， Vdiff a'Vdiff B为上主桥臂差模分量及下主桥臂差模分量的αΒ分量。 [0068]实际运行中，上辅助桥臂电压ViqVib和下辅助桥臂电压V2QV2B中既含有输入频率 分量又含有输出频率分量，而输入、输出侧电流is/isB和ila'ilB分别只包含本侧的频率分 量，为保证式(14) -式(16)成立，将其分解为如下输入输出两种不同频率分量的形式： [0069] (18) [0070] 针对不同的频率分量，分别采用如下的同步旋转坐标变换矩阵: (19) [0071] [0072] Qw = cos sinGj (20) -sin(y/ cosily [0073] %恤产 cos® sin 卬 ¢21) —sin cos 纾 [0074]将式(18)及式(19)变换为dq坐标系下的系统交流侧数学模型为: [0075] y v '凡声，f rf ji V V 户」L/题05 (22) [0076] [0077] [0078] (23) 其中，4为输入侧电网的角频率，4为输出侧电网的角频率。 根据式（10）描述了共模电压与内部环流的关系，对其内部不同频率分量进行分 解，由于主桥臂中含有fs与片两种频率分量，则其内部环流主要为两种频率的负序2次谐波 分量的叠加。采用从abc三相静止坐标系变换到d-2q-2旋转坐标系（分别以2 3s以及2 3 1速度 反。方向旋转）的变换矩阵可以将负序2次谐波分量变换为直流分量，根据式（12）及式（21） 可推得其变换矩阵分别为Tabc/dqo s （一2。）和Tabc/dqO 1 （以。）。而根据式（13）及式（22）可推得其 反变换矩阵分别为Tdqo/abc s（-20）^T，o/abc 1 （-2。）:针对不同频率分量，对式（10）进行d-2q-2 CiqU/dDC S CiqU/dDC 1 坐标变化得： 一 [0079] ^comm _d _fsV framm q Js口 户 =R ^cir d fa工二 fMg.力 f d+ A—— dl ^ird fsi. 户 + 20/ j f0 + 00 (24) [0080] 匕琬“ comm fl —R + L士 dt lcir ά_β一β + * qj‘曲 _d _β0 + 00.回J (25) [0081] 有功、无功分配 [0082] 考虑MFTP -MMC系统的单相等效电路，如图2所示。 [0083]应用叠加原理，输入侧单相等效电路如图3所示，若令： [0084] V 凡gl = %% =Rt +y &lt;T ~γ ΤΛ = + “fs Λ&gt;,τ τ (26) £约2二4+ § 一%陷一九 二 ’蜘 _djV[/呦'4 .九 十 匕力V2q_fl . [0085] 则稳态下式（22）可改写为： [0086] 匕d =此却一8^+匕MJ 、噎=勺匕-%£即&amp; + *啊.启 (27) [0087]第一辅助桥臂和主桥臂总共吸收的有功功率和无功功率分别为: [0088] J . (28) [0089]为保证第一辅助桥臂吸收有功功率为零，需满足以下方程： 血9。1 % fsisd+Vlq fsisq = 0 (29) [0091]为实现第一辅助桥臂和主桥臂间吸收无功功率比例的动态分配，引入分配系数 使得主桥臂吸收无功功率满足 [。。92] k1Qbs = Vdiff q fsisd-Vdiff d fsisq (30) [0093]即，当勺 = 1时7,无功功率全部由主桥臂吸收。 [0094] 联立式(27) - 式(30),得： 匕 *=--砧0M 力+% 九* ==z(l—占)。瓦 - j+q (31) %Τ—d—力= + .2 ： ( 1 -先)。加 [0096] % (32) = % j 一产*( ।—幻氏 4H十( [0097]实际中，第一辅助桥臂需要吸收少量的有功功率以补偿桥臂中的有功损耗，避免 子模块中的直流电容持续放电，从而保证直流电压恒定。在此，设第一辅助桥臂吸收的有功 功率为Pbs loss，亦即 [°°98] Vld_fsisd+Vlq_fsisq = PbsJoss (33) [0099] 重新解得 [0100] (34) [0101] [0102] [0103] [0104] [0105] [0106] [0107] -左J&amp;.一直才4・ 附+Q a+ % - %+% 的+q 同理，输出侧单相等效电路如图4所示。 系统稳态运行时,则有： 嗫=1勺/d + 组 4呵工% + (36) 、%二-%% — 绚力十勺 loss &lt; 匕山— ZdJ + '频_d_jl (37) V -V λ-V ' 1/2时*匆_/? T,期/ 第二辅助桥臂和主桥臂总共吸收的无功功率为: Qbl = ^2td_fl ^lq-^2tq_fl Id (35) [0108] [0109] [0110] 为保证第一辅助桥臂吸收有功功率为零，需满足以下方程： ^2td_f 1 Id - ^2tq_f 1 I lq = θ 同样地，为实现第一辅助桥臂和主桥臂间吸收无功功率比例的动态分配，引入分 配系数k2，使得主桥臂吸收无功功率满足: [0111] [0112] [0113] ^bl—^diff_d_fl-1-lq~^diff_q_ f3d (40) 即，当卜2=邛寸，无功功率全部由主桥臂吸收。 联立式(36)-式(40),得： [0114] (41) [0115] = %_力一『；『(।―占)ο” =匕1 +/(J3。“ (42) [0116] 实际中，第一辅助桥臂需要吸收少量的有功功率以补偿桥臂中的有功损耗，避免 子模块中的直流电容持续放电，从而保证直流电压恒定。在此，设第一辅助桥臂吸收的有功 功率为Ρ1 [0117] [0118] 'bs』ss，亦即 -V i -V i =P ，2d_fl,ld，2q_fl,lq 1 bl_loss 重新解得 (43) [0119] [0120] [0121] [0122] km toss 卞UM 坊+% 』(f)。 为十% (44) 嬴(T )盘+言产m (45) 勿/=匕卬 J + j2 ；尸(1 一 内)Qbl + j2 ; j2 Phi loss 因此得功率分配策略如图5所示： MFTP-MMC数学模型与传统的并网换流器的数学模型相似，采用基于电网电压定向 的前馈解耦控制策略如下： [0123]为简化控制器的设计，在式(23)和式(24)的第一式中，作如下变量替换，令 [0124] ¢46) Vd JI =1&amp;碓+ sL,q)% = -九 + ①i4% + fi [0125]《，/ . ='42+ S42)% = l% —电 Leg% + (47) [0126]通过PI调节实现有功电流和无功电流的前馈解耦闭环控制，其中，V'd fs，V' q fs和 V'd fjV' q门由电流闭环的PI调节器得到，其控制原理如图6所示。 [0127] 针对MFTP-MMC换流器的外环控制,主桥臂对于第一三相交流系统及第二三相交流 系统均可采用定有功功率/无功功率或定有功功率/交流电压(P/Q或P/Vac)控制、恒压恒频 (V/f)控制、虚拟同步机(VSG)控制、定直流电压/交流电压或定直流电压/无功功率(Vdc/ Vac或Vdc/Q)控制，主桥臂对于直流系统采用定直流电压、定直流电流或定有功功率控制。 为保证换流器稳定运行,三个端口中只能有一侧采用定直流电压控制ο第一辅助桥臂系统 及第二辅助桥臂系统分别对于各自三相交流系统采用电流定向的定直流电压控制。 [0128] 对于MFTP-MMC的环流抑制策略,根据式(24)及式(25),作如下变量替换，令: [0129] ^ar_d= ( R + SL)idr. a=匕*“协一d_fs - 2①sL* .q =(R + sL)'r_g一用=^comm_q_fs + ^^s^cir _d _fs (48) [0130] 匕一dj=(R + s£)* d『23% q_ft 匕u =(灭=嗫丽+2附£%&gt; d_# ¢49) [0131]通过PI调节实现有功电流和无功电流的前馈解耦闭环控制，其中，V' V' cir q fs和V' cir d fi，V' cirq fl由电流闭环的PI调节器得至U，其控制原理如图7所示。 [0132「系统稳态值计算而K值优化 [0133] 设第一三相交流系统及第二三相交流系统均为三相对称，不失一般性，设MFTPMMC稳态工作时第一三相交流系统及第二三相交流系统的电压和电流为： '匕=曦 cos(oj) 8 = &amp; cos(@f - θ) [0134],曦:曦cos@f-2乃/3) , ι1 = L,cos@f-6-2乃/3) (50) .曦=曦 cosQf + 2然/3)也=&amp; cos(%-£+ 2句3) 匕=% cos®/) = ilm cos(3-φ) [0135] ，/b =匕- 2兀3 &lt; ib - Ilm cos(q/-φ-2π/3) .腺=曦 cos⑷f +2兀/3) [ζ = Ilm cos(&lt;^Z -(3+ 2^/3) (51) [0136] 采用等功率变换矩阵以及同步旋转坐标变换矩阵，得MFTP-MMC换流器的稳态解 为： [0137] (52) [0138] 九/=曦-&amp;μ + 里cos θ-sin £ (53) [。139] %/=曦-Μ -叫北=出此Λ“ sm d -岛%&amp; cos £（54） [0140]匕w J = % +纥g/出一班工精的=£匕皿十*R四2,加cos伊+ JI©% sinp（55） [0141]匕，= % + 均 + 域Ly$d = l&amp;R叫 Ji,” sin 0 + £地L叫 Jcosp （56） [0142] jiL-匕/丽 sin£-万以£；（57） [0143] Qbl -匕-嗫g/“ 二 l1·%Λ sin 夕一·10»/%%（58） ,2 — J/24产 人仲一尸3六十尸的一# [0144] 3 4 q（59） =2匕+万&amp;1%+万发4片”—3曦凡G&amp;COS6 —3曦RjjQind *2 - （/2 +片 々1J々旧.#十尸加.# [0145] 3 2 7（60） =34, +万况M： + 5嫁+ 3嗫42&amp;COS0+ 3匕血％九sin夕 [0146]胃=二+0=^ 匕 （61） [0147]『=钎，；(62) [0148]稳态时各桥臂调制信号示意图如图8所示。 [0149]其中，第一辅助桥臂系统的调制波函数为-mz+m' J第二辅助桥臂系统的调制波函 数为Fi+m' 2,主桥臂的调制函数为mi+m?。 [0150] 在MFTP-MMC稳态运行时，为使主桥臂和辅助桥臂不过调制,从而最大化MFTP-MMC 与第一三相交流系统及第二三相交流系统交换的有功和无功功率,设定优化目标为： [0151] min {max (¦ - 2m21 +1 m' J I - 2mx ¦ + ¦ m' 21 , ¦ mx ¦ +1 m21)} (63) [0152]当系统稳态时，可忽略辅助桥臂的功率损耗Pbs I*和Pbi i°ss，由式(31)-式(32)和 式⑷)-式(42),得： - [0155] [0156] (66) ¢67) [0157] 将式(57)〜(62)代入式(64)〜(67)中，可得 [0158] ，= 2(1一幻(曦 sin68) NV dcr [0159] 2(1%乂小访0+“小) 侬) -NV [0160] _#：Msin%-2曦恁/小沁@ + “以瑞 +匕co『@-2曦禹矶&amp;cos@ + %X (70) 叫—不 LUIolJ 优=1Μ 12 ΝΡ [0162]由式(68)-式(71)，通过调节&amp;和k2的值，即可改变主桥臂和辅助桥臂的稳态调制 度,进而计算出符合优化目标式(63)的g和k?的最优值,从而对系统的整体性能进行优化。 [0163] 仿真验证试验 [0164] 在MATLAB/SIMULINK平台下搭建MFTP-MMC系统模型，输入侧接入35kV,50/3Hz分频 交流系统，输出侧接入35kV, 50Hz工频交流系统，直流侧接入140kV直流系统,主要参数如表 1所示。 [0165]表 1 设备 项目 参数 [0166] 额定容量 1QQMW 换流器 载波周期 L 2ms 直流电压 I4QkV CN 113346780 A 说明 书 轴助桥臂3华桥 桥臂子模块数 主桥臂12半桥 子模块电压额定值 40/3 kV 子模块电容 20mF 轴助桥臂10ml! 桥臂电感 主桥臂20 mH 辅助桥臂0.01Ω 桥臂等效电阻 主桥臂0. 01Ω 直流电感 2cMi [0167] 直流电阻 频率 50/3Hz 输入交流系统 线电压有效位 35kV 输入功率 100W 频率 5010 输力交流系统 线电压有效值 35kV 输事功率 直流电压 MOkV 直流系统 输出功率 50MW [0168] MFTP-MMC直流侧采用定直流电压控制，主桥臂对于第一三相交流系统及第二三相 交流系统采用P/Q控制,测试结果,如果图9a至图9f所示。 [EN CN113346780A]: Technical field of a multi-frequency three-port modular multi-level converter [0001] The present invention relates to a converter, in particular to a multi-frequency three-port modular multi-level converter. Background technique [0002] With the access of a high proportion of new energy sources, the re-electrification of energy terminal consumption, and the advancement of power electronic frequency conversion technology, the power system tends to develop with multiple frequencies. Therefore, the application prospects of high-voltage and high-power multi-port converters are very broad, and they play a very important role in asynchronous networking, offshore wind power, long-distance frequency division transmission, offshore oil and gas exploitation, and the construction of future submarine power transmission and distribution systems. [0003] There are many types of two-port inverter topologies, which can be used as a reference for the design of three-port inverters. Modular Multilevel Converter (Modular Multilevel Converter, MMC) has been fully researched and mature in technology. It has been practically applied in many projects at home and abroad. Back-to-back MMC (BTB-MMC) can be used to achieve AC-DC -Alternating frequency conversion function. Modular Multilevel Matrix Converter (Modular Multilevel Matrix Converter, M3C) has high power density and high redundancy, without intermediate DC link, and realizes direct power conversion. However, the large number of bridge arms makes the M3c circulation channels numerous, and the coupling between the systems on both sides of its connection is high, and the control strategy is complicated. The hexagonal modular multi-level alternating current converter (Hexverter) can directly connect two systems of different frequencies with only 6 bridge arms, but its topology determines that there is only one internal circulation channel without adding two compensation equipment. On the other side, it is necessary to satisfy the strong constraint relationship between reactive power and circulating current, which makes the control strategy of Hexverter system difficult to realize. The Y-type modular multilevel alternating current converter (YMMC) only needs 6 equivalent bridge arms, and has a simple and symmetrical structure without circulating current. However, the main bridge arm bears the currents of the systems on both sides at the same time, and requires more powerful IGBT devices, which is not economical in high current scenarios. [0004] Leading out the DC bus of the back-to-back MMC can realize the function of a low-frequency-DC-power frequency three-port converter. However, the traditional MMC based on half-bridge sub-modules does not have the ability to block DC faults. Therefore, when a short-circuit fault occurs on the DC side of the three-port converter, the AC side circuit breaker can only rely on the AC side circuit breaker to cut off the entire converter to achieve fault isolation and fault recovery. Poor characteristics. It is also an effective method to replace all or part of the half-bridge modules with full-bridge sub-modules or clamped dual sub-modules to achieve DC fault blocking, but the cost is significantly increased. The use of sub-module hybrid MMC requires a comprehensive consideration between the fault current clearance capability and investment cost, and the balanced configuration of sub-module types. Summary of the invention [0005] The purpose of the present invention is to overcome the above-mentioned shortcomings of the prior art, to provide a multi-frequency three-port modular multi-level converter, the converter has a highly modular design, easy to expand, and output voltage waveform quality And the advantages of good power characteristics. [0006] To achieve the above objective, the multi-frequency three-port modular multi-level converter of the present invention includes a first three-phase AC system, a second three-phase AC system, a first auxiliary bridge arm system, and a second auxiliary The bridge arm system, the upper main bridge arm system and the lower main bridge arm system, wherein the output end of the first three-phase AC system is connected to the second three-phase AC system via the first auxiliary bridge arm system and the second auxiliary bridge arm system in turn. Connected, one end of the upper main bridge arm system is connected with the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system, and one end of the lower main bridge arm system is connected with the first auxiliary bridge arm system and the second auxiliary bridge arm system The lines between the systems are connected, the other end of the upper main bridge arm system is connected to the positive pole of the DC system, and the other end of the lower main bridge arm system is connected to the positive pole of the DC system. One end is connected to the negative pole of the DC system. [0007] The frequency and amplitude of the first three-phase AC system and the second three-phase AC system are different. [0008] The output voltage and current of the first three-phase AC system are respectively Vsu, Vsv, VswAnd iu, Iv, Iw; The output voltage and current of the second three-phase AC system are respectively Vsa, Vsb, VscAnd ia, Ib, Ic； [0009] The upper main bridge arm system includes upper main bridge arms px, py, pz; the lower main bridge arm system includes lower main bridge arms nx, ny, nz; the first auxiliary bridge arm system includes first auxiliary bridge arms ux, vy , Wz; The second auxiliary bridge arm system includes second auxiliary bridge arms ax, by, cz; [0010] The upper main bridge arm px, the lower main bridge arm nx, the first auxiliary bridge arm ux, the second auxiliary bridge arm ax, and the phase a in the first three-phase AC system and the phase a in the second three-phase AC system The line of is connected to node X; [0011] The upper main bridge arm py, the lower main bridge arm ny, the first auxiliary bridge arm uy, the second auxiliary bridge arm ay, and the phase b in the first three-phase AC system and the phase b in the second three-phase AC system The line of is connected to node Y; [0012] The upper main bridge arm pz, the lower main bridge arm nz, the first auxiliary bridge arm uz, the second auxiliary bridge arm az, and the phase c in the first three-phase AC system and the phase c in the second three-phase AC system The line of is connected to node Z. [0013] The upper main bridge arm and the lower main bridge arm are both formed by a first inductor L, a first equivalent resistance R, and 2n first half-bridge sub-modules in series; [0014] Both the first auxiliary bridge arm and the second auxiliary bridge arm are formed by the second inductor Ls l, the second equivalent resistance Rs l and n/2 second H-bridge sub-modules are connected in series. [0015] The upper main bridge arm and the lower main bridge arm adopt constant active power/reactive power or constant active power/AC voltage control, constant voltage and constant frequency control, virtual control for the first three-phase AC system and the second three-phase AC system. Synchronous machine control, constant DC voltage/AC voltage or constant DC voltage/reactive power control. [0016] The upper main bridge arm system and the lower main bridge arm system adopt constant DC voltage, constant DC current or constant active power control for the DC system. [0017] The first auxiliary bridge arm system uses current-oriented constant DC voltage control for the first three-phase AC system; the second auxiliary bridge arm system uses current-oriented constant DC voltage control for the second three-phase AC system. [0018] For the outer loop control of the converter, the reactive power distribution coefficient &amp; and &amp; are introduced into the control strategies on the input side and the output side respectively, and the reactive power is achieved by adjusting the size of the reactive power distribution coefficient &amp; and kernel. The distribution between the main bridge arm system, the lower main bridge arm system, the first auxiliary bridge arm system and the second auxiliary bridge arm system and the reasonable allocation between the auxiliary bridge arms. [0019] The circulating current suppression strategy of the converter adopts the feedforward decoupling control technology based on the negative sequence double frequency Parker transform to extract the circulating current components generated by the system frequency of the first three-phase AC system and the second three-phase AC system, and suppress The 2nd harmonic component in the internal circulation. [0020] The present invention has the following beneficial effects: [0021] In the specific operation of the multi-frequency three-port modular multi-level converter of the present invention, two three-phase AC systems of the same or different frequencies and amplitudes are directly connected to the DC system, and the DC system is passed through at the same time. The side is connected to the DC grid to realize the energy exchange between AC frequency 1-AC frequency 2-DC different frequency systems. It has the advantages of highly modular design, easy expansion, good output voltage waveform quality and power characteristics, and can be widely used High-voltage, high-power, multi-frequency power conversion applications. At the same time, it should be noted that the present invention directly realizes AC frequency-AC frequency-DC power conversion and frequency control, does not have the problem of reactive power constraint, can output a higher DC voltage, has a DC fault self-clearing function, and is used in mixed multi-frequency power The system has broad application prospects and competitive advantages. Description of the drawings [0022] FIG. 1 is a diagram of the main circuit model of MFTP-MMC; [0023] FIG. 2 is a single-phase equivalent circuit diagram of MFTP-MMC; [0024] FIG. 3 is a single-phase equivalent circuit diagram of the input side of the MFTP-MMC; [0025] FIG. 4 is a single-phase equivalent circuit diagram of the output side of the MFTP-MMC; [0026] FIG. 5 is a block diagram of MFTP-MMC power allocation strategy; [0027] FIG. 6 is a block diagram of MFTP-MMC input and output side feedforward decoupling closed-loop control strategy; [0028] FIG. 7 is a block diagram of MFTP-MMC circulation suppression strategy; [0029] FIG. 8 is a schematic diagram of the bridge arm modulation wave when the MFTP-MMC is running in a steady state; [0030] Figure 9a is &amp;=1«2=1: MFTP-MMC's voltage and current waveforms on the frequency division side; [0031] Fig. 9b is &amp;=1«2When =1, the input active power and reactive power waveform diagram of the frequency division side of MFTP-MMC; [0032] Figure 9c is &amp;=1«2=1: MFTP-MMC's power frequency side voltage and current waveforms; [0033] Figure 9d is &amp; = 1«2=1, MFTP-MMC's power frequency side output active power and reactive power diagram; [0034] Figure 96 is &amp; = 1«2=1: MFTP-MMC main bridge arm and auxiliary bridge arm DC voltage waveform diagram; [0035] Figure 9f is &amp; = 1«2When =1, the output power waveform of MFTP-MMC on the DC side. Detailed ways [0036] In order to enable those skilled in the art to better understand the solutions of the present invention, the technical solutions in the embodiments of the present invention will be described clearly and completely with reference to the accompanying drawings in the embodiments of the present invention. Obviously, the described The embodiments are only a part of the embodiments of the present invention, not all the embodiments, and are not intended to limit the scope of the present invention. In addition, in the following description, descriptions of well-known structures and technologies are omitted to avoid unnecessary confusion of the concepts disclosed in the present invention. Based on the embodiments of the present invention, all other embodiments obtained by those of ordinary skill in the art without creative work shall fall within the protection scope of the present invention. [0037] The drawings show schematic structural diagrams of the disclosed embodiments of the present invention. These figures are not drawn to scale, some details are enlarged and some details may be omitted for clarity of presentation. The shapes of the various regions and layers shown in the figure and the relative size and positional relationship between them are only exemplary. In practice, there may be deviations due to manufacturing tolerances or technical limitations. Areas/layers with different shapes, sizes, and relative positions can be designed as needed. [0038] Referring to FIG. 1, the multi-frequency three-port modular multi-level converter of the present invention includes a first three-phase AC system, a second three-phase AC system, a first auxiliary bridge arm system, and a second auxiliary bridge Arm system, upper main bridge arm system and lower main bridge arm system, wherein the output end of the first three-phase AC system is connected to the second three-phase AC system via the first auxiliary bridge arm system and the second auxiliary bridge arm system in turn , One end of the upper main bridge arm system is connected with the line between the first auxiliary bridge arm system and the second auxiliary bridge arm system, and one end of the lower main bridge arm system is connected with the first auxiliary bridge arm system and the second auxiliary bridge arm system The lines between them are connected, the other end of the upper main bridge arm system is connected with the positive pole of the DC system, and the other end of the lower main bridge arm system is connected with the negative pole of the DC system. [0039] The frequency and amplitude of the first three-phase AC system and the second three-phase AC system are different, and the output voltage and current of the first three-phase AC system are respectively Vsu, Vsv, VswAnd iu, Iv, Iw; The output voltage and current of the second three-phase AC system are respectively Vsa, Vsb, VscAnd ia, Ib, Ic; The upper main bridge arm system includes the upper main bridge arms px, py, pz; the lower main bridge arm system includes the lower main bridge arms nx, ny, nz; the first auxiliary bridge arm system includes the first auxiliary bridge arms ux, vy, wz ; The second auxiliary bridge arm system includes the second auxiliary Auxiliary bridge arms ax, by, cz; upper main bridge arm px, lower main bridge arm nx, first auxiliary bridge arm ux, second auxiliary bridge arm ax and phase a and second three-phase communication in the first three-phase AC system The line between phase a in the system is connected to node X; the upper main bridge arm py, the lower main bridge arm ny, the first auxiliary bridge arm uy, the second auxiliary bridge arm ay, and the phase b and the first three-phase AC system The line between phase b in the two-three-phase AC system is connected to node Y; the upper main bridge arm pz, the lower main bridge arm nz, the first auxiliary bridge arm uz, the second auxiliary bridge arm az, and the first three-phase AC system The line between the c-phase and the c-phase in the second three-phase AC system is connected to node Z, and the upper main bridge arm and the lower main bridge arm are all composed of the first inductance L, the first equivalent resistance R, and 2n first half bridges. The sub-modules are connected in series; the first auxiliary bridge arm and the second auxiliary bridge arm are both formed by the second inductance Ls", the second equivalent resistance Ιζ,ι, and n/2 second H bridge sub-modules in series. [0040] The upper main bridge arm and the lower main bridge arm adopt constant active power/reactive power or constant active power/AC voltage control, constant voltage and constant frequency control, virtual control for the first three-phase AC system and the second three-phase AC system. Synchronous machine control, constant DC voltage/AC voltage or constant DC voltage/reactive power control; the upper main bridge arm system and the lower main bridge arm system adopt constant DC voltage, constant DC current or constant active power control for the DC system; first The auxiliary bridge arm system uses current-oriented constant DC voltage control for the first three-phase AC system; the second auxiliary bridge arm system uses current-oriented constant DC voltage control for the second three-phase AC system; the outer loop control for the converter , The reactive power distribution coefficient &amp; and k2 are introduced into the control strategies on the input side and the output side respectively, and the reactive power i
[JA JP2021093819A]: マルチレベル電力変換器の制御装置 [EN JP2021093819A]: Multi-level power converter controller | [JA JP2021093819A]: 【課題】フライングキャパシタを有するマルチレベル電力変換器の制御装置において、フライングキャパシタ、半導体素子を破損させることなく安全に停止させる。 【解決手段】直流電源Cdcと、直流電源Cdcに接続された複数の半導体素子S1~S4と、半導体素子S1~S4に接続されたフライングキャパシタCfcと、を備えたマルチレベル電力変換器の制御装置において、ホールド回路1~4は、装置停止時に、フライングキャパシタCfcの充電状態に応じて、半導体素子S1~S4のゲート信号をオフするタイミングを遅らせる。 【選択図】図3 [EN JP2021093819A]: PROBLEM TO BE SOLVED: To safely stop a control device of a multi-level power converter having a flying capacitor without damaging the flying capacitor and a semiconductor element. SOLUTION: A control device for a multi-level power converter including a DC power supply Cdc, a plurality of semiconductor elements S1 to S4 connected to the DC power supply Cdc, and a flying capacitor Cfc connected to the semiconductor elements S1 to S4. In, the hold circuits 1 to 4 delay the timing of turning off the gate signals of the semiconductor elements S1 to S4 according to the charging state of the flying capacitor Cfc when the device is stopped. [Selection diagram] Fig. 3 | JP2021093819A | 2021-06-17 | JP2019222555A | 2019-12-10 | JP2019222555A, 2019-12-10 | JP2021093819A: 2021-06-17 | 株式会社明電舎 |  | H02M7/48: I H02M7/483: I |  |  |  | [JA JP2021093819A]: 直流電源と、直流電源に接続された複数の半導体素子と、半導体素子に接続されたフライングキャパシタと、を備えたマルチレベル電力変換器の制御装置であって、 装置停止時に、前記フライングキャパシタの充電状態に応じて、前記半導体素子のゲート信号をオフするタイミングを遅らせるホールド回路を備えたことを特徴とするマルチレベル電力変換器の制御装置。 フライングキャパシタ電圧と電圧指令値とを比較する比較器を備え、 装置停止時、かつ、前記フライングキャパシタ電圧が前記電圧指令値よりも大きい場合、前記フライングキャパシタを充電するスイッチングパターンとならないように前記ホールド回路を動作させ、 装置停止時、かつ、前記フライングキャパシタ電圧が前記電圧指令値よりも小さい場合、前記フライングキャパシタを放電するスイッチングパターンとならないように前記ホールド回路を動作させることを特徴とする請求項1記載のマルチレベル電力変換器の制御装置。 前記マルチレベル電力変換器は、 前記直流電源と、 前記直流電源の正極と負極との間に順次直列接続された第1~第4半導体素子と、 前記第1,第2半導体素子の接続点と前記第3,第4半導体素子の接続点との間に接続されたフライングキャパシタと、 を備え、前記第2,第3半導体素子の接続点を出力端子とすることを特徴とする請求項2記載のマルチレベル電力変換器の制御装置。 前記比較器は、 前記フライングキャパシタ電圧が前記電圧指令値よりも大きい場合に信号を出力する第1比較器と、 前記フライングキャパシタ電圧が前記電圧指令値よりも小さい場合に信号を出力する第2比較器と、であり、 前記ホールド回路は、 装置停止時に出力される停止信号および前記第2比較器の信号が入力された時、前記第1半導体素子のゲート信号がオフする時間を遅らせる第1ホールド回路と、 前記停止信号および前記第1比較器の信号が入力された時、前記第2半導体素子のゲート信号がオフする時間を遅らせる第2ホールド回路と、 前記停止信号および前記第1比較器の信号が入力された時、前記第3半導体素子のゲート信号がオフとなる時間を遅らせる第3ホールド回路と、 前記停止信号および前記第2比較器の信号が入力された時、前記第4半導体素子のゲート信号がオフとなる時間を遅らせる第4ホールド回路と、 であることを特徴とする請求項3記載のマルチレベル電力変換器の制御装置。 [EN JP2021093819A]: A control device for a multi-level power converter including a DC power supply, a plurality of semiconductor elements connected to the DC power supply, and a flying capacitor connected to the semiconductor element. When the device is stopped, the flying capacitor is charged. A control device for a multi-level power converter, which comprises a hold circuit for delaying the timing of turning off the gate signal of the semiconductor element according to a state. A comparer for comparing the flying capacitor voltage and the voltage command value is provided, and when the device is stopped and the flying capacitor voltage is larger than the voltage command value, the holding is performed so as not to be a switching pattern for charging the flying capacitor. The claim is characterized in that the circuit is operated, and when the device is stopped and the flying capacitor voltage is smaller than the voltage command value, the hold circuit is operated so as not to have a switching pattern for discharging the flying capacitor. 1 The control device for the multi-level power converter described. The multi-level power converter includes the DC power supply, first to fourth semiconductor elements sequentially connected in series between the positive electrode and the negative electrode of the DC power supply, and connection points of the first and second semiconductor elements. 2. The invention according to claim 2, further comprising a flying capacitor connected between the connection points of the third and fourth semiconductor elements, and using the connection points of the second and third semiconductor elements as output terminals. Multi-level power converter controller. The comparer is a first comparison device that outputs a signal when the flying capacitor voltage is larger than the voltage command value, and a second comparison device that outputs a signal when the flying capacitor voltage is smaller than the voltage command value. The hold circuit is a first hold that delays the off time of the gate signal of the first semiconductor element when the stop signal output when the device is stopped and the signal of the second comparator are input. The circuit, the second hold circuit that delays the time when the gate signal of the second semiconductor element is turned off when the stop signal and the signal of the first comparer are input, and the stop signal and the first comparer. When a signal is input, the third hold circuit that delays the time when the gate signal of the third semiconductor element is turned off, and when the stop signal and the signal of the second comparator are input, the fourth semiconductor element The control device for the multi-level power converter according to claim 3, wherein the fourth hold circuit delays the time when the gate signal of the gate signal is turned off. | [JA JP2021093819A]: 本発明は、フライングキャパシタを有するマルチレベル電力変換器の停止方法に関する。 特許文献1では、5レベル電力変換器を停止する際に、半導体素子を所定の順番で遮断することにより負荷側に印加される過電圧を防止している。 特開2018-117423号公報 しかし、特許文献1におけるマルチレベル電力変換器はフライングキャパシタを有していないため、フライングキャパシタ型のマルチレベル電力変換器にはスイッチングパターンをそのまま適用できない。 加えて、マルチレベル電力変換器を誘導性の負荷に接続した場合、装置停止後も電流が流れ続けるためフライングキャパシタの過充電もしくは過放電が発生し、フライングキャパシタの破損もしくは半導体素子の故障が発生する恐れがある。図6にフライングキャパシタを有する3レベル電力変換器を示す。 これは第1,第4半導体素子S1,S4には直流電源(コンデンサ)Cdcの電圧Vdcとフライングキャパシタ電圧V1の差分の電圧Vdc-V1、第2,第3半導体素子S2,S3にはフライングキャパシタ電圧V1の2種類の電圧が印加されるためであり、第1~第4半導体素子S1~S4のすべての過電圧故障を防ぐためにはフライングキャパシタCfcの過充電及び過放電の両方を防ぐ必要がある。 また、図6は、半導体素子に過電圧が印加される例を示している。四角で囲った半導体素子は導通している状態を表し、破線の矢印は電流の経路を表す。フライングキャパシタCfcの過電圧故障により装置が停止した場合、図6に示したパターンではフライングキャパシタCfcの充電が継続するため、フライングキャパシタ電圧V1が上昇し、フライングキャパシタCfcの破損やフライングキャパシタCfcに並列接続される第2半導体素子S2の過電圧故障につながる危険性がある。 以上示したようなことから、フライングキャパシタを有するマルチレベル電力変換器の制御装置において、フライングキャパシタ、半導体素子を破損させることなく安全に停止させることが課題となる。 本発明は、前記従来の問題に鑑み、案出されたもので、その一態様は、直流電源と、直流電源に接続された複数の半導体素子と、半導体素子に接続されたフライングキャパシタと、を備えたマルチレベル電力変換器の制御装置であって、装置停止時に、前記フライングキャパシタの充電状態に応じて、前記半導体素子のゲート信号をオフするタイミングを遅らせるホールド回路を備えたことを特徴とする。 また、その一態様として、フライングキャパシタ電圧と電圧指令値とを比較する比較器を備え、装置停止時、かつ、前記フライングキャパシタ電圧が前記電圧指令値よりも大きい場合、前記フライングキャパシタを充電するスイッチングパターンとならないように前記ホールド回路を動作させ、装置停止時、かつ、前記フライングキャパシタ電圧が前記電圧指令値よりも小さい場合、前記フライングキャパシタを放電するスイッチングパターンとならないように前記ホールド回路を動作させることを特徴とする。 また、その一態様として、前記マルチレベル電力変換器は、前記直流電源と、前記直流電源の正極と負極との間に順次直列接続された第1~第4半導体素子と、前記第1,第2半導体素子の接続点と前記第3,第4半導体素子の接続点との間に接続されたフライングキャパシタと、を備え、前記第2,第3半導体素子の接続点を出力端子とすることを特徴とする。 また、その一態様として、前記比較器は、前記フライングキャパシタ電圧が前記電圧指令値よりも大きい場合に信号を出力する第1比較器と、前記フライングキャパシタ電圧が前記電圧指令値よりも小さい場合に信号を出力する第2比較器と、であり、前記ホールド回路は、装置停止時に出力される停止信号および前記第2比較器の信号が入力された時、前記第1半導体素子のゲート信号がオフする時間を遅らせる第1ホールド回路と、前記停止信号および前記第1比較器の信号が入力された時、前記第2半導体素子のゲート信号がオフする時間を遅らせる第2ホールド回路と、前記停止信号および前記第1比較器の信号が入力された時、前記第3半導体素子のゲート信号がオフとなる時間を遅らせる第3ホールド回路と、前記停止信号および前記第2比較器の信号が入力された時、前記第4半導体素子のゲート信号がオフとなる時間を遅らせる第4ホールド回路と、であることを特徴とする。 本発明によれば、フライングキャパシタを有するマルチレベル電力変換器の制御装置において、フライングキャパシタ、半導体素子を破損させることなく安全に停止させることが可能となる。 フライングキャパシタ型3レベル電力変換器の主回路構成例を示す回路図。 スイッチングパターン例を示す図。 実施形態における制御装置を示すブロック図。 実施形態の動作例を示す図(V1&gt;Vref)。 実施形態の動作例を示す図(V1&lt;Vref)。 過電圧が発生する例を示す図。 以下、本願発明におけるマルチレベル電力変換器の制御装置の実施形態を図1~図5に基づいて詳述する。 [実施形態] 使用する半導体素子の耐圧を高耐圧化せずに回路自体を高圧化するための手法として半導体素子を多数直列に接続したマルチレベル電力変換器が検討されている。このマルチレベル電力変換器の一種として図1に示すようなフライングキャパシタ型のマルチレベル電力変換器が検討されている。図1に3レベルのフライングキャパシタ型のマルチレベル電力変換器を示す。なお、本実施形態では、3レベルの電力変換器について説明するが、フライングキャパシタを有していれば、他の主回路構成でも良い。 まず、図1に基づいて、3レベルのフライングキャパシタ型の電力変換器の構成を説明する。図1に示すように、マルチレベル電力変換器は、直流電源(コンデンサ)Cdcを有する。コンデンサCdcの正極と負極との間には、第1~第4半導体素子S1~S4が順次直列接続される。第1,第2半導体素子S1,S2の接続点と第3,第4半導体素子S3,S4の接続点との間にはフライングキャパシタCfcが接続される。 なお、第2,第3半導体素子S2,S3の接続点を出力端子とする。また、コンデンサCdcの電圧をVdc、フライングキャパシタCfcの電圧をV1、第2,第3半導体素子S2,S3の接続点の電流をi1とする。 3レベルの場合、一個のフライングキャパシタCfcと4つのIGBTなどの第1~第4半導体素子S1~S4より1アームが構成される。図1の構成ではコンデンサCdcの電圧をVdc,フライングキャパシタ電圧V1をVdc/2に制御することで動作することに特徴がある。 図2のように4種類のスイッチングパターンを使用することで3レベルの電圧を出力することができる。すなわち、(a)の場合はVdc、(b)の場合は0、(c),(d)の場合はVdc/2の3レベルの電圧を出力することができる。また、Vdc/2の電圧出力時に、電流i1の方向に応じてスイッチングパターンを(c),(d)から選択することでフライングキャパシタCfcの充電及び放電を選択できるので、フライングキャパシタ電圧V1を制御することが可能となる。 本実施形態は停止時にフライングキャパシタCfcの過充電による破損及び第1~第4半導体素子(IGBT)S1~S4の過電圧による破損を抑制することができる停止方法を説明する。本実施形態では、停止時にフライングキャパシタCfcの充電状態を加味して第1~第4半導体素子S1~S4の遮断するタイミングをずらすことにより、フライングキャパシタCfcの過充電を防ぐ同時に、第1~第4半導体素子S1~S4に過電圧が印加されることを防止する手法を説明する。 本実施形態における制御回路の構成例を図3に示す。図3に示すように、本実施形態の制御回路は、第1~第4ホールド回路1~4と、第1,第2比較器5,6と、を備える。第1比較器5は、フライングキャパシタ電圧V1と電圧指令値Vrefとを比較し、フライングキャパシタ電圧V1の方が大きい場合、信号を出力する。第2比較器6は、フライングキャパシタ電圧V1と電圧指令値Vrefとを比較し、フライングキャパシタ電圧V1の方が小さい場合、信号を出力する。 第1ホールド回路1は、第1半導体素子S1のゲート信号と装置停止時に出力される停止信号と第2比較器6の出力とを入力し、停止信号が入力され、且つ、フライングキャパシタ電圧V1が電圧指令値Vrefよりも小さい場合に動作し、第1半導体素子S1のゲート信号がオフするまでの時間を遅らせる。 第2ホールド回路2は、第2半導体素子S2のゲート信号と停止信号と第1比較器5の出力とを入力し、停止信号が入力され、且つ、フライングキャパシタ電圧V1が電圧指令値Vrefよりも大きい場合に動作し、第2半導体素子S2のゲート信号がオフするまでの時間を遅らせる。 第3ホールド回路3は、第3半導体素子S3のゲート信号と停止信号と第1比較器5の出力とを入力し、停止信号が入力され、且つ、フライングキャパシタ電圧V1が電圧指令値Vrefよりも大きい場合に動作し、第3半導体素子S3のゲート信号がオフするまでの時間を遅らせる。 第4ホールド回路4は、第4半導体素子S4のゲート信号と停止信号と第2比較器6の出力とを入力し、停止信号が入力され、且つ、フライングキャパシタ電圧V1が電圧指令値Vrefよりも小さい場合に動作し、第4半導体素子S4のゲート信号がオフするまでの時間を遅らせる。 図3の制御回路は第1~第4半導体素子S1~S4のゲートの状態をフライングキャパシタの充電状態に応じて任意の期間、維持する第1~第4ホールド回路1~4を設けた点に特徴がある。第1~第4ホールド回路1~4は停止信号が入力された場合、および、フライングキャパシタCfcの電圧状態が判定条件を満たしたときにのみ動作する。 図4に本実施形態の制御回路を適用した場合の動作例(V1&gt;Vref)を示す。図4の四角で囲った半導体素子は導通している状態を表し、破線の矢印は電流i1が正の場合、実線の矢印は電流i1が負の場合を表している。本実施形態の場合、フライングキャパシタCfcに流れる電流i1が放電方向にしか流れず過充電することなく運転ができる。すなわち、V1&gt;Vrefの場合は、第2,第3ホールド回路2,3を動作させることにより、フライングキャパシタCfcを充電するスイッチングパターンにならない。 図5に本実施形態の制御回路を適用した場合の動作例(V1&lt;Vref)を示す。図5の四角で囲った半導体素子は導通している状態を表し、破線の矢印は電流i1が正の場合、実線の矢印は電流i1が負の場合を表している。本実施形態の場合、フライングキャパシタCfcに流れる電流が充電方向にしか流れず、過放電することなく運転ができる。すなわち、V1&lt;Vrefの場合は、第1,第4ホールド回路1,4を動作させることにより、フライングキャパシタCfcを放電させるスイッチングパターンにならない。 したがって、本実施形態を適用することで、フライングキャパシタCfcの充電状況に応じて停止後も適切にフライングキャパシタCfcの充電及び放電が選択できるため過充電及び過放電を引き起こすことなく安全な停止方法を提供できる。 以上示したように、本実施形態によれば、フライングキャパシタを有するマルチレベル電力変換器においてフライングキャパシタ、半導体素子を破損させることなく安全に停止できる。 以上、本発明において、記載された具体例に対してのみ詳細に説明したが、本発明の技術思想の範囲で多彩な変形および修正が可能であることは、当業者にとって明白なことであり、このような変形および修正が特許請求の範囲に属することは当然のことである。 S1~S4:第1~第4半導体素子 Cdc:直流電源(コンデンサ) Cfc:フライングキャパシタ 1~4:第1~第4ホールド回路 5,6:第1,第2比較器 [EN JP2021093819A]: The present invention relates to a method of stopping a multi-level power converter having a flying capacitor. In Patent Document 1, when the 5-level power converter is stopped, the semiconductor elements are shut off in a predetermined order to prevent an overvoltage applied to the load side. JP-A-2018-117423 However, since the multi-level power converter in Patent Document 1 does not have a flying capacitor, the switching pattern cannot be applied as it is to the flying capacitor type multi-level power converter. In addition, when a multi-level power converter is connected to an inductive load, the current continues to flow even after the device is stopped, causing overcharging or overdischarging of the flying capacitor, resulting in damage to the flying capacitor or failure of the semiconductor element. There is a risk of Figure 6 shows a 3-level power converter with a flying capacitor. This is the voltage Vdc-V1 of the difference between the DC power supply (capacitor) Cdc voltage Vdc and the flying capacitor voltage V1 for the first and fourth semiconductor elements S1 and S4, and the flying capacitor for the second and third semiconductor elements S2 and S3. This is because two types of voltage V1 are applied, and it is necessary to prevent both overcharging and overdischarging of the flying capacitor Cfc in order to prevent all overvoltage failures of the first to fourth semiconductor elements S1 to S4. .. Further, FIG. 6 shows an example in which an overvoltage is applied to the semiconductor element. The semiconductor element surrounded by a square represents a conducting state, and the broken line arrow represents a current path. When the device is stopped due to an overvoltage failure of the flying capacitor Cfc, the flying capacitor Cfc continues to be charged in the pattern shown in Fig. 6, so the flying capacitor voltage V1 rises and the flying capacitor Cfc is damaged or connected in parallel to the flying capacitor Cfc. There is a risk of overvoltage failure of the second semiconductor element S2. From the above, it is an issue to safely stop the flying capacitor and the semiconductor element in the control device of the multi-level power converter having the flying capacitor without damaging them. The present invention has been devised in view of the above-mentioned conventional problems, and one aspect thereof includes a DC power supply, a plurality of semiconductor elements connected to the DC power supply, and a flying capacitor connected to the semiconductor elements. It is a control device of a multi-level power converter provided, and is characterized by including a hold circuit that delays the timing of turning off the gate signal of the semiconductor element according to the charging state of the flying capacitor when the device is stopped. .. Further, as one aspect thereof, a comparator for comparing the flying capacitor voltage and the voltage command value is provided, and switching for charging the flying capacitor when the device is stopped and when the flying capacitor voltage is larger than the voltage command value. The hold circuit is operated so as not to form a pattern, and when the device is stopped and the flying capacitor voltage is smaller than the voltage command value, the hold circuit is operated so as not to form a switching pattern for discharging the flying capacitor. It is characterized by that. Further, as one aspect thereof, the multi-level power converter includes the DC power supply, first to fourth semiconductor elements sequentially connected in series between the positive electrode and the negative electrode of the DC power supply, and the first and first semiconductor elements. 2 A flying capacitor connected between a connection point of a semiconductor element and a connection point of the third and fourth semiconductor elements is provided, and the connection point of the second and third semiconductor elements is used as an output terminal. It is a feature. Further, as one aspect thereof, the comparator is a first comparator that outputs a signal when the flying capacitor voltage is larger than the voltage command value, and when the flying capacitor voltage is smaller than the voltage command value. A second comparator that outputs a signal, and the hold circuit turns off the gate signal of the first semiconductor element when the stop signal output when the device is stopped and the signal of the second comparator are input. A first hold circuit that delays the time to stop, a second hold circuit that delays the time when the gate signal of the second semiconductor element is turned off when the stop signal and the signal of the first comparator are input, and the stop signal. And when the signal of the first comparer is input, the third hold circuit which delays the time when the gate signal of the third semiconductor element is turned off, the stop signal and the signal of the second comparer are input. At that time, it is characterized by a fourth hold circuit that delays the time when the gate signal of the fourth semiconductor element is turned off. According to the present invention, in a control device of a multi-level power converter having a flying capacitor, it is possible to safely stop the flying capacitor and the semiconductor element without damaging them. A circuit diagram showing a main circuit configuration example of a flying capacitor type 3-level power converter. The figure which shows the example of a switching pattern. The block diagram which shows the control device in an embodiment. The figure which shows the operation example of an embodiment (V1&gt; Vref). The figure which shows the operation example of an embodiment (V1 &lt;Vref). The figure which shows the example which an overvoltage occurs. Hereinafter, embodiments of the control device for the multi-level power converter according to the present invention will be described in detail with reference to FIGS. 1 to 5. [Embodiment] A multi-level power converter in which a large number of semiconductor elements are connected in series is being studied as a method for increasing the high voltage of the circuit itself without increasing the withstand voltage of the semiconductor element to be used. As a kind of this multi-level power converter, a flying capacitor type multi-level power converter as shown in FIG. 1 is being studied. Figure 1 shows a 3-level flying capacitor type multi-level power converter. In this embodiment, a three-level power converter will be described, but other main circuit configurations may be used as long as it has a flying capacitor. First, the configuration of a three-level flying capacitor type power converter will be described with reference to FIG. As shown in FIG. 1, the multi-level power converter has a DC power supply (capacitor) Cdc. The first to fourth semiconductor elements S1 to S4 are sequentially connected in series between the positive electrode and the negative electrode of the capacitor Cdc. A flying capacitor Cfc is connected between the connection points of the first and second semiconductor elements S1 and S2 and the connection points of the third and fourth semiconductor elements S3 and S4. The connection points of the second and third semiconductor elements S2 and S3 are used as output terminals. The voltage of the capacitor Cdc is Vdc, the voltage of the flying capacitor Cfc is V1, and the current at the connection points of the second and third semiconductor elements S2 and S3 is i1. In the case of 3 levels, 1 arm is composed of 1 flying capacitor Cfc and 1st to 4th semiconductor elements S1 to S4 such as 4 IGBTs. The configuration shown in Fig. 1 is characterized in that it operates by controlling the voltage of the capacitor Cdc to Vdc and the flying capacitor voltage V1 to Vdc / 2. As shown in Fig. 2, 3 levels of voltage can be output by using 4 types of switching patterns. That is, it is possible to output three levels of voltage: Vdc in the case of (a), 0 in the case of (b), and Vdc / 2 in the case of (c) and (d). In addition, when the voltage of Vdc / 2 is output, charging and discharging of the flying capacitor Cfc can be selected by selecting the switching pattern from (c) and (d) according to the direction of the current i1, so the flying capacitor voltage V1 is controlled. It becomes possible to do. This embodiment describes a stopping method capable of suppressing damage due to overcharging of the flying capacitor Cfc and damage due to overvoltage of the first to fourth semiconductor elements (IGBTs) S1 to S4 at the time of stopping. In the present embodiment, the charging state of the flying capacitor Cfc is taken into consideration when stopped, and the timing of shutting off the first to fourth semiconductor elements S1 to S4 is shifted to prevent overcharging of the flying capacitor Cfc, and at the same time, the first to first to first semiconductor elements are prevented from being overcharged. 4 A method for preventing an overvoltage from being applied to the semiconductor elements S1 to S4 will be described. A configuration example of the control circuit in this embodiment is shown in FIG. As shown in FIG. 3, the control circuit of the present embodiment includes first to fourth hold circuits 1 to 4 and first and second comparators 5 and 6. The first comparator 5 compares the flying capacitor voltage V1 with the voltage command value Vref, and outputs a signal when the flying capacitor voltage V1 is larger. The second comparator 6 compares the flying capacitor voltage V1 with the voltage command value Vref, and outputs a signal when the flying capacitor voltage V1 is smaller. The first hold circuit 1 inputs the gate signal of the first semiconductor element S1, the stop signal output when the device is stopped, and the output of the second comparator 6, the stop signal is input, and the flying capacitor voltage V1 is set. It operates when it is smaller than the voltage command value Vref, and delays the time until the gate signal of the first semiconductor element S1 turns off. The second hold circuit 2 inputs the gate signal and stop signal of the second semiconductor element S2 and the output of the first comparator 5, the stop signal is input, and the flying capacitor voltage V1 is higher than the voltage command value Vref. It operates when it is large, and delays the time until the gate signal of the second semiconductor element S2 turns off. The third hold circuit 3 inputs the gate signal and stop signal of the third semiconductor element S3 and the output of the first comparator 5, the stop signal is input, and the flying capacitor voltage V1 is higher than the voltage command value Vref. It operates when it is large, and delays the time until the gate signal of the third semiconductor element S3 is turned off. The fourth hold circuit 4 inputs the gate signal and stop signal of the fourth semiconductor element S4 and the output of the second comparator 6, the stop signal is input, and the flying capacitor voltage V1 is higher than the voltage command value Vref. It operates when it is small, and delays the time until the gate signal of the fourth semiconductor element S4 turns off. The control circuit shown in FIG. 3 is provided with first to fourth hold circuits 1 to 4 that maintain the gate state of the first to fourth semiconductor elements S1 to S4 for an arbitrary period according to the charging state of the flying capacitor. There is a feature. The 1st to 4th hold circuits 1 to 4 operate only when a stop signal is input and when the voltage state of the flying capacitor Cfc satisfies the judgment condition. FIG. 4 shows an operation example (V1&gt; Vref) when the control circuit of this embodiment is applied. The semiconductor elements surrounded by the squares in FIG. 4 represent the conductive state, the broken line arrows represent the case where the current i1 is positive, and the solid line arrows represent the case where the current i1 is negative. In the case of this embodiment, the current i1 flowing through the flying capacitor Cfc flows only in the discharge direction, and the operation can be performed without overcharging. That is, when V1&gt; Vref, the switching pattern for charging the flying capacitor Cfc is not obtained by operating the second and third hold circuits 2 and 3. FIG. 5 shows an operation example (V1 &lt;Vref) when the control circuit of this embodiment is applied. The semiconductor element surrounded by the square in FIG. 5 represents a conductive state, the broken line arrow represents the case where the current i1 is positive, and the solid line arrow represents the case where the current i1 is negative. In the case of this embodiment, the current flowing through the flying capacitor Cfc flows only in the charging direction, and the operation can be performed without over-discharging. That is, when V1 &lt;Vref, the switching pattern for discharging the flying capacitor Cfc is not obtained by operating the first and fourth hold circuits 1 and 4. Therefore, by applying this embodiment, charging and discharging of the flying capacitor Cfc can be appropriately selected even after stopping according to the charging status of the flying capacitor Cfc, so that a safe stopping method without causing overcharging and overdischarging can be performed. Can be provided. As described above, according to the present embodiment, in a multi-level power converter having a flying capacitor, the flying capacitor and the semiconductor element can be safely stopped without being damaged. Although the above description has been made in detail only with respect to the specific examples described in the present invention, it is clear to those skilled in the art that various modifications and modifications can be made within the scope of the technical idea of the present invention. It goes without saying that such modifications and modifications fall within the scope of the claims. S1 to S4: 1st to 4th semiconductor elements Cdc: DC power supply (capacitor) Cfc: Flying capacitor 1 to 4: 1st to 4th hold circuits 5,6: 1st and 2nd comparators
[ZH CN113395007A]: 一种适用于级联H桥多电平逆变器的新型功率均衡调制方法 [EN CN113395007A]: A new power balance modulation method suitable for cascaded H-bridge multilevel inverters | [ZH CN113395007A]: 本发明是一种适用于级联H桥多电平逆变器的均衡调制方法，属于多电平变流器PWM技术领域。该方法基于两倍的三角载波周期，使三角载波在不同载波层之间进行周期循环，与正弦调制波比较产生优化的脉冲信号。本发明的方法不仅可以实现各级联单元功率均衡控制，使直流侧电源放电保持一致，进而提高逆变器输出电压质量；也可以减少功率均衡所需时间；同时还可以具有最优的线电压谐波消谐性能。此外，该方法可以拓展至n个级联单元，从而提高了逆变器的实用性。 [EN CN113395007A]: The invention is a balanced modulation method suitable for cascaded H-bridge multilevel inverters, and belongs to the technical field of multilevel converter PWM. This method is based on twice the triangular carrier period, which makes the triangular carrier cycle cycle between different carrier layers, and compares with the sinusoidal modulation wave to generate an optimized pulse signal. The method of the present invention can not only realize the power balance control of the connected units at all levels, keep the DC side power supply discharge consistent, thereby improving the output voltage quality of the inverter; it can also reduce the time required for power balance; at the same time, it can also have the optimal line voltage. Harmonic elimination performance. In addition, the method can be extended to n cascade units, thereby improving the practicability of the inverter. | CN113395007A | 2021-09-14 | CN202110658681A | 2021-06-15 | CN202110658681A, 2021-06-15 | CN113395007A: 2021-09-14 | 安徽理工大学 |  | H02M7/5387: I H02M1/088: I H02M1/12: I H02M1/32: I |  |  |  | [ZH CN113395007A]: 1 .一种适用于级联H桥多电平逆变器的新型功率均衡调制方法，其特征是包括： ⑴该方法适用于n个H桥单元级联多电平逆变器，该拓扑的逆变器直流侧均为电源，且 电源电压相等。 (2)该方法应用与n单元级联H桥多电平逆变器时，需要n个幅值相等、频率相同的三角 载波，呈横向交替层叠排列。以横轴为参考线，横轴上方为H桥单元左桥臂所对应的载波区 域，横轴下方为H桥单元右桥臂所对应的载波区域。其中每个三角载波均在对应载波区域的 不同载波层进行周期循环，与正弦调制波调制产生优化的脉冲信号，从而实现级联单元输 出功率均衡，并保持最优的线电压消谐性能。 [EN CN113395007A]: 1 . A novel power balance modulation method suitable for cascaded H-bridge multilevel inverters, which is characterized by: This method is suitable for n H-bridge unit cascaded multilevel inverters. The DC sides of the converter are all power supplies, and the power supply voltages are equal. (2) When this method is applied to an n-unit cascaded H-bridge multilevel inverter, n triangular carrier waves with the same amplitude and the same frequency are required to be arranged alternately and stacked horizontally. Taking the horizontal axis as the reference line, the upper part of the horizontal axis is the carrier area corresponding to the left arm of the H-bridge unit, and the lower part of the horizontal axis is the carrier area corresponding to the right arm of the H-bridge unit. Among them, each triangular carrier is cycled periodically on different carrier layers in the corresponding carrier area, and modulated with a sinusoidal modulation wave to generate an optimized pulse signal, so as to realize the output power balance of the cascade unit and maintain the optimal line voltage harmonic elimination performance. | [ZH CN113395007A]: 一种适用于级联H桥多电平逆变器的新型功率均衡调制方法 技术领域 [0001]本发明属于多电平变流器PWM技术领域，具体涉及一种适用于级联H桥多电平逆变 器的新型功率均衡调制方法。 背景技术 [0002] 近年来，多电平逆变器由于电压应力小、电磁干扰小以及不存在开关管串联均压 问题，在高压大功率领域逐渐取代传统的两电平逆变器，成为了研究的热点。常见的多电平 逆变器拓扑有飞跨电容型、二极管箝位型以及级联H桥(Cascaded H-bridge，CHB)型等，其 中CHB型逆变器因其结构简单、易拓展、易模块化等优点，目前已在静止无功补偿器、电力有 源滤波器、电力电子变压器等场合得到广泛应用。 [0003]多电平调制技术作为多电平逆变器控制中的关键技术之一，直接决定了逆变器输 出电压质量和逆变器的性能。载波移相调制(Carrier Phase-Shifted PWM，CPS-PWM)法能 够实现级联单元间的功率自均衡，但在合成线电压电平时存在不规律的跳变现象而导致线 电压质量较差;而载波同向层叠调制(In-Phase Disposition PWM，IPD-PWM)法具有线电压 最优的性能，但无法实现级联单元功率均衡控制。目前主流的一些解决功率均衡问题的方 法是脉冲信号周期轮换法，如1/4周期脉冲轮换法、1/2周期脉冲轮换法等，都是在输出周期 层面进行功率均衡，功率均衡时间较长，且随着级联数的增加，均衡时间会进一步增加。因 此，需要综合考虑级联输出功率均衡和输出线电压质量，解决两者之间存在的矛盾，同时缩 短功率均衡时间，提高该拓扑逆变器的实用性。 发明内容 [0004] 发明目的 [0005]本发明是针对级联H桥多电平逆变器，提出一种新型功率调制方法，解决级联输出 功率均衡和输出线电压质量之间存在的矛盾，同时缩短功率均衡时间。 [0006] 技术方案 [0007]本发明技术方案如下： [0008] 1)该级联H桥多电平逆变器由n个H桥单元级联而成，其直流侧均为电源，且电源电 压相等，即Ud1 = Ud2=…= Udn = E。 [0009] 2)对于n个级联单元,本发明的方法需要n个幅值相等、频率相同的三角载波，呈横 向交替层叠排列。以横轴为参考线，横轴上方为H桥单元左桥臂所对应的载波区域，横轴下 方为H桥单元右桥臂所对应的载波区域。其中每个三角载波均在对应载波区域的不同载波 层进行周期循环，与正弦调制波调制产生优化的脉冲信号。 [0010] 3)逆变器输出电压的理论总电平数为2n+1。 [0011] 有益效果 [0012]本发明的方法既可以使级联H桥多电平逆变器在各级联单元输出功率均衡，同时 缩短功率均衡时间，还可以保证线电压消谐性能最优，从而改善了逆变器输出特性，同时本 发明的方法还可以应用于n个单元的级联H桥多电平逆变器，提高了该逆变器拓扑的实用 性。 附图说明 [0013]下面结合附图和实施实例对本发明方法作进一步说明。 [0014]图1是级联Η桥多电平逆变器拓扑主电路。 [0015]图2是载波的排列方式，其中（a）为级联单元左桥臂所对应的载波排列情况；（b）为 级联单元右桥臂所对应的载波排列情况。 [0016] 图3是新型功率均衡调制原理图。 [0017]图4是应用本发明所提的新型功率均衡调制法各级联单元输出电压仿真波形，其 中（a）为调制比M=0.6时逆变器输出波形，（b）为M=0.9时逆变器输出波形。 [0018]图5是在M=0.6时各级联单元输出电压的频谱分析图。 [0019]图6是在M=0.9时各级联单元输出电压的频谱分析图。 [0020]图7是在M=0.9时各级联单元瞬时输出功率波形图。 [0021]图8是任取的一个载波循环周期Tr内各级联单元瞬时输出功率波形图。 [0022]图9是在M=0.9时逆变器输出电压的频谱分析图。 [0023]图10是在M=0.9时逆变器输出线电压的频谱分析图。 [0024]图11是三种调制方法下调制比与总谐波失真率（THD）关系的曲线图。 具体实施方式 [0025]图1给出了 CHB型逆变器的电路拓扑,该拓扑包含η个Η桥单元，每个Η桥单元直流侧 均为电源，且电源电压相等，即% = %=…=%η = Ε。此外，Η桥单元的功率开关器件使用 IGBT、GTO等全控型器件，具体器件选择根据电压等级、开关频率等影响因素综合考虑进行 选择。 [0026]该拓扑每个单元均可以输出7、0和1三种电平,则每个单元输出电压可以表示为 [°°2力 uoi = xUdi （1） [0028]式中，u°i为第i个Η桥单元的输出电压，i = 1,2 ,…η, χ为Η桥单元输出电平情况,χ =7,0,1网由为级联单元的直流侧电源电压。 [0029]由式⑴可得该拓扑逆变器的输出电压u。为 * [0030] % = ⑵ [0031] 为了方便分析，下面以三单元CHB型逆变器为例对本发明方法的原理进行说明。当 η = 3时，根据式⑴-⑵可知逆变器最多可以输出七电平的电压波形,各个电平合成原理如 表1所示。可见除了峰值电平外，其余电平都有冗余的合成方式，这也决定了调制方式的多 样性，为该拓扑逆变器输出性能的改进提供了有利条件。 [0032] 表1逆变器输出电压电平合成情况 输出电压电平 电平合成方式（χρχ2,χ3） 3Ε (1,1,1) 2Ε (1,1,0),(1,0,1),(0,1,1) Ε (1,0,0) , (0,1,0) , (0,0,1) , (1,-1,1) , (1,1,-1) , (-1,1,1) 0 (0,0,0) (0,1,-1), (0,-1,1), (1,-1,0), (1,0,-1), (-1,1,0), (-1,0,1) -Ε (0,-1,0) , (0,0,-1) , (-1,0,0) , (-1,-1,1) , (-1,1,-1) , (1,-1,-1) -2Ε (-1,-1,0), (-1,0,-1), (0,-1,-1) -3Ε (-1,-1,-1) [0034]对于该拓扑而言，需要6个幅值、频率、相位都相等的三角载波，其排列情况如图2 所示，设三角载波幅值为E,频率为1/T。。图2中，对横向排列的载波进行分层，自上至下依次 排序,最上层为第1层,最下层则为第6层。左桥臂所对应的三角载波如图2 (a)所示分布在第 1-3层载波层,而右桥臂所对应的载波图2⑹所示分布在第4-6层载波层。 [0035]图2(a)中，ν0ι+、νθ2+、ν03+分别为第i个Η桥单元左桥臂所对应的载波,Ί；为一个循环 周期,且满足Τ== 6Τ°。在载波层第1层，有111、110、101、011四种电平合成方式；在载波层第2 层，有110、101、011、100、001、010六种电平合成方式；在载波层第3层,有100、001、010、000 四种电平合成方式,可见该方法充分利用了该逆变器本身的电平合成方式冗余特性。载波 νθι+、νθ2+、νθ3+在不同载波层进行周期循环，以载波为例进行说明。在。〜2(内，%1+在载 波层第一层;在2T。〜4T。时,ν»向下平移E个单位,从载波层第一层进入第二层；在4T。〜6T。 内，ν。向下平移E个单位，从载波层第二层进入第三层,此时为一个循环周期后续周期 重复上述动作，以作周期循环。 [0036]图2⑹中，ν…、七、ν°3.分别为第i个Η桥单元右桥臂所对应的载波,分布于横轴下 方的三个载波层。在载波层第4层，有-100、00-1、0-10、000四种电平合成方式；在载波第5 层，有-l-10、-10-l、0-l-l、-100、00-l、0-10六种电平合成方式；在载波第6层,有-l-l-l、l-10、-10-l、0-l-l,可见右桥臂的调制区域的电平合成方式与左桥臂呈对称状态，即载波 周期循环的方向与左桥臂相反。 [0037]图3给出了新型均衡调制方法的调制原理图，vref为正弦调制波，其表达式满足式 ⑶，u°]、u°2、u03为级联单元输出电压,u。为逆变器输出电压。 [0038] vref = 3ME sin (ω t) (3) [0039] /中,M为调制比，3为调制波的角频率。 [0040]图3中，调制波Ve分别与三角载波丫01+、％2+、％3+、丫θ1.、丫°2.、43.比较产生功率开关 的脉冲驱动信号A、B、C、H、P和Q。当调制波vref大于ν°ι+、ν°2+、ν°3+时,脉冲驱动信号A、B、C取1, 否则取0；当调制波Qef小于ν°]_、ν°2 .、V°3 一时,脉冲驱动信号H、P、Q取1,否则取0。此时,各单元 功率开关脉冲驱动信号逻辑信号表达式为： [0041] 乌=彳 214 =后 [04= A 匕2=。[屐4=0 (4) [0042]各级联单元输出电压可由各功率开关的逻辑脉冲信号表示，其关系表达式为 [0043] =(Α-Η)χΕ + (Α·Η)χΕ (5) [0044] 42 =(8,乃xE +(反加xE (6) [0045] uo^(C-Q)xE + (C-Q)xE (7) [0046]由式(5)-⑺可知，应用本发明的方法，每个级联Η桥均可以输出3种电平状态，且 不存在同一桥臂同时导通的情况。 [0047] [0048] 下面对输出电压进行双重傅里叶变换，输出电压u。可以表示为 KO Ε ·κο 皤(7) = 32Esin(创)十—£ {g泡 cos[(2m-1)^/ + 2«^]) tn=i (2m-L)n w=_ffi J GO 灯 ,8. +Σ7―2 Σ {§，，.“ sin [2用。/ +(2”1)加} 川=]/WL /j=—go [0049]式中，3°为载波的频率,C%n为余弦参数,S*n为正弦参数。 [0050]余弦参数为 [0051] C,„ „ = 8 £ Λ[(6^ -3)½].-i― cos 2# + 发〔 [0052]正弦参数S*n为 [0053] Smn = 2nJ2n；(6mMn) (10) [0054]由式(8)可知，采用本发明的新型功率均衡调制法得到的逆变器输出电压在m=l (2/i-HA)arcsini -cos (2/7 + A)arcsinί (9) 时最低次谐波主要集中在九及其边带谐波处。 [0055] 下面以三单元CHB型逆变器为例，利用Matlab2018/Simulink搭建仿真平台，对本 发明的新型功率均衡调制方法的特点及性能作进一步说明。具体参数设置如下:直流侧电 源电压E为1000V,负载电阻R为50Q ,滤波电感L为10mH,基波频率Μ为50Hz,三角载波频率九 为7.2kHz。 [0056] 调制比为0.6和0.9时的级联单元输出电压和逆变器输出电压波形如图4所示，其 中图4 (a)为M=0.6时的输出电压波形情况，图4⑹为M=0.9时的输出电压情况。 [0057] 从图4 (a)可以看出，在M = 0.6时各级联单元输出电压波形基本一致，此时逆变器 输出五电平的电压波形;从图4(b)可以看出，在M = 0.9时各级联单元输出电压波形也基本 保持一致,而此时逆变器可以输出七电平的电压波形。此外，由图4还可以看出，随着调制比 的增大,逆变器输出电压脉宽随之变宽，但各级联单元输出电压波形始终保持一致,并不受 调制比变化的影响。 [0058]为了深入分析各级联单元输出电压之间的关系，对其进行频谱分析，图5图6分别 给出了调制比为0.6和0.9时各级联单元输出电压的频谱分析情况。 [0059]由图5图6可知，不同调制度下各级联单元输出电压的频谱分布基本相同，且调制 度的变化并几乎不影响级联单元输出电压频谱分布，所以逆变器输出电压的频谱分布也不 会随调制度的改变而改变。此外,M = 0.6时，各级联输出电压的基波幅值分别为601.5V、 599丫、599.6丫⑶=0.9时，各级联输出电压的基波幅值分别为902.5丫、901.卜、901.2丫，因此 在不同调制比下各级联单元输出电压的基波幅值近似相等，则各单元输出电压可以实现均 衡分配。又由于级联关系是级联单元间的串联关系，因此各单元输出电流是相同的,所以各 级联单元输出功率可以实现均衡控制。 [0060] 各级联单元瞬时输出功率如图7所示，p。ι、p。2、P。3分别为各级联单元输出功率，可 见各单元输出功率波形近似相同，经Matlab的mean工具测量，在输出周期Τ。内，各单元输出 功率平均值P。ι、P。2、P。3分别为24296W、24223W、24291W,所以各级联单元输出功率近似相等， 从而可以实现了各级联输出功率自均衡。为了说明在功率均衡时间的优越性，对循环周期 时间I (Τ== 6Τ°)内的输出功率情况进行分析，如图8所示为任意取得一个Ί；内级联单元输 出功率情况。经测量，在Tr内各级联单元输出功率的平均值Po1、Po2、Po3分别为48097W、 48123W、48142W,则Po1、Po2、Po3近似相等。此时，实现功率均衡时间仅使用了83.3us,远小于 输出周期时间(To = 0.2s)。综上分析可知本发明的方法可在Tr内实现功率均衡，而一般情况 下载波周期时间远小于输出周期，所以在实现功率均衡前提下，本发明的方法进一步缩短 了功率均衡时间。 [0061]图9给出了M = 0.9时逆变器输出电压频谱分布情况，可见输出电压的主要谐波频 率在fc处，与式⑻分析情况相吻合。 [0062]图10给出了M=0.9时逆变器输出线电压频谱分布情况，图11给出了M=0.9时采用 IPD-PWM、CPS-PWM及本发明的方法所得到的线电压总谐波失真率(THD)与调制度M的关系曲 线，可见采用IPD-PWM法得到线电压的THD在全调制范围内都比CPS-PWM小，而采用本发明的 方法得到线电压的THD与在全调制范围内与IPD-PWM法具有相同的谐波性能，因此本发明的 方法也具有最优的线电压消谐性能。 [0063]应当理解的是，对于本领域普通技术人员来说，可以根据上述说明加以改进或变 换，而所有这些改进和变换都应属于本发明所附权要求的保护范围。 [EN CN113395007A]: A new type of power balance modulation method suitable for cascaded H-bridge multilevel inverterTechnical field [0001] The present invention belongs to the technical field of multilevel converter PWM, and specifically relates to a novel power balance modulation method suitable for cascaded H-bridge multilevel inverters. Background technique [0002] In recent years, multi-level inverters have gradually replaced the traditional two-level inverters in the field of high-voltage and high-power because of low voltage stress, low electromagnetic interference, and the absence of the problem of voltage equalization in series. Hot spot. Common multi-level inverter topologies include flying capacitor type, diode clamp type, and cascaded H-bridge (CHB) type. Among them, the CHB type inverter is simple in structure, easy to expand, and easy to expand. Modularization and other advantages have been widely used in static var compensators, power active filters, power electronic transformers and other occasions. [0003] Multi-level modulation technology, as one of the key technologies in multi-level inverter control, directly determines the output voltage quality of the inverter and the performance of the inverter. Carrier Phase-Shifted PWM (CPS-PWM) method can achieve self-equalization of power between cascaded units, but there is an irregular jump phenomenon when the line voltage level is synthesized, resulting in poor line voltage quality; and In-Phase Disposition PWM (IPD-PWM) method has the best performance of line voltage, but it cannot realize the power balance control of cascade unit. At present, some mainstream methods to solve the problem of power balance are pulse signal cycle rotation methods, such as 1/4 cycle pulse rotation method, 1/2 cycle pulse rotation method, etc., all of which perform power balance at the output cycle level, and the power balance time is longer. And as the number of cascades increases, the equalization time will further increase. Therefore, it is necessary to comprehensively consider the cascaded output power balance and the quality of the output line voltage to resolve the contradiction between the two, while shortening the power balance time and improving the practicability of the topology inverter. Summary of the invention [0004] Purpose of the invention [0005] The present invention proposes a new type of power modulation method for cascaded H-bridge multilevel inverters to solve the contradiction between cascaded output power balance and output line voltage quality, and at the same time shorten the power balance time. [0006] Technical Solution [0007] The technical scheme of the present invention is as follows: [0008] 1) The cascaded H-bridge multilevel inverter is formed by cascading n H-bridge units, and the DC sides are all power supplies, and the power supply voltages are equal, that is, Ud1 = Ud2=...= Udn = E. [0009] 2) For n cascaded units, the method of the present invention requires n triangular carrier waves with the same amplitude and the same frequency, which are alternately stacked in a horizontal arrangement. Taking the horizontal axis as the reference line, the upper part of the horizontal axis is the carrier area corresponding to the left arm of the H-bridge unit, and the lower part of the horizontal axis is the carrier area corresponding to the right arm of the H-bridge unit. Among them, each triangular carrier is cycled periodically on different carrier layers in the corresponding carrier area, and modulated with a sinusoidal modulation wave to generate an optimized pulse signal. [0010] 3) The theoretical total number of levels of the inverter output voltage is 2n+1. [0011] Benefits [0012] The method of the present invention can not only equalize the output power of the cascaded H-bridge multilevel inverter at each level of the connected unit, but also shorten the power equalization time, and can also ensure the optimal line voltage harmonic elimination performance, thereby improving the inverse Converter output characteristics, while the The invented method can also be applied to a cascaded H-bridge multilevel inverter with n units, which improves the practicability of the inverter topology. Description of the drawings [0013] The method of the present invention will be further described below with reference to the drawings and implementation examples. [0014] FIG. 1 is the main circuit of the cascaded H-bridge multi-level inverter topology. [0015] FIG. 2 is an arrangement of carriers, where (a) is the arrangement of carriers corresponding to the left arm of the cascade unit; (b) is the arrangement of carriers corresponding to the right arm of the cascade unit. [0016] FIG. 3 is a schematic diagram of a novel power balance modulation. [0017] FIG. 4 is a simulation waveform of the output voltage of the connected unit of the new power balance modulation method proposed by the present invention, where (a) is the inverter output waveform when the modulation ratio M=0.6, and (b) is M=0.9 When the inverter outputs the waveform. [0018] FIG. 5 is a spectrum analysis diagram of the output voltage of each level of the connection unit when M=0.6. [0019] FIG. 6 is a spectrum analysis diagram of the output voltage of each level of the connection unit when M=0.9. [0020] FIG. 7 is a waveform diagram of the instantaneous output power of the connected units when M=0.9. [0021] FIG. 8 is an arbitrary waveform diagram of the instantaneous output power of the connected units within a carrier cycle period Tr. [0022] FIG. 9 is a spectrum analysis diagram of the inverter output voltage when M=0.9. [0023] FIG. 10 is a spectrum analysis diagram of the inverter output line voltage when M=0.9. [0024] FIG. 11 is a graph showing the relationship between modulation ratio and total harmonic distortion (THD) under three modulation methods. Detailed ways [0025] Figure 1 shows the circuit topology of the CHB inverter. The topology includes n H bridge units. Each H bridge unit is a power supply on the DC side, and the power supply voltages are equal, that is, %=%=...=% η = Ε. In addition, the power switching devices of the H-bridge unit use fully-controlled devices such as IGBTs and GTOs, and the specific device selection is selected based on comprehensive consideration of influencing factors such as voltage level and switching frequency. [0026] In this topology, each unit can output three levels of 7, 0, and 1, so the output voltage of each unit can be expressed as [°°2 Force uoi = xUdi （1） [0028] In the formula, u°i is the output voltage of the i-th H bridge unit, i=1,2,...η, χ is the output level of the H bridge unit, and χ=7,0,1 network is the level DC side power supply voltage of the connected unit. [0029] The output voltage u of the topology inverter can be obtained by formula (1). for * [0030] % = ⑵ [0031] For the convenience of analysis, the principle of the method of the present invention will be described below by taking a three-unit CHB inverter as an example. When η = 3, according to formula -, it can be known that the inverter can output a voltage waveform of seven levels at most, and the synthesis principle of each level is shown in Table 1. It can be seen that in addition to the peak level, the other levels have redundant synthesis methods, which also determines the diversity of modulation methods and provides favorable conditions for the improvement of the output performance of the topology inverter. [0032] Table 1 Inverter output voltage level synthesis Output voltage level Level synthesis method (χρχ2,χ3） 3Ε (1,1,1) 2Ε (1,1,0),(1,0,1),(0,1,1) Ε (1,0,0) , (0,1,0) , (0,0,1) , (1,-1,1) , (1,1,-1) , (-1,1,1) 0 (0,0,0) (0,1,-1), (0,-1,1), (1,-1,0), (1,0,-1), (-1,1,0), (-1,0,1) -Ε (0,-1,0) , (0,0,-1) , (-1,0,0) , (-1,-1,1) , (-1,1,-1) , (1,-1,-1) -2Ε (-1,-1,0), (-1,0,-1), (0,-1,-1) -3Ε (-1,-1,-1) [0034] For this topology, 6 triangular carriers with equal amplitude, frequency, and phase are required, and the arrangement is shown in FIG. 2, assuming that the triangular carrier amplitude is E and the frequency is 1/T. . In Figure 2, the horizontally arranged carriers are layered and sorted from top to bottom. The top layer is the first layer, and the bottom layer is the sixth layer. The triangular carrier corresponding to the left bridge arm is distributed on the carrier layer 1-3 as shown in Figure 2 (a), and the carrier corresponding to the right bridge arm is distributed on the carrier layer 4-6 as shown in Figure 2. [0035] In FIG. 2(a), ν0ι+, νθ2+, and ν03+ are respectively the carrier corresponding to the left arm of the i-th H bridge unit, Ί; is a cycle period, and satisfies Τ==6Τ°. In the first layer of the carrier layer, there are four levels of 111, 110, 101, 011; in the second layer of the carrier layer, there are six levels of 110, 101, 011, 100, 001, 010; in the carrier In the third layer, there are four level synthesis methods of 100, 001, 010, and 000. It can be seen that this method makes full use of the redundancy characteristics of the inverter's own level synthesis mode. Carriers νθι+, νθ2+, and νθ3+ are cycled periodically in different carrier layers, and the carrier is taken as an example for description. exist. ~2(Inside, %1+ is in the first layer of the carrier layer; at 2T. ~4T. When ν» is shifted down by E units, from the first layer of the carrier layer to the second layer; in 4T.~6T. In , Ν. Shift down E units, from the second layer of the carrier layer to the third layer, at this time, repeat the above actions for a cycle cycle and subsequent cycles to make a cycle cycle. [0036] In Figure 2, ν..., VII, ν°3. are the carriers corresponding to the right bridge arm of the i-th H bridge unit, which are distributed in the three carrier layers below the horizontal axis. On the fourth layer of the carrier layer, there are four levels of -100, 00-1, 0-10, and 000; on the fifth layer of the carrier, there are -l-10, -10-l, 0-ll, -100 , 00-l, 0-10 six level synthesis methods; in the 6th layer of the carrier, there are -lll, l-10, -10-l, 0-ll, you can see the level synthesis mode of the modulation area of the right bridge arm It is symmetrical with the left bridge arm, that is, the direction of the carrier cycle cycle is opposite to that of the left bridge arm. [0037] FIG. 3 shows the modulation principle diagram of the new balanced modulation method, vref is a sinusoidal modulation wave, and its expression satisfies the formula (3), u°], u°2, and u03 are the output voltages of the cascade unit, u. Output voltage for the inverter. [0038] vref = 3ME sin (ω t) (3) [0039] In /, M is the modulation ratio, and 3 is the angular frequency of the modulating wave. [0040] In FIG. 3, the modulation wave Ve is compared with the triangular carrier Y01+, %2+, %3+, Yθ1., Y°2., 43. to generate the pulse drive signals A, B, and C of the power switch, respectively. , H, P and Q. When the modulating wave vref is greater than ν°ι+, ν°2+, ν°3+, the pulse drive signals A, B, C take 1, otherwise take 0; when the modulating wave Qef is less than ν°]_, ν°2. ,V°3 At one time, the pulse drive signals H, P, Q take 1, otherwise take 0. At this time, the logic signal expression of each unit power switch pulse drive signal is: [0041] Wu= 214 = After [04= A dagger 2=. [clog4=0 (4) [0042] The output voltage of each level of the connected unit can be represented by the logic pulse signal of each power switch, and the relational expression is [0043] =(Α-Η)χΕ + (Α·Η)χΕ (5) [0044] 42 = (8, is xE + (inversely add xE (6) [0045] uo^(CQ)xE + (CQ)xE (7) [0046] It can be seen from equations (5)- that, applying the method of the present invention, each cascaded H bridge can output 3 level states, and There is no situation where the same bridge arm is turned on at the same time. [0047] [0048] Next, double Fourier transform is performed on the output voltage to output the voltage u. It can be expressed as KO Ε ·κο white(7) = 32Esin(Invasive)ten-£ {gbubblecos[(2m-1)^/ + 2«^]) tn=i (2m-L)n w=_ffi J GO lights, 8. +Σ72 Σ {§,,." sin [2 is used. / +(2"1) plus} Sichuan=]/WL /j=-go [0049] In the formula, 3° is the frequency of the carrier, C%n is the cosine parameter, and S*n is the sine parameter. [0050] The cosine parameter is [0051] C,= 8 £ Λ[(6^ -3)½].-i cos 2# + send [0052] The sine parameter S*n is [0053] Smn = 2nJ2n; (6mMn) (10) [0054] It can be seen from equation (8) that the output voltage of the inverter obtained by the novel power balance modulation method of the present invention is m = l (2/i-HA) arcsini When -cos (2/7 + A)arcsinί (9), the lowest harmonics are mainly concentrated at the ninth and its sideband harmonics. [0055] Taking a three-unit CHB inverter as an example, a simulation platform is built using Matlab2018/Simulink to further illustrate the characteristics and performance of the novel power balance modulation method of the present invention. The specific parameters are set as follows: DC side power supply voltage E is 1000V, load resistance R is 50Q, filter inductance L is 10mH, fundamental frequency M is 50Hz, and triangular carrier frequency 9 is 7.2kHz. [0056] The cascaded unit output voltage and inverter output voltage waveforms when the modulation ratio is 0.6 and 0.9 are shown in Figure 4, where Figure 4 (a) is the output voltage waveform when M=0.6, and Figure 4 is M =0.9 when the output voltage situation. [0057] As can be seen from Figure 4 (a), when M = 0.6, the output voltage waveforms of the connected units are basically the same. At this time, the inverter outputs a five-level voltage waveform; as can be seen from Figure 4 (b) , When M = 0.9, the output voltage waveforms of the connected units at all levels are basically the same, and the inverter can output a seven-level voltage waveform at this time. In addition, it can be seen from Figure 4 that as the modulation ratio increases, the inverter output voltage pulse width becomes wider, but the output voltage waveforms of the connected units at all levels are always consistent and are not affected by the modulation ratio changes. . [0058] In order to deeply analyze the relationship between the output voltages of the connected units at various levels and perform a spectrum analysis on them, Fig. 5 and Fig. 6 respectively show the spectrum analysis conditions of the output voltages of the connected units at each level when the modulation ratio is 0.6 and 0.9. [0059] It can be seen from FIG. 5 and FIG. 6 that the spectral distribution of the output voltage of the cascade unit under different modulation degrees is basically the same, and the change of the modulation degree hardly affects the output voltage spectral distribution of the cascade unit, so the output voltage of the inverter is The frequency spectrum distribution will not change with the modulation degree. In addition, when M = 0.6, the fundamental wave amplitudes of the output voltage of each stage are 601.5V, 599 Ah, and 599.6 Ah respectively. When = 0.9, the fundamental wave amplitudes of the output voltage of each stage are 902.5 Ah and 901. Bu, respectively. , 901.2 Ah, therefore, the fundamental wave amplitudes of the output voltages of the connected units at different modulation ratios are approximately equal, and the output voltages of each unit can be evenly distributed. Also, because the cascade relationship is a series relationship between cascaded units, the output current of each unit is the same, so the output power of the cascaded units can be balanced and controlled. [0060] The instantaneous output power of each level of the connected unit is shown in Figure 7, p. ι, p. 2. P. 3 is the output power of the connected units at all levels. It can be seen that the output power waveforms of each unit are approximately the same, measured by the mean tool of Matlab, in the output cycle T. Inside, the average value P of the output power of each unit. ι, P. 2. P. 3 are 24296W, 24223W, and 24291W respectively, so the output power of the connected units at each level is approximately equal, so that the output power self-equalization of the connected units at each level can be realized. In order to illustrate the superiority of the power equalization time, the output power situation in the cycle time I (Τ== 6Τ°) is analyzed, as shown in Fig. 8 is an arbitrary Ί; the internal cascade unit output The output power situation. After measurement, at TrThe average value of the output power of the internal connection unit Po1, Po2, Po348097W, 48123W, 48142W, then Po1, Po2, Po3Approximately equal. At this time, only 83.3us is used to achieve power balance time, which is much less than the output cycle time (To = 0.2s). Based on the above analysis, it can be seen that the method of the present invention can be used in TrIn general, the cycle time of the download wave is much shorter than the output cycle. Therefore, the method of the present invention further shortens the power equalization time under the premise of realizing the power balance. [0061] Figure 9 shows the frequency spectrum distribution of the inverter output voltage when M = 0.9. It can be seen that the main harmonic frequency of the output voltage is at fcAt the same time, it is consistent with the analysis of formula . [0062] Fig. 10 shows the frequency spectrum distribution of the inverter output line voltage when M=0.9, and Fig. 11 shows the total line voltage obtained by using IPD-PWM, CPS-PWM and the method of the present invention when M=0.9. The relationship curve between the harmonic distortion rate (THD) and the modulation degree M, it can be seen that the THD of the line voltage obtained by the IPD-PWM method is smaller than that of the CPS-PWM in the full modulation range, and the THD of the line voltage obtained by the method of the present invention is smaller than that of the CPS-PWM method. In the full modulation range, it has the same harmonic performance as the IPD-PWM method, so the method of the present invention also has the best line voltage harmonic elimination performance. [0063] It should be understood that for those of ordinary skill in the art, improvements or transformations can be made based on the above description, and all these improvements and transformations should fall within the protection scope of the appended claims of the present invention.
[JA JP2020182338A]: 半導体スイッチング素子駆動回路及びマルチレベル電力変換器 [EN JP2020182338A]: SEMICONDUCTOR SWITCHING ELEMENT DRIVE CIRCUIT AND MULTI-LEVEL POWER CONVERTER | [JA JP2020182338A]: 【課題】マルチレベル電力変換器の半導体スイッチング素子を駆動するにあたって、新たな電源を追加することなく負電圧を生成する。 【解決手段】マルチレベル電力変換器に設けられた半導体スイッチング素子SW1~SW4を駆動する半導体スイッチング素子駆動回路6において、第1の駆動回路8aは、第1のコンデンサ9(a)と、第2のコンデンサ10(a)と、充電状態の第2のコンデンサから放電された電力を充電することで半導体スイッチング素子SW1を遮断状態にするための負電圧を生成する第3のコンデンサ16(a)と、を備える。 【選択図】図2 [EN JP2020182338A]: To generate a negative voltage without adding a new power supply when driving a semiconductor switching element of a multi-level power converter.SOLUTION: In a semiconductor switching element drive circuit 6 for driving semiconductor switching elements SW1 to SW4 provided in a multi-level power converter, a first drive circuit 8a includes a first capacitor 9(a), a second capacitor 10(a), and a third capacitor 16(a) for generating a negative voltage for cutting off the semiconductor switching element SW1 by charging power discharged from a second capacitor in a charged state.SELECTED DRAWING: Figure 2 | JP2020182338A | 2020-11-05 | JP2019084659A | 2019-04-25 | JP2019084659A, 2019-04-25 | JP2020182338A: 2020-11-05 | IHI CORP | KATSURA KENSHIRO YAMAGUCHI KOJI | H02M1/08: I H02M7/487: I |  |  |  | [JA JP2020182338A]: マルチレベル電力変換器に設けられたn個(nは4以上の整数)の半導体スイッチング素子を駆動する半導体スイッチング素子駆動回路であって、 前記半導体スイッチング素子ごとに設けられた複数の駆動回路を備え、 前記各駆動回路は、 前記半導体スイッチング素子を導通状態にするための正電圧を生成する第1のコンデンサと、 第1の端部が前記第1のコンデンサの第1の端部に接続されている第2のコンデンサと、 充電状態の前記第2のコンデンサから放電された電力を充電することで前記半導体スイッチング素子を遮断状態にするための負電圧を生成する第3のコンデンサと、 前記第1のコンデンサの第1の端部と前記半導体スイッチング素子の制御端子とを接続することにより前記正電圧を前記半導体スイッチング素子の制御端子に印加して前記半導体スイッチング素子を導通状態とする導通用駆動回路と、 前記第3のコンデンサの第1の端部と前記制御端子とを接続することにより前記負電圧を前記半導体スイッチング素子の制御端子に印加して前記半導体スイッチング素子を遮断状態とする遮断用駆動回路と、 を備えることを特徴とする半導体スイッチング素子駆動回路。 前記第3のコンデンサは、第1の端部が前記第2のコンデンサの第2の端部に接続され、 充電状態の前記第2のコンデンサの第1の端部と前記第3のコンデンサの第2の端部とを接続することにより前記第3のコンデンサを充電させる充電回路と、 を備えることを特徴とする請求項1に記載の半導体スイッチング素子駆動回路。 前記充電回路は、導通状態の前記半導体スイッチング素子を経由して前記第3のコンデンサを充電させることを特徴とする請求項2に記載の半導体スイッチング素子駆動回路。 正極性の制御用電源をさらに備え、 前記複数の駆動回路は、第1~第nの駆動回路を備え、 前記第m(mは1以上かつn未満の整数)の駆動回路に設けられた前記第1のコンデンサの第1の端部と、前記第(m+1)の駆動回路に設けられた前記第1のコンデンサの第1の端部とは、ダイオードを介して接続されており、 前記第1の駆動回路に設けられた前記第1のコンデンサの第1の端部は、前記制御用電源の正極端子に接続されている、 ことを特徴とする、請求項1から3のいずれか一項に記載の半導体スイッチング素子駆動回路。 請求項1から4のいずれか一項に記載の半導体スイッチング素子駆動回路と、 前記半導体スイッチング素子駆動回路により駆動されるn個の半導体スイッチング素子と、 を備えることを特徴とするマルチレベル電力変換器。 [EN JP2020182338A]: It is a semiconductor switching element drive circuit for driving n (n is an integer of 4 or more) semiconductor switching elements provided in a multi-level power converter, and includes a plurality of drive circuits provided for each of the semiconductor switching elements. Each of the drive circuits is connected to a first capacitor that generates a positive voltage for making the semiconductor switching element conductive, and a first end portion connected to the first end portion of the first capacitor. A second capacitor, a third capacitor that generates a negative voltage for cutting off the semiconductor switching element by charging the power discharged from the second capacitor in a charged state, and the first capacitor. By connecting the first end of the capacitor and the control terminal of the semiconductor switching element, the positive voltage is applied to the control terminal of the semiconductor switching element to bring the semiconductor switching element into a conductive state. By connecting the first end of the third capacitor and the control terminal, the negative voltage is applied to the control terminal of the semiconductor switching element to bring the semiconductor switching element into a cutoff state. A circuit and a semiconductor switching element drive circuit characterized by comprising. The first end of the third capacitor is connected to the second end of the second capacitor, and the first end of the second capacitor in a charged state and the third of the third capacitor are charged. The semiconductor switching element drive circuit according to claim 1, further comprising a charging circuit for charging the third capacitor by connecting the end of the second capacitor. The semiconductor switching element drive circuit according to claim 2, wherein the charging circuit charges the third capacitor via the semiconductor switching element in a conductive state. A positive control power supply is further provided, and the plurality of drive circuits include first to nth drive circuits, and the m (m is an integer greater than or equal to 1 and less than n) drive circuits provided. The first end of the first capacitor and the first end of the first capacitor provided in the (m + 1) drive circuit are connected via a diode. Any one of claims 1 to 3, characterized in that the first end of the first capacitor provided in the first drive circuit is connected to the positive electrode terminal of the control power supply. The semiconductor switching element drive circuit according to the section. A multi-level power converter including the semiconductor switching element drive circuit according to any one of claims 1 to 4 and n semiconductor switching elements driven by the semiconductor switching element drive circuit. .. | [JA JP2020182338A]: 本発明は、半導体スイッチング素子駆動回路及びマルチレベル電力変換器に関する。 特許文献1には、半導体スイッチング素子を用いて負荷駆動用電源から供給される入力電圧をスイッチングし、所定の出力電圧を出力するマルチレベル電力変換器が開示されている。 近年、電力変換器に用いられる半導体スイッチング素子として、高速スイッチング、大電流駆動及び高耐圧を可能にする化合物半導体スイッチング素子(例えば、GaNデバイスやSiCデバイス等)が開発されており、その中でもノーマリーオフ型の半導体スイッチング素子が利用されつつある。 このノーマリーオフ型の半導体スイッチング素子は、通常のシリコンを主体とした構成の半導体スイッチング素子に比べると閾値電圧が低い。そのため、確実に半導体スイッチング素子を遮断状態に制御するには制御端子に負電圧を印加する必要がある。 すなわち、閾値電圧が低い半導体スイッチング素子をスイッチング制御するには、駆動電圧として正電圧の他に負電圧を生成する必要がある。 特開2009-177951号公報 そのため、上記特許文献1に記載のマルチレベル電力変換器において、負電圧を生成するには、新たな電源を追加する必要がある。その結果、装置が大型化し、高コストになる。 本発明は、このような事情に鑑みてなされたもので、その目的は、マルチレベル電力変換器の半導体スイッチング素子を駆動するにあたって、新たな電源を追加することなく負電圧を生成することである。 (1)本発明の一態様は、マルチレベル電力変換器に設けられたn個(nは4以上の整数)の半導体スイッチング素子を駆動する半導体スイッチング素子駆動回路であって、前記半導体スイッチング素子ごとに設けられた複数の駆動回路を備え、前記各駆動回路は、前記半導体スイッチング素子を導通状態にするための正電圧を生成する第1のコンデンサと、第1の端部が前記第1のコンデンサの第1の端部に接続されている第2のコンデンサと、充電状態の前記第2のコンデンサから放電された電力を充電することで前記半導体スイッチング素子を遮断状態にするための負電圧を生成する第3のコンデンサと、前記第1のコンデンサの第1の端部と前記半導体スイッチング素子の制御端子とを接続することにより前記正電圧を前記半導体スイッチング素子の制御端子に印加して前記半導体スイッチング素子を導通状態とする導通用駆動回路と、前記第3のコンデンサの第1の端部と前記制御端子とを接続することにより前記負電圧を前記半導体スイッチング素子の制御端子に印加して前記半導体スイッチング素子を遮断状態とする遮断用駆動回路と、を備えることを特徴とする半導体スイッチング素子駆動回路である。 (2)上記(1)の半導体スイッチング素子駆動回路であって、前記第3のコンデンサは、第1の端部が前記第2のコンデンサの第2の端部に接続され、充電状態の前記第2のコンデンサの第1の端部と前記第3のコンデンサの第2の端部とを接続することにより前記第3のコンデンサを充電させる充電回路と、を備えてもよい。 (3)上記(2)の半導体スイッチング素子駆動回路であって、前記充電回路は、導通状態の前記半導体スイッチング素子を経由して前記第3のコンデンサを充電させてもよい。 (4)上記(1)から上記(3)のいずれかの半導体スイッチング素子駆動回路であって、正極性の制御用電源をさらに備え、前記複数の駆動回路は、第1~第nの駆動回路を備え、前記第m(mは1以上かつn未満の整数)の駆動回路に設けられた前記第1のコンデンサの第1の端部と、前記第(m+1)の駆動回路に設けられた前記第1のコンデンサの第1の端部とは、ダイオードを介して接続されており、前記第1の駆動回路に設けられた前記第1のコンデンサの第1の端部は、前記制御用電源の正極端子に接続されていてもよい。 (5)上記(1)から上記(4)のいずれかの半導体スイッチング素子駆動回路と、前記半導体スイッチング素子駆動回路により駆動されるn個の半導体スイッチング素子と、を備えるマルチレベル電力変換器である。 以上説明したように、本発明によれば、マルチレベル電力変換器の半導体スイッチング素子を駆動するにあたって、新たな電源を追加することなく負電圧を生成することができる。 本実施形態に係るマルチレベル電力変換器Aの概略構成図である。 本実施形態に係る半導体スイッチング素子駆動回路6の回路図である。 本実施形態におけるマルチレベル電力変換器Aの出力電圧V及び出力電流Iの波形図である。 本実施形態に係る動作パターン(1)を示す図である。 本実施形態に係る動作パターン(2)を示す図である。 本実施形態に係る動作パターン(3)を示す図である。 本実施形態に係る動作パターン(4)を示す図である。 本実施形態に係る第1の動作モードを示す図である。 本実施形態に係る第2の動作モードを示す図である。 本実施形態に係る第3の動作モードを示す図である。 本実施形態に係る第4の動作モードを示す図である。 本実施形態に係る第5の動作モードを示す図である。 本実施形態に係る第1の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 本実施形態に係る第2の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 本実施形態に係る第3の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 本実施形態に係る第4の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 以下に、本実施形態に係る半導体スイッチング素子駆動回路を備えたマルチレベル電力変換器Aについて、説明する。 本実施形態に係るマルチレベル電力変換器Aは、3レベルの電圧を出力するマルチレベルインバータである。ただし、これに限定されず、マルチレベル電力変換器Aは、3以上のレベルの電圧を出力するマルチレベルインバータ又はマルチレベルコンバータであればよい。 本実施形態のマルチレベル電力変換器Aは、ダイオードクランプ方式の3レベルNPC(Neutral Point Clamped)インバータである。ただし、これに限定されず、マルチレベル電力変換器Aは、フライングキャパシタ方式であってもよい。 以下に、本実施形態に係るマルチレベル電力変換器Aの構成について、図1を用いて説明する。図1は、本実施形態に係るマルチレベル電力変換器Aの概略構成図である。 図1に示すように、第1の入力端子P、第2の入力端子N、第3の入力端子NP、出力端子OUT、n(nは4以上の整数)個のスイッチング素子SW、コンデンサC1、コンデンサC2、ダイオードD1、ダイオードD2、制御信号発生部5及び半導体スイッチング素子駆動回路6を備える。 第1の入力端子Pは、第1の直流電源100の正極端子に接続される。第1の直流電源100は、電力変換器Aからモータ等の負荷に供給される電力の供給源である。 第2の入力端子Nは、第1の直流電源100の負極端子に接続される。 第3の入力端子NPは、第1の直流電源100の中間電位点に接続される。ただし、これに限定されず、第3の入力端子NPは、グランドに接続されてもよい。 出力端子OUTは、3レベルの電圧を出力する端子である。出力端子OUTは、上記負荷に接続される。 n個のスイッチング素子SWは、第1の入力端子Pと第2の入力端子Nとの間において、直列に接続されている。なお、本実施形態では、マルチレベル電力変換器Aは、3レベルの電圧を出力するマルチレベルインバータであるため、n=4である。すなわち、出力電圧のレベル数をK(3以上の整数)とした場合には、n=2K-2となる。 本実施形態に係るn個のスイッチング素子SWは、スイッチング素子SW1~SW4を備える。 スイッチング素子SW1~SW4は、第1の入力端子Pと第2の入力端子Nとの間において、直列に接続されている。各スイッチング素子SW1~SW4は、半導体スイッチング素子駆動回路6から供給されるゲート電圧に基づいてオン又オフする半導体スイッチング素子である。これにより、マルチレベル電力変換器Aは、第1の直流電源100から供給される入力電圧を所望のレベルの電圧に変換して負荷に出力する。 例えば、各スイッチング素子SW1~SW4は、MOSFET(metal-oxide-semiconductor field-effect transistor)、IGBT(Insulated Gate Bipolar Transistor)、SiC(炭化珪素)やGaN(窒化ガリウム)等のワイドギャップ半導体のスイッチング素子等である。本実施形態では、各スイッチング素子SW1~SW4は、n型のMOSFETである場合について、説明する。 スイッチング素子SW1のドレイン端子は、スイッチング素子SW2のソース端子に接続されている。スイッチング素子SW1のソース端子は、第2の入力端子Nに接続されている。スイッチング素子SW1のゲート端子は、半導体スイッチング素子駆動回路6に接続されている。 スイッチング素子SW2のドレイン端子は、スイッチング素子SW3のソース端子に接続されている。スイッチング素子SW3のソース端子とスイッチング素子SW2のドレイン端子とは、出力端子OUTに接続されている。 スイッチング素子SW2のソース端子は、スイッチング素子SW1のドレイン端子に接続されている。スイッチング素子SW2のゲート端子は、半導体スイッチング素子駆動回路6に接続されている。 スイッチング素子SW3のドレイン端子は、スイッチング素子SW4のソース端子に接続されている。スイッチング素子SW3のソース端子は、スイッチング素子SW2のドレイン端子に接続されている。スイッチング素子SW3のゲート端子は、半導体スイッチング素子駆動回路6に接続されている。 スイッチング素子SW4のドレイン端子は、第1の入力端子Pに接続されている。スイッチング素子SW4のソース端子は、スイッチング素子SW3のドレイン端子に接続されている。スイッチング素子SW4のゲート端子は、半導体スイッチング素子駆動回路6に接続されている。 コンデンサC1は、第1の端部が第1の入力端子Pに接続され、第2の端部が第3の入力端子NPに接続されている。 コンデンサC2は、第1の端部がコンデンサC1の第2の端部及び第3の入力端子NPに接続され、第2の端部が第2の入力端子Nに接続されている。 ダイオードD1は、アノードが第3の入力端子NPに接続され、カソードがスイッチング素子SW4のソース端子及びスイッチング素子SW3のドレイン端子に接続されている。 ダイオードD2は、カソードが第3の入力端子NPに接続され、アノードがスイッチング素子SW2のソース端子及びスイッチング素子SW1のドレイン端子に接続されている。 制御信号発生部5は、半導体スイッチング素子駆動回路6に接続されている。制御信号発生部5は、半導体スイッチング素子駆動回路6に対して、上記ゲート電圧の生成を指示する制御信号を出力する。制御信号とは、例えば、PWM(pulse width modulation)信号である。 半導体スイッチング素子駆動回路6は、制御信号発生部5から出力される制御信号に基づいて、スイッチング素子SW1~SW4のそれぞれをオン又はオフに制御する。半導体スイッチング素子駆動回路6は、片電源である第2の直流電源7からの出力電圧に基づいて、スイッチング素子SW1~SW4のそれぞれのゲート端子に、ゲート電圧を出力する。 以下において、本実施形態に係る半導体スイッチング素子駆動回路6の具体的な構成について、図2を用いて説明する。図2は、本実施形態に係る半導体スイッチング素子駆動回路6の回路図である。 図2に示すように、半導体スイッチング素子駆動回路6は、第2の直流電源7及び複数の駆動回路8を備える。 第2の直流電源7は、正極性の制御用電源である。例えば、第2の直流電源7は、スイッチング素子SW1~SW4を駆動するための電源であってもよいし、不図示の他の装置を駆動するための電源であってもよい。第2の直流電源7の出力電圧は、出力電圧VDDである。 複数の駆動回路8は、第mの駆動回路から第(m+1)の駆動回路を備える。なお、mは、1以上かつn未満の整数である。本実施形態では、n=4であるため、複数の駆動回路8は、第1の駆動回路8a、第2の駆動回路8b、第3の駆動回路8c及び第4の駆動回路8dを備える。 第1の駆動回路8aは、スイッチング素子SW1に対応して設けられている。第1の駆動回路8aは、第2の直流電源7からの出力電圧VDDに基づいて、スイッチング素子SW1のオン又はオフを制御する。具体的には、第1の駆動回路8aは、スイッチング素子SW1を十分にオンさせるために、そのゲート端子に印加する正電圧をゲート電圧として生成し、その生成した正電圧をスイッチング素子SW1のゲート端子に印加する。また、第1の駆動回路8aは、スイッチング素子SW1を十分にオフ(遮断状態)させるために、そのゲート端子に印加する負電圧をゲート電圧として生成して、その生成した負電圧をスイッチング素子SW1のゲート端子に印加する。 第2の駆動回路8bは、スイッチング素子SW2に対応して設けられている。第2の駆動回路8bは、第2の直流電源7からの出力電圧VDDに基づいて、スイッチング素子SW2のオン又はオフを制御する。具体的には、第2の駆動回路8bは、スイッチング素子SW2を十分にオンさせるために、そのゲート端子に印加する正電圧をゲート電圧として生成し、その生成した正電圧をスイッチング素子SW2のゲート端子に印加する。また、第2の駆動回路8bは、スイッチング素子SW2を十分にオフ(遮断状態)させるために、そのゲート端子に印加する負電圧をゲート電圧として生成して、その生成した負電圧をスイッチング素子SW2のゲート端子に印加する。 第3の駆動回路8cは、スイッチング素子SW3に対応して設けられている。第3の駆動回路8cは、第2の直流電源7からの出力電圧VDDに基づいて、スイッチング素子SW3のオン又はオフを制御する。具体的には、第3の駆動回路8cは、スイッチング素子SW3を十分にオンさせるために、そのゲート端子に印加する正電圧をゲート電圧として生成し、その生成した正電圧をスイッチング素子SW3のゲート端子に印加する。また、第3の駆動回路8cは、スイッチング素子SW3を十分にオフ(遮断状態)させるために、そのゲート端子に印加する負電圧をゲート電圧として生成して、その生成した負電圧をスイッチング素子SW3のゲート端子に印加する。 第4の駆動回路8dは、スイッチング素子SW4に対応して設けられている。第4の駆動回路8dは、第2の直流電源7からの出力電圧VDDに基づいて、スイッチング素子SW4のオン又はオフを制御する。具体的には、第4の駆動回路8dは、スイッチング素子SW4を十分にオンさせるために、そのゲート端子に印加する正電圧をゲート電圧として生成し、その生成した正電圧をスイッチング素子SW4のゲート端子に印加する。また、第4の駆動回路8dは、スイッチング素子SW4を十分にオフ(遮断状態)させるために、そのゲート端子に印加する負電圧をゲート電圧として生成して、その生成した負電圧をスイッチング素子SW4のゲート端子に印加する。 以下に、本実施形態に係る第1の駆動回路8aから第4の駆動回路8dの構成について、具体的に説明する。なお、同様の機能を有する構成部については同一の符号を付し、その説明を省略する場合がある。ただし、第1の駆動回路8aから第4の駆動回路8dの各構成部を区別する目的として、第1の駆動回路8aの各構成部の符号の末尾に添え字「a」を付し、第2の駆動回路8bの各構成部の符号の末尾に添え字「b」を付し、第3の駆動回路8cの各構成部の符号の末尾に添え字「c」を付し、第4の駆動回路8dの各構成部の符号の末尾に添え字「d」を付して説明する場合がある。 まず、本実施形態に係る第1の駆動回路8aの構成について説明する。 第1の駆動回路8aは、正電源用コンデンサ9a(第1のコンデンサ)、負電源バッファ用コンデンサ10a(第2のコンデンサ)、逆流防止用ダイオード11a、制限抵抗12a、充放電制御部13a、整流用ダイオード14a、電圧制限用ダイオード15a、負電源用コンデンサ16a(第3のコンデンサ)及び制限抵抗17aを備える。 正電源用コンデンサ9aは、第1の端部が第2の直流電源7の正極端子に接続され、第2の端部が第2の直流電源7の負極端子及びスイッチング素子SW1のソース端子に接続されている。 負電源バッファ用コンデンサ10aは、第1の端部が正電源用コンデンサ9aの第1の端部及び第2の直流電源7の正極端子に接続され、第2の端部が整流用ダイオード14aのカソード及び電圧制限用ダイオード15aのアノードに接続されている。 逆流防止用ダイオード11aは、アノードが負電源バッファ用コンデンサ10aの第1の端子に接続され、カソードが制限抵抗12aを介してスイッチング素子SW1のドレイン端子に接続されている。 制限抵抗12aは、第1の端部が逆流防止用ダイオード11aのカソードに接続され、第2の端部がスイッチング素子SW1のドレイン端子に接続されている。 充放電制御部13aは、制御信号発生部5から出力される制御信号に基づいて、正電源用コンデンサ9a、負電源バッファ用コンデンサ10a、及び負電源用コンデンサ16aの充放電を制御する。以下に、充放電制御部13aの構成について、具体的に説明する。 充放電制御部13aは、スイッチング素子20a(導通用駆動回路)及びスイッチング素子21a(遮断用駆動回路)を備える。 スイッチング素子20aは、スイッチング素子SW1のゲート端子に導通用駆動信号を供給する。導通用駆動信号とは、スイッチング素子20aをオンさせる信号であり、例えば、正電圧のゲート電圧である。例えば、スイッチング素子20aは、NPN型のIGBTである。 スイッチング素子21aは、スイッチング素子SW1のゲート端子に遮断用駆動信号を供給する。遮断用駆動信号とは、スイッチング素子20aをオフさせる信号であり、例えば、負電圧のゲート電圧である。例えば、スイッチング素子21aは、PNP型のIGBTである。 なお、本実施形態では、充放電制御部13aは、スイッチング素子20a及びスイッチング素子21aを用いたプッシュプル回路であるが、これに限定されず、スイッチング素子SW1のオン又はオフを制御する制御回路であれば特に限定されない。 スイッチング素子20aのコレクタ端子は、正電源用コンデンサ9aの第1の端部及び負電源バッファ用コンデンサ10aの第1の端部に接続されている。スイッチング素子20aのエミッタ端子は、スイッチング素子21aのエミッタ端子に接続されている。スイッチング素子20aのベース端子とスイッチング素子21aのベース端子とは制御信号発生部5に接続されている。スイッチング素子20aのエミッタ端子とスイッチング素子21aのエミッタ端子との接続点は、制限抵抗17aを介してスイッチング素子SW1のゲート端子に接続されている。スイッチング素子21aのコレクタ端子は、負電源用コンデンサ16aの第1の端部に接続されている。 整流用ダイオード14aは、アノードが負電源用コンデンサ16aの第1の端部に接続され、カソードが負電源バッファ用コンデンサ10aの第2の端部に接続されている。 電圧制限用ダイオード15aは、負電源用コンデンサ16aに対して並列に接続されている。例えば、電圧制限用ダイオード15aは、アノードが負電源バッファ用コンデンサ10aの第2の端部に接続され、カソードが正電源用コンデンサ9aの第2の端部に接続されている。電圧制限用ダイオード15aは、負電源用コンデンサ16aの両端の電圧を所定の電圧に制限する。前記所定の電圧は、スイッチング素子SW1のゲート端子に印加する負電圧のゲート電圧に相当する。したがって、スイッチング素子SW1がオフされる場合のゲート電圧やスイッチング素子SW1のゲート端子の耐圧に基づいて設定される。本実施形態では、電圧制限用ダイオード15aは、いわゆるツェナーダイオードであって、ツェナーダイオードの降伏電圧が前記所定の電圧に相当する。 負電源用コンデンサ16aは、第1の端部が整流用ダイオード14aのアノード及びスイッチング素子21aのコレクタ端子に接続され、第2の端部が正電源用コンデンサ9aの第2の端部及び第2の直流電源7の負極端子に接続されている。また、負電源用コンデンサ16aの第2の端部は、スイッチング素子SW1のソース端子に接続されている。 制限抵抗17aは、第1の端部がスイッチング素子20aのエミッタ端子とスイッチング素子21aのエミッタ端子とに接続され、第2の端部がスイッチング素子SW1のゲート端子に接続されている。 次に、本実施形態に係る第2の駆動回路8bの構成について説明する。 第2の駆動回路8bは、正電源用コンデンサ9b(第1のコンデンサ)、負電源バッファ用コンデンサ10b(第2のコンデンサ)、逆流防止用ダイオード11b、制限抵抗12b、充放電制御部13b、整流用ダイオード14b、電圧制限用ダイオード15b、負電源用コンデンサ16b(第3のコンデンサ)、制限抵抗17b、制限抵抗18b及び逆流防止用ダイオード19bを備える。 正電源用コンデンサ9bは、第1の端部が逆流防止用ダイオード19bのカソードに接続され、第2の端部がスイッチング素子SW2のソース端子に接続されている。 負電源バッファ用コンデンサ10bは、第1の端部が正電源用コンデンサ9bの第1の端部及び逆流防止用ダイオード19bのカソードに接続され、第2の端部が整流用ダイオード14bのカソード及び電圧制限用ダイオード15bのアノードに接続されている。 逆流防止用ダイオード11bは、アノードが負電源バッファ用コンデンサ10bの第1の端子に接続され、カソードが制限抵抗12bを介してスイッチング素子SW2のドレイン端子に接続されている。 制限抵抗12bは、第1の端部が逆流防止用ダイオード11bのカソードに接続され、第2の端部がスイッチング素子SW2のドレイン端子に接続されている。 充放電制御部13bは、制御信号発生部5から出力される制御信号に基づいて、正電源用コンデンサ9b、負電源バッファ用コンデンサ10b、及び負電源用コンデンサ16bの充放電を制御する。以下に、充放電制御部13bの構成について、具体的に説明する。 充放電制御部13bは、スイッチング素子20b(導通用駆動回路)及びスイッチング素子21b(遮断用駆動回路)を備える。 スイッチング素子20bは、スイッチング素子SW2のゲート端子に導通用駆動信号を供給する。例えば、スイッチング素子20bは、NPN型のIGBTである。 スイッチング素子21bは、スイッチング素子SW2のゲート端子に遮断用駆動信号を供給する。例えば、スイッチング素子21bは、PNP型のIGBTである。 なお、本実施形態では、充放電制御部13bは、スイッチング素子20b及びスイッチング素子21bを用いたプッシュプル回路であるが、これに限定されず、スイッチング素子SW2のオン又はオフを制御する制御回路であれば特に限定されない。 スイッチング素子20bのコレクタ端子は、正電源用コンデンサ9bの第1の端部及び負電源バッファ用コンデンサ10bの第1の端部に接続されている。スイッチング素子20bのエミッタ端子は、スイッチング素子21bのエミッタ端子に接続されている。スイッチング素子20bのベース端子とスイッチング素子21bのベース端子とは制御信号発生部5に接続されている。スイッチング素子20bのエミッタ端子とスイッチング素子21bのエミッタ端子との接続点は、制限抵抗17bを介してスイッチング素子SW2のゲート端子に接続されている。スイッチング素子21bのコレクタ端子は、負電源用コンデンサ16bの第1の端部に接続されている。 整流用ダイオード14bは、アノードが負電源用コンデンサ16bの第1の端部に接続され、カソードが負電源バッファ用コンデンサ10bの第2の端部に接続されている。 電圧制限用ダイオード15bは、負電源用コンデンサ16bに対して並列に接続されている。例えば、電圧制限用ダイオード15bは、アノードが負電源バッファ用コンデンサ10bの第2の端部に接続され、カソードが正電源用コンデンサ9bの第2の端部に接続されている。電圧制限用ダイオード15bは、負電源用コンデンサ16bの両端の電圧を所定の電圧に制限する。前記所定の電圧は、スイッチング素子SW2のゲート端子に印加する負電圧のゲート電圧に相当する。したがって、スイッチング素子SW2がオフされる場合のゲート電圧やスイッチング素子SW2のゲート端子の耐圧に基づいて設定される。本実施形態では、電圧制限用ダイオード15bは、いわゆるツェナーダイオードであって、ツェナーダイオードの降伏電圧が前記所定の電圧に相当する。 負電源用コンデンサ16bは、第1の端部が整流用ダイオード14bのアノード及びスイッチング素子21bのコレクタ端子に接続され、第2の端部が正電源用コンデンサ9bの第2の端部に接続されている。また、負電源用コンデンサ16bの第2の端部は、スイッチング素子SW2のソース端子に接続されている。 制限抵抗17bは、第1の端部がスイッチング素子20bのエミッタ端子とスイッチング素子21bのエミッタ端子とに接続され、第2の端部がスイッチング素子SW2のゲート端子に接続されている。 制限抵抗18bは、第1の端部が第2の直流電源7の正極端子に接続され、第2の端部が逆流防止用ダイオード19bのアノードに接続されている。 逆流防止用ダイオード19bは、アノードが制限抵抗18bを介して第2の直流電源7の正極端子に接続され、カソードが正電源用コンデンサ9bの第1の端部及び負電源バッファ用コンデンサ10bの第1の端部に接続されている。 次に、本実施形態に係る第3の駆動回路8cの構成について説明する。 第3の駆動回路8cは、正電源用コンデンサ9c(第1のコンデンサ)、負電源バッファ用コンデンサ10c(第2のコンデンサ)、逆流防止用ダイオード11c、制限抵抗12c、充放電制御部13c(第3のコンデンサ)、整流用ダイオード14c、電圧制限用ダイオード15c、負電源用コンデンサ16c、制限抵抗17c、制限抵抗18c及び逆流防止用ダイオード19cを備える。 正電源用コンデンサ9cは、第1の端部が逆流防止用ダイオード19cのカソードに接続され、第2の端部がスイッチング素子SW3のソース端子に接続されている。 負電源バッファ用コンデンサ10cは、第1の端部が正電源用コンデンサ9cの第1の端部及び逆流防止用ダイオード19cのカソードに接続され、第2の端部が整流用ダイオード14cのカソード及び電圧制限用ダイオード15cのアノードに接続されている。 逆流防止用ダイオード11cは、アノードが負電源バッファ用コンデンサ10cの第1の端子に接続され、カソードが制限抵抗12cを介してスイッチング素子SW3のドレイン端子に接続されている。 制限抵抗12cは、第1の端部が逆流防止用ダイオード11cのカソードに接続され、第2の端部がスイッチング素子SW3のドレイン端子に接続されている。 充放電制御部13cは、制御信号発生部5から出力される制御信号に基づいて、正電源用コンデンサ9c、負電源バッファ用コンデンサ10c、及び負電源用コンデンサ16cの充放電を制御する。以下に、充放電制御部13cの構成について、具体的に説明する。 充放電制御部13cは、スイッチング素子20c(導通用駆動回路)及びスイッチング素子21c(遮断用駆動回路)を備える。 スイッチング素子20cは、スイッチング素子SW3のゲート端子に導通用駆動信号を供給する。例えば、スイッチング素子20cは、NPN型のIGCTである。 スイッチング素子21cは、スイッチング素子SW3のゲート端子に遮断用駆動信号を供給する。例えば、スイッチング素子21cは、PNP型のIGCTである。 なお、本実施形態では、充放電制御部13cは、スイッチング素子20c及びスイッチング素子21cを用いたプッシュプル回路であるが、これに限定されず、スイッチング素子SW3のオン又はオフを制御する制御回路であれば特に限定されない。 スイッチング素子20cのコレクタ端子は、正電源用コンデンサ9cの第1の端部及び負電源バッファ用コンデンサ10cの第1の端部に接続されている。スイッチング素子20cのエミッタ端子は、スイッチング素子21cのエミッタ端子に接続されている。スイッチング素子20cのベース端子とスイッチング素子21cのベース端子とは制御信号発生部5に接続されている。スイッチング素子20cのエミッタ端子とスイッチング素子21cのエミッタ端子との接続点は、制限抵抗17cを介してスイッチング素子SW3のゲート端子に接続されている。スイッチング素子21cのコレクタ端子は、負電源用コンデンサ16cの第1の端部に接続されている。 整流用ダイオード14cは、アノードが負電源用コンデンサ16cの第1の端部に接続され、カソードが負電源バッファ用コンデンサ10cの第2の端部に接続されている。 電圧制限用ダイオード15cは、負電源用コンデンサ16cに対して並列に接続されている。例えば、電圧制限用ダイオード15cは、アノードが負電源バッファ用コンデンサ10cの第2の端部に接続され、カソードが正電源用コンデンサ9cの第2の端部に接続されている。電圧制限用ダイオード15cは、負電源用コンデンサ16cの両端の電圧を所定の電圧に制限する。前記所定の電圧は、スイッチング素子SW3のゲート端子に印加する負電圧のゲート電圧に相当する。したがって、スイッチング素子SW3がオフされる場合のゲート電圧やスイッチング素子SW3のゲート端子の耐圧に基づいて設定される。本実施形態では、電圧制限用ダイオード15cは、いわゆるツェナーダイオードであって、ツェナーダイオードの降伏電圧が前記所定の電圧に相当する。 負電源用コンデンサ16cは、第1の端部が整流用ダイオード14cのアノード及びスイッチング素子21cのコレクタ端子に接続され、第2の端部が正電源用コンデンサ9cの第2の端部に接続されている。また、負電源用コンデンサ16cの第2の端部は、スイッチング素子SW3のソース端子に接続されている。 制限抵抗17cは、第1の端部がスイッチング素子20cのエミッタ端子とスイッチング素子21cのエミッタ端子とに接続され、第2の端部がスイッチング素子SW3のゲート端子に接続されている。 制限抵抗18cは、第1の端部が逆流防止用ダイオード19bのカソードに接続され、第2の端部が逆流防止用ダイオード19cのアノードに接続されている。 逆流防止用ダイオード19cは、アノードが制限抵抗18cを介して逆流防止用ダイオード19bのカソードに接続され、カソードが正電源用コンデンサ9cの第1の端部及び負電源バッファ用コンデンサ10cの第1の端部に接続されている。 次に、本実施形態に係る第4の駆動回路8dの構成について説明する。 第4の駆動回路8dは、正電源用コンデンサ9d(第1のコンデンサ)、負電源バッファ用コンデンサ10d(第2のコンデンサ)、逆流防止用ダイオード11d、制限抵抗12d、充放電制御部13d、整流用ダイオード14d、電圧制限用ダイオード15d、負電源用コンデンサ16d(第3のコンデンサ)、制限抵抗17d、制限抵抗18d及び逆流防止用ダイオード19dを備える。 正電源用コンデンサ9dは、第1の端部が逆流防止用ダイオード19dのカソードに接続され、第2の端部がスイッチング素子SW4のソース端子に接続されている。 負電源バッファ用コンデンサ10dは、第1の端部が正電源用コンデンサ9dの第1の端部及び逆流防止用ダイオード19dのカソードに接続され、第2の端部が整流用ダイオード14dのカソード及び電圧制限用ダイオード15dのアノードに接続されている。 逆流防止用ダイオード11dは、アノードが負電源バッファ用コンデンサ10dの第1の端子に接続され、カソードが制限抵抗12dを介してスイッチング素子SW4のドレイン端子に接続されている。 制限抵抗12dは、第1の端部が逆流防止用ダイオード11dのカソードに接続され、第2の端部がスイッチング素子SW4のドレイン端子に接続されている。 充放電制御部13dは、制御信号発生部5から出力される制御信号に基づいて、正電源用コンデンサ9d、負電源バッファ用コンデンサ10d、及び負電源用コンデンサ16dの充放電を制御する。以下に、充放電制御部13dの構成について、具体的に説明する。 充放電制御部13dは、スイッチング素子20d(導通用駆動回路)及びスイッチング素子21d(遮断用駆動回路)を備える。 スイッチング素子20dは、スイッチング素子SW4のゲート端子に導通用駆動信号を供給する。例えば、スイッチング素子20dは、NPN型のIGCTである。 スイッチング素子21dは、スイッチング素子SW4のゲート端子に遮断用駆動信号を供給する。例えば、スイッチング素子21dは、PNP型のIGCTである。 なお、本実施形態では、充放電制御部13dは、スイッチング素子20d及びスイッチング素子21dを用いたプッシュプル回路であるが、これに限定されず、スイッチング素子SW4のオン又はオフを制御する制御回路であれば特に限定されない。 スイッチング素子20dのコレクタ端子は、正電源用コンデンサ9dの第1の端部及び負電源バッファ用コンデンサ10dの第1の端部に接続されている。スイッチング素子20dのエミッタ端子は、スイッチング素子21dのエミッタ端子に接続されている。スイッチング素子20dのベース端子とスイッチング素子21dのベース端子とは制御信号発生部5に接続されている。スイッチング素子20dのエミッタ端子とスイッチング素子21dのエミッタ端子との接続点は、制限抵抗17dを介してスイッチング素子SW4のゲート端子に接続されている。スイッチング素子21dのコレクタ端子は、負電源用コンデンサ16dの第1の端部に接続されている。 整流用ダイオード14dは、アノードが負電源用コンデンサ16dの第1の端部に接続され、カソードが負電源バッファ用コンデンサ10dの第2の端部に接続されている。 電圧制限用ダイオード15dは、負電源用コンデンサ16dに対して並列に接続されている。例えば、電圧制限用ダイオード15dは、アノードが負電源バッファ用コンデンサ10dの第2の端部に接続され、カソードが正電源用コンデンサ9dの第2の端部に接続されている。電圧制限用ダイオード15dは、負電源用コンデンサ16dの両端の電圧を所定の電圧に制限する。前記所定の電圧は、スイッチング素子SW4のゲート端子に印加する負電圧のゲート電圧に相当する。したがって、スイッチング素子SW4がオフされる場合のゲート電圧やスイッチング素子SW4のゲート端子の耐圧に基づいて設定される。本実施形態では、電圧制限用ダイオード15dは、いわゆるツェナーダイオードであって、ツェナーダイオードの降伏電圧が前記所定の電圧に相当する。 負電源用コンデンサ16dは、第1の端部が整流用ダイオード14dのアノード及びスイッチング素子21dのコレクタ端子に接続され、第2の端部が正電源用コンデンサ9dの第2の端部に接続されている。また、負電源用コンデンサ16dの第2の端部は、スイッチング素子SW4のソース端子に接続されている。 制限抵抗17dは、第1の端部がスイッチング素子20dのエミッタ端子とスイッチング素子21dのエミッタ端子とに接続され、第2の端部がスイッチング素子SW4のゲート端子に接続されている。 制限抵抗18dは、第1の端部が逆流防止用ダイオード19cのカソードに接続され、第2の端部が逆流防止用ダイオード19dのアノードに接続されている。 逆流防止用ダイオード19dは、アノードが制限抵抗18dを介して逆流防止用ダイオード19cのカソードに接続され、カソードが正電源用コンデンサ9dの第1の端部及び負電源バッファ用コンデンサ10dの第1の端部に接続されている。 以下に、本実施形態におけるマルチレベル電力変換器Aの動作について、図3~図7を用いて説明する。図3は、本実施形態におけるマルチレベル電力変換器Aの出力電圧V及び出力電流Iの波形図である。 マルチレベル電力変換器Aの半導体スイッチング素子駆動回路6は、スイッチング素子SW1~SW4を、予め設定された複数の動作パターン(1)~(4)に従ってオン又はオフすることで、出力端子OUTから正弦波を出力する通常動作を実行する。複数の動作パターン(1)~(4)は、図3に示すように、出力電圧V及び出力電流Iの正負の関係から既定される。各動作パターン(1)~(4)は、スイッチング素子SW1~SW4のスイッチング動作を示す。 具体的には、動作パターン(1)は、図4に示すように、第1の状態と第2の状態とを交互に繰り返す動作パターンである。第1の状態は、図4(a)に示すように、スイッチング素子S1及びスイッチング素子SW2がオフ状態であり、スイッチング素子S3及びスイッチング素子SW4がオン状態である。第2の状態は、図4(b)に示すように、スイッチング素子S1及びスイッチング素子SW4がオフ状態であり、スイッチング素子S2及びスイッチング素子SW3がオン状態である。 なお、動作パターン(1)は、出力電圧V及び出力電流Iがともに正(V&gt;0、I&gt;0)の場合に行われる動作パターンである。 動作パターン(2)は、図5に示すように、第3の状態と第4の状態とを交互に繰り返す動作パターンである。第3の状態は、図5(a)に示すように、スイッチング素子S3及びスイッチング素子SW4がオフ状態であり、スイッチング素子S1及びスイッチング素子SW2がオン状態である。第4の状態は、図5(b)に示すように、スイッチング素子S1及びスイッチング素子SW4がオフ状態であり、スイッチング素子S2及びスイッチング素子SW3がオン状態である。 なお、動作パターン(2)は、出力電圧Vが負であり、出力電流Iが正(V&lt;0、I&gt;0)の場合に行われる動作パターンである。 動作パターン(3)は、図6に示すように、第5の状態と第6の状態とを交互に繰り返す動作パターンである。第5の状態は、図6(a)に示すように、スイッチング素子S3及びスイッチング素子SW4がオフ状態であり、スイッチング素子S1及びスイッチング素子SW2がオン状態である。第6の状態は、図6(b)に示すように、スイッチング素子S1及びスイッチング素子SW4がオフ状態であり、スイッチング素子S2及びスイッチング素子SW3がオン状態である。 なお、動作パターン(3)は、出力電圧V及び出力電流Iがともに負(V&lt;0、I&lt;0)の場合に行われる動作パターンである。 動作パターン(4)は、図7に示すように、第7の状態と第8の状態とを交互に繰り返す動作パターンである。第7の状態は、図7(a)に示すように、スイッチング素子S1及びスイッチング素子SW4がオフ状態であり、スイッチング素子S2及びスイッチング素子SW3がオン状態である。第8の状態は、図7(b)に示すように、スイッチング素子S1及びスイッチング素子SW2がオフ状態であり、スイッチング素子S3及びスイッチング素子SW4がオン状態である。 なお、動作パターン(4)は、出力電圧Vが正であり、出力電流Iが負(V&gt;0、I&lt;0)の場合に行われる動作パターンである。 このように、半導体スイッチング素子駆動回路6は、出力電圧V及び出力電流Iの正負の関係に基づいて、動作パターン(1)から動作パターン(4)から一つを選択し、その選択した動作パターンに従ってスイッチング素子SW1~SW4のスイッチング動作を制御することで出力端子OUTから正弦波を出力する通常動作を実行する。ただし、半導体スイッチング素子駆動回路6は、通常動作を実行するにあたって、事前に充電動作を実行する必要がある。充電動作とは、正電源用コンデンサ9b~9d及び負電源バッファ用コンデンサ10b~10dを充電する動作である。なお、正電源用コンデンサ9a及び負電源バッファ用コンデンサ10aは、スイッチング素子SW1~SW4のスイッチング動作に関係なく、常に充電される。 以下に、本実施形態に係る充電動作について、図8~12を用いて説明する。 半導体スイッチング素子駆動回路6は、スイッチング素子SW1~SW4をオン状態又はオフ状態に制御することで充電動作を実行する。半導体スイッチング素子駆動回路6は、第1の動作モードから第5の動作モードのうち、複数の動作を実行することで充電動作を実行する。 &lt;第1の動作モード&gt; 第1の動作モードは、図8に示すように、半導体スイッチング素子駆動回路6が、スイッチング素子SW1をオン状態に制御し、スイッチング素子SW2~SW4をオフ状態に制御するモードである。第1のモードでは、第2の直流電源7からの電流は、制限抵抗18b、逆流防止用ダイオード19b、正電源用コンデンサ9b、スイッチング素子SW1からなる第1の充電回路W1を通る。これにより、正電源用コンデンサ9bが充電される。また、第2の直流電源7からの電流は、制限抵抗18b、逆流防止用ダイオード19b、負電源バッファ用コンデンサ10b、電圧制限用ダイオード15b、スイッチング素子SW1からなる第2の充電回路W2を通る。これにより、負電源バッファ用コンデンサ10bが充電される。したがって、第1の動作モードでは、スイッチング素子SW1がオン状態に制御されることで、第2の直流電源7から正電源用コンデンサ9b及び負電源バッファ用コンデンサ10bに対して電荷が充電される。 &lt;第2の動作モード&gt; 第2の動作モードは、図9に示すように、半導体スイッチング素子駆動回路6がスイッチング素子SW1及びSW2をオン状態に制御し、スイッチング素子SW3及びSW4をオフ状態に制御するモードである。したがって、第1の充電回路W1及び第2の充電回路W2が形成されるため、第2の直流電源7から正電源用コンデンサ9b及び負電源バッファ用コンデンサ10bに対して電荷が充電される。 さらに、第2の動作モードでは、スイッチング素子SW2がオン状態であるため、第2の直流電源7からの電流は、制限抵抗18b、逆流防止用ダイオード19b、制限抵抗18c、逆流防止用ダイオード19c、正電源用コンデンサ9c、スイッチング素子SW2、スイッチング素子SW1からなる第3の充電回路W3を通る。これにより、正電源用コンデンサ9cが充電される。また、第2の直流電源7からの電流は、制限抵抗18b、逆流防止用ダイオード19b、制限抵抗18c、逆流防止用ダイオード19c、負電源バッファ用コンデンサ10c、電圧制限用ダイオード15c、スイッチング素子SW2、スイッチング素子SW1からなる第4の充電回路W4を通る。これにより、負電源バッファ用コンデンサ10cが充電される。 &lt;第3の動作モード&gt; 第3の動作モードは、図10に示すように、半導体スイッチング素子駆動回路6がスイッチング素子SW2をオン状態に制御し、スイッチング素子SW1、SW3及びSW4をオフ状態に制御するモードである。第3の動作モードでは、正電源用コンデンサ9bが充電されている状態において実行される動作モードであって、スイッチング素子SW2のみがオン状態に制御されることで、正電源用コンデンサ9bの電荷が正電源用コンデンサ9c及び負電源バッファ用コンデンサ10cへ充電される。正電源用コンデンサ9bが充電されている状態とは、例えば、正電源用コンデンサ9bが第2の直流電源7の正極端子の電位(VDD)と同電位まで充電されている状態である。 具体的には、正電源用コンデンサ9bからの電流は、制限抵抗18c、逆流防止用ダイオード19c、正電源用コンデンサ9c、スイッチング素子SW2からなる第5の充電回路W5を通る。これにより、正電源用コンデンサ9cが充電される。また、正電源用コンデンサ9bからの電流は、制限抵抗18c、逆流防止用ダイオード19c、負電源バッファ用コンデンサ10c、電圧制限用ダイオード15c、スイッチング素子SW2からなる第6の充電回路W6を通る。これにより、負電源バッファ用コンデンサ10cが充電される。 &lt;第4の動作モード&gt; 第4の動作モードは、図11に示すように、半導体スイッチング素子駆動回路6がスイッチング素子SW2及びSW3をオン状態に制御し、スイッチング素子SW1及びSW4をオフ状態に制御するモードである。第4の動作モードでは、正電源用コンデンサ9bが充電されている状態において実行される動作モードであって、スイッチング素子SW2及びSW3がオン状態に制御されることで、正電源用コンデンサ9bの電荷が正電源用コンデンサ9c,9d及び負電源バッファ用コンデンサ10c,10dへ充電される。 具体的には、第5の充電回路W5及び第6の充電回路W6が形成されているため、正電源用コンデンサ9c及び負電源バッファ用コンデンサ10cが充電される。 さらに、スイッチング素子SW3がオン状態であるため、正電源用コンデンサ9bからの電流は、制限抵抗18c、逆流防止用ダイオード19c、制限抵抗18d、逆流防止用ダイオード19d、正電源用コンデンサ9d、スイッチング素子SW3、スイッチング素子SW2からなる第7の充電回路W7を通る。これにより、正電源用コンデンサ9dが充電される。また、正電源用コンデンサ9bからの電流は、制限抵抗18c、逆流防止用ダイオード19c、制限抵抗18d、逆流防止用ダイオード19d、負電源バッファ用コンデンサ10d、電圧制限用ダイオード15d、スイッチング素子SW3、スイッチング素子SW2からなる第8の充電回路W8を通る。これにより、負電源バッファ用コンデンサ10dが充電される。 &lt;第5の動作モード&gt; 第5の動作モードは、図12に示すように、半導体スイッチング素子駆動回路6がスイッチング素子SW3をオン状態に制御し、スイッチング素子SW1、SW2及びSW4をオフ状態に制御するモードである。第5の動作モードでは、正電源用コンデンサ9cが充電されている状態において実行される動作モードであって、スイッチング素子SW3のみがオン状態に制御されることで、正電源用コンデンサ9cの電荷が正電源用コンデンサ99d及び負電源バッファ用コンデンサ10dへ充電される。正電源用コンデンサ9cが充電されている状態とは、例えば、正電源用コンデンサ9cが第2の直流電源7の正極端子の電位(VDD)と同電位まで充電されている状態である。 具体的には、スイッチング素子SW3がオン状態であるため、正電源用コンデンサ9cからの電流は、制限抵抗18d、逆流防止用ダイオード19d、正電源用コンデンサ9d、スイッチング素子SW3からなる第9の充電回路W9を通る。これにより、正電源用コンデンサ9dが充電される。また、正電源用コンデンサ9cからの電流は、制限抵抗18d、逆流防止用ダイオード19d、負電源バッファ用コンデンサ10d、電圧制限用ダイオード15d、スイッチング素子SW3からなる第10の充電回路W10を通る。これにより、負電源バッファ用コンデンサ10dが充電される。 このように、例えば、半導体スイッチング素子駆動回路6は、通常動作を実行する前において、第1の動作モード、第2の動作モード、第4の動作モードの順に動作モードを切り替えることで充電動作を実行する。これにより、半導体スイッチング素子駆動回路6は、正電源用コンデンサ9b~9d及び負電源バッファ用コンデンサ10b~10dを充電することができる。ただし、充電動作は、正電源用コンデンサ9b~9d及び負電源バッファ用コンデンサ10b~10dを充電できればよく、第1の動作モード、第2の動作モード、第4の動作モードの順に動作モードを切り替える動作に限定されない。例えば、充電動作は、第2の動作モード、第4の動作モードの順に切り替える動作であってもよいし、第1の動作モード、第2の動作モード、第5の動作モードの順に切り替える動作であってもよい。 以下に、本実施形態におけるマルチレベル電力変換器Aの通常動作について、図13~16を用いて具体的に説明する。まず、動作パターン(1)の場合について説明する。 &lt;第1の状態&gt; 図13は、本実施形態に係る第1の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 図13に示すように、充放電制御部13aは、スイッチング素子21aをオン状態に制御することで、負電源用コンデンサ16aの第1の端部とスイッチング素子SW1のゲート端子とを導通させる。これにより、負電源用コンデンサ16aに充電されていた電荷は、スイッチング素子SW1の入力容量200a、スイッチング素子21aを通り、負電源用コンデンサ16aに戻る経路を通る。この場合には、入力容量200aに充電されていた電荷が放電されるので、スイッチング素子SW1がオンからオフに移行する。換言すれば、負電源用コンデンサ16aに充電されていた負電荷は、スイッチング素子21a、入力容量200aを通り、負電源用コンデンサ16aの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16aの第1の端部からスイッチング素子b2のゲート端子に負電荷が供給されることで、スイッチング素子SW1のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW1がオフ状態になる。 同様に、図13に示すように、充放電制御部13bは、スイッチング素子21bがオンされているため、負電源用コンデンサ16bの第1の端部とスイッチング素子SW2のゲート端子とを導通させる。これにより、負電源用コンデンサ16bに充電されていた電荷は、スイッチング素子SW2の入力容量200b、スイッチング素子21bを通り、負電源用コンデンサ16bに戻る経路を通る。この場合には、入力容量200bに充電されていた電荷が放電されるので、スイッチング素子SW2がオンからオフに移行する。換言すれば、負電源用コンデンサ16bに充電されていた負電荷は、スイッチング素子21b、入力容量200bを通り、負電源用コンデンサ16bの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16bの第1の端部からスイッチング素子SW2のゲート端子に負電荷が供給されることで、スイッチング素子SW2のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW2がオフ状態になる。 充放電制御部13cは、スイッチング素子20cをオン状態に制御し、スイッチング素子21cをオフ状態に制御する。これにより、正電源用コンデンサ9cに充電されていた電荷は、スイッチング素子20c、スイッチング素子SW3の入力容量200cを経由し、正電源用コンデンサ9cの第2の端部に戻る経路を通る。したがって、入力容量200cは、正電源用コンデンサ9cから放電された電荷により充電を開始する。その後、入力容量200cに一定量の電荷が充電されると、スイッチング素子SW3がオフ状態からオン状態に移行する。 スイッチング素子SW3がオン状態に移行すると、負電源バッファ用コンデンサ10cに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10cに充電されていた電荷は、逆流防止用ダイオード11c、制限抵抗12c、スイッチング素子SW3、負電源用コンデンサ16c、整流用ダイオード14cを経由し、負電源バッファ用コンデンサ10cの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16cは、負電源バッファ用コンデンサ10cから放電された電荷により充電される。すなわち、負電源用コンデンサ16cの第2の端部には正電荷が充電され、負電源用コンデンサ16cの第1の端部には負電荷が充電される。換言すれば、第1の状態では、充電状態の負電源バッファ用コンデンサ10cの第1の端部と負電源用コンデンサ16cの第2の端部とを接続することにより負電源用コンデンサ16cを充電させる第11の充電回路W11を形成する。第11の充電回路W11は、導通状態のスイッチング素子SW3を経由して負電源用コンデンサ16cを充電させる。なお、本実施形態の第1の状態では、第11の充電回路W11は、負電源バッファ用コンデンサ10c、逆流防止用ダイオード11c、制限抵抗12c、スイッチング素子SW3、負電源用コンデンサ16c及び整流用ダイオード14cを備える。 充放電制御部13dは、スイッチング素子20dをオン状態に制御し、スイッチング素子21dをオフ状態に制御する。これにより、正電源用コンデンサ9dに充電されていた電荷は、スイッチング素子20d、スイッチング素子SW4の入力容量200dを経由し、正電源用コンデンサ9dの第2の端部に戻る経路を通る。したがって、入力容量200dは、正電源用コンデンサ9dから放電された電荷により充電を開始する。その後、入力容量200dに一定量の電荷が充電されると、スイッチング素子SW4がオフ状態からオン状態に移行する。 スイッチング素子SW4がオン状態に移行すると、負電源バッファ用コンデンサ10dに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10dに充電されていた電荷は、逆流防止用ダイオード11d、制限抵抗12d、スイッチング素子SW4、負電源用コンデンサ16d、整流用ダイオード14dを経由し、負電源バッファ用コンデンサ10dの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16dは、負電源バッファ用コンデンサ10dから放電された電荷により充電される。すなわち、負電源用コンデンサ16dの第2の端部には正電荷が充電され、負電源用コンデンサ16dの第1の端部には負電荷が充電される。換言すれば、第1の状態では、充電状態の負電源バッファ用コンデンサ10dの第1の端部と負電源用コンデンサ16dの第2の端部とを接続することにより負電源用コンデンサ16dを充電させる第12の充電回路W12を形成する。第12の充電回路W12は、導通状態のスイッチング素子SW4を経由して負電源用コンデンサ16dを充電させる。なお、本実施形態の第1の状態では、第12の充電回路W12は、負電源バッファ用コンデンサ10d、逆流防止用ダイオード11d、制限抵抗12d、スイッチング素子SW4、負電源用コンデンサ16d及び整流用ダイオード14dを備える。 &lt;第2の状態&gt; 図14は、本実施形態に係る第2の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 図14に示すように、充放電制御部13aは、スイッチング素子21aをオン状態に制御して、負電源用コンデンサ16aの第1の端部とスイッチング素子SW1のゲート端子とを導通させる。これにより、負電源用コンデンサ16aの第1の端部からスイッチング素子SW1のゲート端子に負電荷が供給され、スイッチング素子SW1のゲート端子に負電圧のゲート電圧が印加される。したがって、スイッチング素子SW1がオフ状態になる。 充放電制御部13dは、スイッチング素子21dがオフ状態に制御し、スイッチング素子21dがオン状態に制御する。そのため、負電源用コンデンサ16dの第1の端部とスイッチング素子SW4のゲート端子とが導通する。これにより、負電源用コンデンサ16dに充電されていた電荷は、スイッチング素子SW4の入力容量200d、スイッチング素子21dを通り、負電源用コンデンサ16dに戻る経路を通る。この場合には、入力容量200dに充電されていた電荷が放電されるので、スイッチング素子SW4がオン状態からオフ状態に移行する。換言すれば、負電源用コンデンサ16dに充電されていた負電荷は、スイッチング素子21d、入力容量200dを通り、負電源用コンデンサ16dの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16dの第1の端部からスイッチング素子SW4のゲート端子に負電荷が供給されることで、スイッチング素子SW4のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW4がオフ状態になる。 充放電制御部13bは、スイッチング素子20bをオン状態に制御し、スイッチング素子21bをオフ状態に制御する。これにより、正電源用コンデンサ9bに充電されていた電荷は、スイッチング素子20b、スイッチング素子SW2の入力容量200bを経由し、正電源用コンデンサ9bの第2の端部に戻る経路を通る。したがって、入力容量200bは、正電源用コンデンサ9bから放電された電荷により充電を開始する。その後、入力容量200bに一定量の電荷が充電されると、スイッチング素子SW2がオフ状態からオン状態に移行する。 スイッチング素子SW2がオン状態に移行すると、負電源バッファ用コンデンサ10bに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10bに充電されていた電荷は、逆流防止用ダイオード11b、制限抵抗12b、スイッチング素子SW2、負電源用コンデンサ16b、整流用ダイオード14bを経由し、負電源バッファ用コンデンサ10bの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16bは、負電源バッファ用コンデンサ10bから放電された電荷により充電される。すなわち、負電源用コンデンサ16bの第2の端部には正電荷が充電され、負電源用コンデンサ16bの第1の端部には負電荷が充電される。換言すれば、第2の状態では、充電状態の負電源バッファ用コンデンサ10bの第1の端部と負電源用コンデンサ16bの第2の端部とを接続することにより負電源用コンデンサ16bを充電させる第13の充電回路W13を形成する。第13の充電回路W13は、導通状態のスイッチング素子SW2を経由して負電源用コンデンサ16bを充電させる。なお、本実施形態の第2の状態では、第13の充電回路W13は、負電源バッファ用コンデンサ10b、逆流防止用ダイオード11b、制限抵抗12b、スイッチング素子SW2、負電源用コンデンサ16b及び整流用ダイオード14bを備える。 充放電制御部13cは、第1の状態と同様に、スイッチング素子20cをオン状態に制御し、スイッチング素子21cをオフ状態に制御する。これにより、スイッチング素子SW3がオン状態に制御される。 次に、本実施形態に係る動作パターン(2)の場合について説明する。&lt;第3の状態&gt; 図15は、本実施形態に係る第3の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 図15に示すように、充放電制御部13aは、スイッチング素子20aをオン状態に制御し、スイッチング素子21aをオフ状態に制御する。これにより、正電源用コンデンサ9aに充電されていた電荷は、スイッチング素子20a、スイッチング素子SW1の入力容量200aを経由し、正電源用コンデンサ9aの第2の端部に戻る経路を通る。したがって、入力容量200aは、正電源用コンデンサ9aから放電された電荷により充電を開始する。その後、入力容量200aに一定量の電荷が充電されると、スイッチング素子SW1がオフ状態からオン状態に移行する。 スイッチング素子SW1がオン状態に移行すると、負電源バッファ用コンデンサ10aに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10aに充電されていた電荷は、逆流防止用ダイオード11a、制限抵抗12a、スイッチング素子SW1、負電源用コンデンサ16a、整流用ダイオード14aを経由し、負電源バッファ用コンデンサ10aの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16aは、負電源バッファ用コンデンサ10aから放電された電荷により充電される。すなわち、負電源用コンデンサ16aの第2の端部には正電荷が充電され、負電源用コンデンサ16aの第1の端部には負電荷が充電される。換言すれば、第3の状態では、充電状態の負電源バッファ用コンデンサ10aの第1の端部と負電源用コンデンサ16aの第2の端部とを接続することにより負電源用コンデンサ16aを充電させる第14の充電回路W14を形成する。第14の充電回路W14は、導通状態のスイッチング素子SW1を経由して負電源用コンデンサ16aを充電させる。なお、本実施形態の第3の状態では、第14の充電回路W14は、負電源バッファ用コンデンサ10a、逆流防止用ダイオード11a、制限抵抗12a、スイッチング素子SW1、負電源用コンデンサ16a及び整流用ダイオード14aを備える。 同様に、図15に示すように、充放電制御部13bは、スイッチング素子20bをオン状態に制御し、スイッチング素子21bをオフ状態に制御する。これにより、正電源用コンデンサ9bに充電されていた電荷は、スイッチング素子20b、スイッチング素子SW2の入力容量200bを経由し、正電源用コンデンサ9bの第2の端部に戻る経路を通る。したがって、入力容量200bは、正電源用コンデンサ9bから放電された電荷により充電を開始する。その後、入力容量200bに一定量の電荷が充電されると、スイッチング素子SW2がオフ状態からオン状態に移行する。 スイッチング素子SW2がオン状態に移行すると、第13の充電回路W13が形成されるため、負電源バッファ用コンデンサ10bに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10bに充電されていた電荷は、逆流防止用ダイオード11b、制限抵抗12b、スイッチング素子SW2、負電源用コンデンサ16b、整流用ダイオード14bを経由し、負電源バッファ用コンデンサ10bの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16bは、負電源バッファ用コンデンサ10bから放電された電荷により充電される。 充放電制御部13cは、スイッチング素子20cをオフ状態に制御し、スイッチング素子21cをオン状態に制御する。そのため、負電源用コンデンサ16cの第1の端部とスイッチング素子SW3のゲート端子とが導通する。これにより、負電源用コンデンサ16cに充電されていた電荷は、スイッチング素子SW3の入力容量200c、スイッチング素子21cを通り、負電源用コンデンサ16cに戻る経路を通る。この場合には、入力容量200cに充電されていた電荷が放電されるので、スイッチング素子SW3がオン状態からオフ状態に移行する。換言すれば、負電源用コンデンサ16cに充電されていた負電荷は、スイッチング素子21c、入力容量200cを通り、負電源用コンデンサ16cの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16cの第1の端部からスイッチング素子SW3のゲート端子に負電荷が供給されることで、スイッチング素子SW3のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW3がオフ状態になる。 充放電制御部13dは、スイッチング素子21dがオフ状態に制御し、スイッチング素子21dがオン状態に制御する。そのため、負電源用コンデンサ16dの第1の端部とスイッチング素子SW4のゲート端子とが導通する。これにより、負電源用コンデンサ16dに充電されていた電荷は、スイッチング素子SW4の入力容量200d、スイッチング素子21dを通り、負電源用コンデンサ16dに戻る経路を通る。この場合には、入力容量200dに充電されていた電荷が放電されるので、スイッチング素子SW4がオン状態からオフ状態に移行する。換言すれば、負電源用コンデンサ16dに充電されていた負電荷は、スイッチング素子21d、入力容量200dを通り、負電源用コンデンサ16dの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16dの第1の端部からスイッチング素子SW4のゲート端子に負電荷が供給されることで、スイッチング素子SW4のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW4がオフ状態になる。 &lt;第4の状態&gt; 図16は、本実施形態に係る第4の状態のときの半導体スイッチング素子駆動回路6の動作の流れを示す説明図である。 図16に示すように、充放電制御部13aは、スイッチング素子20aをオフ状態に制御し、スイッチング素子21aをオン状態に制御する。そのため、負電源用コンデンサ16aの第1の端部とスイッチング素子SW1のゲート端子とが導通する。これにより、負電源用コンデンサ16aに充電されていた電荷は、スイッチング素子SW1の入力容量200a、スイッチング素子21aを通り、負電源用コンデンサ16aに戻る経路を通る。この場合には、入力容量200aに充電されていた電荷が放電されるので、スイッチング素子SW1がオン状態からオフ状態に移行する。換言すれば、負電源用コンデンサ16aに充電されていた負電荷は、スイッチング素子21a、入力容量200aを通り、負電源用コンデンサ16aの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16aの第1の端部からスイッチング素子SW1のゲート端子に負電荷が供給されることで、スイッチング素子SW1のゲート端子に負電圧のゲート電圧が印加される。これにより、スイッチング素子SW1がオフ状態になる。 充放電制御部13bは、第3の状態と同様に、スイッチング素子20bをオン状態に制御し、スイッチング素子21bをオフ状態に制御する。これにより、スイッチング素子SW2がオン状態に制御される。 充放電制御部13cは、スイッチング素子20cをオン状態に制御し、スイッチング素子21cをオフ状態に制御する。これにより、正電源用コンデンサ9cに充電されていた電荷は、スイッチング素子20c、スイッチング素子SW3の入力容量200cを経由し、正電源用コンデンサ9cの第2の端部に戻る経路を通る。したがって、入力容量200cは、正電源用コンデンサ9cから放電された電荷により充電を開始する。その後、入力容量200cに一定量の電荷が充電されると、スイッチング素子SW3がオフ状態からオン状態に移行する。 スイッチング素子SW3がオン状態に移行すると、第11の充電回路W11が形成されるため、負電源バッファ用コンデンサ10cに充電された電荷が放電される。したがって、負電源バッファ用コンデンサ10cに充電されていた電荷は、逆流防止用ダイオード11c、制限抵抗12c、スイッチング素子SW3、負電源用コンデンサ16c、整流用ダイオード14cを経由し、負電源バッファ用コンデンサ10cの第2の端部に戻る経路を通る。したがって、負電源用コンデンサ16cは、負電源バッファ用コンデンサ10cから放電された電荷により充電される。 充放電制御部13dは、第4の状態と同様に、スイッチング素子20dをオフ状態に制御し、スイッチング素子21dをオン状態に制御する。これにより、スイッチング素子SW4がオフ状態に制御される。 動作パターン(3)の半導体スイッチング素子駆動回路6の動作は、動作パターン(2)と同様であるため、説明を省略する。動作パターン(4)の半導体スイッチング素子駆動回路6の動作は、動作パターン(1)と同様であるため、説明を省略する。 また、動作パターン(1)及び動作パターン(2)において、説明の便宜上、各駆動回路8において、正電源用コンデンサ9及び負電源バッファ用コンデンサ10への充電に関しては説明を省略したが、例えば、第1の充電回路W1から第10の充電回路W10の少なくともいずれかが形成された場合には、正電源用コンデンサ9及び負電源バッファ用コンデンサ10への充電が行われる。 上述したように、半導体スイッチング素子駆動回路6は、マルチレベル電力変換器の複数の半導体スイッチング素子SW1~SW4を駆動する。半導体スイッチング素子駆動回路6は、半導体スイッチング素子SW1~SW4ごとに設けられた複数の駆動回路8(第1の駆動回路8aから第4の駆動回路8d)を備える。各駆動回路8は、正電源用コンデンサ9、負電源バッファ用コンデンサ10、負電源用コンデンサ16、スイッチング素子20及びスイッチング素子21を備える。 正電源用コンデンサ9は、半導体スイッチング素子SWを導通状態にするための正電圧を生成する。負電源バッファ用コンデンサ10は、第1の端部が正電源用コンデンサ9の第1の端部に接続されている。負電源用コンデンサ16は、充電状態の負電源バッファ用コンデンサ10から放電された電力を充電することで半導体スイッチング素子SWを遮断状態にするための負電圧を生成する。スイッチング素子20は、正電源用コンデンサ9の第1の端部と半導体スイッチング素子SWの制御端子とを接続することにより正電圧を半導体スイッチング素子SWの制御端子に印加して半導体スイッチング素子SWを導通状態とする。スイッチング素子21は、負電源用コンデンサ16の第1の端部と半導体スイッチング素子SWの制御端子とを接続することにより負電圧を半導体スイッチング素子SWの制御端子に印加して半導体スイッチング素子SWを遮断状態とする。 これにより、半導体スイッチング素子駆動回路6は、マルチレベル電力変換器の半導体スイッチング素子SWを駆動するにあたって、新たな電源を追加することなく負電圧を生成することができる。 以上、この発明の実施形態について図面を参照して詳述してきたが、具体的な構成はこの実施形態に限られるものではなく、この発明の要旨を逸脱しない範囲の設計等も含まれる。 A マルチレベル電力変換器SW1~SW4 スイッチング素子(半導体スイッチング素子)9a~9d 正電源用コンデンサ(第1のコンデンサ)10a~10d 負電源バッファ用コンデンサ(第2のコンデンサ)16a~16d 負電源用コンデンサ(第3のコンデンサ)20a~20d スイッチング素子(導通用駆動回路)21a~21d スイッチング素子(遮断用駆動回路)7 第2の直流電源(制御用電源) [EN JP2020182338A]: The present invention relates to a semiconductor switching element drive circuit and a multi-level power converter. Patent Document 1 discloses a multi-level power converter that uses a semiconductor switching element to switch an input voltage supplied from a load drive power supply and outputs a predetermined output voltage. In recent years, compound semiconductor switching elements (for example, GaN devices, SiC devices, etc.) that enable high-speed switching, large-current drive, and high withstand voltage have been developed as semiconductor switching elements used in power converters, among which normally. Off-type semiconductor switching elements are being used. This normally-off type semiconductor switching element has a lower threshold voltage than a semiconductor switching element having a configuration mainly composed of ordinary silicon. Therefore, it is necessary to apply a negative voltage to the control terminal in order to reliably control the semiconductor switching element in the cutoff state. That is, in order to control switching a semiconductor switching element having a low threshold voltage, it is necessary to generate a negative voltage in addition to the positive voltage as the drive voltage. JP 2009-177951 Therefore, in the multi-level power converter described in Patent Document 1, it is necessary to add a new power source in o
[ZH CN113162447A]: 一种基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器 [EN CN113162447A]: A power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC | [ZH CN113162447A]: 本发明公开了一种基于降压型AC‑DC和中频隔离型DC‑DC的电力电子变压器，降压型AC‑DC换流器与中频隔离型DC‑DC换流器通过直流端口相连接，且降压型AC‑DC换流器与中频隔离型DC‑DC换流器的子模块数量相解耦。本发明采用子模块数量相解耦的降压型AC‑DC换流器和中频隔离型DC‑DC换流器来构建电力电子变压器，降压型AC‑DC换流器引入电力电子变压器的拓扑中，降低了电力电子变压器中第一直流端口的电压等级，进而减小中频隔离型DC‑DC换流器中的子模块数量，以实现紧凑化设计，显著地降低系统的成本和体积，提高功率密度和运行效率；同时，该电力电子变压器具有多种类型的交直流端口，便于实现“源‑网‑荷‑储”系统的能量一体化管理。 [EN CN113162447A]: The invention discloses a power electronic transformer based on a step-down AC-DC and an intermediate frequency isolation type DC-DC. A step-down AC-DC converter and an intermediate frequency isolation type DC-DC converter are connected through a DC port, And the number of sub-modules of the step-down AC-DC converter and the intermediate frequency isolated DC-DC converter are decoupled. The invention uses a step-down AC-DC converter with decoupling of the number of sub-modules and an intermediate frequency isolated DC-DC converter to construct a power electronic transformer, and the step-down AC-DC converter introduces the topology of the power electronic transformer In the power electronic transformer, the voltage level of the first DC port in the power electronic transformer is reduced, thereby reducing the number of sub-modules in the intermediate frequency isolated DC-DC converter to achieve a compact design and significantly reduce the cost and volume of the system. Improve power density and operating efficiency; at the same time, the power electronic transformer has multiple types of AC and DC ports, which is convenient to realize the integrated energy management of the "source-grid-load-storage" system. | CN113162447A | 2021-07-23 | CN202110455313A | 2021-04-26 | CN202110455313A, 2021-04-26 | CN113162447A: 2021-07-23 | 清华大学 |  | H02M7/483: I H02J3/38: I H02M3/335: I H02M7/5387: I H02M7/797: I |  |  |  | [ZH CN113162447A]: 1 .一种基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其特征在于，所述电 力电子变压器包括降压型AC-DC换流器⑴和中频隔离型DC-DC换流器（2），所述降压型ACDC换流器（1）与中频隔离型DC-DC换流器⑵通过直流端口相连接，且降压型AC-DC换流器 ⑴与中频隔离型DC-DC换流器⑵的子模块数量相解耦。 2 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述降压型AC-DC换流器⑴的交流侧接入交流电网或交流电源，所述降压型ACDC换流器（1）的直流侧通过第一直流端口与中频隔离型DC-DC换流器⑵相连;所述中频隔 离型DC-DC换流器⑵的第二直流端口连接储能系统或逆变器系统。 3 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述降压型AC-DC换流器⑴的交流侧电压Vacp和直流侧电压Vdc满足:VacpWVdc。 4 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述降压型AC-DC换流器⑴的拓扑结构采用全桥型模块化多电平换流器结构或 混合型模块化多电平换流器结构。 5 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述降压型AC-DC换流器（1）用于降低第一直流端口的电压等级，以减小后级中 频隔离型DC-DC换流器⑵的子模块数量。 6 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述中频隔离型DC-DC换流器⑵的工作频率小于2kHz。 7 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述中频隔离型DC-DC换流器⑵采用额定电压等级23.3kV的高压器件。 8 .根据权利要求7所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述高压器件的类型为绝缘栅双极型晶体管或集成门极换流晶闸管。 9 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述中频隔离型DC-DC换流器⑵的拓扑结构采用模块化组合型、器件串联型或 模块化多电平换流器型。 10 .根据权利要求1所述的基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器，其 特征在于:所述中频隔离型DC-DC换流器⑵的拓扑结构采用具有多绕组隔离变压器进行构 建，以实现多端口或双极运行。 [EN CN113162447A]: 1 A power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC, characterized in that the power electronic transformer includes a step-down AC-DC converter and intermediate frequency isolation DC-DC converter The step-down ACDC converter (1) is connected to the intermediate frequency isolation type DC-DC converter (2) through a DC port, and the step-down AC-DC converter (1) is connected to the intermediate frequency isolation type The number of sub-modules of the DC-DC converter is decoupled. 2 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the AC side of the step-down AC-DC converter (1) is connected to the AC power grid Or an AC power supply, the DC side of the step-down ACDC converter (1) is connected to an intermediate frequency isolated DC-DC converter through a first DC port; the intermediate frequency isolated DC-DC converter The second DC port is connected to the energy storage system or inverter system. 3 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the AC side voltage V of the step-down AC-DC converter acpAnd DC side voltage VdcMeet: VacpWVdc。 4 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation type DC-DC according to claim 1, characterized in that: the topological structure of the step-down AC-DC converter (1) adopts a full-bridge type Modular multilevel converter structure or hybrid modular multilevel converter structure. 5 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the step-down AC-DC converter (1) is used to reduce the first The voltage level of the DC port is used to reduce the number of sub-modules of the intermediate frequency isolation DC-DC converter (2) in the subsequent stage. 6 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the operating frequency of the intermediate frequency isolation DC-DC converter (2) is less than 2kHz. 7 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the intermediate frequency isolation DC-DC converter adopts a rated voltage level of 23.3kV High-voltage devices. 8 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 7, characterized in that: the type of the high voltage device is insulated gate bipolar transistor or integrated gate commutation Thyristor. 9 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the topology of the intermediate frequency isolation DC-DC converter adopts modular combination Type, device series type or modular multi-level converter type. 10 The power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC according to claim 1, characterized in that: the intermediate frequency isolation DC-DC converter (2) adopts a topology with multiple windings The isolation transformer is constructed to achieve multi-port or bipolar operation. | [ZH CN113162447A]: 一种基于降压型AC-DC和中频隔离型DC-DC的电力电子变压器 技术领域 [0001] 本发明属于电力电子技术领域，特别涉及一种基于降压型AC-DC和中频隔离型DCDC的电力电子变压器。 背景技术 [0002]随着能源紧缺和环境污染问题的日益突出，大规模新能源发电、高渗透分布式发 电、新能源交通工具以及大规模储能系统等的发展趋势不可逆转。电力系统也正向“源-网荷-储”协调优化运行的新阶段发展，并将成为未来能源互联网的核心和纽带。传统电力系 统是自上而下的树状结构;在其电源、电网、负荷、储能等各个环节中，可用于调控的一次装 备主要是分段和联络开关、变压器分接头、投切电容器等非智能手段，且具有操作寿命有 限、调节精度较低的缺点。而未来电力系统是由自下而上的电能自治单元通过对等互联形 成的，是一个开放、互联、对等、分享的体系;这个体系要求信息和电能的高度融合，要求具 备精确、连续、快速、灵活的调控手段;在这种背景催生下，基于电力电子技术的“电能路由 器”概念应运而生。 [0003] 近年来，电力电子装置与系统已经可以满足广泛的应用需求，包括家用电器、不间 断电源、工业生产、机车牵引及新型电力系统等各个行业。面向这些应用的电力电子装置正 朝着高功率密度、高能量密度、高效能及智能化、模块化的方向发展，并呈现出新的特点：1） 更多地采用硅基功率半导体模块组合技术和宽禁带功率半导体器件；2）更多地采用由多个 变换单元灵活组合的方式构成的多功能变换器;3）更多地形成多端口、多级联、多流向和多 形态的电能变换形式。以上所述特点都大大提高了电力电子装置的变换效率和路由能力， 奠定了电能路由器的技术基础。由于能源互联网的形式多样，电能路由器的组网形式也呈 现多样化的趋势。 [0004]因此，如何实现多端口、低成本、高功率密度的紧凑化电力电子变压器设计成为亟 待解决的技术问题。 发明内容 [0005] 本发明的技术目的是提供一种基于降压型AC-DC和中频隔离型DC-DC的电力电子 变压器，该电力电子变压器的降压型AC-DC换流器和中频隔离型DC-DC换流器的子模块数量 相解耦，通过将降压型AC-DC换流器引入电力电子变压器的拓扑中，有效减少中频隔离型 DC-DC换流器中的子模块数量，降低了系统的成本和体积，同时该电力电子变压器具有多种 类型的交直流端口，便于实现“源-网-荷-储”系统的能量一体化管理。 [0006]为实现上述技术目的，本发明采取的技术方案为:一种基于降压型AC-DC和中频隔 离型DC-DC的电力电子变压器，电力电子变压器包括降压型AC-DC换流器和中频隔离型DCDC换流器，降压型AC-DC换流器与中频隔离型DC-DC换流器通过直流端口相连接，且降压型 AC-DC换流器与中频隔离型DC-DC换流器的子模块数量相解耦。 [0007] 进一步地，所述降压型AC-DC换流器的交流侧接入交流电网或交流电源，所述降压 型AC-DC换流器的直流侧通过第一直流端口与中频隔离型DC-DC换流器相连;所述中频隔离 型DC-DC换流器的第二直流端口连接储能系统或逆变器系统。 [0008] 进一步地，所述降压型AC-DC换流器的交流侧电压Vacp和直流侧电压Vdc满足:VacpW Vdc。 [0009] 进一步地，所述降压型AC-DC换流器的拓扑结构采用全桥型模块化多电平换流器 结构或混合型模块化多电平换流器结构。 [0010] 进一步地，所述降压型AC-DC换流器用于降低第一直流端口的电压等级，以减小后 级中频隔离型DC-DC换流器的子模块数量。 [0011] 进一步地，所述中频隔离型DC-DC换流器的工作频率小于2kHz。 [0012] 进一步地，所述中频隔离型DC-DC换流器采用额定电压等级23.3kV的高压器件。 [0013]进一步地，所述高压器件的类型为绝缘栅双极型晶体管或集成门极换流晶闸管。 [0014] 进一步地，所述中频隔离型DC-DC换流器的拓扑结构采用模块化组合型、器件串联 型或模块化多电平换流器型。 [0015] 进一步地，所述中频隔离型DC-DC换流器的拓扑结构采用具有多绕组隔离变压器 进行构建，以实现多端口或双极运行。 [0016]与现有技术相比，本发明具有以下有益效果:本发明首次将降压型AC-DC换流器引 入电力电子变压器的拓扑中，采用子模块数量相解耦的降压型AC-DC换流器和中频隔离型 DC-DC换流器来构建电力电子变压器，其中降压型AC-DC换流器用来降低电力电子变压器中 第一直流端口的电压等级，以此来减小中频隔离型DC-DC换流器中的子模块数量，DC-DC换 流器采用中频隔离和高压器件进行构建以实现紧凑化设计，也可采用具有多绕组隔离变压 器进行构建以实现多端口或双极运行，进而可以显著地降低系统的成本和体积，提高功率 密度和运行效率；同时，该电力电子变压器具有多种类型的交直流端口，便于实现“源-网荷-储”系统的能量一体化管理。 附图说明 [0017]图1为本发明基于降压型AC-DC和中频隔离型DC-DC换流器的电力电子变压器结构 示意图； [0018] 图2为全桥降压型MMC拓扑结构； [0019]图3为混合降压型MMC拓扑结构； [0020]图4为输入串联输出并联型DC-DC拓扑结构； [0021]图5为器件串联型DC-DC拓扑结构； [0022] 图6为MMC型DC-DC拓扑结构； [0023] 图7为五电平MMC拓扑结构； [0024]图8为通过多绕组隔离变压器来构造第二直流端口为多端口的中频隔离型DC-DC 换流器。 [0025] 其中的附图标记为：降压型AC-DC换流器1、中频隔离型DC-DC换流器2。 具体实施方式 [0026]下面结合附图对本发明的技术方案作进一步详细说明。以下实施例仅用于 说明本发明而不用于限制本发明的范围。 [0027]如图1所示，本发明提供了一种基于降压型AC-DC和中频隔离型DC-DC的电力电子 变压器，包括降压型AC-DC换流器1和中频隔离型DC-DC换流器2；降压型AC-DC换流器1的交 流侧用于接入交流电网/交流电源，降压型AC-DC换流器1的直流侧通过第一直流端口与中 频隔离型DC-DC换流器2相连;而中频隔离型DC-DC换流器2的第二直流端口可以进一步连接 储能系统或逆变器系统;且降压型AC-DC换流器1与中频隔离型DC-DC换流器2的子模块数量 相解耦，即降压型AC-DC换流器1的子模块数量仅根据直流端口电压确定，而与中频隔离型 DC-DC换流器2的子模块数量无关，相较于传统的级联H桥型电力电子变压器中，级联H桥的 子模块数量必须与DC-DC换流器的子模块数量相同，本系统的设计无一定约束性。 [0028] 其中，降压型AC-DC换流器1的交流侧电压Vacp和直流侧电压Vdc满足:VacpWVdc，即 交流侧电压的峰值应小于直流侧电压;降压型AC-DC换流器1的拓扑结构采用全桥型模块化 多电平换流器(MMC)结构(如图2所示)或混合型模块化多电平换流器结构(如图3所示)或其 他能实现降压功能的AC-DC换流器，用于降低第一直流端口的电压等级，从而减小后级中频 隔离型DC-DC换流器2的子模块数量，降低系统成本，提高功率密度。 [0029] 其中，全桥型模块化多电平换流器(MMC)即每一个子模块均为全桥的MMC换流器， 而混合型模块化多电平换流器则是指所采用的子模块中既包含全桥也包含半桥的MMC换流 器。 [0030]对基于全桥子模块的三相MMC,由于其相比半桥子模块额外多了负电平输出的能 力，可以通过合适的调制方式使其在保证其直流电压恒定的前提下实现降压运行。在降压 情况下，随着负投入子模块个数增加，交流电压峰值增高，端口电平数也会增加，使得输出 波形质量更好，控制更为灵活。 [0031] 为更直观地说明三相全桥MMC换流器降压原理，以如图7 (a)所示的单桥臂四模块， 即五电平MMC拓扑结构来分析。 [0032]额定情况下，交流侧的输出电压uva在一个MMC工频周期内需经历八个不同的工作 状态，如图7(b)所示。假设直流侧电压Udc的中点电位为电压参考点，则会出现五种电平状 态。降压N0为2的情况下，交流侧的输出电压uva在一个MMC工频周期内需经历十二个不同的 工作状态，如图7(c)所示。最多负投入两个子模块，uva的峰峰值也较额定情况升高1.5倍，其 电平数由额定的五电平升至七电平。因为MMC的电平数直接影响到其输出交流电压的波形 质量，所以此时交流侧的输出电压uva波形质量较额定运行时有所提高。可以看出，通过调制 作用使得其能够在保持直流电压恒定的情况下，输出交流相电压峰值略高于单极电流电 压，可有效降低输入换流器的电流，进而降低换流器的运行损耗。 [0033]其中，中频隔离型DC-DC换流器2的拓扑结构采用模块化组合型(例如:输入串联输 出并联，如图4所示)、器件串联型(如图5所示)或MMC型(如图6所示)，也可以采用具有多绕 组隔离变压器进行构建，以实现多端口或双极运行； [0034] 其中，模块化组合型DC-DC换流器是通过多个中频隔离型DC-DC换流器2在两侧的 直流端口进行串并联组合而成，以提高换流器的电压和电流容量等级。其中，两端的直流端 口的连接方式可以为串联连接或并联连接，图4给出了模块化组合型DC-DC换流器是在输入 侧进行串联连接构造出第一直流端口，而在输出侧进行并联连接构造出第二直流端口。模 块化组合型DC-DC换流器避免了开关器件的直接串联，不仅实现了高低压等级的变换，还实 现了高低压直流母线的电气隔离以及功率的双向流动。 [0035] 器件串联型DC-DC换流器是指采用功率器件直接串联的方式来构造满足中高压大 容量的DC-DC换流器，即在每一个桥臂中直接串联一定数量的开关管，如图5所示。该方案具 有较好的经济性和较高的功率密度，但是该技术方案对于系统回路的杂散电感具有较高的 要求。 [0036] MMC型DC-DC换流器是基于模块化多电平的思想进行构造的，如图6所示。相比于器 件串联型的DC-DC换流器，MMC型DC-DC换流器通过将一系列的子模块进行串并联组合以支 撑较高的电压等级，该技术方案可以有效减少器件串联的难度和可靠性，但是器件数量增 加了一倍。 [0037]图8给出了通过多绕组隔离变压器来构造第二直流端口为多端口的中频隔离型 DC-DC换流器2,通过引入多绕组隔离变压器，可以在第二端口处构造出离散的多直流端口， 或通过合适的连接实现双极运行。 [0038] 进一步地，中频隔离型DC-DC换流器2的工作频率小于2kHz；中频隔离型DC-DC换流 器2采用高压器件(额定电压等级23.3kV)以降低子模块数量，高压器件类型可以是绝缘栅 双极型晶体管(IGBT)或集成门极换流晶闸管(IGCT)。 [0039] 本发明通过采用降压型AC-DC换流器1和中频隔离型DC-DC换流器2来构建电力电 子变压器，可以显著地降低系统的成本和体积，提高功率密度和运行效率；同时，该电力电 子变压器具有多种类型的交直流端口，便于实现“源-网-荷-储”系统的能量一体化管理。 [0040]以上仅是本发明的优选实施方式，本发明的保护范围并不仅局限于上述实施例， 凡属于本发明思路下的技术方案均属于本发明的保护范围。应当指出，对于本技术领域的 普通技术人员来说，在不脱离本发明原理前提下的若干改进和润饰，应视为本发明的保护 范围。 [EN CN113162447A]: A technical field of power electronic transformers based on step-down AC-DC and intermediate frequency isolation DC-DC [0001] The present invention belongs to the field of power electronics technology, and in particular relates to a power electronic transformer based on step-down AC-DC and intermediate frequency isolation DCDC. Background technique [0002] With the increasingly prominent problems of energy shortage and environmental pollution, the development trends of large-scale new energy power generation, high-permeability distributed power generation, new energy vehicles, and large-scale energy storage systems are irreversible. The power system is also developing towards a new stage of coordinated and optimized operation of "source-network load-storage", and will become the core and link of the future energy Internet. The traditional power system is a top-down tree structure; in its power supply, power grid, load, energy storage and other links, the primary equipment that can be used for regulation is mainly segmentation and tie switches, transformer taps, switching capacitors, etc. Non-intelligent means, and has the shortcomings of limited operating life and low adjustment accuracy. The future power system is formed by bottom-up power autonomous units through peer-to-peer interconnection. It is an open, interconnected, peer-to-peer, and shared system; this system requires a high degree of integration of information and power, and requires accurate, continuous, Fast and flexible control means; in this context, the concept of "electric energy router" based on power electronics technology came into being. [0003] In recent years, power electronic devices and systems have been able to meet a wide range of application requirements, including various industries such as household appliances, uninterruptible power supplies, industrial production, locomotive traction, and new power systems. Power electronic devices for these applications are developing in the direction of high power density, high energy density, high efficiency, intelligence, and modularization, and present new features: 1) More use of silicon-based power semiconductor module combination technology And wide bandgap power semiconductor devices; 2) More use of multi-functional converters composed of multiple conversion units flexibly combined; 3) More forms of multi-port, multi-cascade, multi-flow and multi-form electric energy Change form. The above-mentioned features have greatly improved the conversion efficiency and routing capabilities of power electronic devices, and laid the technical foundation for the electric energy router. Due to the diverse forms of the energy Internet, the networking forms of power routers also show a diversified trend. [0004] Therefore, how to achieve a multi-port, low-cost, high-power-density compact power electronic transformer design has become an urgent technical problem to be solved. Summary of the invention [0005] The technical purpose of the present invention is to provide a power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC, the step-down AC-DC converter of the power electronic transformer and intermediate frequency isolation DC -The number of sub-modules of the DC converter is decoupled. By introducing the step-down AC-DC converter into the power electronic transformer topology, the number of sub-modules in the intermediate frequency isolation DC-DC converter is effectively reduced, and the The cost and volume of the system are improved. At the same time, the power electronic transformer has multiple types of AC and DC ports, which is convenient to realize the integrated energy management of the "source-network-load-storage" system. [0006] In order to achieve the above technical objectives, the technical solution adopted by the present invention is: a power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC, the power electronic transformer includes step-down AC-DC converter And intermediate frequency isolated DCDC converter, step-down AC-DC converter and intermediate frequency isolated DC-DC converter are connected through the DC port, and step-down AC-DC converter and intermediate frequency isolated DC -The number of sub-modules of the DC converter is decoupled. [0007] Further, the AC side of the step-down AC-DC converter is connected to an AC power grid or an AC power source, and the step-down The DC side of the AC-DC converter is connected to the intermediate frequency isolated DC-DC converter through the first DC port; the second DC port of the intermediate frequency isolated DC-DC converter is connected to the energy storage system or the inverter Converter system. [0008] Further, the AC side voltage V of the step-down AC-DC converteracpAnd DC side voltage VdcMeet: VacpW Vdc. [0009] Further, the topological structure of the step-down AC-DC converter adopts a full-bridge modular multilevel converter structure or a hybrid modular multilevel converter structure. [0010] Further, the step-down AC-DC converter is used to reduce the voltage level of the first DC port to reduce the number of sub-modules of the intermediate frequency isolation DC-DC converter in the subsequent stage. [0011] Further, the operating frequency of the intermediate frequency isolated DC-DC converter is less than 2 kHz. [0012] Further, the intermediate frequency isolation type DC-DC converter adopts a high voltage device with a rated voltage level of 23.3kV. [0013] Further, the type of the high-voltage device is an insulated gate bipolar transistor or an integrated gate commutated thyristor. [0014] Further, the topological structure of the intermediate frequency isolation type DC-DC converter adopts a modular combination type, a device series type or a modular multilevel converter type. [0015] Further, the topological structure of the intermediate frequency isolation type DC-DC converter is constructed with a multi-winding isolation transformer to realize multi-port or bipolar operation. [0016] Compared with the prior art, the present invention has the following beneficial effects: For the first time, the present invention introduces a step-down AC-DC converter into the topology of a power electronic transformer, and uses a step-down AC with decoupled sub-module numbers. -DC converters and intermediate frequency isolation DC-DC converters are used to construct power electronic transformers. The step-down AC-DC converter is used to reduce the voltage level of the first DC port in the power electronic transformer to reduce The number of sub-modules in the small intermediate frequency isolated DC-DC converter. The DC-DC converter is constructed with intermediate frequency isolation and high voltage devices to achieve a compact design, or it can be constructed with a multi-winding isolation transformer to achieve multiple ports Or bipolar operation, which can significantly reduce the cost and volume of the system, and improve the power density and operating efficiency. At the same time, the power electronic transformer has multiple types of AC and DC ports, which is convenient to realize the "source-network load-storage" system Integrated energy management. Description of the drawings [0017] FIG. 1 is a schematic diagram of the structure of a power electronic transformer based on a step-down AC-DC and an intermediate frequency isolated DC-DC converter according to the present invention; [0018] Figure 2 is a full-bridge step-down MMC topology; [0019] Figure 3 is a hybrid step-down MMC topology; [0020] Figure 4 is an input series output parallel DC-DC topology; [0021] Figure 5 is a device series DC-DC topology; [0022] FIG. 6 is an MMC-type DC-DC topology; [0023] FIG. 7 is a five-level MMC topology; [0024] FIG. 8 is an intermediate frequency isolated DC-DC converter with a multi-port second DC port constructed by a multi-winding isolation transformer. [0025] The reference signs are: step-down AC-DC converter 1, intermediate frequency isolation type DC-DC converter 2. Detailed ways [0026] The technical solution of the present invention will be described in further detail below in conjunction with the accompanying drawings. The following examples are only for The description of the present invention is not intended to limit the scope of the present invention. [0027] As shown in FIG. 1, the present invention provides a power electronic transformer based on step-down AC-DC and intermediate frequency isolation DC-DC, including step-down AC-DC converter 1 and intermediate frequency isolation DC -DC converter 2; the AC side of the step-down AC-DC converter 1 is used to connect to the AC grid/AC power source, and the DC side of the step-down AC-DC converter 1 is connected to the first DC port through the first DC port The intermediate frequency isolated DC-DC converter 2 is connected; and the second DC port of the intermediate frequency isolated DC-DC converter 2 can be further connected to the energy storage system or inverter system; and the step-down AC-DC converter 1 It is decoupled from the number of sub-modules of the intermediate frequency isolated DC-DC converter 2, that is, the number of sub-modules of the step-down AC-DC converter 1 is only determined by the DC port voltage, and it is decoupled from the intermediate frequency isolated DC-DC The number of sub-modules of the converter 2 is irrelevant. Compared with the traditional cascaded H-bridge power electronic transformer, the number of sub-modules of the cascaded H-bridge must be the same as that of the DC-DC converter. The design is not restrictive. [0028] Among them, the AC side voltage V of the step-down AC-DC converter 1acpAnd DC side voltage VdcMeet: VacpWVdc, That is, the peak value of the AC side voltage should be less than the DC side voltage; the topological structure of the step-down AC-DC converter 1 adopts a full-bridge modular multilevel converter (MMC) structure (as shown in Figure 2) or Hybrid modular multi-level converter structure (as shown in Figure 3) or other AC-DC converters capable of reducing voltage, used to reduce the voltage level of the first DC port, thereby reducing the subsequent stages The number of sub-modules of the intermediate frequency isolated DC-DC converter 2 reduces the system cost and improves the power density. [0029] Among them, the full-bridge modular multilevel converter (MMC) refers to the MMC converter in which each sub-module is a full bridge, and the hybrid modular multilevel converter refers to the adopted The sub-module of contains both full-bridge and half-bridge MMC converters. [0030] For the three-phase MMC based on the full-bridge sub-module, due to its additional negative level output capability compared with the half-bridge sub-module, it can be reduced by a suitable modulation method under the premise of ensuring a constant DC voltage. Pressure operation. In the case of step-down, as the number of negative input sub-modules increases, the peak value of the AC voltage increases, and the number of port levels also increases, resulting in better output waveform quality and more flexible control. [0031] In order to more intuitively explain the step-down principle of the three-phase full-bridge MMC converter, a single-arm four-module, that is, a five-level MMC topology structure as shown in FIG. 7(a) is used for analysis. [0032] Under rated conditions, the output voltage u on the AC sidevaIt needs to experience eight different working states in one MMC power frequency cycle, as shown in Figure 7(b). Assuming that the DC side voltage UdcThe midpoint potential of is the voltage reference point, and there will be five level states. When the step-down N0 is 2, the output voltage u of the AC sidevaTwelve different working states need to be experienced in one MMC power frequency cycle, as shown in Figure 7(c). Up to two sub-modules are negatively input, uvaThe peak-to-peak value of is also 1.5 times higher than the rated situation, and its level number has risen from the rated five-level to seven-level. Because the level of MMC directly affects the waveform quality of its output AC voltage, the output voltage u at the AC side at this timevaThe quality of the waveform is improved compared to the rated operation. It can be seen that the output AC phase voltage peak value is slightly higher than the unipolar current voltage under the condition of keeping the DC voltage constant through the modulation effect, which can effectively reduce the current input to the converter, thereby reducing the operation loss of the converter . [0033] Among them, the topological structure of the intermediate frequency isolation type DC-DC converter 2 adopts modular combination type (for example: input series and output parallel connection, as shown in FIG. 4), device series type (as shown in FIG. 5) or MMC Type (as shown in Figure 6), can also be constructed with a multi-winding isolation transformer to achieve multi-port or bipolar operation; [0034] Among them, the modular combined DC-DC converter is a series-parallel combination of multiple intermediate frequency isolated DC-DC converters 2 on both sides of the DC ports to increase the converter voltage and Current capacity level. Among them, the DC ports at both ends can be connected in series or in parallel. Figure 4 shows that the modular combined DC-DC converter is connected in series on the input side to construct the first DC port, and at the output The two sides are connected in parallel to construct a second DC port. The modular combined DC-DC converter avoids the direct series connection of switching devices, and not only realizes the conversion of high and low voltage levels, but also The electrical isolation of the high and low voltage DC bus and the two-way flow of power have been realized. [0035] The device series DC-DC converter refers to the direct series connection of power devices to construct a DC-DC converter that meets the requirements of medium and high voltage and large capacity, that is, a certain number of switch tubes are directly connected in series in each bridge arm , As shown in Figure 5. This solution has better economy and higher power density, but this technical solution has higher requirements for the stray inductance of the system loop. [0036] The MMC type DC-DC converter is constructed based on the idea of modular multilevel, as shown in Figure 6. Compared with the series-connected DC-DC converter, the MMC-type DC-DC converter supports a higher voltage level by combining a series of sub-modules in series and parallel. This technical solution can effectively reduce the series connection of devices. Difficulty and reliability, but the number of devices has doubled. [0037] FIG. 8 shows a multi-winding isolation transformer to construct an intermediate frequency isolation DC-DC converter 2 with a multi-port second DC port. By introducing a multi-winding isolation transformer, a discrete structure can be constructed at the second port. Multiple DC ports, or through a suitable connection to achieve bipolar operation. [0038] Further, the working frequency of the intermediate frequency isolation type DC-DC converter 2 is less than 2kHz; the intermediate frequency isolation type DC-DC converter 2 uses high-voltage devices (rated voltage level 23.3kV) to reduce the number of sub-modules. The type can be insulated gate bipolar transistor (IGBT) or integrated gate commutated thyristor (IGCT). [0039] The present invention uses a step-down AC-DC converter 1 and an intermediate frequency isolation DC-DC converter 2 to construct a power electronic transformer, which can significantly reduce the cost and volume of the system, and improve power density and operating efficiency At the same time, the power electronic transformer has multiple types of AC and DC ports, which is convenient to realize the integrated energy management of the "source-network-load-storage" system. [0040] The above are only the preferred embodiments of the present invention, and the protection scope of the present invention is not limited to the above-mentioned embodiments. All technical solutions that fall under the idea of the present invention belong to the protection scope of the present invention. It should be pointed out that for those of ordinary skill in the art, several improvements and modifications without departing from the principle of the present invention should be regarded as the protection scope of the present invention.
[ZH CN113328454A]: 一种柔性多状态开关、柔性交直流互联系统以及控制方法 [EN CN113328454A]: Flexible multi-state switch, flexible AC-DC interconnection system and control method | [ZH CN113328454A]: 本申请提供柔性多状态开关、柔性交直流互联系统以及控制方法：包括至少两个链式换流器；所述链式换流器包括三个能量均衡换流链，所述功率单元由第一直流电容与功率组件构成；所述功率组件为半桥、全桥或直接串联连接方式；所述直流均衡单元包括三个端口，分别定义为第一、二、三直流端口，其中第一、二直流端口级联，首端、尾端分别定义为换流链的第一均衡端口、第二均衡端口；所述第三直流端口与第一直流电容的正极或负极连接；还包括至少一个直流互联单元；所述直流互联单元两端分别连接位于两个链式换流器的任意不同功率单元上的第一直流电容。 [EN CN113328454A]: This application provides a flexible multi-state switch, a flexible AC/DC interconnection system, and a control method: including at least two chain converters; the chain converter includes three energy-balanced converter chains, and the power unit consists of a first DC capacitors and power components are formed; the power components are half-bridge, full-bridge or direct series connection; the DC equalization unit includes three ports, which are defined as the first, second, and third DC ports, of which the first and second The DC ports are cascaded, and the head end and the tail end are respectively defined as the first equalization port and the second equalization port of the converter chain; the third DC port is connected to the positive or negative pole of the first DC capacitor; it also includes at least one DC interconnect Unit; The two ends of the DC interconnection unit are respectively connected to the first DC capacitors located on any different power units of the two chain converters. | CN113328454A | 2021-08-31 | CN202010089448A | 2020-02-13 | CN202010089448A, 2020-02-13 | CN113328454A: 2021-08-31 | 南京南瑞继保电气有限公司 南京南瑞继保工程技术有限公司 |  | H02J3/36: I H02J3/48: I H02J5/00: I |  |  |  | [ZH CN113328454A]: 1 .一种柔性多状态开关，其特征在于，包括： 至少两个链式换流器和至少一个直流互联单元； 所述链式换流器包括三个能量均衡换流链;所述能量均衡换流链包括N个功率单元以 及与功率单元一一对应的N个直流均衡单元，所述N为大于等于1的整数； 所述功率单元由第一直流电容与功率组件构成;所述功率组件为半桥、全桥或直接串 联连接方式； 所述功率单元的交流端级联，首端、尾端分别定义为换流链的第一功率端口、第二功率 端口 ； 所述直流均衡单元包括三个端口，分别定义为第一、二、三直流端口，其中第一、二直流 端口级联，首端、尾端分别定义为换流链的第一均衡端口、第二均衡端口 ；所述第三直流端 口与第一直流电容的正极或负极连接； 所述直流均衡单元包括第一开关单元和第二开关单元； 所述直流互联单元两端分别连接位于两个链式换流器的任意不同功率单元上的第一 直流电容。 2 .根据权利要求1所述的柔性多状态开关，其特征在于，所述直流均衡单元用于调节相 邻功率单元第一直流电容之间的电压平衡。 3 .根据权利要求1所述的柔性多状态开关，其特征在于，所述直流均衡单元的第一、二 开关单元的一端分别与第一、二直流端口连接；第一开关单元与第二开关单元的另一端连 接后与第三直流端口连接。 4 .根据权利要求3所述的柔性多状态开关，其特征在于，所述直流均衡单元还包括第四 直流端口，还包括第三、四开关单元，所述第三、四开关单元一端与第一、二直流端口连接， 另一端连接后与第四直流端口连接;所述第四直流端口与第一直流电容的负极或正极连 接。 5 .根据权利要求1所述的柔性多状态开关，其特征在于，所述直流均衡单元的第一、二 开关单元的一端分别与第一、二直流端口连接；第一开关单元的另一端与第二端口连接，第 二开关单元的另一端与第三端口连接。 6 .根据权利要求1所述的柔性多状态开关，其特征在于，所述直流均衡单元还包括第五 开关，所述第五开关并联连接于第一、二直流端口之间。 7 .根据权利要求1所述的柔性多状态开关，其特征在于，所述三个换流链的第一功率端 口或第二功率端口连接在一起，未连接的一端分别连接电网的ABC三相，构成星型连接方 式;或者三个换流链的第一功率端口与相邻换流链的第二功率端口相互连接，构成闭环，三 个换流链的第一功率端口或第二功率端口分别连接电网的ABC三相，构成角型连接方式。 8 .根据权利要求7所述的柔性多状态开关，其特征在于，当三个换流链为星型连接时， 所述三个换流链的第一均衡端口或第二均衡端口连接在一起；当三个换流链为角型连接 时，所述三个换流链的第一均衡端口与相邻换流链的第二均衡端口相互连接，构成闭环。 9 .根据权利要求1所述的柔性多状态开关，其特征在于，所述第一、二开关单元分别包 括第一、二开关，所述第一、二开关为功率半导体器件或机械开关。 10 .根据权利要求9所述的柔性多状态开关，其特征在于，所述第一、二开关单元还包括 限流电阻、电感或/和熔丝，所述电阻、电感或/和熔丝与第一、二开关串联。 11 .根据权利要求4所述的柔性多状态开关，其特征在于，所述第一、二、三、四开关单元 分别包括第一、二、三、四开关，所述第一、二、三、四开关为功率半导体器件或机械开关。 12 .根据权利要求11所述的柔性多状态开关，其特征在于，所述第一、二、三、四开关单 元还包括限流电阻、电感或/和熔丝，所述电阻、电感或/和熔丝与第一、二、三、四开关串联。 13 .根据权利要求1所述的柔性多状态开关，其特征在于，所述直流互联单元由互联单 元直交变换器、隔离变压器与互联单元交直变换器构成;所述互联单元直交变换器将直流 变换为交流，连接隔离变压器的原边；隔离变压器的副边连接互联单元交直变换器的交流 侧，互联单元交直变换器将交流变换为直流。 14 .根据权利要求1所述的柔性多状态开关，其特征在于，所述换流链还包括至少一个 耗能单元，串联在换流链中的任意位置或并联在第一直流电容的两端。 15 .根据权利要求14所述的柔性多状态开关，其特征在于，所述耗能单元包括串联连接 的耗能电阻以及快速开关。 16 .根据权利要求14所述的柔性多状态开关，其特征在于，所述耗能单元包括第一快速 开关、阻尼电阻、第二快速开关、耗能电阻以及第二直流电容，第二直流电容与第二快速开 关和耗能电阻串联后，与阻尼电阻、第一快速开关并联。 17 .一种柔性交直流互联系统，其特征在于，所述柔性交直流互联系统包括如权利要求 1-16所述的柔性多状态开关，所述柔性交直流互联系统还包括直直换流器和/或直交换流 器。 18 .根据权利要求17所述的柔性交直流互联系统，其特征在于，所述直直换流器的输入 端连接链式换流器中任意功率单元的第一直流电容，输出端备用或者连接到直流母线。 19 .根据权利要求17所述的柔性交直流互联系统，其特征在于，直交换流器的直流端连 接链式换流器中任意功率单元的第一直流电容，交流端备用或者连接到交流母线。 20 .根据权利要求18所述的柔性交直流互联系统，其特征在于，所述柔性交直流互联系 统还包括母线互联直直换流器，所述母线互联直直换流器用于连接任意两个直流母线。 21 .根据权利要求19所述的柔性交直流互联系统，其特征在于，所述柔性交直流互联系 统还包括互联交直交换流器，所述互联交直交换流器用于连接任意两个交流母线。 22 .一种基于权利要求1-13任一项所述柔性多状态开关的控制方法，其特征在于，所述 柔性多状态开关通过自行判断或接受外部指令，进入以下工作状态，包括： 双侧电能治理状态:所述柔性多状态开关中两个链式换流器独立补偿连接点的电能质 量，包括无功功率、谐波电压/电流、不平衡电压/电流； 双侧自动均压状态:所述柔性多状态开关中两个链式换流器利用直流均衡单元实现直 流电压自动均衡控制； 有功可控传输状态:所述柔性多状态开关中两个链式换流器之间利用直流互联单元进 行受控的有功功率传输； 短路电流转移状态:所述柔性多状态开关中两个链式换流器在外部系统故障发生后， 转移部分故障电流，减小流经故障点的短路电流； 无源供电状态:所述柔性多状态开关中单个链式换流器补偿连接点交流母线失电，其 链式换流器转换为电压/频率控制模式，从另一个链式换流器中获得有功功率，为失电的补 偿连接点交流母线供电。 23.根据权利要求22所述的控制方法，其特征在于，所述柔性多状态开关能够在多种状 态切换，所述方法包括以下步骤： 步骤1：柔性多状态开关启动后进入双侧自动均压状态； 步骤2：柔性多状态开关在双侧电能治理状态和有功可控传输状态中任意切换，或同时 运行于上述两种状态； 步骤3：当交流系统发生临时性故障时，柔性多状态开关根据相应的判据进入短路电流 转移状态； 步骤4：当任意一个与链式换流器连接的交流母线失电时，柔性多状态开关进入无源供 电状态，由正常的交流母线向失电交流系统供电。 24.一种基于权利要求14-16任一项所述柔性多状态开关的控制方法，其特征在于，所 述柔性多状态开关通过自行判断或接受外部指令，进入以下工作状态，包括： 双侧电能治理状态:所述柔性多状态开关中两个链式换流器独立补偿连接点的电能质 量，包括无功功率、谐波电压/电流、不平衡电压/电流； 双侧自动均压状态:所述柔性多状态开关中两个链式换流器利用直流均衡单元实现直 流电压自动均衡控制； 双侧独立耗能状态:所述柔性多状态开关中两个链式换流器利用耗能单元消耗有功功 率，维持换流器功率单元的直流电容电压稳定。 有功可控传输状态:所述柔性多状态开关中两个链式换流器之间利用直流互联单元进 行受控的有功功率传输； 短路电流转移状态:所述柔性多状态开关中两个链式换流器在外部系统故障发生后， 转移部分故障电流，减小流经故障点的短路电流； 无源供电状态:所述柔性多状态开关中单个链式换流器补偿连接点交流母线失电，其 链式换流器转换为电压/频率控制模式，从另一个链式换流器中获得有功功率，为失电的补 偿连接点交流母线供电。 25.根据权利要求24所述的控制方法，其特征在于，所述柔性多状态开关能够在多种状 态切换，所述方法包括以下步骤： 步骤1：柔性多状态开关启动后进入双侧自动均压状态； 步骤2：柔性多状态开关在双侧电能治理状态和有功可控传输状态中任意切换，或同时 运行于上述两种状态； 步骤3：当交流系统发生临时性故障时，柔性多状态开关根据相应的判据进入双侧独立 耗能状态或短路电流转移状态； 步骤4：当任意一个与链式换流器连接的交流母线失电时，柔性多状态开关进入无源供 电状态，由正常的交流母线向失电交流系统供电。 26.一种基于权利要求17-21任一项所述柔性交直流互联系统的控制方法，其特征在 于， 当柔性多状态开关中两个链式换流器的补偿连接点均失电，直流母线或交流母线上所 连接的电源向系统反送电，单侧或双侧链式换流器转换为电压/频率控制模式，为失电的补 偿连接点供电。 [EN CN113328454A]: 1 A flexible multi-state switch, characterized by comprising: at least two chain converters and at least one DC interconnection unit; the chain converter includes three energy-balanced converter chains; the energy-balanced converter The flow chain includes N power units and N DC equalization units corresponding to the power units one-to-one, where N is an integer greater than or equal to 1; the power unit is composed of a first DC capacitor and a power component; the power component is Half-bridge, full-bridge or direct series connection; the AC ends of the power unit are cascaded, and the head end and the tail end are respectively defined as the first power port and the second power port of the converter chain; the DC equalization unit includes three Two ports are respectively defined as the first, second, and third DC ports, where the first and second DC ports are cascaded, and the head end and the tail end are respectively defined as the first equalization port and the second equalization port of the converter chain; The three DC ports are connected to the positive or negative pole of the first DC capacitor; the DC equalization unit includes a first switch unit and a second switch unit; the two ends of the DC interconnection unit are respectively connected to any different ones located in the two chain converters The first DC capacitor on the power unit. 2 The flexible multi-state switch according to claim 1, wherein the DC balance unit is used to adjust the voltage balance between the first DC capacitors of adjacent power units. 3 The flexible multi-state switch according to claim 1, wherein one ends of the first and second switching units of the DC balancing unit are respectively connected to the first and second DC ports; the first switching unit and the second switching unit The other end of the device is connected to the third DC port. 4 The flexible multi-state switch according to claim 3, wherein the DC balance unit further comprises a fourth DC port, and further comprises a third and a fourth switch unit, one end of the third and fourth switch unit is connected to the first , Two DC ports are connected, and the other end is connected to the fourth DC port; the fourth DC port is connected to the negative electrode or the positive electrode of the first DC capacitor. 5 The flexible multi-state switch according to claim 1, wherein one ends of the first and second switching units of the DC balancing unit are connected to the first and second DC ports, respectively; the other end of the first switching unit is connected to the first The two ports are connected, and the other end of the second switch unit is connected with the third port. 6 The flexible multi-state switch according to claim 1, wherein the DC balance unit further comprises a fifth switch, and the fifth switch is connected in parallel between the first and second DC ports. 7 The flexible multi-state switch according to claim 1, wherein the first power port or the second power port of the three converter chains are connected together, and the unconnected end is respectively connected to the ABC three phases of the power grid, A star connection is formed; or the first power port of the three converter chains is connected to the second power port of the adjacent converter chain to form a closed loop, and the first power port or the second power port of the three converter chains are respectively connected The ABC three phases connected to the power grid form an angular connection. 8 The flexible multi-state switch according to claim 7, wherein when the three converter chains are connected in a star shape, the first equalization port or the second equalization port of the three converter chains are connected together; When the three converter chains are connected in an angular shape, the first equalization ports of the three converter chains and the second equalization ports of the adjacent converter chains are connected to each other to form a closed loop. 9 The flexible multi-state switch according to claim 1, wherein the first and second switch units comprise first and second switches respectively, and the first and second switches are power semiconductor devices or mechanical switches. 10 The flexible multi-state switch according to claim 9, wherein the first and second switch units further comprise a current-limiting resistor, an inductor or/and a fuse, and the resistor, an inductor or/and a fuse are connected to the first One and two switches are connected in series. 11 The flexible multi-state switch according to claim 4, wherein the first, second, third, and fourth switch units respectively comprise first, second, third, and fourth switches, and the first, second, third, and fourth switch units The four switches are power semiconductor devices or mechanical switches. 12 The flexible multi-state switch according to claim 11, wherein the first, second, third, and fourth switch units further comprise current-limiting resistors, inductors, or/and fuses, and the resistors, inductors, or/and The fuse is connected in series with the first, second, third, and fourth switches. 13 The flexible multi-state switch according to claim 1, wherein the DC interconnection unit is composed of an interconnection unit DC/AC converter, an isolation transformer, and an interconnection unit AC/DC converter; the interconnection unit DC/AC converter converts DC into AC is connected to the primary side of the isolation transformer; the secondary side of the isolation transformer is connected to the AC side of the AC-DC converter of the interconnection unit, and the AC-DC converter of the interconnection unit converts AC to DC. 14 The flexible multi-state switch according to claim 1, wherein the commutation chain further comprises at least one energy consuming unit, which is connected in series at any position in the commutation chain or connected in parallel to both ends of the first DC capacitor. 15 The flexible multi-state switch according to claim 14, wherein the energy consumption unit comprises an energy consumption resistor and a fast switch connected in series. 16 The flexible multi-state switch according to claim 14, wherein the energy consumption unit comprises a first fast switch, a damping resistor, a second fast switch, an energy consumption resistor, and a second DC capacitor, the second DC capacitor and After the second fast switch and the energy dissipation resistor are connected in series, they are connected in parallel with the damping resistor and the first fast switch. 17 A flexible AC/DC interconnection system, characterized in that the flexible AC/DC interconnection system comprises the flexible multi-state switch as claimed in claims 1-16, and the flexible AC/DC interconnection system further comprises a DC/DC converter and / Or direct current exchanger. 18 The flexible AC-DC interconnection system according to claim 17, wherein the input end of the direct-to-direct converter is connected to the first DC capacitor of any power unit in the chain converter, and the output end is reserved or connected to DC bus. 19 The flexible AC-DC interconnection system according to claim 17, wherein the DC terminal of the DC converter is connected to the first DC capacitor of any power unit in the chain converter, and the AC terminal is reserved or connected to the AC bus. 20 The flexible AC-DC interconnection system according to claim 18, wherein the flexible AC-DC interconnection system further comprises a bus-interconnected direct-to-direct converter, and the bus-interconnected direct-to-direct converter is used to connect any two direct-current converters. Busbar. twenty one The flexible AC-DC interconnection system according to claim 19, wherein the flexible AC-DC interconnection system further comprises an interconnecting AC-DC converter, and the interconnecting AC-DC converter is used to connect any two AC busbars. twenty two A control method based on the flexible multi-state switch according to any one of claims 1-13, wherein the flexible multi-state switch enters the following working states through self-determination or receiving external instructions, including: double-sided electrical energy Governance status: The two chain converters in the flexible multi-state switch independently compensate the power quality of the connection point, including reactive power, harmonic voltage/current, unbalanced voltage/current; automatic voltage equalization on both sides: all The two chain converters in the flexible multi-state switch use a DC equalization unit to achieve automatic DC voltage equalization control; active power controllable transmission state: the two chain converters in the flexible multi-state switch use a DC interconnection unit between the two chain converters Carrying out controlled active power transmission; Short-circuit current transfer state: the two chain converters in the flexible multi-state switch transfer part of the fault current after an external system failure occurs to reduce the short-circuit current flowing through the fault point; none Source power supply status: A single chain converter in the flexible multi-state switch compensates for the loss of the AC bus at the connection point, and the chain converter is converted to voltage/frequency control mode to obtain active power from another chain converter Power, which supplies power to the AC bus of the compensation connection point that is lost. 23. The control method according to claim 22, characterized in that the flexible multi-state switch can switch in multiple states, and the method comprises the following steps: Step 1: After the flexible multi-state switch is activated, it enters the automatic equalization on both sides. Step 2: The flexible multi-state switch can switch arbitrarily between the dual-sided power management state and the active controllable transmission state, or run in the above two states at the same time; Step 3: When the AC system has a temporary failure, the flexible multi-state The switch enters the short-circuit current transfer state according to the corresponding criterion; Step 4: When any AC bus connected to the chain converter loses power, the flexible multi-state switch enters the passive power supply state, and the normal AC bus loses power AC system power supply. 24. A control method based on the flexible multi-state switch according to any one of claims 14-16, wherein the flexible multi-state switch enters the following working states through self-determination or receiving external instructions, including: double-sided Power management status: The two chain converters in the flexible multi-state switch independently compensate the power quality of the connection point, including reactive power, harmonic voltage/current, unbalanced voltage/current; dual-side automatic voltage equalization status: The two chain converters in the flexible multi-state switch utilize a DC equalization unit to achieve automatic DC voltage equalization control; independent energy consumption state on both sides: the two chain converters in the flexible multi-state switch utilize energy consumption units Consumes active power and maintains the DC capacitor voltage of the converter power unit to be stable. Active controllable transmission state: the two chain converters in the flexible multi-state switch utilize the DC interconnection unit for controlled active power transmission; the short-circuit current transfer state: the two chain converters in the flexible multi-state switch After an external system failure occurs, the converter transfers part of the fault current to reduce the short-circuit current flowing through the fault point; Passive power supply state: a single chain converter in the flexible multi-state switch compensates for the loss of the AC bus at the connection point , The chain converter is converted to voltage/frequency control mode, and the active power is obtained from another chain converter to supply power to the AC bus of the compensation connection point of the loss of power. 25. The control method according to claim 24, wherein the flexible multi-state switch can be switched in multiple states, and the method comprises the following steps: Step 1: After the flexible multi-state switch is started, it enters the automatic equalization on both sides. Step 2: The flexible multi-state switch can switch arbitrarily between the dual-sided power management state and the active controllable transmission state, or run in the above two states at the same time; Step 3: When the AC system has a temporary failure, the flexible multi-state The switch enters the dual-side independent energy consumption state or the short-circuit current transfer state according to the corresponding criterion; Step 4: When any AC bus connected to the chain converter loses power, the flexible multi-state switch enters the passive power supply state. The normal AC bus bar supplies power to the power-loss AC system. 26. A control method based on the flexible AC-DC interconnection system of any one of claims 17-21, wherein when the compensation connection points of the two chain converters in the flexible multi-state switch are both de-energized, the DC The power supply connected to the busbar or AC busbar sends power back to the system, and the single-side or double-side chain converter is converted to voltage/frequency control mode to supply power to the compensation connection point of the loss of power. | [ZH CN113328454A]: 一种柔性多状态开关、柔性交直流互联系统以及控制方法 技术领域 [0001]本申请涉及电力电子技术领域，具体涉及柔性多状态开关、柔性交直流互联系统 以及控制方法。 背景技术 [0002]随着用户对用电需求、电能质量及供电可靠性等要求的不断提高，传统的供电网 络越来越难以满足用户的供电需求。现有的供配电网络其中一条线路过负荷或者故障时， 经常导致较大范围的停电。在双母线供电的情况下，经常出现一条母线负荷过重，另一条母 线轻载，存在用电负荷不平衡的情况，如果两路母线之间利用电力电子技术实现互联，既可 以提高供电可靠性，也可以实现有功功率的平衡。同时，在交直流配电网中，分布式发电在 电网中的应用范围越来越广泛，且逐渐成为大电网的有效补充，分布式电源、负荷以及储能 装置构成微网，众多分布式电源、负荷以及储能装置的类型不同，包含直流或交流，电压等 级、容量也不相同，如何将上述低压单元经济、有效地接入，进行统一管理是较难解决的问 题。 [0003] 现有技术中基于全控器件的电压源换流器(voltage source converter，VSC)背 靠背组建的柔性合环装置可以实现配电网络的合环运行，提高供电可靠性，并可以实现有 功功率相互传输，但是上述方式成本过高;且互联方式单一，仅能够实现两路中压交流电源 之间的互联，无法提供低压交直流系统接入或实现低压交直流互联。并不能成为经济、有效 的解决方案。 发明内容 [0004]本发明的目的在于，提供一种柔性多状态开关以及柔性交直流互联系统可实现两 路交流电源有功功率的相互支援，并达到直流电压均衡控制效果，同时提供低压交直流端 口，便于实现低压交直流系统接入、实现低压交直流互联，成本低，可靠性高。本发明同时提 供相应的控制方法。 [0005]为了达到上述目的，本发明的解决方案是： [0006] 一种柔性多状态开关，包括： [0007] 至少两个链式换流器和至少一个直流互联单元； [0008] 所述链式换流器包括三个能量均衡换流链;所述能量均衡换流链包括N个功率单 元以及与功率单元一一对应的N个直流均衡单元，所述N为大于等于1的整数； [0009]所述功率单元由第一直流电容与功率组件构成;所述功率组件为半桥、全桥或直 接串联连接方式； [0010]所述功率单元的交流端级联，首端、尾端分别定义为换流链的第一功率端口、第二 功率端口； [0011]所述直流均衡单元包括三个端口，分别定义为第一、二、三直流端口，其中第一、二 直流端口级联，首端、尾端分别定义为换流链的第一均衡端口、第二均衡端口 ；所述第三直 流端口与第一直流电容的正极或负极连接； [0012]所述直流均衡单元包括第一开关单元和第二开关单元； [0013]所述直流互联单元两端分别连接位于两个链式换流器的任意不同功率单元上的 第一直流电容。 [0014]作为本发明的进一步优选方案，所述直流均衡单元用于调节相邻功率单元第一直 流电容之间的电压平衡。 [0015]作为本发明的进一步优选方案，所述直流均衡单元的第一、二开关单元的一端分 别与第一、二直流端口连接;第一开关单元与第二开关单元的另一端连接后与第三直流端 口连接。 [0016]作为本发明的进一步优选方案，所述直流均衡单元还包括第四直流端口，还包括 第三、四开关单元，所述第三、四开关单元一端与第一、二直流端口连接，另一端连接后与第 四直流端口连接;所述第四直流端口与第一直流电容的负极或正极连接。 [0017]作为本发明的进一步优选方案，所述直流均衡单元的第一、二开关单元的一端分 别与第一、二直流端口连接;第一开关单元的另一端与第二端口连接，第二开关单元的另一 端与第三端口连接。 [0018]作为本发明的进一步优选方案，所述直流均衡单元还包括第五开关，所述第五开 关并联连接于第一、二直流端口之间。 [0019]作为本发明的进一步优选方案，所述三个换流链的第一功率端口或第二功率端口 连接在一起，未连接的一端分别连接电网的ABC三相，构成星型连接方式；或者三个换流链 的第一功率端口与相邻换流链的第二功率端口相互连接，构成闭环，三个换流链的第一功 率端口或第二功率端口分别连接电网的ABC三相，构成角型连接方式。 [0020]作为本发明的进一步优选方案，当三个换流链为星型连接时，所述三个换流链的 第一均衡端口或第二均衡端口连接在一起；当三个换流链为角型连接时，所述三个换流链 的第一均衡端口与相邻换流链的第二均衡端口相互连接，构成闭环。 [0021]作为本发明的进一步优选方案，所述第一、二开关单元分别包括第一、二开关，所 述第一、二开关为功率半导体器件或机械开关。 [0022]作为本发明的进一步优选方案，所述第一、二开关单元还包括限流电阻、电感或/ 和熔丝，所述电阻、电感或/和熔丝与第一、二开关串联。 [0023]作为本发明的进一步优选方案，所述第一、二、三、四开关单元分别包括第一、二、 三、四开关，所述第一、二、三、四开关为功率半导体器件或机械开关。 [0024]作为本发明的进一步优选方案，所述第一、二、三、四开关单元还包括限流电阻、电 感或/和熔丝，所述电阻、电感或/和熔丝与第一、二、三、四开关串联。 [0025]作为本发明的进一步优选方案，所述直流互联单元由互联单元直交变换器、隔离 变压器与互联单元交直变换器构成；所述互联单元直交变换器将直流变换为交流，连接隔 离变压器的原边;隔离变压器的副边连接互联单元交直变换器的交流侧，互联单元交直变 换器将交流变换为直流。 [0026]作为本发明的进一步优选方案，所述换流链还包括至少一个耗能单元，串联在换 流链中的任意位置或并联在第一直流电容的两端。 [0027]作为本发明的进一步优选方案，所述耗能单元包括串联连接的耗能电阻以及快速 开关。 [0028]作为本发明的进一步优选方案，所述耗能单元包括第一快速开关、阻尼电阻、第二 快速开关、耗能电阻以及第二直流电容，第二直流电容与第二快速开关和耗能电阻串联后， 与阻尼电阻、第一快速开关并联。 [0029]本发明同时提供了一种柔性交直流互联系统，所述柔性交直流互联系统包括如上 所述的柔性多状态开关，所述柔性交直流互联系统还包括直直换流器和/或直交换流器。 [0030]作为本发明的进一步优选方案，所述直直换流器的输入端连接链式换流器中任意 功率单元的第一直流电容，输出端备用或者连接到直流母线。 [0031]作为本发明的进一步优选方案，直交换流器的直流端连接链式换流器中任意功率 单元的第一直流电容，交流端备用或者连接到交流母线。 [0032]作为本发明的进一步优选方案，所述柔性交直流互联系统还包括母线互联直直换 流器，所述母线互联直直换流器用于连接任意两个直流母线。 [0033]作为本发明的进一步优选方案，所述柔性交直流互联系统还包括互联交直交换流 器，所述互联交直交换流器用于连接任意两个交流母线。 [0034]本发明同时提供了上述柔性多状态开关的控制方法，所述柔性多状态开关通过自 行判断或接受外部指令，进入以下工作状态，包括： [0035]双侧电能治理状态:所述柔性多状态开关中两个链式换流器独立补偿连接点的电 能质量，包括无功功率、谐波电压/电流、不平衡电压/电流； [0036]双侧自动均压状态:所述柔性多状态开关中两个链式换流器利用直流均衡单元实 现直流电压自动均衡控制； [0037]有功可控传输状态:所述柔性多状态开关中两个链式换流器之间利用直流互联单 元进行受控的有功功率传输； [0038]短路电流转移状态:所述柔性多状态开关中两个链式换流器在外部系统故障发生 后，转移部分故障电流，减小流经故障点的短路电流； [0039]无源供电状态:所述柔性多状态开关中单个链式换流器补偿连接点交流母线失 电，其链式换流器转换为电压/频率控制模式，从另一个链式换流器中获得有功功率，为失 电的补偿连接点交流母线供电。 [0040]作为本发明的进一步优选方案，所述柔性多状态开关能够在多种状态切换，所述 方法包括以下步骤： [0041] 步骤1：柔性多状态开关启动后进入双侧自动均压状态； [0042]步骤2：柔性多状态开关在双侧电能治理状态和有功可控传输状态中任意切换，或 同时运行于上述两种状态； [0043]步骤3：当交流系统发生临时性故障时，柔性多状态开关根据相应的判据进入短路 电流转移状态； [0044] 步骤4：当任意一个与链式换流器连接的交流母线失电时，柔性多状态开关进入无 源供电状态，由正常的交流母线向失电交流系统供电。 [0045]本发明同时提供了另一种上述柔性多状态开关的控制方法，所述柔性多状态开关 通过自行判断或接受外部指令，进入以下工作状态，包括： [0046] 双侧电能治理状态：所述柔性多状态开关中两个链式换流器独立补偿连接点的电 能质量，包括无功功率、谐波电压/电流、不平衡电压/电流； [0047]双侧自动均压状态:所述柔性多状态开关中两个链式换流器利用直流均衡单元实 现直流电压自动均衡控制； [0048]双侧独立耗能状态:所述柔性多状态开关中两个链式换流器利用耗能单元消耗有 功功率，维持换流器功率单元的直流电容电压稳定。 [0049]有功可控传输状态:所述柔性多状态开关中两个链式换流器之间利用直流互联单 元进行受控的有功功率传输； [0050]短路电流转移状态:所述柔性多状态开关中两个链式换流器在外部系统故障发生 后，转移部分故障电流，减小流经故障点的短路电流； [0051]无源供电状态:所述柔性多状态开关中单个链式换流器补偿连接点交流母线失 电，其链式换流器转换为电压/频率控制模式，从另一个链式换流器中获得有功功率，为失 电的补偿连接点交流母线供电。 [0052]作为本发明的进一步优选方案，所述柔性多状态开关能够在多种状态切换，所述 方法包括以下步骤： [0053] 步骤1：柔性多状态开关启动后进入双侧自动均压状态； [0054]步骤2：柔性多状态开关在双侧电能治理状态和有功可控传输状态中任意切换，或 同时运行于上述两种状态； [0055]步骤3：当交流系统发生临时性故障时，柔性多状态开关根据相应的判据进入双侧 独立耗能状态或短路电流转移状态； [0056] 步骤4：当任意一个与链式换流器连接的交流母线失电时，柔性多状态开关进入无 源供电状态，由正常的交流母线向失电交流系统供电。 [0057]本发明还提供了上述柔性交直流互联系统的控制方法，包括： [0058]当柔性多状态开关中两个链式换流器的补偿连接点均失电，直流母线或交流母线 上所连接的电源向系统反送电，单侧或双侧链式换流器转换为电压/频率控制模式，为失电 的补偿连接点供电。 [0059] 有益效果： [0060] (1)本申请提供的技术方案:在两个链式换流器中换流链的功率单元之间的直流 互联单元实现了两个换流器的有功功率传输；链式换流器内部的直流均衡单元在角内构成 闭环，当直流电压不均衡时，直流均衡单元会自动实现直流电压均衡调节，因此功率单元之 间的直流互联单元可以任意设置；即当两个链式换流器互联时，当有功功率传输时，局部的 直流电容电压不平衡可以被每个链式换流器内部平衡掉。 [0061] (2)本发明链式换流器中换流链的功率单元的直流电容可以引出低压直流端口， 额外增加直交变换器，即可提供低压交流端口，可以方便的与低压交直流母线连接，或者直 接与低压交直流电源或负荷连接，构成交直流互联系统。交直流互联系统可以实现有功功 率传输，端口之间的功率不平衡造成的直流电压不均可以通过链式换流器的直流均衡单元 实现自动均衡控制。 [0062] (3)本申请提供的技术方案中的链式换流器本身可作为静止无功发生器，调节交 流电网补偿点的电能质量，可解决功率因数，谐波以及不平衡问题。 附图说明 [0063]为了更清楚地说明本申请实施例中的技术方案，下面将对实施例描述中所需要使 用的附图作简单地介绍，显而易见地，下面描述中的附图仅仅是本申请的一些实施例，对于 本领域普通技术人员来讲，在不付出创造性劳动的前提下，还可以根据这些附图获得其他 的附图。 [0064]图1是本申请实施例提供的一种柔性多状态开关构成示意图； [0065]图2A是本申请实施例提供的直流均衡单元构成示意图之一； [0066]图2B是本申请实施例提供的直流均衡单元构成示意图之二； [0067]图2c是本申请实施例提供的直流均衡单元构成示意图之三； [0068]图2D是本申请实施例提供的直流均衡单元构成示意图之四； [0069]图3A是本申请实施例提供的功率单元构成示意图之一； [0070]图3B是本申请实施例提供的功率单元构成示意图之二； [0071]图3c是本申请实施例提供的功率单元构成示意图之三； [0072]图4是本申请实施例提供的耗能单元构成示意图； [0073]图5是本申请实施例提供的一种直流互联单元构成示意图。 [0074]图6A是本申请实施例提供的一种链式换流器构成示意图之一。 [0075]图6B是本申请实施例提供的一种链式换流器构成示意图之二。 [0076]图7是本申请实施例提供的一种柔性交直流互联系统构成示意图。 [0077]图8是本申请实施例提供的一种多状态开关控制方法示意图。 [0078] 附图标记： [0079] 1、能量均衡换流链;2、功率单元;3、直流均衡单元;4、耗能单元;5、直流互联单元； 具体实施方式 [0080]下面将结合本申请实施例中的附图，对本申请实施例中的技术方案进行清楚、完 整地描述，显然，所描述的实施例是本申请一部分实施例，而不是全部的实施例。基于本申 请中的实施例，本领域技术人员在没有做出创造性劳动前提下所获得的所有其他实施例， 都属于本申请保护的范围。 [0081]应当理解，本申请的权利要求、及附图中的术语“第一”、“第二”、“第三”、 “第四”等是用于区别不同对象，而不是用于描述特定顺序。本申请的和权利要求书 中使用的术语“包括”指示所描述特征、整体、步骤、操作、元素和/或组件的存在，但并不排 除一个或多个其它特征、整体、步骤、操作、元素、组件和/或其集合的存在或添加。 [0082]如图1所示:本发明实施例提供一种柔性多状态开关，包括： [0083] 至少两个链式换流器和至少一个直流互联单元； [0084] 所述链式换流器包括三个能量均衡换流链1；所述能量均衡换流链1包括N个功率 单元2以及与功率单元一一对应的N个直流均衡单元3,所述N为大于等于1的整数； [0085]所述功率单元由第一直流电容与功率组件构成;所述功率组件为半桥、全桥或直 接串联连接方式； [0086]其中，本实例中所述功率单元中的功率组件由三种方式构成： [0087] ⑴两个全控型功率半导体器件以半桥连接形式构成，如图3A所示。其中两个全控 型功率半导体器件为带有反并联二极管的IGBT,分别为T1和T2,T1的集电极与第一直流电 容C1的正极连接,T2的集电极与T1的发射极连接,T2的发射极与C1的负极连接,T1的发射极 与T2的发射极引出作为功率单元的两个交流端。 [0088] ⑵由四个全控型功率半导体器件以全桥连接形式构成，如图3B所示。其中四个全 控型功率半导体器件为带有反并联二极管的IGBT，分别为T3-T6,其中T3和T4构成一个桥 臂，T5和T6构成一另个桥臂:T3的集电极与第一直流电容C1的正极连接，T4的集电极与T3的 发射极连接，T4的发射极与C1的负极连接;T5的集电极与第一直流电容C1的正极连接，T6的 集电极与T5的发射极连接，T6的发射极与C1的负极连接;两个桥臂的中点引出作为功率单 元的两个交流端。 [0089] (3)由一个全控型功率半导体器件与缓冲回路并联构成，所述缓冲回路由二极管 与电容串联构成，如图3c所示。其中全控型功率半导体器件T7的集电极经过二极管D1与第 一直流电容C1的正极连接，T7的发射极与第一直流电容C1的负极连接。 [0090]所述功率单元的交流端级联，首端、尾端分别定义为换流链的第一功率端口乂1、第 二功率端DX2； [0091] 所述直流均衡单元包括三个端口，分别定义为第一、二、三直流端口，分别为D1, D2,D3；其中第一、二直流端口级联，首端、尾端分别定义为换流链的第一均衡端口丫1、第二 均衡端口 Y2 ；所述第三直流端口与第一直流电容的正极或负极连接； [0092] 所述直流均衡单元包括第一开关单元K1和第二开关单元K2； [0093]所述直流互联单元5两端分别连接位于两个换流器的任意不同功率单元上的第一 直流电容。 [0094]其中，所述直流均衡单元包括以下几种构成与连接方式： [0095] (1)如图2A所示，第一、二开关单元的一端分别与第一直流端口口1、第二直流端口 D2连接;第一开关单元与第二开关单元的另一端连接后与第三直流端口口3连接。 [0096] ⑵如图2B所示，所述直流均衡单元的第一、二开关单元的一端分别与第一直流端 口 D1、第二直流端口口2连接;第一开关单元的另一端与第二端口连接，第二开关单元的另一 端与第三端口口3连接。 [0097] (3)如图2c所示，第一、二开关单元的一端分别与第一直流端口口1、第二直流端口 D2连接;第一开关单元与第二开关单元的另一端连接后与第三直流端口口3连接;所述直流 均衡单元还包括第四直流端口口4,还包括第三开关单元K3与第四开关单元K4,所述第三、四 开关单元一端与第一、二直流端口连接,另一端连接后与第四直流端口连接。 [0098]如图2A所示,所述直流均衡单元还包括第五开关K5,所述第五开关并联连接于第 一、二直流端口之间。 [0099] 其中，所述第一、二、三、四开关单元分别包括第一、二、三、四开关，所述第一、二、 三、四开关为功率半导体器件或机械开关。图2A、2B的实施例中第一、二开关为机械开关，图 2c的实施例中第一、二、三、四开关均为带有反并联二极管的IGBT。其中，第一、二、三、四开 关也可以为二极管。 [0100] 其中，所述第一、二、三、四开关单元还包括限流电阻、电感或/和熔丝，所述电阻、 电感或/和熔丝与第一、二、三、四开关串联。如图2D所示，本实施例中第二开关单元为第二 开关与限流电阻R1,限流电感L1,熔丝F1串联连接。 [0101]其中，本实施例中所述链式换流器的连接方式包括： [0102] (1)三个换流链的第一功率端DX1连接在一起，第二功率端DX2分别连接电网的 ABC三相;或第二功率端口 X2连接在一起，第一功率端DX1分别连接电网的ABC三相，构成星 型连接方式。 [0103]优选的实施例中，三个换流链的第一功率端DX1连接在一起，同时三个换流链的 第一均衡端口丫1连接在一起，第二功率端口 X2分别连接电网的ABC三相;或者是第二功率端 □ X2连接在一起，同时第二均衡端口丫2连接在一起，第一功率端DX1分别连接电网的ABC三 相。如图6A所示。 [0104] (2)三个换流链的第一功率端口与相邻换流链的第二功率端口相互连接,构成闭 环，三个换流链的第一功率端口 X1或第二功率端DX2分别连接电网的ABC三相,构成角型连 接方式。如图6B所示;所述三个换流链的第一均衡端口丫1与相邻换流链的第二均衡端口丫2 相互连接，构成闭环。 [0105] 其中，所述换流链还包括至少一个耗能单元，所述耗能单元包括所述耗能单元包 括串联连接的耗能电阻以及快速开关，耗能单元串联在换流链中的任意位置或并联在第一 直流电容的两端。如图4所示:在本实施例中，耗能单元包括第一快速开关K6与阻尼电阻R2 还包括第二快速开关K7、耗能电阻R3,以及第二直流电容C2,第二直流电容与第二快速开关 和耗能电阻串联后，与阻尼电阻、第一快速开关并联。 [0106] 其中，所述直流互联单元5由互联单元直交变换器15、隔离变压器17与互联单元交 直变换器16构成;所述互联单元直交变换器15将直流变换为交流，连接隔离变压器的原边; 隔离变压器的副边连接互联单元交直变换器的交流侧，互联单元交直变换器16将交流变换 为直流。如图5所示，在本实施例中，在互联单元直交变换器15与原边绕组之间还包括电容， 在副边绕组与互联单元直交变换器16之间还包括电容与电感。 [0107] 本发明还包括一种柔性交直流互联系统，所述柔性交直流互联系统包括上述柔性 多状态开关，所述柔性交直流互联系统还包括直直换流器和/或直交换流器。 [0108]其中，直直换流器的输入端连接链式换流器中任意功率单元的第一直流电容，输 出端备用或者连接到直流母线。 [0109] 在本实施例中，如图7所示:柔性交直流互联系统共包括2个链式换流器,2个直直 换流器，每个链式换流器连接1个直直换流器，具体通过其中1个功率单元的直流电容与所 述直直换流器连接，直直换流器的输出连接一条直流母线;每个直直换流器连接一条直流 母线，共包括两个直直换流器，共连接两条直流母线。 [0110]其中，直交换流器的直流端连接链式换流器中任意功率单元的第一直流电容，交 流端备用或者连接到交流母线。 [0111] 在本实施例中，如图7所示:柔性交直流互联系统共包括2个链式换流器,2个直交 换流器;每个链式换流器连接1个直交换流器，具体通过其中1个功率单元的直流电容与所 述直交换流器连接，直交换流器的输出连接一条交流母线;每个直交换流器连接一条交流 母线，共包括两个直交换流器，共连接两条交流母线。 [0112] 所述柔性交直流互联系统还包括母线互联直直换流器，所述母线互联直直换流器 用于连接任意两个直流母线。 [0113] 在本实例例中，包括1个母线互联直直换流器，所述1个母线互联直直换流器与2个 直流母线连接。 [0114] 所述柔性交直流互联系统还包括互联交直交换流器，所述互联交直交换流器用于 任意两个交流母线连接。 [0115] 在本实例例中，包括1个母线互联交直交换流器，所述1个母线互联交直交换流器 与2个交流母线连接。 [0116]本发明还提供了一种柔性多状态开关的控制方法，所述柔性多状态开关可自行判 断或接受外部指令，进入以下工作状态，包括： [0117]双侧电能治理状态:所述柔性多状态开关多状态开关中两个链式换流器独立补偿 连接点的电能质量，包括无功功率、谐波电压/电流、不平衡电压/电流； [0118]双侧自动均压状态:所述柔性多状态开关中两个链式换流器利用直流均衡单元实 现直流电压自动均衡控制； [0119]双侧独立耗能状态:所述柔性多状态开关中两个链式换流器利用耗能单元消耗有 功功率，维持换流器功率单元的直流电容电压稳定。 [0120]有功可控传输状态:所述柔性多状态开关中两个链式换流器之间利用直流互联单 元进行受控的有功功率传输； [0121]短路电流转移状态:所述柔性多状态开关中两个链式换流器在外部系统故障发生 后，转移部分故障电流，减小流经故障点的短路电流； [0122]无源供电状态:所述柔性多状态开关中单个链式换流器补偿连接点失电，其链式 换流器转换为电压/频率控制模式，从另一个链式换流器中获得有功功率，为失电的补偿连 接点供电。 [0123]其中，所述柔性多状态开关可以在多种状态切换，所述方法包括以下步骤： [0124] 步骤1：柔性多状态开关启动后进入双侧自动均压状态； [0125]步骤2：柔性多状态开关在双侧电能治理状态和有功可控传输状态中任意切换，或 同时运行于上述两种状态； [0126]步骤3：当交流系统发生临时性故障时，柔性多状态开关根据相应的判据进入双侧 独立耗能状态或短路电流转移状态； [0127]如当系统发生过压故障、装置内部故障时，柔性多状态开关进入双侧独立耗能状 态； [0128]如当系统发生过流故障时，柔性多状态开关进入短路电流转移状态。 [0129]步骤4：当任意一个与链式换流器连接的交流母线失电时，柔性多状态开关进入无 源供电状态，由正常的交流母线向失电交流系统供电。 [0130]本发明还提供了一种所述柔性交直流互联系统的控制方法，所述直流母线连接负 载或电源;交流母线连接负载或电源;互联直直换流器处于运行或闭锁状态；互联交直交换 流器处于运行或闭锁状态。 [0131]所述柔性多状态开关中两个链式换流器的补偿连接点均失电，其直流母线或交流 母线上所连接的电源向系统反送电，单侧或双侧链式换流器转换为电压/频率控制模式，为 失电的补偿连接点供电。 [0132]以上对本申请实施例进行了详细介绍，本文中应用了具体个例对本申请的原理及 实施方式进行了阐述，以上实施例的说明仅用于帮助理解本申请的方法及其核心思想。同 时，本领域技术人员依据本申请的思想，基于本申请的具体实施方式及应用范围上做出的 改变或变形之处，都属于本申请保护的范围。综上所述，本内容不应理解为对本申请 的限制。 [EN CN113328454A]: Technical field of flexible multi-state switch, flexible AC-DC interconnection system and control method [0001] This application relates to the field of power electronics technology, in particular to flexible multi-state switches, flexible AC/DC interconnection systems, and control methods. Background technique [0002] With the continuous improvement of users' requirements for power consumption, power quality, and power supply reliability, it is increasingly difficult for traditional power supply networks to meet the power supply needs of users. When one of the lines of the existing power supply and distribution network is overloaded or faulty, a large-scale blackout is often caused. In the case of dual-bus power supply, one bus is often overloaded and the other bus is lightly loaded, and there is an imbalance in the electrical load. If the two buses are interconnected by power electronic technology, the reliability of power supply can be improved. , Can also achieve the balance of active power. At the same time, in the AC and DC distribution network, distributed power generation is more and more widely used in the power grid, and has gradually become an effective supplement to the large power grid. Distributed power sources, loads, and energy storage devices form microgrids, and many distributed power sources The types of loads and energy storage devices are different, including DC or AC, and the voltage level and capacity are also different. How to connect the above-mentioned low-voltage units economically and effectively and conduct unified management is a difficult problem to solve. [0003] In the prior art, a back-to-back flexible loop closure device based on a full-control device-based voltage source converter (VSC) can realize the loop-closing operation of the power distribution network, improve the reliability of power supply, and achieve active power The power is transferred to each other, but the cost of the above methods is too high; and the interconnection method is single, which can only realize the interconnection between two medium-voltage AC power sources, and cannot provide low-voltage AC/DC system access or realize low-voltage AC/DC interconnection. It cannot be an economical and effective solution. Summary of the invention [0004] The purpose of the present invention is to provide a flexible multi-state switch and a flexible AC-DC interconnection system that can realize the mutual support of the active power of two AC power sources and achieve the effect of DC voltage equalization control, while providing a low-voltage AC and DC port, which is convenient Realize low-voltage AC/DC system access and low-voltage AC/DC interconnection, with low cost and high reliability. The present invention also provides corresponding control methods. [0005] In order to achieve the above objective, the solution of the present invention is: [0006] A flexible multi-state switch, including: [0007] At least two chain converters and at least one DC interconnection unit; [0008] The chain converter includes three energy-balanced converter chains; the energy-balanced converter chain includes N power units and N DC balance units corresponding to the power units one-to-one, where N is greater than An integer equal to 1; [0009] The power unit is composed of a first DC capacitor and a power component; the power component is a half-bridge, full-bridge or direct series connection; [0010] The AC end of the power unit is cascaded, and the head end and the tail end are respectively defined as the first power port and the second power port of the converter chain; [0011] The DC balance unit includes three ports, which are respectively defined as the first, second, and third DC ports, wherein the first and second DC ports are cascaded, and the head end and the tail end are respectively defined as the first equalizer of the converter chain Port, the second equalization port; the third straight The flow port is connected to the positive electrode or the negative electrode of the first DC capacitor; [0012] The DC balance unit includes a first switch unit and a second switch unit; [0013] The two ends of the DC interconnection unit are respectively connected to first DC capacitors located on any different power units of the two chain converters. [0014] As a further preferred solution of the present invention, the DC balance unit is used to adjust the voltage balance between the first DC capacitors of adjacent power units. [0015] As a further preferred solution of the present invention, one ends of the first and second switching units of the DC balance unit are connected to the first and second DC ports respectively; the other ends of the first switching unit and the second switching unit are connected to The third DC port is connected. [0016] As a further preferred solution of the present invention, the DC balance unit further includes a fourth DC port, and further includes a third and a fourth switch unit, one end of the third and fourth switch unit is connected to the first and second DC ports, The other end is connected to the fourth direct current port after being connected; the fourth direct current port is connected to the negative electrode or the positive electrode of the first direct current capacitor. [0017] As a further preferred solution of the present invention, one end of the first and second switch units of the DC balance unit is connected to the first and second DC ports respectively; the other end of the first switch unit is connected to the second port, and the second end of the first switch unit is connected to the second port. The other end of the switch unit is connected to the third port. [0018] As a further preferred solution of the present invention, the DC balance unit further includes a fifth switch, and the fifth switch is connected in parallel between the first and second DC ports. [0019] As a further preferred solution of the present invention, the first power port or the second power port of the three converter chains are connected together, and the unconnected end is respectively connected to the ABC three-phase of the power grid, forming a star connection; Or the first power ports of the three converter chains are connected to the second power ports of the adjacent converter chains to form a closed loop, and the first or second power ports of the three converter chains are respectively connected to the ABC three-phase of the grid , Forming an angular connection. [0020] As a further preferred solution of the present invention, when the three converter chains are connected in a star shape, the first equalization port or the second equalization port of the three converter chains are connected together; when the three converter chains are connected together In the case of an angular connection, the first equalization ports of the three converter chains and the second equalization ports of the adjacent converter chains are connected to each other to form a closed loop. [0021] As a further preferred solution of the present invention, the first and second switch units respectively include first and second switches, and the first and second switches are power semiconductor devices or mechanical switches. [0022] As a further preferred solution of the present invention, the first and second switch units further include a current-limiting resistor, an inductance or/and a fuse, and the resistor, inductance or/and a fuse are connected in series with the first and second switches. [0023] As a further preferred solution of the present invention, the first, second, third, and fourth switch units respectively include first, second, third, and fourth switches, and the first, second, third, and fourth switches are power semiconductor devices Or mechanical switch. [0024] As a further preferred solution of the present invention, the first, second, third, and fourth switch units further include a current-limiting resistor, an inductor or/and a fuse, and the resistor, an inductor or/and a fuse are connected to the first, Two, three, and four switches are connected in series. [0025] As a further preferred solution of the present invention, the DC interconnection unit is composed of an interconnection unit DC/AC converter, an isolation transformer, and an interconnection unit AC/DC converter; the interconnection unit DC/AC converter converts DC to AC, and is connected to the isolation transformer Primary side: The secondary side of the isolation transformer is connected to the AC side of the AC-DC converter of the interconnection unit, and the AC-DC converter of the interconnection unit converts AC to DC. [0026] As a further preferred solution of the present invention, the converter chain further includes at least one energy-consuming unit, which is connected in series at any position in the converter chain or connected in parallel to both ends of the first DC capacitor. [0027] As a further preferred solution of the present invention, the energy consumption unit includes a series connection of energy consumption resistors and fast switch. [0028] As a further preferred solution of the present invention, the energy consumption unit includes a first fast switch, a damping resistor, a second fast switch, an energy consumption resistor, and a second DC capacitor. After the energy resistor is connected in series, it is connected in parallel with the damping resistor and the first fast switch. [0029] The present invention also provides a flexible AC-DC interconnection system. The flexible AC-DC interconnection system includes the flexible multi-state switch as described above, and the flexible AC-DC interconnection system further includes a DC-DC converter and/or Straight current exchanger. [0030] As a further preferred solution of the present invention, the input end of the direct-to-direct converter is connected to the first direct current capacitor of any power unit in the chain converter, and the output end is reserved or connected to the direct current bus. [0031] As a further preferred solution of the present invention, the DC end of the direct converter is connected to the first DC capacitor of any power unit in the chain converter, and the AC end is standby or connected to the AC bus. [0032] As a further preferred solution of the present invention, the flexible AC-DC interconnection system further includes a bus-interconnected direct-to-direct converter, and the bus-interconnected direct-to-direct converter is used to connect any two DC buses. [0033] As a further preferred solution of the present invention, the flexible AC-DC interconnection system further includes an interconnecting AC-DC converter, and the interconnecting AC-DC converter is used to connect any two AC busbars. [0034] The present invention also provides a method for controlling the above-mentioned flexible multi-state switch. The flexible multi-state switch enters the following working states through self-determination or receiving external instructions, including: [0035] Two-sided power management state: the two chain converters in the flexible multi-state switch independently compensate the power quality of the connection point, including reactive power, harmonic voltage/current, and unbalanced voltage/current; [0036] Double-sided automatic voltage equalization state: the two chain converters in the flexible multi-state switch utilize DC equalization units to realize DC voltage automatic equalization control; [0037] Active power controllable transmission state: the two chain converters in the flexible multi-state switch utilize a DC interconnection unit for controlled active power transmission; [0038] Short-circuit current transfer state: the two chain converters in the flexible multi-state switch transfer part of the fault current after an external system fault occurs, and reduce the short-circuit current flowing through the fault point; [0039] Passive power supply state: the single chain converter in the flexible multi-state switch compensates for the loss of the AC bus at the connection point, and the chain converter is converted to a voltage/frequency control mode, and the chain converter is converted from another chain converter. The active power is obtained from the generator to supply power to the AC bus of the compensation connection point of the loss of power. [0040] As a further preferred solution of the present invention, the flexible multi-state switch can be switched in multiple states, and the method includes the following steps: [0041] Step 1: After the flexible multi-state switch is started, it enters the automatic pressure equalization state on both sides; [0042] Step 2: The flexible multi-state switch arbitrarily switches between the dual-sided power management state and the active controllable transmission state, or runs in the above two states at the same time; [0043] Step 3: When a temporary failure occurs in the AC system, the flexible multi-state switch enters the short-circuit current transfer state according to the corresponding criterion; [0044] Step 4: When any AC bus connected to the chain converter loses power, the flexible multi-state switch enters a passive power supply state, and the normal AC bus supplies power to the lost AC system. [0045] The present invention also provides another control method of the above-mentioned flexible multi-state switch. The flexible multi-state switch enters the following working states through self-determination or receiving external instructions, including: [0046] Double-sided power management state: the two chain converters in the flexible multi-state switch independently compensate the electrical power at the connection point Energy quality, including reactive power, harmonic voltage/current, unbalanced voltage/current; [0047] Two-sided automatic voltage equalization state: the two chain converters in the flexible multi-state switch utilize DC equalization units to realize DC voltage automatic equalization control; [0048] Two-sided independent energy consumption state: the two chain converters in the flexible multi-state switch use energy consumption units to consume active power and maintain the DC capacitor voltage of the converter power unit to be stable. [0049] Active power controllable transmission state: the two chain converters in the flexible multi-state switch utilize a DC interconnection unit for controlled active power transmission; [0050] Short-circuit current transfer state: the two chain converters in the flexible multi-state switch transfer part of the fault current after an external system failure occurs, so as to reduce the short-circuit current flowing through the fault point; [0051] Passive power supply state: a single chain converter in the flexible multi-state switch compensates for the loss of the AC bus at the connection point, and the chain converter is converted to a voltage/frequency control mode, and the other chain converter is converted The active power is obtained from the generator to supply power to the AC bus of the compensation connection point of the loss of power. [0052] As a further preferred solution of the present invention, the flexible multi-state switch can be switched in multiple states, and the method includes the following steps: [0053] Step 1: After the flexible multi-state switch is started, it enters the automatic pressure equalization state on both sides; [0054] Step 2: The flexible multi-state switch arbitrarily switches between the two-sided power management state and the active controllable transmission state, or runs in the above two states at the same time; [0055] Step 3: When a temporary failure occurs in the AC system, the flexible multi-state switch enters the dual-side independent energy consumption state or the short-circuit current transfer state according to the corresponding criterion; [0056] Step 4: When any AC bus connected to the chain converter loses power, the flexible multi-state switch enters a passive power supply state, and the normal AC bus supplies power to the lost AC system. [0057] The present invention also provides a control method of the above-mentioned flexible AC-DC interconnection system, including: [0058] When the compensation connection points of the two chain converters in the flexible multi-state switch are both de-energized, the power supply connected to the DC bus or the AC bus sends power back to the system, and the single-sided or double-sided chain converter Switch to voltage/frequency control mode to supply power to the compensation connection point of the loss of power. [0059] Beneficial effects: [0060] (1) The technical solution provided by this application: the DC interconnection unit between the power units of the converter chain in the two chain converters realizes the active power transmission of the two converters; the chain converter The DC balance unit inside the converter forms a closed loop in the angle. When the DC voltage is unbalanced, the DC balance unit will automatically realize the DC voltage balance adjustment, so the DC interconnection unit between the power units can be set arbitrarily; that is, when the two chain exchanges When the converters are interconnected, when the active power is transmitted, the local DC capacitor voltage imbalance can be balanced by each chain converter. [0061] (2) The DC capacitor of the power unit of the converter chain in the chain converter of the present invention can lead to a low-voltage DC port, and an additional DC-AC converter can provide a low-voltage AC port, which can be easily connected to the low-voltage AC-DC bus. Connect or directly connect with low-voltage AC and DC power sources or loads to form an AC and DC interconnection system. The AC-DC interconnection system can realize active power transmission, and the DC voltage unevenness caused by the power imbalance between the ports can be automatically balanced and controlled by the DC equalization unit of the chain converter. [0062] (3) The chain converter in the technical solution provided by this application can itself be used as a static var generator to adjust the power quality of the AC grid compensation point, and can solve the power factor, harmonics and unbalance problems. Description of the drawings [0063] In order to more clearly illustrate the technical solutions in the embodiments of the present application, the following will briefly introduce the drawings needed in the description of the embodiments. Obviously, the drawings in the following description are only some of the present application. Embodiments, for those of ordinary skill in the art, without creative work, other drawings can be obtained based on these drawings. [0064] FIG. 1 is a schematic diagram of a flexible multi-state switch provided by an embodiment of the present application; [0065] FIG. 2A is one of the schematic diagrams of the structure of the DC balance unit provided by the embodiment of the present application; [0066] FIG. 2B is the second schematic diagram of the structure of the DC balance unit provided by the embodiment of the present application; [0067] FIG. 2c is the third schematic diagram of the structure of the DC balance unit provided by the embodiment of the present application; [0068] FIG. 2D is a fourth schematic diagram of the structure of the DC balance unit provided by the embodiment of the present application; [0069] FIG. 3A is one of the schematic diagrams of the power unit structure provided by an embodiment of the present application; [0070] FIG. 3B is the second schematic diagram of the power unit structure provided by an embodiment of the present application; [0071] FIG. 3c is the third schematic diagram of the power unit structure provided by an embodiment of the present application; [0072] FIG. 4 is a schematic diagram of the structure of an energy consumption unit provided by an embodiment of the present application; [0073] FIG. 5 is a schematic diagram of the structure of a DC interconnection unit provided by an embodiment of the present application. [0074] FIG. 6A is one of the schematic diagrams of the structure of a chain converter provided by an embodiment of the present application. [0075] FIG. 6B is the second structural diagram of a chain converter provided by an embodiment of the present application. [0076] FIG. 7 is a schematic diagram of the structure of a flexible AC-DC interconnection system provided by an embodiment of the present application. [0077] FIG. 8 is a schematic diagram of a multi-state switch control method provided by an embodiment of the present application. [0078] Reference signs: [0079] 1. Energy balance converter chain; 2. Power unit; 3. DC balance unit; 4. Energy consumption unit; 5. DC interconnection unit; [0080] The following will clearly and completely describe the technical solutions in the embodiments of the present application in conjunction with the accompanying drawings in the embodiments of the present application. Obviously, the described embodiments are part of the embodiments of the present application, not all of the embodiments. . Based on the embodiments in this application, all other embodiments obtained by those skilled in the art without creative work shall fall within the protection scope of this application. [0081] It should be understood that the terms "first", "second", "third", and "fourth" in the claims of this application and the accompanying drawings are used to distinguish different objects, not to describe Specific order. The term "
[KO KR20110010168U]: Ｈ-브릿지 멀티레벨 인버터의 입력 전압 검출 회로 [EN KR20110010168U]: - INPUT VOLTAGE DETECTION CIRCUIT OF H-BRIDGE MULTILEVEL INVERTER | [KO KR20110010168U]: 본 고안은 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로를 제공한다. 본 고안은 전원계통과 연결되는 변압기의 1차 측에 인가되는 고 전압을 저 전압으로 변환하여 제어부로 전송하고 입력 전압을 검출하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 있어서; 상기 입력 전압 검출 회로는 변압기 1차측에 인가되는 고 전압을 저 전압으로 변환하는 파워 트랜스포머와, 상기 파워 트랜스포머에서 출력되는 전압을 제어부로 전달하기 위한 절연보드를 포함하는 것을 특징으로 한다. 따라서, 본 고안은 입력 전압 검출 회로의 소손 등 문제 발생 시 저압부인 제어부로 고압이 인가되지 않도록 하여 제어부의 소손을 방지하고, 제어부를 조작하는 운전자의 안전을 도모할 수 있도록 한다. | KR20110010168U | 2011-10-27 | KR20100004202U | 2010-04-21 | KR20100004202U, 2010-04-21 | KR20110010168U: 2011-10-27 | 현대중공업 주식회사 |  | G01R19/145: I G01R19/155: I | G01R15/08: I G01R15/144: I G01R19/0084: I |  |  | [KO KR20110010168U]: 전원계통과 연결되는 변압기의 1차 측에 인가되는 고 전압을 저 전압으로 변환하여 제어부로 전송하고 입력 전압을 검출하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 있어서; 상기 입력 전압 검출 회로는 변압기 1차측에 인가되는 고 전압을 저 전압으로 변환하는 파워 트랜스포머와, 상기 파워 트랜스포머에서 출력되는 전압을 제어부로 전달하기 위한 절연보드를 포함하는 것을 특징으로 하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로. 제 1항에 있어서; 상기 파워 트랜스포머는 고 전압이 인가되는 1차 측과 저 전압을 출력하는 2차 측 간이 물리적으로 절연되어 있는 것을 특징으로 하는 H-멀티레벨 인버터의 입력 전압 검출 회로. [EN KR20110010168U]: Send a high voltage applied to the primary side of the transformer is connected to the power supply system to convert a low voltage to the control unit and the input voltage detection circuit according to the H- bridge multilevel inverter for detecting an input voltage; And a power transformer for converting the input voltage detection circuit is a high voltage applied to the transformer primary side at a low voltage, to the H-bridge multi-voltage output from the power transformer comprises an insulating board for transmitting to the control unit level, the inverter input voltage detection circuit. The method of claim 1; The power transformer is a high voltage is applied to the primary side and the low voltage output of the secondary side, characterized in that liver is isolated physically to H- multilevel inverter input voltage detection circuit. | [KO KR20110010168U]: Ｈ-브릿지 멀티레벨 인버터의 입력 전압 검출 회로{INPUT VOLTAGE DETECTION CIRCUIT OF H-BRIDGE MULTILEVEL INVERTER} 본 고안은 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 관한 것으로, 좀 더 상세하게는 변압기의 1차측 전원을 검출하기 위한 입력 전압 검출 회로의 소손시 발생할 수 있는 제어부로의 고전압 인가를 방지하기 위한 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 관한 것이다. 일반적으로, H-브릿지 멀티레벨 인버터는 고전압 전동기의 가변속장치로 도 1에 도시한 바와 같이 전원계통(1)과 연결되는 변압기(2)와, 상기 변압기(2)의 출력 전압을 전원으로 사용하는 다수 개의 파워 셀(3)로 구성된다. 상기 다수 개의 파워 셀(3)은 각 상별로 각각 직렬 접속되며, 각각의 파워 셀(3)은 독립된 단상인버터 구조를 갖는다. 그리고, 여러 개의 파워 셀(3)을 직렬로 연결함으로써, 저 전압 파워 셀(3)을 얻을 수 있다. 그리고, 각 저 전압 파워 셀(3)에서 AC를 DC로 변환 후 다시 AC로 변환하는 방식으로 고 전압 전동기를 가변속하고 있다. 이때, 상기 다수개의 파워 셀(3)은 변압기 2차 측 전압(2b)에 따라 동작하며, 상기 변압기 2차측 전압(2b)은 변압기 1차 측 전압(2a) 변동에 비례하여 출력된다. 즉, 변압기 1차 측 전압(2a)인가 시 변압기 2차 측(2b)이 전압을 받아 동작하는 파워 셀(3)에도 전압이 인가되게 되며, 상기 파워 셀(3)에 인가되는 전압은 변압기 1차 측 입력 전압(2a)에 비례하여 상승한다. 상기 전원계통(1)에서 변압기 1차 측(2a)에 인가되는 고 전압은 저항과 제너다이오드로 구성된 입력 전압 검출 회로(4)를 통해 입력 전압이 검출되고, 고전압이 저전압으로 변환되어 제어부(5)로 전달된다. 이때, 상기 변압기(2)가 속한 패널은 고압부에 해당되며, 상기 제어부(5)가 속하는 패널은 저압부에 해당된다. 그러나, 변압기 1차 측(2a)에 연결된 입력 전압 검출 회로(4)의 소손 시 즉, 입력 전압 검출 회로(4)가 단선 되거나 저항 또는 제너다이오드가 열화 등의 소손 발생시 저압부인 제어부(5)로 고압이 인가되는 문제가 발생할 수 있다. 상기 저압부로 분류되는 제어부(5)에 고압이 인가되게 되면 운전자의 안전에 문제가 생길 수 있으며, 입력 전압 검출회로로부터 전압을 받아들이는 제어부의 절연 파괴 및 연관 회로의 소자 소손 등 2차 소손이 발생 될 수 있는 문제점이 있다. 본 고안은 상기와 같은 문제점을 해결하기 위하여 안출된 것으로, 본 고안의 목적은 입력 전압 검출 회로의 소손 등 문제 발생 시 저압부인 제어부로 고압이 인가되지 않도록 하여 제어부의 소손을 방지하고, 제어부를 조작하는 운전자의 안전을 도모할 수 있도록 하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로를 제공하는 데 있다. 상기한 목적을 달성하기 위하여, 본 고안은 전원계통과 연결되는 변압기의 1차 측에 인가되는 고 전압을 저 전압으로 변환하여 제어부로 전송하고 입력 전압을 검출하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 있어서; 상기 입력 전압 검출 회로는 변압기 1차측에 인가되는 고 전압을 저 전압으로 변환하는 파워 트랜스포머와, 상기 파워 트랜스포머에서 출력되는 전압을 제어부로 전달하기 위한 절연보드로 구성되는 것을 특징으로 한다. 여기서, 상기 파워 트랜스포머는 고 전압이 인가되는 1차 측과 저 전압을 출력하는 2차 측 간이 물리적으로 절연되어 있는 것을 특징으로 한다. 이와 같이 본 고안의 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로에 따르면, 1차 측과 2차 측 간이 물리적으로 절연되어 있는 파워 트랜스포머가 구비되고, 상기 파워 트랜스포머에 소손이 발생하였을 경우 상기 제어부에 고압이 인가되지 않도록 상기 전압을 절연시켜 제어부로 전송하는 절연보드가 구비되어 제어부에 저 전압만이 인가되도록 함으로써 제어부의 소손을 방지하고, 제어부를 조작하는 운전자의 안전을 도모할 수 있는 효과가 있다. 도 1은 종래의 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로 구성도를 도시한 도면. 도 2는 본 고안의 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로 구성도를 도시한 도면. 도 3은 본 고안의 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로 구성을 도시한 블럭도. 이하, 첨부된 도면을 참조하여 본 고안에 따른 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로의 바람직한 실시예를 상세히 설명하도록 한다. 도 2, 도 3에 도시한 바와 같이 본 고안은 전원계통(100)과 연결되는 변압기(200)의 1차 측에 인가되는 고 전압을 저 전압으로 변환하여 제어부로(400) 전송하고 입력 전압을 검출하는 H-브릿지 멀티레벨 인버터의 입력 전압 검출 회로(300)에 있어서; 상기 입력 전압 검출 회로(300)는 변압기(200)의 1차 측에 인가되는 고 전압을 저 전압으로 변환하는 파워 트랜스포머(310)와, 상기 파워 트랜스포머(310)에서 출력되는 저 전압을 제어부(400)로 전달하기 위한 절연보드(320)를 포함한다. 상기 파워 트랜스포머(310)에는 H-브릿지 멀티레벨 인버터 입력단에 연결된 전원계통(100)이 ON 되면서 변압기(200) 1차 측에 인가되는 고 전압이 파워 트랜스포머(310)의 1차 측에 동일하게 인가된다. 또한, H-브릿지 멀티레벨 인버터의 운전 시에도 변압기(200) 1차 측에 인가되는 전압과 위상은 동일하게 파워 트랜스포머(310)의 1차 측에 전달되며, 전원계통의 OFF와 동시에 변압기(200) 1차 측에 인가되는 전압과 파워 트랜스포머(310) 1차측에 인가되는 전압도 해제되게 된다. 상기 파워 트랜스포머(310)는 전압을 인가받는 1차 측과 전압을 출력하는 2차 측 간 물리적으로 절연되어 있다. 따라서, 상기 파워 트랜스포머(310)의 1차 측에 인가된 6600V의 고압은 2차 측에서는 저압인 110V를 출력한다. 이렇게, 파워 트랜스포머(310)의 2차 측을 통하여 출력된 110V의 전압은 절연보드(320)를 통해 제어부(400)로 전달된다. 상기 절연보드(320)는 상기 파워 트랜스포머(310)에서 출력된 전압이 고 전압인 경우 전압을 절연시켜 110V 전압으로 유지시켜 준다. 따라서, 상기 파워 트랜스포머(310)에 소손 등 문제가 발생하여 상기 파워 트랜스포머(310)에서 고 전압이 출력되게 된 경우, 상기 제어부(400)에 고전압이 인가되지 않도록 상기 절연보드(320)가 전압을 다운시켜 저 전압만이 제어부(400)에 인가되도록 함으로서, 제어부(400)의 소손을 방지하고, 제어부(400)를 조작하는 운전자의 안전을 도모하게 된다. 본 고안은 상술한 특정의 바람직한 실시 예에 한정되지 아니하며, 청구범위에서 청구하는 본 고안의 요지를 벗어남이 없이 당해 고안이 속하는 기술분야에서 통상의 지식을 가진 자라면 누구든지 다양한 변형실시가 가능한 것은 물론이고, 그와 같은 변경은 청구범위 기재의 범위 내에 있게 된다. 100: 전원계통 200: 변압기 300: 입력 전압 검출 회로 310: 파워 트랜스포머 320: 절연보드 400: 제어부 500: 파워 셀 [EN KR20110010168U]: H- bridge multilevel inverter input voltage detection circuit {INPUT VOLTAGE DETECTION CIRCUIT OF H-BRIDGE MULTILEVEL INVERTER} This is designed to prevent the high voltage applied to the H- bridge multilevel inverter input voltage relates to a detecting circuit, more particularly to the control that may occur in deterioration of the input voltage detection circuit for detecting the primary side of the power transformer It relates to the input voltage detection circuit of the H- bridge multilevel inverter. In general, H-bridge multilevel inverter using the output voltage of the transformer is connected to the power supply system 1 as shown in Fig. 1 by a variable speed electric motor of the high-voltage unit (2), the transformer (2) as a power source is composed of a plurality of power cell (3). The plurality of power cells (3) are each connected in series for each phase, each power cell (3) has an independent single phase inverter structure. And, by connecting multiple power cell (3) in series, it is possible to obtain a low-voltage power cells (3). Then, each of the low voltage AC from the power cell (3) is variable and the high-voltage electric motor by converting back to the AC after the conversion to DC. In this case, the plurality of power cell (3) operates according to the voltage transformer secondary side (2b), said transformer secondary voltage (2b) is an output voltage in proportion to the transformer primary side (2a) varies. Namely, the transformer primary-side voltage (2a) is on, the transformer secondary side (2b) and the voltage to be applied to power cell (3) for operation receives the voltage, voltage to the power cell (3) is a transformer the primary side rises proportional to the input voltage (2a). A high voltage applied to the transformer primary side (2a) in the power supply system 1 is the input voltage detected by the input voltage detection circuit 4 is composed of a resistance and a Zener diode, a high voltage is converted to a low voltage control section (5 ) it is transmitted to. At this time, the panel belongs to the transformer (2) is for the high pressure, the panel belonging to the control unit 5 is available for the low-pressure part. However, the transformer primary side (2a) upon deterioration of the input voltage detection circuit 4 is connected to the other words, the input voltage detection circuit 4, a low-pressure Mrs. control occurs burnout of the disconnection or resistor or a zener diode is deteriorated 5 It may cause a problem that a high pressure is applied. If to be a high voltage is applied to the control unit (5) is classified as part the low-pressure can lead to problems with the driver's safety, the input voltage element burn out such secondary burnout is generated from the detection circuit to accept a voltage control section of the dielectric breakdown and the associated circuit There are problems that can be. The subject innovation has been made to solve the above problems, Object of the present invention are not damaged, such as the input voltage to the high pressure generated when the low-pressure problem wife control of the detection circuit is applied to prevent the deterioration of the control unit, and, H-bridge multi-level to promote the safety of the driver to operate the control unit to provide an input voltage detection circuit of the inverter. In order to achieve the above object, the subject innovation is H- Bridge sends a high voltage to be applied to the primary side of the transformer is connected to the power supply system to the control unit is converted into a low voltage, and for detecting the input voltage to multilevel inverter of the input voltage In the detection circuit; And a power transformer for converting the input voltage detection circuit is a high voltage applied to the transformer primary side at a low voltage, the voltage output from the power transformer being composed of a white board for transmitting to the control unit. Here, the power transformer is characterized in that the isolated secondary side for outputting a simple physically primary side and the low voltage is a high voltage is applied. In accordance with the input voltage detection circuit of the H- bridge multilevel inverter of the subject innovation as described above, the primary side and the secondary side of the power transformer is provided which is simple and isolated physically, to the control unit if the burnout has occurred in the power transformer not be applied to high voltage insulated the voltage is provided with a board isolated for transmitting to the control unit to prevent burn out of control by ensuring that is only a low voltage is applied to the control unit, and has an effect to promote the safety of the driver to operate the control unit . Figure 1 is a diagram illustrating the configuration of a conventional voltage detection circuit is also input H- bridge multilevel inverter. Figure 2 shows the schematic of the input voltage detection circuit H- bridge multilevel inverter according to the present invention; 3 is a block diagram showing the configuration of the input voltage detection circuit H- bridge multilevel inverter according to the present invention; Hereinafter, a preferred embodiment of the input voltage detection circuit with reference to the accompanying drawings H- bridge multilevel inverter according to this devised to be described in detail. 2, as shown in FIG. 3, the subject innovation is the power supply system 100, and connection that the transformer 200 of the first high voltage applied to the side of the controller is converted into a low voltage 400, the transmission and the input voltage an input voltage detection circuit 300 for detecting the H- bridge multilevel inverter; And a power transformer (310) for converting one of the high voltage applied to the primary side low voltage of the input voltage detection circuit 300 includes a transformer 200, a control unit for a low voltage output from the power transformers (310, 400 ) a white board 320 for transfer to. The power transformer (310) is applied equally to the primary side of the power supply system connected to the H- bridge multilevel inverter input terminal 100 is ON, while the transformer 200, first high voltage power is applied to the transformer primary side (310) It is. In addition, even when the H-bridge driving transformer, and transmission of the multilevel inverter 200, first, the voltage and phase are applied to the primary side to the primary side of the same power transformer (310), and at the same time OFF of the power supply transformer system (200 ) 1 and the voltage applied to the primary side of power transformer 310, the primary voltage to be applied to also be released. The power transformer 310 is physically isolated between the secondary side for outputting a voltage is applied to the primary side and the receiving voltage. Thus, the 6600V high voltage applied to the primary side of the power transformer 310 and outputs a low-voltage secondary side of 110V. In this manner, the voltage of 110V is output through the secondary side of the power transformer 310 is transmitted to the controller 400 through the insulating board (320). The insulating board 320 keeps a 110V voltage to isolate the voltage when the voltage output from the power transformer 310 and voltage. Therefore, when the power transformer (310) to be burned, such as occurs, the power transformer 310, a high voltage is to be output from by the controller 400 from being applied with a high voltage in the insulation board 320 is a voltage down to be applied to only a low voltage by the controller 400, to prevent burnout of the controller 400, and is the control unit 400 to achieve the safe operation of the driver. The subject innovation is not limited to the preferred embodiments of the specific, in the art the art devised without departing from the spirit of the subject innovation are charged by the appended claims by those of ordinary skill if that various modifications are possible at any thing and, of course, it changed in such a way it is possible within the scope of the claims described. 100: Power Grid 200: Transformer 300: input voltage detection circuit 310: power transformers 320: 400 insulation boards: control 500: Power Cell
[EN WO2021092720A1]: MULTI-LEVEL POWER CONVERTOR AND METHOD FOR MULTI-LEVEL POWER CONVERTOR [FR WO2021092720A1]: CONVERTISSEUR DE COURANT À NIVEAUX MULTIPLES ET PROCÉDÉ DE CONVERTISSEUR DE COURANT À NIVEAUX MULTIPLES | [EN WO2021092720A1]: A multi-level power convertor and a method for a multi-level power convertor. The multi-level power convertor (100) comprises a DC port; an AC port; a first power converting unit (1) coupled to the DC port and comprising a first AC terminal (11) adapted to provide a first plurality of voltage levels; a second power converting unit (2) coupled to the DC port and comprising a second AC terminal (21) adapted to provide a second plurality of voltage levels of the same number as the first plurality of voltage levels, wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; a coupling inductor (3) comprising first and second windings (31, 32) with the same number of turns, wherein the first winding (31) comprises a first end (311) coupled to the first AC terminal (11) and a second end (312), the second winding (32) comprises a third end (321) coupled to the second AC terminal (21) and a fourth end (322), and the second end (312) of the first winding (31) and the third end (321) of the second winding (32) are namesake ends of the first and second windings (31, 32); and an inductive filtering unit (4) arranged between the AC port and the second and fourth ends (312, 322) of the first and second windings (31, 32). [FR WO2021092720A1]: Convertisseur de courant à niveaux multiples et un procédé d'un convertisseur de courant à niveaux multiples. Le convertisseur de courant à niveaux multiples (100) comprend un orifice CC ; un orifice CA ; une première unité de conversion de courant (1) couplée à l'orifice CC et comprenant une première borne CA (11) conçue pour fournir une première pluralité de niveaux de tension ; une deuxième unité de conversion de courant (2) couplée à l'orifice CC et comprenant une deuxième borne CA (21) conçue pour fournir une deuxième pluralité de niveaux de tension du même nombre que la première pluralité de niveaux de tension, la deuxième pluralité de niveaux de tension étant déphasés de 90 degrés par rapport à la première pluralité de niveaux de tension ; un inducteur de couplage (3) comprenant des premier et deuxième enroulements (31, 32) ayant le même nombre de spires, le premier enroulement (31) comprenant une première extrémité (311) couplée à la première borne CA (11) et une deuxième extrémité (312), le deuxième enroulement (32) comprenant une troisième extrémité (321) couplée à la deuxième borne CA (21) et une quatrième extrémité (322), et la deuxième extrémité (312) du premier enroulement (31) et la troisième extrémité (321) du deuxième enroulement (32) sont des extrémités homonymes des premier et deuxième enroulements (31, 32) ; et une unité de filtrage inductif (4) disposée entre l'orifice CA et les deuxième et quatrième extrémités (312, 322) des premier et deuxième enroulements (31, 32). | WO2021092720A1 | 2021-05-20 | CN2019117102W | 2019-11-11 | CN2019117102W, 2019-11-11 | WO2021092720A1: 2021-05-20 | ABB SCHWEIZ AG YANG FU SHI YAMING | YANG FU SHI YAMING | H02M7/483: I | H02M7/487: A H02M7/493: I H02M1/0043: I H02M1/0064: A H02M1/0095: A H02M7/4833: A H02M7/4837: I | CN103346690A CN108809133A CN103368427A CN102882409A KR20160027408A |  | [EN WO2021092720A1]: A multi-level power convertor (100) comprising: a DC port; an AC port; a first power converting unit (1) coupled to the DC port and comprising a first AC terminal (11) adapted to provide a first plurality of voltage levels; a second power converting unit (2) coupled to the DC port and comprising a second AC terminal (21) adapted to provide a second plurality of voltage levels of the same number as the first plurality of voltage levels, wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; a coupling inductor (3) comprising first and second windings (31, 32) with the same number of turns, wherein the first winding (31) comprises a first end (311) coupled to the first AC terminal (11) and a second end (312) , the second winding (32) comprises a third end (321) coupled to the second AC terminal (21) and a fourth end (322) , and the second end (312) of the first winding (31) and the third end (321) of the second winding (32) are namesake ends of the first and second windings (31, 32) ; andan inductive filtering unit (4) arranged between the AC port and the second and fourth ends (312, 322) of the first and second windings (31, 32) . The multi-level power convertor (100) according to claim 1, wherein the second and fourth ends (312, 322) of the first and second windings (31, 32) are coupled to a common node (N0) , and wherein the inductive filtering unit (4) comprises an inductor (L0) arranged between the common node (N0) and the AC port. The multi-level power convertor (100) according to claim 1, wherein the inductive filtering unit (4) comprises: a first inductor (L1) arranged between the second end (312) of the first winding (31) and the AC port; anda second inductor (L2) arranged between the fourth end (322) of second winding (32) and the AC port. The multi-level power convertor (100) according to claim 1, wherein the inductive filtering unit (4) comprises an additional coupling inductor comprising third and fourth windings (41, 42) ,wherein the third winding (41) is arranged between the second end (312) of the first winding (31) and the AC port,wherein the fourth winding (42) is arranged between the fourth end (322) of second winding (32) and the AC port, andwherein namesake ends of the third and fourth windings (41, 42) are connected to the AC port. The multi-level power convertor (100) according to claim 1, wherein each of the first and second AC terminals (11, 21) provides five voltage levels, and the AC port provides nine voltage levels. The multi-level power convertor (100) according to claim 1, wherein the DC port comprises first and second DC terminals (DC+, DC-) , and wherein the first power converting unit (1) comprises: first and second capacitors (C1, C2) connected in series between the first and second DC terminals (DC+, DC-) ; first, second, third, and fourth switching semiconductor devices (S1, S2, S3, S4) connected in series between the first and second DC terminals (DC+, DC-) , wherein a first node (N1) between the first and second capacitors (C1, C2) is connected to a second node (N2) between the second and third switching semiconductor devices (S2, S3) ; fifth and sixth switching semiconductor devices (S5, S6) connected in series between a third node (N3) and the first AC terminal (11) , the third node (N3) being between the first and second switching semiconductor devices (S1, S2) ; seventh and eighth switching semiconductor devices (S7, S8) connected in series between a fourth node (N4) and the first AC terminal (11) , the fourth node (N4) being between the third and fourth switching semiconductor devices (S3, S4) ; anda third capacitor (C3) connected between a fifth node (N5) and a sixth node (N6) , the fifth node (N5) being between the fifth and sixth switching semiconductor devices (S5, S6) , and the sixth node (N6) being between the seventh and eighth switching semiconductor devices (S7, S8) . The multi-level power convertor (100) according to claim 6, wherein the second power converting unit (2) comprises: the first and second capacitors (C1, C2) shared with the first power converting unit (1) ; the first, second, third, and fourth switching semiconductor devices (S1, S2, S3, S4) shared with the first power converting unit (1) ; ninth and tenth switching semiconductor devices (S9, S10) connected in series between the third node (N3) and the second AC terminal (21) ; eleventh and twelfth switching semiconductor devices (S11, S12) connected in series between the fourth node (N4) and the second AC terminal (21) ; anda fourth capacitor (C4) connected between a seventh node (N7) and a eighth node (N8) , the seventh node (N7) being between the ninth and tenth switching semiconductor devices (S9, S10) , and the eighth node (N8) being between the eleventh and twelfth switching semiconductor devices (S11, S12) . The multi-level power convertor (100) according to claim 6, wherein the second power converting unit (2) comprises: the first and second capacitors (C1, C2) shared with the first power converting unit (1) ; thirteenth, fourteenth, fifteenth, and sixteenth switching semiconductor devices (S13, S14, S15, S16) connected in series between the first and second DC terminals (DC+, DC-) , wherein a ninth node (N9) between the fourteenth and fifteenth switching semiconductor devices (S14, S15) is connected to the first node (N1) ; ninth and tenth switching semiconductor devices (S9, S10) connected in series between the a tenth node (N10) and the second AC terminal (21) , the tenth node (N10) being between the thirteenth and fourteenth switching semiconductor devices (S13, S14) ; eleventh and twelfth switching semiconductor devices (S11, S12) connected in series between an eleventh node (N11) and the second AC terminal (21) , the eleventh node (N11) being between the fifteenth and sixteenth switching semiconductor devices (S15, S16) ; anda fourth capacitor (C4) connected between a seventh node (N7) and a eighth node (N8) , the seventh node (N7) being between the ninth and tenth switching semiconductor devices (S9, S10) , and the eighth node (N8) being between the eleventh and twelfth switching semiconductor devices (S11, S12) . The multi-level power convertor (100) according to claim 1, wherein each of the first and second AC terminals (11, 21) provides nine voltage levels, and the AC port provides seventeen voltage levels. The multi-level power convertor (100) according to claim 1, wherein the multi-level power convertor (100) operates as an inverter when the DC port is used as an input and the AC port is used as an output, andwherein the multi-level power convertor (100) operates as a rectifier when the AC port is used as an input and the DC port is used as an output. A method for a multi-level power convertor (100) , the multi-level power convertor (100) comprising a DC port; an AC port; a first power converting unit (1) coupled to the DC port and comprising a first AC terminal (11) ; a second power converting unit (2) coupled to the DC port and comprising a second AC terminal (21) ; a coupling inductor (3) comprising first and second windings (31, 32) with the same number of turns, wherein the first winding (31) comprises a first end (311) coupled to the first AC terminal (11) and a second end (312) , the second winding (32) comprises a third end (321) coupled to the second AC terminal (21) and a fourth end (322) , and the second end (312) of the first winding (31) and the third end (321) of the second winding (32) are namesake ends of the first and second windings (31, 32) ; and an inductive filtering unit (4) arranged between the AC port and the second and fourth ends (312, 322) of the first and second windings (31, 32) ,the method comprising: providing a first plurality of voltage levels to the first end (311) of the first winding (31) from the first AC terminal (11) ; providing a second plurality of voltage levels of the same number as the first plurality of voltage levels to the third end (321) of the second winding (32) from the second AC terminal (21) , wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; andoutputting a third plurality of voltage levels via the second end (312) of the first winding (31) and the fourth end (322) of the second winding (32) , wherein the number of the third plurality of voltage levels equals to the sum of the number of the first plurality of voltage levels and the number of the second plurality of voltage levels minus one. The method according to claim 11, wherein the second and fourth ends (312, 322) of the first and second windings (31, 32) are coupled to a common node (N0) , and wherein the inductive filtering unit (4) comprises an inductor (L0) arranged between the common node (N0) and the AC port. The method according to claim 11, wherein the inductive filtering unit (4) comprises: a first inductor (L1) arranged between the second end (312) of the first winding (31) and the AC port; anda second inductor (L2) arranged between the fourth end (322) of second winding (32) and the AC port. The method according to claim 11, wherein the inductive filtering unit (4) comprises an additional coupling inductor comprising third and fourth windings (41, 42) ,wherein the third winding (41) is arranged between the second end (312) of the first winding (31) and the AC port,wherein the fourth winding (42) is arranged between the fourth end (322) of second winding (32) and the AC port, andwherein namesake ends of the third and fourth windings (41, 42) are connected to the AC port. | [EN WO2021092720A1]: [Title established by the ISA under Rule 37.2] MULTI-LEVEL POWER CONVERTOR AND METHOD FOR MULTI-LEVEL POWER CONVERTOR FIELD Embodiments of present disclosure generally relate to the field of power convertors, and more particularly, to a multi-level power convertor and a method for a multi-level power convertor. BACKGROUND Currently, multi-level power converters are widely used in various fields, which can effectively decrease the switching frequency and improve the output waveform quality. Fig. 1 illustrates a schematic circuit diagram of a conventional multi-level power convertor 100. As shown in Fig. 1, the multi-level power convertor 100 includes a DC port and an AC port. The DC port includes DC terminals DC+ and DC-. Capacitors C1 and C2 are connected in series between the DC terminals DC+ and DC-. Switching semiconductor devices S1, S2, S3, and S4 are connected in series between the DC terminals DC+ and DC-. The switching semiconductor devices S1, S2, S3, and S4 are line frequency switches. A node N1 between the capacitors C1 and C2 is connected to a node N2 between the switching semiconductor devices S2 and S3. A first branch including switching semiconductor devices S5, S6, S17, and S18 is connected in series between a node N3 and an inductor L. A second branch including switching semiconductor devices S7, S8, S19, and S20 are connected in series between a node N4 and the inductor L. The switching semiconductor devices S5, S6, S17, S18, S7, S8, S19, and S20 are high frequency switches. Capacitors C3, C5, and C7 are connected between the first and second branches respectively. The switching semiconductor devices S1, S2, S3, S4, S5, S6, S17, S18, S7, S8, S19, and S20 may be switched on and off under control of respective driving signals. With the above arrangement, the multi-level power convertor 100 may output nine voltage levels at the AC port. When the multi-level power convertor 100 operates, the capacitors C3, C5, and C7 may be connected in series via respective ones of the switching semiconductor devices S5, S6, S17, S18, S7, S8, S19, and S20. In a steady state of the multi-level power convertor 100, the voltages across the capacitors C3, C5, and C7 are stable. However, in a dynamic state of the multi-level power convertor 100, the voltages across the capacitors C3, C5, and C7 may be out of control. For example, the voltage of the capacitor C3, C5, or C7 may become relatively high. In this event, the corresponding switching semiconductor devices S5, S6, S17, S18, S7, S8, S19, or S20 may be susceptible to be damaged. Hence, the performance and reliability of the multi-level power convertor 100 would be adversely affected. Thus, there is need for a solution for improving the performance and reliability of the multi-level power convertor. SUMMARY In view of the foregoing problems, various example embodiments of the present disclosure provide a multi-level power convertor and a method for a multi-level power convertor so as to improve the performance and reliability of the multi-level power convertor. In a first aspect of the present disclosure, example embodiments of the present disclosure provide a multi-level power convertor. The multi-level power convertor comprises a DC port; an AC port; a first power converting unit coupled to the DC port and comprising a first AC terminal adapted to provide a first plurality of voltage levels; a second power converting unit coupled to the DC port and comprising a second AC terminal adapted to provide a second plurality of voltage levels of the same number as the first plurality of voltage levels, wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; a coupling inductor comprising first and second windings with the same number of turns, wherein the first winding comprises a first end coupled to the first AC terminal and a second end, the second winding comprises a third end coupled to the second AC terminal and a fourth end, and the second end of the first winding and the third end of the second winding are namesake ends of the first and second windings; and an inductive filtering unit arranged between the AC port and the second and fourth ends of the first and second windings. In some embodiments, the second and fourth ends of the first and second windings are coupled to a common node, and the inductive filtering unit comprises an inductor arranged between the common node and the AC port. In some embodiments, the inductive filtering unit comprises: a first inductor arranged between the second end of the first winding and the AC port; and a second inductor arranged between the fourth end of second winding and the AC port. In some embodiments, the inductive filtering unit comprises an additional coupling inductor comprising third and fourth windings, the third winding is arranged between the second end of the first winding and the AC port, the fourth winding is arranged between the fourth end of second winding and the AC port, and namesake ends of the third and fourth windings are connected to the AC port. In some embodiments, each of the first and second AC terminals provides five voltage levels, and the AC port provides nine voltage levels. In some embodiments, the DC port comprises first and second DC terminals, and the first power converting unit comprises: first and second capacitors connected in series between the first and second DC terminals; first, second, third, and fourth switching semiconductor devices connected in series between the first and second DC terminals, wherein a first node between the first and second capacitors is connected to a second node between the second and third switching semiconductor devices; fifth and sixth switching semiconductor devices connected in series between a third node and the first AC terminal, the third node being between the first and second switching semiconductor devices; seventh and eighth switching semiconductor devices connected in series between a fourth node and the first AC terminal, the fourth node being between the third and fourth switching semiconductor devices; and a third capacitor connected between a fifth node and a sixth node, the fifth node being between the fifth and sixth switching semiconductor devices, and the sixth node being between the seventh and eighth switching semiconductor devices. In some embodiments, the second power converting unit comprises: the first and second capacitors shared with the first power converting unit; the first, second, third, and fourth switching semiconductor devices shared with the first power converting unit; ninth and tenth switching semiconductor devices connected in series between the third node and the second AC terminal; eleventh and twelfth switching semiconductor devices connected in series between the fourth node and the second AC terminal; and a fourth capacitor connected between a seventh node and a eighth node, the seventh node being between the ninth and tenth switching semiconductor devices, and the eighth node being between the eleventh and twelfth switching semiconductor devices. In some embodiments, the second power converting unit comprises: the first and second capacitors shared with the first power converting unit; thirteenth, fourteenth, fifteenth, and sixteenth switching semiconductor devices connected in series between the first and second DC terminals, wherein a ninth node between the fourteenth and fifteenth switching semiconductor devices is connected to the first node; ninth and tenth switching semiconductor devices connected in series between the a tenth node and the second AC terminal, the tenth node being between the thirteenth and fourteenth switching semiconductor devices; eleventh and twelfth switching semiconductor devices connected in series between an eleventh node and the second AC terminal, the eleventh node being between the fifteenth and sixteenth switching semiconductor devices; and a fourth capacitor connected between a seventh node and a eighth node, the seventh node being between the ninth and tenth switching semiconductor devices, and the eighth node being between the eleventh and twelfth switching semiconductor devices. In some embodiments, each of the first and second AC terminals provides nine voltage levels, and the AC port provides seventeen voltage levels. In some embodiments, the multi-level power convertor operates as an inverter when the DC port is used as an input and the AC port is used as an output, and the multi-level power convertor operates as a rectifier when the AC port is used as an input and the DC port is used as an output. In a second aspect of the present disclosure, example embodiments of the present disclosure provide a method for a multi-level power convertor. The multi-level power convertor comprises a DC port; an AC port; a first power converting unit coupled to the DC port and comprising a first AC terminal; a second power converting unit coupled to the DC port and comprising a second AC terminal; a coupling inductor comprising first and second windings with the same number of turns, wherein the first winding comprises a first end coupled to the first AC terminal and a second end, the second winding comprises a third end coupled to the second AC terminal and a fourth end, and the second end of the first winding and the third end of the second winding are namesake ends of the first and second windings; and an inductive filtering unit arranged between the AC port and the second and fourth ends of the first and second windings. The method comprises providing a first plurality of voltage levels to the first end of the first winding from the first AC terminal; providing a second plurality of voltage levels of the same number as the first plurality of voltage levels to the third end of the second winding from the second AC terminal, wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; and outputting a third plurality of voltage levels via the second end of the first winding and the fourth end of the second winding, wherein the number of the third plurality of voltage levels equals to the sum of the number of the first plurality of voltage levels and the number of the second plurality of voltage levels minus one. In some embodiments, the second and fourth ends of the first and second windings are coupled to a common node, and wherein the inductive filtering unit comprises an inductor arranged between the common node and the AC port. In some embodiments, the inductive filtering unit comprises: a first inductor arranged between the second end of the first winding and the AC port; and a second inductor arranged between the fourth end of second winding and the AC port. In some embodiments, the inductive filtering unit comprises an additional coupling inductor comprising third and fourth windings, the third winding is arranged between the second end of the first winding and the AC port, the fourth winding is arranged between the fourth end of second winding and the AC port, and namesake ends of the third and fourth windings are connected to the AC port. According to various embodiments of the present disclosure, the first plurality of voltage levels and the second plurality of voltage levels may be combined by the coupling inductor into a third plurality of voltage levels; the number of the third plurality of voltage levels is larger than the number of the first plurality of voltage levels and the number of the second plurality of voltage levels respectively. In this way, the multi-level power convertor in accordance with embodiments of the present disclosure may generate the same number of voltage levels as the conventional multi-level power convertor through using less capacitor, reducing the risk of voltage imbalance among the capacitors in the multi-level power convertor and thereby avoiding the damage of the switching semiconductor devices in the multi-level power convertor. Hence, the performance and reliability of the multi-level power convertor may be improved. DESCRIPTION OF DRAWINGS Through the following detailed descriptions with reference to the accompanying drawings, the above and other objectives, features and advantages of the example embodiments disclosed herein will become more comprehensible. In the drawings, several example embodiments disclosed herein will be illustrated in an example and in a non-limiting manner, wherein: Fig. 1 illustrates a schematic circuit diagram of a conventional multi-level power convertor; Fig. 2 illustrates a block diagram of a multi-level power convertor in accordance with an embodiment of the present disclosure; Fig. 3 illustrates an example arrangement of a coupling inductor and an inductive filtering unit in accordance with an embodiment of the present disclosure; Fig. 4 illustrates an example arrangement of the coupling inductor and the inductive filtering unit in accordance with another embodiment of the present disclosure; Fig. 5 illustrates an example arrangement of the coupling inductor and the inductive filtering unit in accordance with yet another embodiment of the present disclosure; Fig. 6 illustrates a schematic circuit diagram of a multi-level power convertor in accordance with an embodiment of the present disclosure; Fig. 7 illustrates a schematic circuit diagram of a multi-level power convertor in accordance with another embodiment of the present disclosure; Fig. 8 illustrates a schematic circuit diagram of a three-phase power converting circuit in accordance with an embodiment of the present disclosure; Fig. 9 illustrates a schematic circuit diagram of a multi-level power convertor in accordance with another embodiment of the present disclosure; and Fig. 10 illustrates a schematic circuit diagram of a multi-level power convertor in accordance with yet another embodiment of the present disclosure. Throughout the drawings, the same or similar reference symbols are used to indicate the same or similar elements. DETAILED DESCRIPTION OF EMBODIEMTNS Principles of the present disclosure will now be described with reference to several example embodiments shown in the drawings. Though example embodiments of the present disclosure are illustrated in the drawings, it is to be understood that the embodiments are described only to facilitate those skilled in the art in better understanding and thereby achieving the present disclosure, rather than to limit the scope of the disclosure in any manner. The term “comprises” or “includes” and its variants are to be read as open terms that mean “includes, but is not limited to. ” The term “or” is to be read as “and/or” unless the context clearly indicates otherwise. The term “based on” is to be read as “based at least in part on. ” The term “being operable to” is to mean a function, an action, a motion or a state can be achieved by an operation induced by a user or an external mechanism. The term “one embodiment” and “an embodiment” are to be read as “at least one embodiment. ” The term “another embodiment” is to be read as “at least one other embodiment. ” The terms “first, ” “second, ” and the like may refer to different or same objects. Other definitions, explicit and implicit, may be included below. A definition of a term is consistent throughout the description unless the context clearly indicates otherwise. Unless specified or limited otherwise, the terms “mounted, ” “connected, ” “supported, ” and “coupled” and variations thereof are used broadly and encompass direct and indirect mountings, connections, supports, and couplings. Furthermore, “connected” and “coupled” are not restricted to physical or mechanical connections or couplings. In the description below, like reference numerals and labels are used to describe the same, similar or corresponding parts in the figures. Other definitions, explicit and implicit, may be included below. As discussed above, the performance and reliability of the conventional multi-level power convertor may be adversely affected due to the use of multiple capacitors. According to embodiments of the present disclosure, to improve the performance and reliability of the multi-level power convertor, the first plurality of voltage levels and the second plurality of voltage levels having a phase shift of 90 degree may be combined by the coupling inductor, such that the multi-level power convertor in accordance with embodiments of the present disclosure may generate the same number of voltage levels as the conventional multi-level power convertor through using less capacitor. The above idea may be implemented in various manners, as will be described in detail in the following paragraphs. Hereinafter, the principles of the present disclosure will be described in detail with reference to Figs. 2-10. Referring to Fig. 2 first, Fig. 2 illustrates a block diagram of a multi-level power convertor 100 in accordance with an embodiment of the present disclosure. As shown in Fig. 2, the multi-level power convertor 100 generally includes a DC port, an AC port, a first power converting unit 1, a second power converting unit 2, a coupling inductor 3, and an inductive filtering unit 4. The multi-level power convertor 100 may be a bidirectional power convertor. The multi-level power convertor 100 may operate as an inverter when the DC port is used as an input and the AC port is used as an output. Instead, the multi-level power convertor 100 may operate as a rectifier when the AC port is used as an input and the DC port is used as an output. The DC port includes first and second DC terminals DC+, DC-. The first power converting unit 1 and the second power converting unit 2 are coupled to the DC port respectively. The first power converting unit 1 includes a first AC terminal 11 for providing a first plurality of voltage levels. The second power converting unit 2 includes a second AC terminal 21 for providing a second plurality of voltage levels. The number of the second plurality of voltage levels is the same as the number of the first plurality of voltage levels. The first and second power converting units 1 and 2 have the same switching cycle. In addition, the second plurality of voltage levels are phase-shifted by 90 degree, i.e., a quarter of the switching cycle of the first and second power converting units 1 and 2, with respect to the first plurality of voltage levels. The coupling inductor 3 includes first and second windings 31, 32 with the same number of turns. The first winding 31 includes a first end 311 coupled to the first AC terminal 11 and a second end 312. The second winding 32 includes a third end 321 coupled to the second AC terminal 21 and a fourth end 322. The second end 312 of the first winding 31 and the third end 321 of the second winding 32 are namesake ends of the first and second windings 31, 32. With such an arrangement, the first and second winding 31, 32 may induce voltages of the same magnitude and opposite directions. The first plurality of voltage levels and the second plurality of voltage levels having a phase shift of 90 degree may be combined by the coupling inductor into a third plurality of voltage levels. The number of the third plurality of voltage levels would equal to the sum of the number of the first plurality of voltage levels and the number of the second plurality of voltage levels minus one. If both the number of the first plurality of voltage levels and the second plurality of voltage levels are five, the number of the third plurality of voltage levels would be nine. If both the number of the first plurality of voltage levels and the second plurality of voltage levels are nine, the number of the third plurality of voltage levels would be seventeen. The inductive filtering unit 4 is arranged between the AC port and the coupling inductor 3 so as to filter the third plurality of voltage levels provided by the coupling inductor 3. The coupling inductor 3 and the inductive filtering unit 4 may have various arrangements, which will be described in detail hereinafter with reference to Figs. 3-5. In an embodiment, as shown in Fig. 3, the second and fourth ends 312, 322 of the first and second windings 31, 32 are coupled to a common node N0. The inductive filtering unit 4 includes an inductor L0 arranged between the common node N0 and the AC port. In another embodiment, as shown in Fig. 4, the inductive filtering unit 4 includes a first inductor L1 and a second inductor L2. The first inductor L1 is arranged between the second end 312 of the first winding 31 and the AC port. The second inductor L2 is arranged between the fourth end 322 of second winding 32 and the AC port. In yet another embodiment, as shown in Fig. 5, the inductive filtering unit 4 includes an additional coupling inductor consisting of third and fourth windings 41, 42. The third winding 41 is arranged between the second end 312 of the first winding 31 and the AC port. The fourth winding 42 is arranged between the fourth end 322 of second winding 32 and the AC port. Namesake ends of the third and fourth windings 41, 42 are connected to the AC port. Fig. 6 illustrates a schematic circuit diagram of a multi-level power convertor 100 in accordance with an embodiment of the present disclosure. As shown in Fig. 6, the coupling inductor 3 and the inductive filtering unit 4 have the same construction and arrangement as those described with reference to Figs. 2 and 3. It is to be understood the coupling inductor 3 and the inductive filtering unit 4 may have other constructions and arrangements, for example those as described above with reference to Figs. 4 and 5. The scope of the present disclosure is not intended to be limited in this respect. In an embodiment, as shown in Fig. 6, the first power converting unit 1 includes capacitors C1, C2, and C3 and switching semiconductor devices S1, S2, S3, S4, S5, S6, S7, and S8. The capacitors C1 and C2 are connected in series between the first and second DC terminals DC+, DC-. The switching semiconductor devices S1, S2, S3, and S4 are line frequency switches. The switching semiconductor devices S1, S2, S3, and S4 are connected in series between the first and second DC terminals DC+, DC-. A first node N1 between the capacitors C1 and C2 is connected to a second node N2 between the switching semiconductor devices S2 and S3. The node N1 may be used as a reference voltage point of the AC port. The switching semiconductor devices S5, S6, S7, and S8 are high frequency switches and have the same switching cycle. The switching semiconductor devices S5 and S6 are connected in series between a third node N3 and the first AC terminal 11. The third node N3 is between the switching semiconductor devices S1 and S2. The switching semiconductor devices S7 and S8 are connected in series between a fourth node N4 and the first AC terminal 11. The fourth node N4 is between the switching semiconductor devices S3 and S4. The third capacitor C3 is connected between a fifth node N5 and a sixth node N6. The fifth node N5 is between the switching semiconductor devices S5 and S6. The sixth node N6 is between the switching semiconductor devices S7 and S8. The switching semiconductor devices S5 and S7 are complementary switches. That is, when the switching semiconductor device S5 is switched on, the switching semiconductor device S7 is switched off, vice versa. Similarly, the switching semiconductor devices S6 and S8 are complementary switches. A driving signal of the switching semiconductor device S5 may lag a half of the switching cycle than that of the switching semiconductor device S6. In an embodiments, as shown in Fig. 6, the second power converting unit 2 includes capacitors C1, C2, and C4 and switching semiconductor devices S1, S2, S3, S4, S9, S10, S11, and S12. The capacitors C1 and C2 and the switching semiconductor devices S1, S2, S3 and S4 are shared by the first power converting unit 1 and the second power converting unit 2. The switching semiconductor devices S9, S10, S11, and S12 are high frequency switches and have the same switching cycle as the switching semiconductor devices S5, S6, S7, and S8. The switching semiconductor devices S9 and S10 are connected in series between the third node N3 and the second AC terminal 21. The switching semiconductor devices S11 and S12 are connected in series between the fourth node N4 and the second AC terminal 21. The fourth capacitor C4 is connected between a seventh node N7 and a eighth node N8. The seventh node N7 is between the switching semiconductor devices S9 and S10. The eighth node N8 is between the switching semiconductor devices S11, S12. The switching semiconductor devices S9 and S10 are complementary switches. Similarly, the switching semiconductor devices S11 and S12 are complementary switches. A driving signal of the switching semiconductor device S9 may lag a half of the switching cycle than that of the switching semiconductor device S10. Driving signals of the switching semiconductor devices S5, S6, S7, and S8 and driving signals of the switching semiconductor devices S9, S10, S11, and S12 have a phase difference of 90 degree, i.e., a quarter of the switching cycle of these switching semiconductor devices. Thus, there is a phase shift of 90 degree between the second plurality of voltage levels and the first plurality of voltage levels. With the above arrangement, each of the first and second power converting units 1, 2 may provide five voltage levels at the respective AC terminals 11, 21. Accordingly, the coupling inductor 3 may provide nine voltage levels at the second end 312 of the first winding 31 and the fourth end 322 of the second winding 32. In comparison with the conventional multi-level power convertor 100 as shown in Fig. 1, the multi-level power convertor 100 as shown in Fig. 6 may provide the same number of voltage levels through using less capacitor, reducing the risk of voltage imbalance among the capacitors in the multi-level power convertor 100 and thereby avoiding the damage of the switching semiconductor devices in the multi-level power convertor 100. Fig. 7 illustrates a schematic circuit diagram of a multi-level power convertor 100 in accordance with another embodiment of the present disclosure. The construction of the multi-level power convertor 100 as shown in Fig. 7 is similar to that of the multi-level power convertor 100 as shown in Fig. 6. The difference between the multi-level power convertors 100 as shown in Figs. 6 and 7 lines in the construction of the second power converting units 2. As shown in Fig. 7, the second power converting unit 2 includes capacitors C1, C2, and C4 and switching semiconductor devices S13, S14, S15, S16, S9, S10, S11, and S12. The switching semiconductor devices S13, S14, S15, and S16 are line frequency switches. The switching semiconductor devices S9, S10, S11, and S12 are high frequency switches. The capacitors C1 and C2 are shared by the first power converting unit 1 and the second power converting unit 2. The switching semiconductor devices S13, S14, S15, and S16 are connected in series between the first and second DC terminals DC+, DC-. A ninth node N9 between the switching semiconductor devices S14 and S15 is connected to the first node N1. The switching semiconductor devices S9 and S10 are connected in series between a tenth node N10 and the second AC terminal 21. The tenth node N10 is between the switching semiconductor devices S13 and S14. The switching semiconductor devices S11 and S12 are connected in series between an eleventh node N11 and the second AC terminal 21. The eleventh node N11 is between the switching semiconductor devices S15 and S16. The fourth capacitor C4 is connected between a seventh node N7 and a eighth node N8. The seventh node N7 is between the switching semiconductor devices S9 and S10. The eighth node N8 is between the switching semiconductor devices S11 and S12. With the above arrangements, the operation of the multi-level power convertor 100 as shown in Fig. 7 is similar to that of the multi-level power convertor 100 as shown in Fig. 6. Each of the multi-level power convertors 100 as described with reference to Figs. 2-7 is a single-phase circuit. However, in other embodiments, each of the multi-level power convertors 100 may be used to form a three-phase circuit. Fig. 8 illustrates a schematic circuit diagram of a three-phase power converting circuit 200 in accordance with an embodiment of the present disclosure. As shown in Fig. 8, the three-phase power converting circuit 200 includes three phases L11, L22, and L33. Each of the phases L11, L22, and L33 includes the multi-level power convertor 100 as described above with reference to Fig. 6. In other embodiments, each of the phases L11, L22, and L33 may include the multi-level power convertor 100 according to other embodiments. Fig. 9 illustrates a schematic circuit diagram of a multi-level power convertor 100 in accordance with another embodiment of the present disclosure. The construction of the multi-level power convertor 100 as shown in Fig. 9 is similar to that of the multi-level power convertor 100 as shown in Fig. 6. The difference between the multi-level power convertors 100 as shown in Figs. 9 and 6 lines in the construction of the first and second power converting units 1, 2. As shown in Fig. 9, the first power converting unit 1 further includes switching semiconductor devices S17, S18, S19, and S20 and capacitors C5 and C7. Similarly, the second power converting unit 2 further includes switching semiconductor devices S21, S22, S23, and S24 and capacitors C6 and C8. With such an arrangement, each of the first and second power converting units 1, 2 may provide nine voltage levels at the respective AC terminals 11 and 12. Then, the coupling inductor 3 may output seventeen voltage levels. Fig. 10 illustrates a schematic circuit diagram of a multi-level power convertor 100 in accordance with yet another embodiment of the present disclosure. The construction of the multi-level power convertor 100 as shown in Fig. 10 is similar to that of the multi-level power convertor 100 as shown in Fig. 7. The difference between the multi-level power convertors 100 as shown in Figs. 10 and 7 lines in the constructions of the first and second power converting units 1, 2. As shown in Fig. 10, the first power converting unit 1 further includes switching semiconductor devices S17, S18, S19, and S20 and capacitors C5 and C7. Similarly, the second power converting unit 2 further includes switching semiconductor devices S21, S22, S23, and S24 and capacitors C6 and C8. With such an arrangement, each of the first and second power converting units 1, 2 may provide nine voltage levels at the respective AC terminals 11 and 12. Then, the coupling inductor 3 may output seventeen voltage levels. In embodiments according to the present disclosure, the switching semiconductor devices in the first and second power converting units 1, 2 may be of various types, for example MOSFET, IGBT and the like. The scope of the present disclosure is not intended to be limited in this respect. In some embodiments, a method for the multi-level power convertor 100 as described above is provided. The method includes providing a first plurality of voltage levels to the first end 311 of the first winding 31 from the first AC terminal 11; providing a second plurality of voltage levels of the same number as the first plurality of voltage levels to the third end 321 of the second winding 32 from the second AC terminal 21, wherein the second plurality of voltage levels are phase-shifted by 90 degree with respect to the first plurality of voltage levels; and outputting a third plurality of voltage levels via the second end 312 of the first winding 31 and the fourth end 322 of the second winding 32, wherein the number of the third plurality of voltage levels equals to the sum of the number of the first plurality of voltage levels and the number of the second plurality of voltage levels minus one. According to various embodiments of the present disclosure, the first plurality of voltage levels and the second plurality of voltage levels having a phase shift of 90 degree may be combined by the coupling inductor 3 into a third plurality of voltage levels; the number of the third plurality of voltage levels equals to th
[DE EP3783792A1]: MEHRSTUFIGER STROMRICHTER MIT AFE-LEISTUNGSZELLENPHASENSTEUERUNG [EN CN112421975A]: MULTILEVEL POWER CONVERTER WITH AFE POWER CELL PHASE CONTROL [FR EP3783792A1]: CONVERTISSEUR DE PUISSANCE MULTINIVEAUX COMPORTANT UNE COMMANDE DE PHASE DE LA CELLULE ÉLECTRIQUE AFE [ZH CN112421975A]: 具有AFE电力单元相位控制的多电平电力转换器 | [EN CN112421975A]: The invention discloses a multilevel power converter with AFE power cell phase control. Power conversion systems and methods to control a multiphase multilevel regenerative power converter with multilevel phase circuits that individually include multiple regenerative power stages with respective power stage outputs connected in series, the individual power stages comprising a DC link circuit a switching rectifier coupled between a respective transformer secondary circuit and the DC link circuit, and a switching inverter coupled between the DC link circuit and the respective power stage output,including a controller that provides inverter switching control signals to control the respective switching inverters, provides rectifier switching control signals to control the respective switchingrectifiers, and controls a non-zero phase relationship between the rectifier switching control signals of the respective switching rectifiers. [ZH CN112421975A]: 公开了具有AFE电力单元相位控制的多电平电力转换器。一种用于控制具有多电平相电路的多相多电平再生电力转换器的电力转换系统和方法，多电平相电路单独地包括各自的电力级输出串联连接的多个再生电力级，单独的电力级包括DC链式电路、耦接在相应变压器次级电路与DC链式电路之间的开关整流器以及耦接在DC链式电路与相应电力级输出之间的开关逆变器，单独的电力级包括控制器，该控制器提供逆变器开关控制信号以控制相应开关逆变器，提供整流器开关控制信号以控制相应开关整流器，以及控制各个开关整流器的整流器开关控制信号之间的非零相位关系。 | EP3783792A1 | 2021-02-24 | EP20186722A | 2020-07-20 | US201916546911A, 2019-08-21 | EP3783792A1: 2021-02-24 US2021058003A1: 2021-02-25 CN112421975A: 2021-02-26 | ROCKWELL AUTOMATION TECH INC | NI ZHITUO NARIMANI MEHDI CHENG ZHONGYUAN ZARGARI NAVID R | H02M7/49: I H02M1/12: I H02M5/458: I H02M1/08: I H02M1/44: I H02M7/483: I | H02M1/12: I H02M7/483: I H02M7/49: I H02M1/0043: A H02M1/08: I H02M1/44: I H02M5/4585: I | US2007058405A1 US6301130B1 US6236580B1 US2017366082A1 |  | [EN CN112421975A]: 1 A power conversion system, comprising: a transformer including a primary circuit and a plurality of secondary circuits; a multi-phase multi-level regenerative power converter including three or more multi-level phase circuits, and a single phase circuit Including multiple regenerative power stages connected in series with their respective power stage outputs, individual power stages include: A DC link circuit, which includes at least one capacitor coupled between a first DC link node and a second DC link node, and a switching rectifier, which includes corresponding secondary circuits each coupled to the secondary circuit A rectifier switching device and a switching inverter between corresponding ones of the first DC link node and the second DC link node, and the switching inverter, which includes each coupled to the first DC link node Node and the inverter switching device between the corresponding DC link node and the corresponding power stage output of the second DC link node, and a power stage controller configured to provide a rectifier switch control signal to operate the A rectifier switching device, and providing an inverter switching control signal to operate the inverter switching device; and a phase controller configured to control the non-zero phase relationship between the rectifier switching control signals of the respective switching rectifiers. 2 The power conversion system of claim 1, wherein the phase controller is configured to control the non-zero phase relationship between the carrier signals of the respective switching rectifiers. 3 The power conversion system of claim 2, wherein the phase controller is configured to provide a non-zero phase relationship between the carrier signals of the regenerative power stage of each of the respective phase circuits. 4 The power conversion system according to claim 3, wherein each of the phase circuits includes an integer m regenerative power stages whose respective power stage outputs are connected in series between a neutral node and a corresponding phase circuit output node, m is greater than 2; wherein the first regenerative power stage of each of the phase circuits is connected to the neutral node, and the m-th power stage of each of the phase circuits is connected to the corresponding phase circuit output node; And wherein, the phase controller is configured to provide a non-zero phase relationship between the carrier signals of the i-th regenerative power stage of each phase circuit, where i=1,...,m. 5 The power conversion system of claim 4, wherein the primary circuit of the transformer is directly connected to a power source. 6 The power conversion system according to claim 4, wherein the separate power stage further comprises a filter circuit connected between a corresponding switching rectifier and a corresponding one of the secondary circuits, and wherein the filtering The inductor circuit includes an inductor that individually has a first terminal directly connected to the corresponding individual phase line of the corresponding secondary circuit in the secondary circuit and a second terminal directly connected to the corresponding phase line of the corresponding switching rectifier. Terminal. 7 The power conversion system according to claim 3, wherein the separate power stage further comprises a filter circuit connected between a corresponding switching rectifier and a corresponding one of the secondary circuits, and wherein the filtering The inductor circuit includes an inductor that individually has a first terminal directly connected to the corresponding individual phase line of the corresponding secondary circuit in the secondary circuit and a second terminal directly connected to the corresponding phase line of the corresponding switching rectifier. Terminal. 8 The power conversion system according to claim 2, wherein each of the phase circuits includes an integer m regenerative power stages whose respective power stage outputs are connected in series between a neutral node and a corresponding phase circuit output node, m is greater than 2; wherein the first regenerative power stage of each of the phase circuits is connected to the neutral node, and the phase power The m-th power stage of each of the circuits is connected to the corresponding phase circuit output node; and wherein the phase controller is configured to provide a non-zero phase relationship between the carrier signals of the i-th regenerative power stage of each phase circuit, Among them, i = 1,···,m. 9 The power conversion system according to claim 8, wherein the primary circuit of the transformer is directly connected to a power source. 10 The power conversion system according to claim 8, wherein the separate power stage further comprises a filter circuit connected between a corresponding switching rectifier and a corresponding one of the secondary circuits, and wherein the filtering The inductor circuit includes an inductor that individually has a first terminal directly connected to the corresponding individual phase line of the corresponding secondary circuit in the secondary circuit and a second terminal directly connected to the corresponding phase line of the corresponding switching rectifier. Terminal. 11 The power conversion system according to claim 2, further comprising a notch filter connected between the primary circuit of the transformer and a power source. 12 The power conversion system according to claim 2, wherein the separate power stage further comprises a filter circuit connected between a corresponding switching rectifier and a corresponding one of the secondary circuits, and wherein the filtering The inductor circuit includes an inductor that individually has a first terminal directly connected to the corresponding individual phase line of the corresponding secondary circuit in the secondary circuit and a second terminal directly connected to the corresponding phase line of the corresponding switching rectifier. Terminal. 13 The power conversion system according to claim 1, wherein each switching inverter is configured to operate in a first mode according to a corresponding inverter switching control signal in the inverter switching control signal to convert from the inverter switching control signal. The power of the DC link circuit is used to provide an output voltage having an amplitude of one of at least two discrete levels at a corresponding output, and to operate in a second mode to transmit the power from the corresponding output to the DC chain circuit; and wherein each switching rectifier is configured to operate in the first mode according to the corresponding rectifier switching control signal in the rectifier switching control signal to convert from the corresponding secondary circuit in the secondary circuit To provide power to the DC link circuit, and operate in the second mode to transmit power from the DC link circuit to a corresponding secondary circuit in the secondary circuit. 14 The power conversion system according to claim 1, wherein each of the phase circuits includes an integer m regenerative power stages whose respective power stage outputs are connected in series between a neutral node and a corresponding phase circuit output node, m is greater than 2; wherein the first regenerative power stage of each of the phase circuits is connected to the neutral node, and the m-th power stage of each of the phase circuits is connected to the corresponding phase circuit output node; And wherein, the phase controller is configured to provide a non-zero phase relationship between the carrier signals of the i-th regenerative power stage of each phase circuit, where i=1,...,m. 15 The power conversion system of claim 1, wherein the primary circuit of the transformer is directly connected to a power source. 16 A method of controlling a multi-phase multi-level regenerative power converter having a multi-level phase circuit, the multi-level phase circuit individually includes a plurality of regenerative power stages connected in series with respective power stage outputs, separate power The stage includes a DC link circuit, a switching rectifier coupled between the corresponding transformer secondary circuit and the DC link circuit, and a switching inverter coupled between the DC link circuit and the output of the corresponding power stage , The method includes: providing an inverter switching control signal to control the corresponding switching inverter; providing a rectifier switching control signal to control the corresponding switching rectifier; and Control the non-zero phase relationship between the rectifier switching control signals of each switching rectifier. 17 The method of claim 16, wherein controlling the non-zero phase relationship between the rectifier switching control signals of the respective switching rectifiers comprises: controlling the non-zero phase relationship between the carrier signals of the respective switching rectifiers. 18 The method of claim 16, wherein controlling the non-zero phase relationship between the rectifier switching control signals of the respective switching rectifiers comprises: providing the carrier signal of the regenerative power stage of each of the respective phase circuits Non-zero phase relationship. 19 The method according to claim 16, wherein each of the phase circuits includes an integer m regenerative power stages whose respective power stage outputs are connected in series between the neutral node and the corresponding phase circuit output node, m is greater than 2; wherein the first regenerative power stage of each of the phase circuits is connected to the neutral node, and the m-th power stage of each of the phase circuits is connected to the corresponding phase circuit output node; and wherein , The non-zero phase relationship between the rectifier switch control signals that control each switching rectifier includes: providing the non-zero phase relationship between the carrier signals of the i-th regenerative power stage of each phase circuit, where i = 1,..., m. 20 A non-transitory computer-readable medium having program instructions that when executed by a processor cause the processor to control a multi-phase multi-level regenerative power converter having a multi-level phase circuit, the The multi-level phase circuit individually includes a plurality of regenerative power stages connected in series with respective power stage outputs, and the individual power stages include a DC link circuit, a secondary circuit coupled between the corresponding transformer secondary circuit and the DC link circuit A switching rectifier and a switching inverter coupled between the DC link circuit and a corresponding power stage output, the computer-readable medium includes computer instructions for the following operations: Provide inverter switching control signals to control Corresponding switching inverters; providing rectifier switching control signals to control the corresponding switching rectifiers; and controlling the non-zero phase relationship between the rectifier switching control signals of each switching rectifier. [ZH CN112421975A]: 1 .一种电力转换系统，包括： 变压器，其包括初级电路和多个次级电路； 多相多电平再生电力转换器，其包括三个或更多个多电平相电路，单独的相电路包括 各自的电力级输出串联连接的多个再生电力级，单独的电力级包括： DC链式电路，其包括耦接在第一DC链式节点与第二DC链式节点之间的至少一个电容 器， 开关整流器，其包括各自耦接在所述次级电路中的相应次级电路与所述第一DC链式节 点和所述第二DC链式节点中的相应DC链式节点之间的整流器开关装置， 开关逆变器，其包括各自耦接在所述第一DC链式节点和所述第二DC链式节点中的相应 DC链式节点与相应电力级输出之间的逆变器开关装置，以及 电力级控制器，其被配置成提供整流器开关控制信号以操作所述整流器开关装置，以 及提供逆变器开关控制信号以操作所述逆变器开关装置;以及 相位控制器，其被配置成控制各个开关整流器的整流器开关控制信号之间的非零相位 关系。 2 .根据权利要求1所述的电力转换系统，其中，所述相位控制器被配置成控制各个开关 整流器的载波信号之间的非零相位关系。 3 .根据权利要求2所述的电力转换系统，其中，所述相位控制器被配置成提供各个相电 路中的每个相电路的再生电力级的载波信号之间的非零相位关系。 4 .根据权利要求3所述的电力转换系统， 其中，所述相电路中的每一个包括各自的电力级输出串联连接在中性节点与相应相电 路输出节点之间的整数m个再生电力级，m大于2； 其中，所述相电路中的每一个的第一再生电力级连接至所述中性节点，并且所述相电 路中的每一个的第m电力级连接至相应相电路输出节点;并且 其中，所述相位控制器被配置成提供各个相电路的第i再生电力级的载波信号之间的 非零相位关系，其中i = 1,··· ,m。 5 .根据权利要求4所述的电力转换系统，其中，所述变压器的所述初级电路直接连接至 电源。 6 .根据权利要求4所述的电力转换系统，其中，单独的电力级还包括连接在相应开关整 流器与所述次级电路中的相应次级电路之间的滤波器电路，并且其中，所述滤波器电路包 括电感器，所述电感器单独地具有直接连接至所述次级电路中的相应次级电路的相应单独 相线的第一端子以及直接连接至相应开关整流器的相应相线的第二端子。 7 .根据权利要求3所述的电力转换系统，其中，单独的电力级还包括连接在相应开关整 流器与所述次级电路中的相应次级电路之间的滤波器电路，并且其中，所述滤波器电路包 括电感器，所述电感器单独地具有直接连接至所述次级电路中的相应次级电路的相应单独 相线的第一端子以及直接连接至相应开关整流器的相应相线的第二端子。 8 .根据权利要求2所述的电力转换系统， 其中，所述相电路中的每一个包括各自的电力级输出串联连接在中性节点与相应相电 路输出节点之间的整数m个再生电力级，m大于2； 其中，所述相电路中的每一个的第一再生电力级连接至所述中性节点，并且所述相电 路中的每一个的第m电力级连接至相应相电路输出节点;并且 其中，所述相位控制器被配置成提供各个相电路的第i再生电力级的载波信号之间的 非零相位关系，其中，i = 1,··· ,m。 9 .根据权利要求8所述的电力转换系统，其中，所述变压器的所述初级电路直接连接至 电源。 10 .根据权利要求8所述的电力转换系统，其中，单独的电力级还包括连接在相应开关 整流器与所述次级电路中的相应次级电路之间的滤波器电路，并且其中，所述滤波器电路 包括电感器，所述电感器单独地具有直接连接至所述次级电路中的相应次级电路的相应单 独相线的第一端子以及直接连接至相应开关整流器的相应相线的第二端子。 11 .根据权利要求2所述的电力转换系统，还包括陷波滤波器，所述陷波滤波器连接在 所述变压器的所述初级电路与电源之间。 12 .根据权利要求2所述的电力转换系统，其中，单独的电力级还包括连接在相应开关 整流器与所述次级电路中的相应次级电路之间的滤波器电路，并且其中，所述滤波器电路 包括电感器，所述电感器单独地具有直接连接至所述次级电路中的相应次级电路的相应单 独相线的第一端子以及直接连接至相应开关整流器的相应相线的第二端子。 13 .根据权利要求1所述的电力转换系统， 其中，各个开关逆变器被配置成根据所述逆变器开关控制信号中的相应逆变器开关控 制信号以第一模式进行操作以转换来自所述DC链式电路的电力来在相应输出处提供具有 至少两个离散电平中的一个离散电平的幅度的输出电压，以及以第二模式进行操作以将来 自相应输出的电力传输至所述DC链式电路;并且 其中，各个开关整流器被配置成根据所述整流器开关控制信号中的相应整流器开关控 制信号以所述第一模式进行操作以转换来自所述次级电路中的相应次级电路的电力来向 所述DC链式电路提供电力，以及以所述第二模式进行操作以将来自所述DC链式电路的电力 传输至所述次级电路中的相应次级电路。 14 .根据权利要求1所述的电力转换系统， 其中，所述相电路中的每一个包括各自的电力级输出串联连接在中性节点与相应相电 路输出节点之间的整数m个再生电力级，m大于2； 其中，所述相电路中的每一个的第一再生电力级连接至所述中性节点，并且所述相电 路中的每一个的第m电力级连接至相应相电路输出节点;并且 其中，所述相控制器被配置成提供各个相电路的第i再生电力级的载波信号之间的非 零相位关系，其中，i = 1,…,m。 15 .根据权利要求1所述的电力转换系统，其中，所述变压器的所述初级电路直接连接 至电源。 16 .一种控制具有多电平相电路的多相多电平再生电力转换器的方法，所述多电平相 电路单独地包括各自的电力级输出串联连接的多个再生电力级，单独的电力级包括DC链式 电路、耦接在相应变压器次级电路与所述DC链式电路之间的开关整流器、以及耦接在所述 DC链式电路与相应电力级输出之间的开关逆变器，所述方法包括： 提供逆变器开关控制信号以控制相应开关逆变器； 提供整流器开关控制信号以控制相应开关整流器；以及 控制各个开关整流器的整流器开关控制信号之间的非零相位关系。 17 .根据权利要求16所述的方法，其中，控制各个开关整流器的整流器开关控制信号之 间的非零相位关系包括： 控制各个开关整流器的载波信号之间的非零相位关系。 18 .根据权利要求16所述的方法，其中，控制各个开关整流器的整流器开关控制信号之 间的非零相位关系包括： 提供各个相电路中的每个相电路的再生电力级的载波信号之间的非零相位关系。 19 .根据权利要求16所述的方法， 其中，所述相电路中的每一个包括各自的电力级输出串联连接在中性节点与相应相电 路输出节点之间的整数m个再生电力级，m大于2； 其中，所述相电路中的每一个的第一再生电力级连接至所述中性节点，并且所述相电 路中的每一个的第m电力级连接至相应相电路输出节点;并且 其中，控制各个开关整流器的整流器开关控制信号之间的非零相位关系包括:提供各 个相电路的第i再生电力级的载波信号之间的非零相位关系，其中，i = 1,··· ,m。 20 .一种具有程序指令的非暂态计算机可读介质，所述程序指令在由处理器执行时使 所述处理器控制具有多电平相电路的多相多电平再生电力转换器，所述多电平相电路单独 地包括各自的电力级输出串联连接的多个再生电力级，单独的电力级包括DC链式电路、耦 接在相应变压器次级电路与所述DC链式电路之间的开关整流器、以及耦接在所述DC链式电 路与相应电力级输出之间的开关逆变器，所述计算机可读介质包括用于以下操作的计算机 指令： 提供逆变器开关控制信号以控制相应开关逆变器； 提供整流器开关控制信号以控制相应开关整流器；以及 控制各个开关整流器的整流器开关控制信号之间的非零相位关系。 | [EN CN112421975A]: Technical field of multi-level power converter with AFE power unit phase control [0001] The disclosed subject matter relates to a multi-level power conversion system. Background technique [0002] Multi-level inverters are sometimes used in motor drives and other power conversion applications to generate high voltage drive signals and provide them to motors or other loads in high power applications. One form of multi-level inverter is the cascaded H-bridge (CHB) inverter architecture, which uses multiple power stages connected in series (for example, H-bridge inverters) to drive each motor winding phase. Each H-bridge is powered by a separate DC source and is driven by a switching signal to generate a positive or negative output voltage, where the series combination of multiple H-bridge stages provides a multi-level inverter output capability for driving a load. Regenerative power converters provide benefits in various applications such as grid-connected motor drives. Summary of the invention [0003] Various aspects of the present disclosure are now summarized in order to facilitate a basic understanding of the present disclosure, wherein the summary is not a comprehensive summary of the present disclosure, and is neither intended to determine certain elements of the present disclosure, nor is it intended In delineating the scope of the present disclosure. On the contrary, the main purpose of this summary is to present the various concepts of the present disclosure in a simplified form before the more detailed description presented below. Describes a multi-phase multi-level regenerative power converter with a multi-level phase circuit. The multi-level phase circuit individually includes respective power stages outputting multiple regenerative power stages connected in series, and the individual power stages include a DC link circuit. , A switching rectifier coupled between the secondary circuit of the corresponding transformer and the DC link circuit and a switching inverter coupled between the DC link circuit and the corresponding power stage output, the multi-phase multi-level regenerative power converter It includes a controller that provides inverter switching control signals to control the corresponding switching inverters, provides rectifier switching control signals to control the corresponding switching rectifiers, and controls the non-zero phase relationship between the rectifier switching control signals of each switching rectifier . Description of the drawings [0004] The following description and drawings set forth in detail certain illustrative implementations of the present disclosure, which indicate several exemplary ways in which the various principles of the present disclosure may be implemented. However, the illustrated examples are not exhaustive of the many possible implementations of the present disclosure. Other objectives, advantages and novel features of the present disclosure will be described in the following detailed description when considered in conjunction with the accompanying drawings. [0005] FIG. 1 is a schematic diagram. [0006] FIG. 2 is a schematic diagram. [0007] FIG. 3 is a schematic diagram. [0008] FIG. 4 is a signal diagram. [0009] Figure 5 is a signal diagram. [0010] FIG. 6 is a signal diagram. [0011] FIG. 7 is a schematic diagram. [0012] FIG. 8 is a signal diagram. [0013] FIG. 9 is a signal diagram. [0014] FIG. 10 is a signal diagram. [0015] FIG. 11 is a signal diagram. [0016] FIG. 12 is a schematic diagram. [0017] FIG. 13 is a signal diagram. [0018] FIG. 14 is a schematic diagram; [0019] FIG. 15 is a signal diagram. [0020] FIG. 16 is a signal diagram. [0021] FIG. 17 is a signal diagram. detailed description [0022] Referring now to the accompanying drawings, several embodiments or implementations are described below in conjunction with the accompanying drawings. In the accompanying drawings, similar reference numerals are always used to refer to similar elements, and various features are not necessarily to scale. draw. Multi-level inverters are sometimes used in motor drives and other power conversion applications to generate high-voltage drive signals and provide them to motors or other loads in high-power applications. One form of multi-level inverter is the cascaded H-bridge (CHB) inverter architecture, which uses multiple power stages connected in series (for example, H-bridge inverters) to drive each motor winding phase. Each H-bridge is powered by a separate DC source and is driven by a switching signal to generate a positive or negative output voltage, where the series combination of multiple H-bridge stages provides a multi-level inverter output capability for driving a load. Regenerative power converters provide benefits in various applications such as grid-connected motor drives. [0023] FIGS. 1 and 2 show an example multi-level inverter motor drive power conversion system 10 having a three-phase multi-level power converter 40. For each of the three parts associated with the motor phases U, V, and W of the motor load 50, there are series connected power levels 100-1, 100-2, 100-3, 100-4, 100-5, 100-6. Other implementations for driving other forms of load 50 are possible, wherein the present disclosure is not limited to motor-driven power converters. In some embodiments, the single power stage 100 includes an inverter 140 or an H-bridge switching circuit with switching devices (for example, Q1 to Q4 in FIG. 2 below), but any of them may be provided in a single power stage 100. A switch circuit 140 of a suitable form to generate a power level output having one of two or more possible levels according to the switch control signal 222 provided by the inverter control part 220 of the power converter controller 200. [0024] The example of FIG. 1 is a multi-phase 13-level power converter 40 with six power stages 100 for each of three motor load phases U, V, and W (e.g., 100- for phase U U1, 100-U2, 100-U3, 100-U4, 100-U5 and 100-U6; 100-V1, 100-V2, 100-V3, 100-V4, 100-V5 and 100-V6 for phase V; And the power levels for phase W (100-W1, 100-W2, 100-W3, 100-W4, 100-W5, 100-W6). However, various aspects of the present disclosure can be implemented in association with a single-phase or multi-phase, multi-level power conversion system having any integer "m" power levels 100, where m is greater than one. In addition, although the illustrated embodiment utilizes cascaded H-bridge power stages 100 to form a multi-level power converter 40 for each phase of the motor drive system 10, other types and forms of power stages 100 may be used, such as The power stage 100 of the switching circuit of more or less than four switching devices, wherein the broader aspects of the present disclosure are not limited to the H-bridge power stage shown in the illustrated embodiment. For example, a single power stage may comprise at least two switching means is greater than or equal to any real number of integer output switch 2 is applied are possible. [0025] The power converter 10 in FIG. 1 is supplied with a multi-phase AC input power from a phase shift transformer 30 having a multi-phase primary circuit 32 that receives three-phase power from an AC power source 20 (shown in In the implementation, it is a triangle configuration Set). The transformer 30 includes 18 three-phase secondary circuits 34, that is, six groups of three-phase secondary circuits 34 in a delta configuration, each of which is in a different phase relationship, but this is not a strict requirement for all possible implementations. Although the primary circuit 32 and the secondary circuit 34 are configured as delta windings in the illustrated example, the "Y"-connected primary windings and/or secondary windings may alternatively be used alone or in combination with delta windings. In addition, although the transformer has a three-phase primary winding 32 and a three-phase secondary winding 34, other single-phase or multi-phase implementations can be used. In addition, although non-phase-shifted implementations are possible, the various secondary circuits 34 in the illustrated embodiment are phase-shifted. [0026] Each of the three-phase secondary circuits 34 in the example of FIG. 1 is coupled to provide AC power to drive the three-phase rectifier 120 of the corresponding power stage 100 of the three-phase multilevel inverter 40. The power converter 40 is a 13-level inverter having six cascaded H-bridge power stages 100U-1 to 100U-6 for motor drive operation, and these six cascaded H-bridge power stages 100U-1 to 100U- 6 has outputs 104U-1 to 104U-6 connected in series (cascaded) to each other between the motor drive neutral point or other reference node N and the first winding U of the three-phase motor load 50. Six power levels 100V-1 to 100V-6 provide a series connection between neutral N and the second winding V voltage output 104V-1 to 104V-6, and six power levels 100W-1 to 100W-6 provide medium The voltage output 104W-1 to 104W-6 of the series connection between the power N and the third winding W of the motor load 50. The controller 200 provides a control signal 222U to the power stages 100U-1 to 100U-6 associated with the first motor winding U, and also provides a control signal 222V to the power stages 100V-1 to 100V-6, and also to the power stage 100W -1 to 100W-6 provides control signal 222W. The controller 200 includes an inverter controller 220 and an AFE phase controller 230 to control the rectification of each switch of the power stage 100 The non-zero phase relationship between the rectifier switch control signals of the converter. [0027] As further shown in FIG. 2, a power stage 100 is provided to serve as the power stage of a single-phase or multi-phase multi-level power converter 40 with a local AFE phase controller 230 in one example. The controller 200 and its components 230, 240 may be implemented using any suitable hardware, software or firmware executed by a processor, or a combination thereof, where an example of the controller 200 includes one or more processing elements, such as a microprocessor, Microcontrollers, DSPs, programmable logic, etc., as well as electronic memories, non-transitory computer readable media such as program memories, and signal conditioning driver circuits, where processing elements are programmed or otherwise configured to implement inverter controller 220 In order to generate a signal 222 suitable for operating the inverter switching device of the power stage inverter switching circuit 140. In addition, the illustrated controller 200 includes an AFE rectifier control part 102 that generates a rectifier switching control signal 103 to operate the rectifier switching device of the rectifier 120. In one example, the local AFE phase controller 230 cooperates with the phase controllers 230 of other power stages 100 to control the non-zero phase relationship between the rectifier switching control signals 103 of the respective switching rectifiers of the power stage 100. [0028] FIG. 2 shows an example H-bridge power stage 100 with a power stage filter 110, an active front end (AFE) switching regulator 120, a DC bus circuit 130, and an output H-bridge inverter 140. The power stage in the figure includes an AC input 108, which has an input terminal 108A that can be connected to receive AC input power (three-phase power in this case) from an AC source through the secondary circuit 34 of the transformer 30 in FIG. 108B and 108C° AC input power is supplied from the terminal 108 through the power stage filter 110 to the switching rectifier circuit 120, which has on-board rectifier switching devices S1 to S6 (such as IGBTs) forming a three-phase active rectifier 120, The three-phase active rectifier 120 receives three-phase AC power from the corresponding transformer secondary circuit 34. [0029] The power unit stage 100 also includes a DC link circuit 130 and a switching circuit (for example, an inverter 140) that provides an output voltage to the power stage output 104 having a first output terminal 104A and a second output terminal 104B Vout. In the illustrated embodiment, the switching rectifier 120 provides DC power across the DC capacitor C connected between the DC link terminals 131 and 132 of the DC link circuit 130. The DC link circuit 130 in turn provides an input to the H-bridge inverter 140 formed by the four inverters xc switching devices Q1 to Q4 (for example, IGBTs) configured in the "H" bridge circuit. In addition, any suitable type of switching device Q can be used For use in power level 100, including but not limited to semiconductor-based switches, such as insulated gate bipolar transistor (QGBT), silicon controlled rectifier (SCR), gate turn off thyristor (GTO), integrated gate commutated thyristor QGCT )Wait. [0030] The H-bridge implementation in FIG. 2 allows switching control signals to be selectively generated by the controller 200 to provide at least two different voltage levels at the output 104 in a controlled manner. For example, when the switching devices Q1 and Q4 are turned on (conducting) and the other devices Q2 and Q3 are turned off (not conducting), a positive value substantially equal to the DC bus voltage across the DC link capacitor C is provided at the output terminals 104A and 104B. DC level voltage (for example, +VDC). Conversely, when Q2 and Q3 are on and Q1 and Q4 are off, a negative output (for example, -VDC) is provided. Therefore, the power stage 100 allows two different output voltages to be selected, and the cascade configuration of six such stages (for example, FIG. 1) allows the inverter control component 220 to selectively generate switching control signals to achieve 13 Different voltage levels for application to the corresponding motor phase U, V or W. Other possible switching circuits can be used to implement two-, three-, or K-level selectable outputs for a single power stage 100, where K is any positive integer greater than one. Any suitable logic or circuit in the controller 200 can be used to provide the inverter switching control signal 222 to a given power stage 100, 400, where the controller 200 can also include such as a comparator, carrier generator or digital logic and signal The signal level amplification of the driver and/or the driver circuit (not shown) to provide a combination sufficient to selectively actuate the switching devices Q1 to Q4, for example. Appropriate drive voltage and/or current level. [0031] The power stage filter 110 in the example of FIG. 2 includes an LCL circuit for each of the three AC phases, the LCL circuit including a first inductor L1, a second inductor L2, a filter capacitor Cf, and Damping resistor Rf. In other examples, the power stage filter can be omitted or replaced with a simple inductance filter with a single inductor in each of the three AC lines (for example, as shown in Figure 3, Figure 7, and Figure 12 below). Using a simple single inductor filter method reduces the cost, size and weight of the multi-phase multi-level power converter 40. The example converter 40 provides an active front end rectifier switching operation with a controlled non-zero phase relationship to control harmonics in the system 10, and may facilitate the simplification and/or elimination of the power stage filter circuit 110. Some examples include an additional notch filter between the AC power source 20 and the primary circuit 32 of the transformer 30 (eg, Figure 3 below). Other examples do not require a notch filter (for example, Figure 7, Figure 12, and Figure 14 below). [0032] Referring also to FIGS. 3 and 4, FIG. 3 shows another example of a multi-phase multi-level power converter 40 that includes a connection between a source 20 and a transformer 30 The notch filter 300 is, for example, a three-phase LCL circuit with or without a damping resistor. In addition, the system 10 of FIG. 3 includes a transformer 30 having a primary circuit 32 and a secondary circuit 34 and a multi-phase multi-level regenerative power converter 40. The converter 40 includes three multilevel phase circuits 42. The separate phase circuit 42 includes three regenerative power stages 100 for 7-level output operation for each phase (power stages 100U-1 to 100U-3 for phase U, power stages 100V-1 to 100V for phase V -3 and power stages 100W-1 to 100W-3 for phase W, where respective power stage outputs 104 are connected in series. FIG. 3 also schematically shows an example of one of the separate power stages 100, which includes an optional power stage filter 110, an active front end, and a switching rectifier 120 (for example, including the one shown in FIG. 2 Shows the rectifier switching devices S1 to S6 connected between the corresponding one of the secondary circuit 34 and the corresponding one of the first DC link node 131 and the second DC link node 132) and the switching inverter 140 (for example, Including each connection as shown in Figure 2 The inverter switching devices Q1 to Q4 connected between the corresponding one of the first chain node 131 and the second DC chain node 132 and the corresponding power stage output 104). [0033] As discussed above in conjunction with FIGS. 1 and 2, the power stage controller 200 in FIG. 2 provides the rectifier switch control signal 103 to operate the rectifier switching devices S1 to S6, and provides the inverter switch control signal 222 to operate The inverter switching devices Q1 to Q4, and the phase controller 230 (for example, the central AFE phase control part 230 in FIG. 1 and/or the local AFE phase control part 230 in FIG. 2) controls each of the system 10 in FIG. 3 The switching rectifier 120 has a non-zero phase relationship between the rectifier switching control signals 103. In one example, the phase controller 230 controls the carrier signal of each switching rectifier 120 Number (for example, signals 401, 402, and 402 in Figure 4, signals 801, 802, and 803 in Figure 8 below, and/or signals 1301, 1302, 1303, 1304, 1305, and 1306 in Figure 13 below) Non-zero phase relationship. In one example, the phase controller 230 provides a non-zero phase between the carrier signals of the regenerative power stage 100 of each of the phase circuits 42 (for example, the signals 401, 402, and 403 in the graph 400 of FIG. 4). Relationship to eliminate or reduce the 31st harmonic. In another example, the phase controller 230 provides non-zero values between the carrier signals of the regenerative power stage 100 of each of the phase circuits 42 (for example, the signals 401, 402, and 403 in the graph 410 of FIG. 4). Phase relationship to eliminate or reduce the 35th harmonic. In another example, the phase controller 230 provides non-zero values between the carrier signals of the regenerative power stage 100 of each of the phase circuits 42 (for example, the signals 401, 402, and 403 in the graph 420 of FIG. 4). Phase relationship to eliminate or reduce the 31st and 35th harmonics. [0034] The controller 200 (FIG. 1) is used in the system 10 of FIG. 3, and operates in one of two modes including a first mode (motor drive) and a second mode (regeneration). In this example, each switching inverter 140 operates in a first mode according to a corresponding one of the inverter switching control signals 222 to convert the power from the DC link circuit 130 to provide at least two The output voltage Vout is of the magnitude of one of the discrete levels, and operates in the second mode to transmit power from the corresponding output 104 to the DC link circuit 130. In addition, each switching rectifier 120 operates in the first mode according to a corresponding one of the rectifier switching control signals 103 to convert the power from the corresponding one of the secondary circuits 34 to provide power to the DC link circuit 130, and to provide power to the DC link circuit 130 in the first mode. The two mode operates to transmit power from the DC link circuit 130 to a corresponding one of the secondary circuits 34. [0035] The use of the switching rectifier 120 facilitates the regeneration operation of the system 10. In addition, the non-zero phase relationship of the carrier signal of each active rectifier circuit 120 facilitates the reduction of controlled harmonics, avoids or alleviates the need for the large power stage filter 110, and potentially alleviates the need for the notch filter 300 . In particular, the example of FIG. 3 reduces the size and complexity of the power stage filter, where the example shown includes a single series inductor in each phase of the corresponding power stage 100. This example includes a notch filter 300, but other examples (eg, FIGS. 7, 12, and 14) do not include a notch filter. For the three-phase AFE 120 of FIG. 3, if the carrier signal in each power stage C is appropriately shifted and the notch filter 300 is added in front of the transformer 30, the selective non-zero phase relationship is beneficial to eliminate the LCL power Stage filter. Alternatively, a notch filter can be added through an additional secondary winding (not shown). A further improvement of this design eliminates the need for notch filter 300. [0036] The following table shows the minimum inductance (L) filter under different rectifier switching frequencies under 1100VDC bus voltage Contrast. [0037] Switching frequency (Hz) Li TDD_P maximum=5% TDD S max=20% 31st harmonic 35th harmonic 48th harmonic Satisfy [0038] 1980 9.9% 3.37% 5.01% 2.24% 1.97% - no 3000 9.9% 2.27% 3.63% - - 1.44% no 4020 3.08% 4.98% 7.24% - - - Yes 9900 2.6% 2.25% 3.8% - - - Yes [0039] The following table shows the comparison at 1100VDC bus voltage and 1980Hz rectifier switching frequency. LCL type Ll(pu) L2(pu) Cfifpu) Rf(pu) TDD_pri TDD sec Standard is met Regular LCL 27.2% 4.65% 11.8% 19.35% No, the DC bus constraints cannot be met LCL (case 1) 6.69% 2.42% 38.4% 12.86% 3.48% 7.41% Yes LCL (case 2) 6.2% 6.07% 18.8% 14.24% 1.25% 2.19% Yes [0041] The indicated case 1 in the above table indicates the weighting on the inductor, and the case 2: introducing more weighting on the capacitor. However, as mentioned above, the use of LCL power stage filters significantly increases the size, weight, and space of the system 10, and the three-phase example shown includes 18 inductors and 9 capacitors for 7-level regenerative CHB drive . In order to promote the regenerative capacity while meeting the power grid harmonic requirements according to IEEE STD 519 2014, different power stage filters 110 are used to reduce the design with the help of carrier shift methods between different regenerative power stages 100 The size of the filter. [0042] As shown in FIG. 3, the phase shift angles of the phase-shifting transformer are δ1, δ2, and δ3 (negative means lagging, and positive means leading). Assuming that the grid frequency is, the SPWM carrier frequency ratio is the initial angle of the carrier of NOA1, A2, and A3. The phases B and C follow the same initial angle sequence of the carrier with 6.2 and 6.3. The power stage filter 110 in FIG. 3 reduces the switching sideband harmonics at the N-2 and N+2 orders. As shown in FIG. 4, the carrier waveforms 401, 402, and 403 between the regenerative power stages 100 in the same phase circuit 42 are shifted to eliminate one harmonic. In addition, the notch filter 300 on the primary side of the transformer reduces another harmonic component. [0043] For the L-level system, for each phase circuit 42, there are m=(LT)/2 cascaded power stages 100. As shown in Figure 3, when the phase shift angle of the transformer from the cascaded power stage 100 is added, ...say, ..., (negative means phase angle delay), the phase of the corresponding power stage carrier signal The shift angle is. 1xc, 92xc,..., 9mxC (X is the corresponding one of the rectifier input phases denoted as A, B, and C below). In order to eliminate N-2 order switching sideband harmonics, a given one of the carrier phase shift angles in the A, B, and C phases satisfies the equation (1). [0044] 2)% + %-3%)) = 0 (1) [0045] In order to eliminate N+2 order harmonics, a similar equation (2) can be derived in one phase. Zhao [0046] Zcos((N + 2)@/ +% +33/)) = 0 (2) j=1 [0047] For example, for the seven-level regeneration system 10 in FIG. 3, suppose Ν = 33, δι = -20°, δ2 = 0°, δ3 = 20°^Ι) Equations (1) and (2) become the following equations and . [0048] cos (31 ω οΐ+θΐχο+60°) +cos (31 ω οΐ+θ2χο) +cos (31 ω Οΐ+θ3χο-60°) =0 (3) [0049] cos (35 ω οΐ+θΐχο+60°) +cos (35 ω ot+e2xc)+cos (35 ω Οΐ+θ3χο-60°) =0 (4) [0050] If N=33, in order to eliminate the 31st-order harmonics, a solution of equation (3) is 9ixc=60. , 92xc = 0°, 93xc = -60. (X = A, B and C phases). In order to eliminate the 35th harmonic, a solution of equation (4) is 9ixc = -60. , /-Ο. , 93xc = 60° (x = A, B and C phases). Once one harmonic component is removed by the carrier shift operation, another harmonic component can be removed by the notch filter 300. In addition, in order to eliminate both the 31st and 35th order harmonics, one solution of equations (3) and (4) is. ixc = 180°, θ2χο = 0°, 93xc = 180° (χ=Α, Β and C phases). [0051] The following table shows example phase shift angles in one phase circuit 42 of the example seven-level system 10 of FIG. 3 corresponding to the carrier signals shown in the graphs 400, 410, and 420 in FIG. Olxc 02xc Remove the N-2 (31st) order (.) 60 0 -60 Remove N+2 (35th) order (.) -60 0 60 [0053] Remove both the N-2 order and N+2 order 180 0 -180 [0054] Similar equations and angles can be calculated for a nine-level three-phase system, where N=33, δι = -15°, and δ2=0. , *=15. , 64 = 30. , Where the above equations and (2) become the following equations and ο [0055] cos (31 ω οΐ+θιΧο+45°) +cos (31 ω ot+92xc) +cos (31 ω οΐ+θ3Χο-45ο) +cos (31 ω ot+ θ 4XC-90 °) =0 (5) cos (35 ω ot+91xc-45°) +cos (35 ω οΐ+θ2χο) +cos (35 ω οΐ+θ3χο+45°) +cos (35 ω οΐ+θ4χο+90°)=0 (6) The following table shows another example carrier shift operation in one phase of the seven-level system. θίχο θ2χο °3xc °4xc Remove the N-2 (31st) order (.) 135 0 135 0 Remove N+2 (35th) order (°) -135 0 -135 0 [0057] It can also be calculated for a nine-level system. h0,. 2*0. 3*°,. 4*° to minimize both the 31st harmonic and the 35th harmonic. [0058] The following describes the voltage and current operation of the example first AFE phase (eg, phase A) in the system 10 of FIG. 3 using the carrier phase shift of the power stage 100 within the example phase and the notch filter 300. [0059] vla = M 2cle cos(30t - 20) +? J-2 M)COS(313°t + 01C + 40) [0060] Iia=Iicos (ω ot-20-α) +I31COS (31 ω οΐ+θΐο+40-β) [0061] v2a = + Learn J-2 QM)COS(3^ot+62c) [0062] l2a=Iicos (ω ot-α) +I31COS (31 ω οΐ+θ2ο-β) [0063] v3a-"Τ. +20) + M)cos(31w()t + 9n-40) [0064] l3a=Iicos (ω ot+20-α) +I31COS (31 ω οΐ+θ3ο-40-β) [0065] Ia=3Iiacos (ω ot-α) +I31A (cos (31 ω οΐ+θΐο+60-β) +cos (31 ω ot+92C-B) +cos (31 ω ot +. 3°-60Mound)) [0066] Οι. ,. The 2c sum is the carrier phase angle of the phase A unit. In order to remove the 31st harmonic: [0067] cos (31 ω οΐ+θΐο+60-β) + cos (31 ω οΐ+θ2ο-β) + cos (31 ω ot+. 3c-60-8) =0 [0068] One solution is [0069] 9lc = 60° [0070] 02c = O° [0071] 93c = -60° [0072] In order to remove the 35th harmonic. [0073] FIG. 5 shows an example graph 500 with an amplitude curve 502 and a phase curve 504, which shows the frequency response of an example notch filter 300 using a damping resistor in each filter phase, This example notch filter 300 has the following LCL filter parameters in one example. frequency LP (pu) CP (pu) RP (pu) 1980 2.84% 2.82% 4.95% [0075] FIG. 6 shows a graph 600 having a spectrum curve 602 representing the harmonic content order of the secondary side of the transformer 30, and a graph having a spectrum curve 612 representing the harmonic content order before the notch filter 300 610 and a graph 620 having a spectrum curve 622 representing the order of the harmonic content at the power supply 20. [0076] Referring now to FIGS. 7-11, another example of the system 10 is shown and described, in which the notch filter is removed and the active front-end switching rectifier carrier signal phase control is modified to also provide out-of-phase circuits 42 corresponds to the non-zero phase relationship between the power stages 100. As seen in the system 10 of FIG. 7, each phase circuit 42 includes a respective power stage output 104 connected in series (for example, as shown in FIG. 1) between the neutral node N and the corresponding phase circuit output nodes U, V, and W. M regenerative power levels 100 between m, where m is greater than 2 (for example, m = 3 in the example of FIG. 7). The first regenerative power stage 100-U1, 100-V1, 100-W1 of each of the phase circuits 42-U, 42-V, 42-W is connected to the neutral node N, and the phase circuits 42-U, 42-W The mth (for example, the third) power stage 100-U1, 100-V1, 100-W1 of each of V and 42W is connected to the corresponding phase circuit output nodes U, V, and W. In this example, the phase controller 230 provides the carrier signal of the i-th regenerative power stage 100-U1, 100-V1, 100-W1 of the corresponding phase circuit 42-U, 42-V, 42-W (for example, the carrier signal of FIG. 8 The non-zero phase relationship between the signals 801, 802 and 803 in the graph 800, where i = [0077] The example of FIG. 7 uses a non-zero carrier signal phase offset between the voltages of each similar (eg, corresponding) cell in the three-phase circuit 42 to reduce or remove two sideband harmonics. For example, the carrier signals of the first power stage 100-U1J00-V1 and 100-W1 are offset from each other by a non-zero phase angle, and the carrier signals of the power stage 100-U2J00-V2 and 100-W2 are offset from each other by a non-zero phase. Angle, and the last (for example, the first power stage 100-U2J00-V2 and 100-W2 carrier signal phase offset from each other by a non-zero phase angle. This example facilitates the need for a notch filter and only use the smallest single inductance power The operation that meets the relevant harmonic content standards in the case of the first-stage filter 110. As shown by the curves 801, 802, and 803 in the graph 800 of FIG. 8, the three-phase Aj, Bj, Cj (j = 1, m ) Uses a 120-degree carrier phase shift angle to reduce N-2, N+2, 2NT, and 2N+1 sideband harmonics. Figure 9 shows the example system 10 of Figure 7 using the carrier waveform of Figure 8 The secondary current curves 902, 904, and 906 as a function of time. Figure 10 provides a secondary side with a representation of the transformer 30 The graph 1000 of the spectrum curve 1002 of the harmonic content order, and FIG. 11 shows a graph with curves 1102 and 1104 respectively showing the voltage and current (multiplied by 10) of the transformer primary 32 of the example system 10 of FIG. 7 Figure 1100. In general, for a three-phase L-level regeneration system, in order to eliminate the N-2, N+2, 2NT, and 2N+1 sideband harmonics of the three-phase regeneration CHB system, in one example, the regeneration units Aj, Bj , Cj (j = 1, m) SPWM (for example, space factor pulse width modulation)
[ZH CN111786579A]: 具有公共高压直流母线的级联多电平整流器及控制策略 [EN CN111786579A]: Cascaded multilevel rectifier with common high-voltage DC bus and control strategy | [ZH CN111786579A]: 本发明具有公共高压直流母线的级联多电平整流器及控制策略，属于AC/DC变换技术及其控制技术。该变换器提供多种主功率电路，每种主功率电路都由若干个模块单元级联组成，用于构成一对公共高压直流母线，极大降低了功率开关管的电压应力，克服了传统整流器由于功率开关管电压应力限制而不能产生高直流母线电压的缺点。本发明提供的整流器及控制策略平衡了输出侧各串联电容电压，实现应用低耐压的功率开关管完成高电压下的大功率整流变换，且不需要使用庞大，笨重，接线复杂的工频移相变压器的隔离，极大简化了主功率电路拓扑，提高了系统的工作效率，体积小，重量轻，成本低，在中高压直流输电、大功率的中高压变频器等领域具有重要的应用价值。 [EN CN111786579A]: The invention discloses a cascaded multilevel rectifier with a common high-voltage DC bus and a control strategy, and belongs to an AC/DC conversion technology and a control technology thereof. A converter provides various main power circuits, and each main power circuit is formed by cascading a plurality of module units and is used for forming a pair of common high-voltage DC buses, so the voltage stress of a power switch tube is greatly reduced, and the defect that a traditional rectifier cannot generate high-DC bus voltage due to voltage stress limitation of the power switch tube is overcome. According to the rectifier and the control strategy provided by the invention, the voltage of each series capacitor at the output side is balanced, and high-power rectification conversion under high voltage is completed by using a low-voltage-withstanding power switch tube; the isolation of a huge, heavy and complex power frequency phase-shifting transformer is not needed, the topology of a main power circuit is greatly simplified, the working efficiency of the system is improved, the size is small, the weight is light, the cost is low, and the method has important application value in thefields of medium-high voltage direct current transmission, high-power medium-high voltage frequency converters and the like. | CN111786579A | 2020-10-16 | CN202010527061A | 2020-06-11 | CN202010527061A, 2020-06-11 | CN111786579A: 2020-10-16 | UNIV CHINA MINING & TECHNOLOGY BEIJING | WANG CONG CHENG HONG ZHAO ZHIHAO LI YAOPU TIAN CHANGGENG DENG JIAQING TAO YANMEI | H02M7/217: I H02J3/36: I H02M1/42: I H02M7/219: I | H02J3/36: I H02M1/4225: I H02M1/4233: I H02M7/217: I H02M7/219: I Y02B70/10: A Y02E40/10: A Y02E60/60: A |  |  | [ZH CN111786579A]: 1.具有公共高压直流母线的级联多电平整流器，包括主功率电路，所述主功率电路包 括高频滤波器、单相二极管整流桥、升压电感L和第一模块单元(A),其特征在于:所述第一 模块单元(A)包括两个开关器件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两 个负载电阻R1、R2和N个级联的第二模块单元(B)，N为正整数，所述第二模块单元(B)包括两 个开关器件Sb1、Sb2,一个输出直流电容Cb，一个滤波电感Lb和一个负载电阻Rb，所述开关器 件SB1的第二接线端(b)与所述开关器件SB2的第一接线端(c)相连，所述开关器件SB2的第二 接线端(d)与所述滤波电感Lb的一端相连，所述滤波电感Lb的另一端与并联连接的所述输出 直流电容Cb和所述负载电阻Rb的第二接线端(f)相连,N个级联的所述第二模块单元(B)，其 中各个所述第二模块单元(B)中开关器件Sb1的第二接线端(b)与下一个所述第二模块单元 (B)中开关器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的所述输出直 流电容Cb和所述负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的所述 输出直流电容Cb和所述负载电阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B) 中所述开关器件Sb1的第一接线端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb 的第一接线端(e)及所述开关器件S1的第二接线端(n)相连,所述开关器件S1的第一接线端 (m)与所述快恢复二极管D1的阳极相连，所述快恢复二极管D1的阴极与并联连接的所述输出 直流电容C1和所述负载电阻R1的一端相连，并联连接的所述输出直流电容C1和所述负载电 阻R1的另一端与级联的第一个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和 所述负载电阻Rb的第一接线端(e)相连，所述开关器件S1的第一接线端(m)与所述升压电感L 的一端相连，所述升压电感L的另一端与所述单相二极管整流桥的整流输出正端相连，所述 开关器件S2的第一接线端(m)与级联的第N个所述第二模块单元(B)中所述开关器件Sb1的第 二接线端(b)相连，级联的第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb 和所述负载电阻Rb的第二接线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2 的一端相连，并联连接的所述输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二 极管D2的阳极相连，所述开关器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述 单相二极管整流桥的整流输出负端相连，所述单相二极管整流桥的交流输入端经所述高频 滤波器串联接入交流电网。 2.采用权利要求1所述的具有公共高压直流母线的级联多电平整流器构成的具有公共 高压直流母线的级联多电平三相星接整流器，包括三相主功率电路，其特征在于:所述三相 主功率电路包括三个高频滤波器和三个第三模块单元(C),所述第三模块单元(C)包括单相 二极管整流桥、升压电感L和第一模块单元(A)，所述第一模块单元(A)包括两个开关器件 S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的第 二模块单元(B) ,N为正整数，所述第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直 流电容Cb,一个滤波电感Lb和一个负载电阻Rb,所述开关器件Sb1的第二接线端(b)与所述开 关器件Sb2的第一接线端(c)相连，所述开关器件Sb2的第二接线端(d)与所述滤波电感Lb的一 端相连，所述滤波电感Lb的另一端与并联连接的所述输出直流电容Cb和所述负载电阻Rb的 第二接线端(f)相连,N个级联的所述第二模块单元(B),其中各个所述第二模块单元(B)中 开关器件Sb1的第二接线端(b)与下一个所述第二模块单元(B)中开关器件Sb1的第一接线端 (a)相连，各个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第 二接线端(f)与下一个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电 阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中所述开关器件Sbi的第一接线 端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端(e)及所述开关器 件Si的第二接线端(n)相连,所述开关器件Si的第一接线端(m)与所述快恢复二极管D1的阳 极相连，所述快恢复二极管D1的阴极与并联连接的所述输出直流电容Ci和所述负载电阻R1 的一端相连，并联连接的所述输出直流电容Ci和所述负载电阻R1的另一端与级联的第一个 所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端 (e)相连，所述开关器件Si的第一接线端(m)与所述升压电感L的一端相连，所述升压电感L 的另一端与所述单相二极管整流桥的整流输出正端相连，所述开关器件S2的第一接线端 (m)与级联的第N个所述第二模块单元(B)中所述开关器件Sbi的第二接线端(b)相连，级联的 第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第二接 线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2的一端相连，并联连接的所述 输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二极管D2的阳极相连，所述开关 器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述单相二极管整流桥的整流输 出负端相连，每相所述第三模块单元(C)剩余2个交流输入端，三相所述第三模块单元(C)的 第一交流输入端构成一组接线端，三相所述第三模块单元(C)的第二交流输入端构成另一 组接线端，其中一组接线端连接到一个公共的中性点上，另外一组接线端分别与三个所述 高频滤波器串联，接入三相电网，构成星形连接。 3.采用权利要求1所述的具有公共高压直流母线的级联多电平整流器构成的具有公共 高压直流母线的级联多电平三相角接整流器，包括三相主功率电路，其特征在于:所述三相 主功率电路包括三个高频滤波器和三个第三模块单元(C)，所述第三模块单元(C)包括单相 二极管整流桥、升压电感L和第一模块单元(A)，所述第一模块单元(A)包括两个开关器件 S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的第 二模块单元(B)，N为正整数，所述第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直 流电容Cb，一个滤波电感Lb和一个负载电阻Rb，所述开关器件Sb1的第二接线端(b)与所述开 关器件Sb2的第一接线端(c)相连，所述开关器件Sb2的第二接线端(d)与所述滤波电感Lb的一 端相连，所述滤波电感Lb的另一端与并联连接的所述输出直流电容Cb和所述负载电阻Rb的 第二接线端(f)相连,N个级联的所述第二模块单元(B),其中各个所述第二模块单元(B)中 开关器件Sb1的第二接线端(b)与下一个所述第二模块单元(B)中开关器件Sb1的第一接线端 (a)相连，各个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第 二接线端(f)与下一个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电 阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中所述开关器件Sb1的第一接线 端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端(e)及所述开关器 件S1的第二接线端(n)相连,所述开关器件S1的第一接线端(m)与所述快恢复二极管D1的阳 极相连，所述快恢复二极管D1的阴极与并联连接的所述输出直流电容C1和所述负载电阻R1 的一端相连，并联连接的所述输出直流电容C1和所述负载电阻R1的另一端与级联的第一个 所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端 (e)相连，所述开关器件S1的第一接线端(m)与所述升压电感L的一端相连，所述升压电感L 的另一端与所述单相二极管整流桥的整流输出正端相连，所述开关器件S2的第一接线端 (m)与级联的第N个所述第二模块单元(B)中所述开关器件Sb1的第二接线端(b)相连，级联的 第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第二接 线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2的一端相连，并联连接的所述 输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二极管D2的阳极相连，所述开关 器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述单相二极管整流桥的整流输 出负端相连，每相所述第三模块单元(C)剩余2个交流输入端，三相所述第三模块单元(C)的 第一交流输入端构成一组接线端，三相所述第三模块单元(C)的第二交流输入端构成另一 组接线端，其中一组接线端分别经三个所述高频滤波器接至三相电网输入端，另一组接线 端依次连接至三相电网中的下一相输入端，构成角形连接。 4.采用权利要求1所述的具有公共高压直流母线的级联多电平整流器构成的具有公共 高压直流母线的级联多电平三相双星接整流器，包括三相主功率电路，其特征在于:所述三 相主功率电路包括三个高频滤波器、六个桥臂电感、一个直流电容和六个第三模块单元 (C)，六个所述第三模块单元(C)构成对接的两组星形连接，即在每组星形连接中，所述第三 模块单元(C)包括单相二极管整流桥、升压电感L和第一模块单元(A)，所述第一模块单元 (A)包括两个开关器件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电 阻R1、R2和N个级联的第二模块单元(B)，N为正整数，所述第二模块单元(B)包括两个开关器 件Sb1、Sb2,一个输出直流电容Cb，一个滤波电感Lb和一个负载电阻Rb，所述开关器件Sb1的第 二接线端(b)与所述开关器件SB2的第一接线端(C)相连，所述开关器件SB2的第二接线端(d) 与所述滤波电感Lb的一端相连，所述滤波电感Lb的另一端与并联连接的所述输出直流电容 Cb和所述负载电阻Rb的第二接线端(f)相连,N个级联的所述第二模块单元(B),其中各个所 述第二模块单元(B)中开关器件Sb1的第二接线端(b)与下一个所述第二模块单元(B)中开关 器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的所述输出直流电容Cb和 所述负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的所述输出直流 电容Cb和所述负载电阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中所述开 关器件Sb1的第一接线端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接 线端(e)及所述开关器件S1的第二接线端(n)相连,所述开关器件S1的第一接线端(m)与所述 快恢复二极管D1的阳极相连，所述快恢复二极管D1的阴极与并联连接的所述输出直流电容 C1和所述负载电阻R1的一端相连，并联连接的所述输出直流电容C1和所述负载电阻R1的另 一端与级联的第一个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载 电阻Rb的第一接线端(e)相连，所述开关器件S1的第一接线端(m)与所述升压电感L的一端相 连，所述升压电感L的另一端与所述单相二极管整流桥的整流输出正端相连，所述开关器件 S2的第一接线端(m)与级联的第N个所述第二模块单元(B)中所述开关器件Sb1的第二接线端 (b)相连，级联的第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负 载电阻Rb的第二接线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2的一端相 连，并联连接的所述输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二极管D2的 阳极相连，所述开关器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述单相二极 管整流桥的整流输出负端相连，每相所述第三模块单元(C)剩余2个交流输入端，三相所述 第三模块单元(C)的第一交流输入端构成一组接线端，三相所述第三模块单元(C)的第二交 流输入端构成另一组接线端，其中一组接线端连接到一个公共中性点，另一组接线端分别 与三个所述桥臂电感的一端相连，而在每相桥臂上的两个所述桥臂电感的另一端各自相 连,并分别经三个所述高频滤波器之一接至三相电网输入端，同时，第一组星形连接中的公 共中性点和第二组星形连接中的公共中性点分别与所述直流电容的两端相连，构成双星形 连接。 5.一种具有公共高压直流母线的级联多电平整流器的控制策略，其特征在于，具有公 共高压直流母线的级联多电平整流器的控制策略步骤如下： (1)对具有公共高压直流母线的级联多电平整流器的输出侧直流电压进行采样，得到N +2个输出侧直流电压信号Uol、Uo2和UoBl、UoB2. . .UoBN； (2)利用下式计算步骤⑴中的N+2个输出侧直流电压信号U0i、U02和展1#陋..内邳的平 均值U。： 1 N +Σϋ ,+U ) N ol j=] oBj o27 (3)将步骤(2)中的U。与直流电压给定信号U。*比较后送入PI电压调节器，得到PI电压调 节器输出直流电流信号幅值Id； (4)将步骤⑴中的N+2个输出侧直流电压信号U0i、U°2和呱1#烟..内渊分别与直流电压 给定信号U。*比较后送入PI电压调节器，得到PI电压调节器输出直流电流信号幅值Idi、Id2和 IdBl&gt;IdB2. . . IdBN； ⑸将步骤⑷中直流电流信号幅值Idl、Id2和IdBl、IdB2. .」dBN分别与步骤⑵中的直流电 流信号幅值Id相加,相加后得到直流电流给定信号幅值及1*、几2*和31*、母2*..」(^*,将直 流电流给定信号幅值Idl*、Id2*和IdBl*、IdB2*..」dBN*与利用锁相环PLL(Phase-Locked loop) 得到的和电网电压相位相同的正弦信号相乘，产生交流电流给定信号idl*、id2»DidBl*、 idB2*. . . idBN*； (6)检测当前tk时刻的电网电压e(tk)和交流电流i (tk)，利用下式预测tk+ι时刻交流电 流idl (tk+1)、id2 (tk+ι)和idBl (tk+ι)、idB2 (tk+1) ... idBN (tk+1)的值： RT /dl(tk+l)=(l - L 工 );(tk)+^[(e(tk)-«di(tk))] RT池(tk+ι )=(1-不工 )i(tk)+^[(e(tk)-Md2(tk))] RT/dB!(tk+l)=(l - 晨 tQ)] RT /dB2(tk+l)=(l -* » . f(tk)+*[(e(tkEdH2(tk))] A /dBN(tk+l)=(l-^ ^)i(tk)+i[(e(tk)-Mdi1N(tk))] L 式中,Ll为升压电感;R为升压电感Ll内阻；Ts为米样周期；Udl (tk)、Ud2 (tk)和UdBl (tk)、UdB2 (tk) . . .UdBN(tk)分别为整流器在第k个采样周期内应用开关状态所对应交流侧电压； ⑺利用下式计算步骤⑹中的Udi (tk)、Ud2 (tk)和UdBl (tk)、UdB2 (tk) . . . UdBN (tk)： 由1 (tk)=S(H (tk)* % (t。 ti(R(tk)=S(R(tk)*£/o2(tk) 汕旧 l(tk)=SdRI (也)* i/oHI(tk) ii(lB2(tk)=S(lB2(tk)* t/oR2(tk) « « « W(lBN(tk)=SdRN (tk ) * i4BN(tk) 式中?Uol (tk) &gt;Uo2 (tk)和UoEl (tk)、UoE2 (tk) . . . UoBN (tk)是tk时刻整流器输出侧N+2个直流 也压信号，Sdl (tk)、Sd2 (tk)和SdBl (tk)、SdB2 (tk) . . . SdBN (tk)是tk时刻整流器对应的开关状态： 1 E)〉orL开关状态为关断 Sdl (tk)、Sd2 (tk)和 SdE ⑴)、SdR2 (tk)…S dRK (tk) = . 0 或者 &lt; °开关状态为导通 -i，α)&lt;οπ.开关状态为关断 (8)构造价值函数gdl、gd2、和gdBl、gdB2· ·・gdBN： gdi= I idi*—idi (tk+1) I gd2= I id2*-id2 (tk+1) I gdBl= I idBl^-idBl (tk+1) I gdB2= I idB2*-idB2 (tk+1) I a « a gdBN= idBN*-idBN (tk+1) 式中，idl*、id2¥tHdBl*、idB2*. . . idBN*为步骤⑸中的交流电流给定信号，idi (tk+1)、id2 (tk+1)和 idBl (tk+1)、idB2 (tk+1) ... idBN (tk+1)为步骤(6)中 tk+1 时刻交流电流预测值； (9)通过价值函数gdl、gd2、和gdBl、gdB2. . .gdBN对整流器的每一个开关状态进行评估，选出 使得价值函数最小的预测电流值所对应的开关状态，生成开关器件的驱动信号Q1 «2和Q1B1、 Q1B2. . .Q1BN；将驱动信号Q2和Q1B2、Q1B3. . .Q1BN取反后得到驱动信号Q2B1、Q2B2. . .Q2BN； (10)将步骤⑼中的驱动信号Q1、Q2和Q1B1、Q1B2. . .Q1BN以及步骤⑼中的驱动信号Q2B1、 Q2B2. . .Q2BN送给对应的开关器件，实现有源功率因数校正，使输入电流正弦化，同时实现对 级联的N+2个输出直流电容电压的均衡控制。 [EN CN111786579A]: 1. A cascaded multilevel rectifier with a common high-voltage DC bus, including a main power circuit including a high-frequency filter, a single-phase diode rectifier bridge, a boost inductor L and a first module unit (A), It is characterized in that: the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, two load resistors R1, R2, and N The cascaded second module unit (B), N is a positive integer, and the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and a load resistor Rb, The second terminal (b) of the switch device SB1 is connected to the first terminal (c) of the switch device SB2, and the second terminal (d) of the switch device SB2 is connected to one end of the filter inductor Lb Connected, the other end of the filter inductor Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel, and the N second module units (B) cascaded , Wherein the second terminal (b) of the switching device Sb1 in each second module unit (B) is connected to the first terminal (a) of the switching device Sb1 in the next second module unit (B), The output direct connected in parallel in each second module unit (B) The second terminal (f) of the current capacitor Cb and the load resistor Rb is connected in parallel with the first terminal (e) of the output DC capacitor Cb and the load resistor Rb in the next second module unit (B) ) Is connected, the first terminal (a) of the switching device Sb1 in the first second module unit (B) of the cascade is connected to the first connection of the output DC capacitor Cb and the load resistance Rb connected in parallel The terminal (e) is connected to the second terminal (n) of the switching device S1, the first terminal (m) of the switching device S1 is connected to the anode of the fast recovery diode D1, and the fast recovery diode D1 The cathode is connected to one end of the output DC capacitor C1 and the load resistor R1 connected in parallel, and the other end of the output DC capacitor C1 and the load resistor R1 connected in parallel is connected to the first cascaded first end The output DC capacitor Cb connected in parallel in the two module unit (B) is connected to the first terminal (e) of the load resistor Rb, and the first terminal (m) of the switching device S1 is connected to the booster One end of the inductor L is connected, the other end of the boost inductor L is connected to the rectified output positive end of the single-phase diode rectifier bridge, and the first terminal (m) of the switching device S2 is connected to the Nth cascade The second terminal (b) of the switching device Sb1 in the second module unit (B) is connected, and the output DC capacitor Cb connected in parallel in the Nth second module unit (B) in the cascade The second terminal (f) of the load resistor Rb is connected to one end of the output DC capacitor C2 and the load resistor R2 connected in parallel, and the output DC capacitor C2 and the load resistor R2 are connected in parallel. The other end is connected to the anode of the fast recovery diode D2, and the second terminal (n) of the switching device S2 is connected to the cathode of the fast recovery diode D2 and the negative terminal of the rectification output of the single-phase diode rectifier bridge, The AC input end of the single-phase diode rectifier bridge is connected to the AC power grid in series through the high frequency filter. 2. A cascaded multi-level three-phase star-connected rectifier with a common high-voltage DC bus composed of the cascaded multi-level rectifier with a common high-voltage DC bus according to claim 1, including a three-phase main power circuit, characterized in that : The three-phase main power circuit includes three high-frequency filters and three third module units (C), and the third module unit (C) includes a single-phase diode rectifier bridge, a boost inductor L and a first module Unit (A), the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, and two load resistors R1, R2 and N A cascaded second module unit (B), N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and a load resistor Rb , The second terminal (b) of the switching device Sb1 is connected to the first terminal (c) of the switching device Sb2, and the second terminal (d) of the switching device Sb2 is connected to the filter inductor Lb One end is connected, the other end of the filter inductor Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel, and the N cascaded second module units (B ), wherein the second terminal (b) of the switching device Sb1 in each of the second module units (B) and the first terminal (b) of the switching device Sb1 in the next second module unit (B) (a) connected, the second terminal (f) of the output DC capacitor Cb and the load resistance Rb connected in parallel in each second module unit (B) is connected in parallel with the next second module unit (B) The output DC capacitor Cb and the load circuit The first terminal (e) of the resistor Rb is connected, and the first terminal (a) of the switching device Sbi in the first second module unit (B) of the cascade is connected in parallel with the output DC capacitor Cb and The first terminal (e) of the load resistor Rb and the second terminal (n) of the switching device Si are connected, and the first terminal (m) of the switching device Si is connected to the fast recovery diode D1 The anode is connected, the cathode of the fast recovery diode D1 is connected to one end of the output DC capacitor Ci and the load resistor R1 connected in parallel, and the other end of the output DC capacitor Ci and the load resistor R1 connected in parallel is connected to The output DC capacitor Cb connected in parallel in the first second module unit (B) of the cascade is connected to the first terminal (e) of the load resistor Rb, and the first connection of the switching device Si The terminal (m) is connected to one end of the boost inductor L, and the other end of the boost inductor L is connected to the positive terminal of the rectified output of the single-phase diode rectifier bridge. The first terminal of the switching device S2 ( m) Connected to the second terminal (b) of the switching device Sbi in the Nth second module unit (B) of the cascade, and in the Nth second module unit (B) of the cascade The second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel is connected to one end of the output DC capacitor C2 and the load resistor R2 connected in parallel, and the parallel connection The other end of the output DC capacitor C2 and the load resistor R2 is connected to the anode of the fast recovery diode D2, and the second terminal (n) of the switching device S2 is connected to the cathode of the fast recovery diode D2 and the single The negative ends of the rectified output of the phase diode rectifier bridge are connected, the remaining 2 AC input ends of the third module unit (C) of each phase, and the first AC input ends of the three-phase third module unit (C) constitute a set of wiring The second AC input terminal of the three-phase third module unit (C) constitutes another set of terminals, one of which is connected to a common neutral point, and the other set of terminals is connected to three The high-frequency filters are connected in series and connected to a three-phase power grid to form a star connection. 3. A cascaded multi-level three-phase corner connection rectifier with a common high-voltage DC bus formed by using the cascaded multi-level rectifier with a common high-voltage DC bus of claim 1, comprising a three-phase main power circuit, characterized in : The three-phase main power circuit includes three high-frequency filters and three third module units (C), the third module unit (C) includes a single-phase diode rectifier bridge, a boost inductor L and a first module Unit (A), the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, and two load resistors R1, R2 and N A cascaded second module unit (B), N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and a load resistor Rb , The second terminal (b) of the switching device Sb1 is connected to the first terminal (c) of the switching device Sb2, and the second terminal (d) of the switching device Sb2 is connected to the filter inductor Lb One end is connected, the other end of the filter inductor Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel, and the N cascaded second module units (B ), wherein the second terminal (b) of the switching device Sb1 in each of the second module units (B) and the first terminal (b) of the switching device Sb1 in the next second module unit (B) (a) connected, the second terminal (f) of the output DC capacitor Cb and the load resistance Rb connected in parallel in each second module unit (B) is connected in parallel with the next second module unit (B) The output DC capacitor Cb is connected to the first terminal (e) of the load resistor Rb, and the first terminal (a) of the switching device Sb1 in the first second module unit (B) of the cascade Connected to the first terminal (e) of the output DC capacitor Cb and the load resistor Rb connected in parallel and the second terminal (n) of the switching device S1, the first terminal of the switching device S1 (m) Connected to the anode of the fast recovery diode D1, the cathode of the fast recovery diode D1 is connected to one end of the output DC capacitor C1 and the load resistor R1 connected in parallel, and the output DC capacitor connected in parallel C1 and the other end of the load resistor R1 are connected in parallel with the first terminal (e) of the output DC capacitor Cb and the load resistor Rb in the first second module unit (B) that is cascaded Connected, the first terminal (m) of the switching device S1 is connected to one end of the boost inductor L, and the other end of the boost inductor L is connected to the rectified output positive end of the single-phase diode rectifier bridge, The first terminal (m) of the switching device S2 is connected to the second terminal (b) of the switching device Sb1 in the Nth second module unit (B) of the cascade connection. The second terminal (f) of the output DC capacitor Cb and the load resistance Rb connected in parallel in the Nth second module unit (B) is connected in parallel with the output DC capacitor C2 and the load One end of the resistor R2 is connected, the other end of the output DC capacitor C2 and the load resistor R2 connected in parallel is connected to the anode of the fast recovery diode D2, and the second terminal (n) of the switching device S2 is connected to the The cathode of the fast recovery diode D2 is connected to the negative terminal of the rectification output of the single-phase diode rectifier bridge, the third module unit (C) of each phase has two AC input terminals, and the three-phase third module unit (C) ) The first AC input terminal constitutes a set of terminals, the second AC input terminal of the three-phase third module unit (C) constitutes another set of terminals, and one set of terminals is passed through the three high frequency The filter is connected to the input terminal of the three-phase power grid, and the other set of terminals is connected to the input terminal of the next phase in the three-phase power grid in turn to form an angular connection. 4. The cascaded multi-level three-phase dual-star connection rectifier with a common high-voltage DC bus constituted by the cascaded multi-level rectifier with a common high-voltage DC bus according to claim 1, including a three-phase main power circuit, characterized in that : The three-phase main power circuit includes three high frequency filters, six bridge arm inductances, one DC capacitor and six third module units (C), and the six third module units (C) form a butt Two sets of star connections, that is, in each set of star connections, the third module unit (C) includes a single-phase diode rectifier bridge, a boost inductor L, and a first module unit (A), the first module unit (A) Including two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, two load resistors R1, R2 and N cascaded second module units (B) , N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and a load resistor Rb, and the second terminal of the switching device Sb1 (b) Connected to the first terminal (C) of the switching device SB2, the second terminal (d) of the switching device SB2 is connected to one end of the filter inductor Lb, and the other end of the filter inductor Lb Connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel, the N second module units (B) cascaded, each of which is The second terminal (b) of the switching device Sb1 in the second module unit (B) is connected to the first terminal (a) of the switching device Sb1 in the second module unit (B), and each second module The second terminal (f) of the output DC capacitor Cb and the load resistance Rb connected in parallel in the unit (B) is connected to the output DC capacitor Cb and the load resistor in parallel in the next second module unit (B). The first terminal (e) of the load resistor Rb is connected, and the first terminal (a) of the switching device Sb1 in the first second module unit (B) of the cascade is connected to the output DC capacitor connected in parallel Cb is connected to the first terminal (e) of the load resistor Rb and the second terminal (n) of the switching device S1, and the first terminal (m) of the switching device S1 is connected to the fast recovery diode The anode of D1 is connected, the cathode of the fast recovery diode D1 is connected to one end of the output DC capacitor C1 and the load resistor R1 connected in parallel, and the other of the output DC capacitor C1 and the load resistor R1 connected in parallel One end is connected to the first terminal (e) of the output DC capacitor Cb and the load resistor Rb connected in parallel in the first second module unit (B) of the cascade connection, and the first terminal (e) of the switching device S1 A terminal (m) is connected to one end of the boost inductor L, and the other end of the boost inductor L is connected to the rectified output positive end of the single-phase diode rectifier bridge, the switching device The first terminal (m) of S2 is connected to the second terminal (b) of the switching device Sb1 in the Nth second module unit (B) of the cascade, and the Nth terminal (b) of the cascade connected The second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel in the two module unit (B) is connected to one end of the output DC capacitor C2 and the load resistor R2 connected in parallel, The other end of the output DC capacitor C2 and the load resistor R2 connected in parallel is connected to the anode of the fast recovery diode D2, and the second terminal (n) of the switching device S2 is connected to the fast recovery diode D2. The cathode is connected to the negative terminal of the rectification output of the single-phase diode rectifier bridge, the third module unit (C) of each phase has 2 remaining AC input terminals, and the first AC input of the three-phase third module unit (C) The second AC input terminal of the three-phase third module unit (C) constitutes another group of terminals, one of which is connected to a common neutral point, and the other group of terminals respectively Connected to one end of the three bridge arm inductances, and the other ends of the two bridge arm inductances on each phase Connected, and respectively connected to the input terminal of the three-phase power grid through one of the three high-frequency filters. At the same time, the common neutral point in the first set of star connections and the common neutral point in the second set of star connections They are respectively connected to the two ends of the DC capacitor to form a double star connection. 5. A control strategy for a cascaded multilevel rectifier with a common high voltage DC bus, characterized in that the steps of the control strategy for a cascade multilevel rectifier with a common high voltage DC bus are as follows: (1) The output side DC voltage of the cascaded multi-level rectifier of the bus is sampled to obtain N +2 output side DC voltage signals Uol, Uo2 and UoBl, UoB2... UoBN; (2) Use the following formula to calculate N in step (1) +2 output-side DC voltage signals U0i, U02 and Zhan1#hou.. The average value U of the inner Pi. : 1 N +Σϋ ,+U) N ol j=] oBj o27 (3) Change the U in step (2). Given signal U with DC voltage. * After comparison, send it to PI voltage regulator to get PI voltage regulator output DC current signal amplitude Id; (4) Combine N+2 output side DC voltage signals U0i, U°2 and 1# in step (1) .. The inner channel is respectively given the signal U with the DC voltage. * After comparison, send it to PI voltage regulator to get PI voltage regulator output DC current signal amplitudes Idi, Id2 and IdBl&gt;IdB2... IdBN; The DC current signal amplitudes Idl, Id2 and IdBl, IdB2 in step ...'' dBN is respectively added to the DC current signal amplitude Id in step (2), and after the addition, the given DC current signal amplitude and 1*, several 2* and 31*, mother 2* are obtained.(^*, the DC current given signal amplitude Idl*, Id2* and IdBl*, IdB2*...'' dBN* is phase-locked with the sine signal with the same phase as the grid voltage obtained by using the phase-locked loop (PLL) Multiply to generate AC current given signals idl*, id2»DidBl*, idB2*... IdBN*; (6) Detect the grid voltage e(tk) and AC current i (tk) at the current tk time, and use the following formula to predict Values of AC current idl (tk+1), id2 (tk+ι) and idBl (tk+ι), idB2 (tk+1) ... idBN (tk+1) at tk+ι: RT /dl(tk+l)=(l-L worker );(tk)+^[(e(tk)-«di(tk))] RT pool (tk+ι) = (1- not working )i(tk)+^[(e(tk)-Md2(tk))] RT/dB!(tk+l)=(l- Morning tQ)] RT /dB2(tk+l)=(l -* ». f(tk)+*[(e(tkEdH2(tk))] A /dBN(tk+l)=(l-^ ^)i(tk)+i[(e(tk)-Mdi1N(tk))] L In the formula, Ll is the boost inductor; R is the internal resistance of the boost inductor Ll; Ts is the meter-like period; Udl (tk), Ud2 (tk) and UdBl (tk), UdB2 (tk)... UdBN(tk) They are the AC side voltage corresponding to the switching state of the rectifier applied during the kth sampling period; Using the following formula to calculate Udi (tk), Ud2 (tk) and UdBl (tk), UdB2 (tk) in step ... UdBN (tk): From 1 (tk)=S(H (tk)*% (t. ti(R(tk)=S(R(tk)*£/o2(tk) Shan old l(tk)=SdRI (also)* i/oHI(tk) ii(lB2(tk)=S(lB2(tk)* t/oR2(tk) «« « W(lBN(tk)=SdRN (tk) * i4BN(tk) where? Uol (tk)&gt; Uo2 (tk) and UoEl (tk), UoE2 (tk)... UoBN (tk) is the output of the rectifier at tk Side N+2 DC voltage signals, Sdl (tk), Sd2 (tk) and SdBl (tk), SdB2 (tk)... SdBN (tk) is the corresponding switch state of the rectifier at tk: 1 E)orL switch state is off Sdl (tk), Sd2 (tk) and SdE ), SdR2 (tk)...S dRK (tk) =. 0 or &lt;°The switch state is on -i,α)&lt;οπ. The switch state is off (8) Construct value functions gdl, gd2, and gdBl, gdB2···gdBN: gdi= I idi*-idi (tk+1) I gd2= I id2* -id2 (tk+1) I gdBl = I idBl^-idBl (tk+1) I gdB2 = I idB2*-idB2 (tk+1) I a «A gdBN= idBN*-idBN (tk+1) where idl*, id2¥tHdBl*, idB2*... IdBN* is the AC current given signal in step , idi (tk+1), id2 (tk+1) and idBl (tk+1), idB2 (tk+1) ... idBN (tk+1) is the predicted value of the AC current at time tk+1 in step (6); (9) through the value function gdl , Gd2, and gdBl, gdB2...gdBN evaluates each switching state of the rectifier, selects the switching state corresponding to the predicted current value that minimizes the cost function, and generates the driving signal Q1 «2 and Q1B1, Q1B2 of the switching device ... Q1BN; Invert the drive signals Q2 and Q1B2, Q1B3... Q1BN to obtain drive signals Q2B1, Q2B2... Q2BN; (10) Combine the drive signals Q1, Q2 and Q1B1, Q1B2 in step .. .Q1BN and the drive signal Q2B1 in step Q2B2... Q2BN is sent to the corresponding switching device to realize active power factor correction, sinusoidal input current, and realize balanced control of the cascaded N+2 output DC capacitor voltage. | [ZH CN111786579A]: 具有公共高压直流母线的级联多电平整流器及控制策略 技术领域 ［0001］本发明属于大功率高电压整流变换技术领域,特别涉及一种具有高电压公共直流 母线的级联多电平整流电路的系统实现方案。 背景技术 ［0002］ 近年来“多电平功率变换器(MultilevelConverter)在中高电压大功率变频调 速、有源电力滤波、高压直流(HVDC)输电和电力系统无功补偿等领域已得到越来越多的成 功应用。多电平变换器的基本电路拓扑结构大致可分为箝位型和单元级联型两大类。目前 在工业中得到广泛应用的由西门子公司或ABB公司生产的二极管箝位型三电平中高压变频 器，以及由罗宾康公司或利德华福公司生产的级联H桥中高压变频器就是这两类产品的典 型代表。在这两类中高压变频器中，无论哪一类，为了应用低耐压的电力电子器件完成高电 压的功率变换，均需在整流输入侧使用体积庞大、接线复杂、价格昂贵的工频移相变压器实 现电气隔离。这使其在许多工业场合的应用受到限制［1］。 ［0003］无工频变压器级联式多电平变换器［2］，近年来在电力电子技术领域受到广泛关 注，被认为是适用于新能源发电系统接入和满足分布式发电需求的智能电网接口或新一代 中高压变频器的理想实现方案。此类变换器用高频变压器取代传统级联式变换器中的工频 移相变压器实现电气隔离，当用于双向功率传输时，整流侧采用级联全控H桥多电平功率变 换器结构。当用于单向功率传输时，整流侧采用单向级联式多电平功率变换器结构(包括： 级联二极管+Boost整流电路，级联无桥整流电路，级联VIENNA整流电路等)。与传统中高压 变频器的整流级相比较，此类变换器整流级的实现方案取消了体积庞大、接线复杂、价格昂 贵的工频移相变压器，从而有效地减小了系统体积、重量和制造成本。然而，此类变换器也 有着明显的缺点，主要表现在:每一相N个级联整流模块会产生N组直流输出端，且由于输入 端不隔离，这N组整流模块直流输出端无法直接串联联接构成一对公共的高压直流输出母 线，因此无法直接用于高压直流输电，也无法直接与多电平逆变电路相连接，用于中高压变 频调速。为了实现公共的高压直流输出母线或实现对N组整流输出直流电压的灵活控制，N 组级联整流模块必须后接N个高频隔离DC-DC变换模块，从而导致整个系统拓扑结构和控制 方式的复杂性增加，工作效率降低。 发明内容 ［0004］本发明的目的是克服上述缺陷，提供一种新型高压大功率级联多电平单位功率因 数整流器实现方案，与传统中高压变频器整流级比较，本发明提供的新型级联整流器无需 在输入端使用工频移相变压器，可以使用低耐压的功率开关管完成高电压下的大功率单位 功率因数整流变换。与无工频变压器级联式多电平变换器比较，本发明提供的新型级联整 流器可在直流侧构成一对公共的高压直流母线，并可灵活的实现对各级联整流模块输出侧 电容电压的平衡控制。本发明提供的新型级联整流器主功率电路的拓扑结构简单，系统的 工作效率高，体积小，重量轻，成本低，在高压直流输电(HVDC)、大功率电力电子变压器，大 功率中高压交-直-交变频器等领域具有重要的应用价值。 [0005]为达到上述目的，本发明提供的具有公共高压直流母线的级联多电平整流器，包 括主功率电路，所述主功率电路包括高频滤波器、单相二极管整流桥、升压电感L和第一模 块单元(A)，其特征在于:所述第一模块单元(A)包括两个开关器件S1、S2，两个快恢复二极管 D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的第二模块单元(B)，N为正整 数，所述第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直流电容Cb，一个滤波电感Lb 和一个负载电阻Rb，所述开关器件SB1的第二接线端(b)与所述开关器件SB2的第一接线端(c) 相连，所述开关器件Sb2的第二接线端(d)与所述滤波电感Lb的一端相连，所述滤波电感Lb的 另一端与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第二接线端(f)相连,N个级 联的所述第二模块单元(B)，其中各个所述第二模块单元(B)中开关器件Sb1的第二接线端 (b)与下一个所述第二模块单元(B)中开关器件Sb1的第一接线端(a)相连，各个第二模块单 元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第二接线端(f)与下一个第二 模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端(e)相连， 级联的第一个第二模块单元(B)中所述开关器件Sb1的第一接线端(a)与并联连接的所述输 出直流电容Cb和所述负载电阻Rb的第一接线端(e)及所述开关器件S1的第二接线端(n)相 连,所述开关器件S1的第一接线端(m)与所述快恢复二极管D1的阳极相连，所述快恢复二极 管D1的阴极与并联连接的所述输出直流电容C1和所述负载电阻R1的一端相连，并联连接的 所述输出直流电容C1和所述负载电阻R1的另一端与级联的第一个所述第二模块单元(B)中 并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端(e)相连，所述开关器件S1 的第一接线端(m)与所述升压电感L的一端相连，所述升压电感L的另一端与所述单相二极 管整流桥的整流输出正端相连，所述开关器件S2的第一接线端(m)与级联的第N个所述第二 模块单元(B)中所述开关器件Sb1的第二接线端(b)相连，级联的第N个所述第二模块单元(B) 中并联连接的所述输出直流电容Cb和所述负载电阻Rb的第二接线端(f)与并联连接的所述 输出直流电容C2和所述负载电阻R2的一端相连，并联连接的所述输出直流电容C2和所述负 载电阻R2的另一端与所述快恢复二极管D2的阳极相连，所述开关器件S2的第二接线端(n)与 所述快恢复二极管D2的阴极及所述单相二极管整流桥的整流输出负端相连，所述单相二极 管整流桥的交流输入端经所述高频滤波器串联接入交流电网。 [0006]为达到上述目的，本发明提供的采用具有公共高压直流母线的级联多电平整流器 构成的具有公共高压直流母线的级联多电平三相星接整流器，包括三相主功率电路，其特 征在于:所述三相主功率电路包括三个高频滤波器和三个第三模块单元(C),所述第三模块 单元(C)包括单相二极管整流桥、升压电感L和第一模块单元(A)，所述第一模块单元(A)包 括两个开关器件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、 R2和N个级联的第二模块单元(B),N为正整数，所述第二模块单元(B)包括两个开关器件Sb1、 Sb2,一个输出直流电容Cb,一个滤波电感Lb和一个负载电阻Rb,所述开关器件Sb1的第二接线 端(b)与所述开关器件SB2的第一接线端(c)相连，所述开关器件SB2的第二接线端(d)与所述 滤波电感Lb的一端相连，所述滤波电感Lb的另一端与并联连接的所述输出直流电容Cb和所 述负载电阻Rb的第二接线端(f)相连,N个级联的所述第二模块单元(B),其中各个所述第二 模块单元(B)中开关器件Sb1的第二接线端(b)与下一个所述第二模块单元(B)中开关器件 Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述 负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的所述输出直流电容Cb 和所述负载电阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中所述开关器件 Sb1的第一接线端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端 (e)及所述开关器件S1的第二接线端(n)相连,所述开关器件S1的第一接线端(m)与所述快恢 复二极管D1的阳极相连，所述快恢复二极管D1的阴极与并联连接的所述输出直流电容C1和 所述负载电阻R1的一端相连，并联连接的所述输出直流电容C1和所述负载电阻R1的另一端 与级联的第一个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻 Rb的第一接线端(e)相连，所述开关器件S1的第一接线端(m)与所述升压电感L的一端相连， 所述升压电感L的另一端与所述单相二极管整流桥的整流输出正端相连，所述开关器件S2 的第一接线端(m)与级联的第N个所述第二模块单元(B)中所述开关器件Sb1的第二接线端 (b)相连，级联的第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负 载电阻Rb的第二接线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2的一端相 连，并联连接的所述输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二极管D2的 阳极相连，所述开关器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述单相二极 管整流桥的整流输出负端相连，每相所述第三模块单元(C)剩余2个交流输入端，三相所述 第三模块单元(C)的第一交流输入端构成一组接线端，三相所述第三模块单元(C)的第二交 流输入端构成另一组接线端，其中一组接线端连接到一个公共的中性点上，另外一组接线 端分别与三个所述高频滤波器串联，接入三相电网，构成星形连接。 [0007]为达到上述目的，本发明提供的采用具有公共高压直流母线的级联多电平整流器 构成的具有公共高压直流母线的级联多电平三相角接整流器，包括三相主功率电路，其特 征在于:所述三相主功率电路包括三个高频滤波器和三个第三模块单元(C)，所述第三模块 单元(C)包括单相二极管整流桥、升压电感L和第一模块单元(A)，所述第一模块单元(A)包 括两个开关器件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、 R2和N个级联的第二模块单元(B)，N为正整数，所述第二模块单元(B)包括两个开关器件Sb1、 Sb2,一个输出直流电容Cb，一个滤波电感Lb和一个负载电阻Rb，所述开关器件Sb1的第二接线 端(b)与所述开关器件SB2的第一接线端(C)相连，所述开关器件SB2的第二接线端(d)与所述 滤波电感Lb的一端相连，所述滤波电感Lb的另一端与并联连接的所述输出直流电容Cb和所 述负载电阻Rb的第二接线端(f)相连,N个级联的所述第二模块单元(B),其中各个所述第二 模块单元(B)中开关器件Sb1的第二接线端(b)与下一个所述第二模块单元(B)中开关器件 Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的所述输出直流电容Cb和所述 负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的所述输出直流电容Cb 和所述负载电阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中所述开关器件 Sb1的第一接线端(a)与并联连接的所述输出直流电容Cb和所述负载电阻Rb的第一接线端 (e)及所述开关器件S1的第二接线端(n)相连,所述开关器件S1的第一接线端(m)与所述快恢 复二极管D1的阳极相连，所述快恢复二极管D1的阴极与并联连接的所述输出直流电容C1和 所述负载电阻R1的一端相连，并联连接的所述输出直流电容C1和所述负载电阻R1的另一端 与级联的第一个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负载电阻 Rb的第一接线端(e)相连，所述开关器件S1的第一接线端(m)与所述升压电感L的一端相连, 所述升压电感L的另一端与所述单相二极管整流桥的整流输出正端相连，所述开关器件S2 的第一接线端(m)与级联的第N个所述第二模块单元(B)中所述开关器件Sbi的第二接线端 (b)相连，级联的第N个所述第二模块单元(B)中并联连接的所述输出直流电容Cb和所述负 载电阻Rb的第二接线端(f)与并联连接的所述输出直流电容C2和所述负载电阻R2的一端相 连，并联连接的所述输出直流电容C2和所述负载电阻R2的另一端与所述快恢复二极管D2的 阳极相连，所述开关器件S2的第二接线端(n)与所述快恢复二极管D2的阴极及所述单相二极 管整流桥的整流输出负端相连，每相所述第三模块单元(C)剩余2个交流输入端，三相所述 第三模块单元(C)的第一交流输入端构成一组接线端，三相所述第三模块单元(C)的第二交 流输入端构成另一组接线端，其中一组接线端分别经三个所述高频滤波器接至三相电网输 入端，另一组接线端依次连接至三相电网中的下一相输入端，构成角形连接。 [0008]为达到上述目的，本发明提供的采用具有公共高压直流母线的级联多电平整流器 构成的具有公共高压直流母线的级联多电平三相双星接整流器，包括三相主功率电路，其 特征在于:所述三相主功率电路包括三个高频滤波器、六个桥臂电感、一个直流电容和六个 第三模块单元(C)，六个所述第三模块单元(C)构成对接的两组星形连接，即在每组星形连 接中，所述第三模块单元(C)包括单相二极管整流桥、升压电感L和第一模块单元(A)，所述 第一模块单元(A)包括两个开关器件S1、S2，两个快恢复二极管D1、D2，两个输出直流电容C1、 C2,两个负载电阻R1、R2和N个级联的第二模块单元(B)，N为正整数，所述第二模块单元(B)包 括两个开关器件Sb1、Sb2,一个输出直流电容Cb，一个滤波电感Lb和一个负载电阻Rb，所述开 关器件SB1的第二接线端(b)与所述开关器件SB2的第一接线端(c)相连，所述开关器件SB2的 第二接线端(d)与所述滤波电感Lb的一端相连，所述滤波电感Lb的另一端与并联连接的所述 输出直流电容Cb和所述负载电阻Rb的第二接线端(f)相连,N个级联的所述第二模块单元 (B),其中各个所述第二模块单元(B)中开关器件Sb1的第二接线端(b)与下一个所述第二模 块单元(B)中开关器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的所述 输出直流电容Cb和所述负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接 的所述输出直流电容Cb和所述负载电阻Rb的第一接线端(e)相连，级联的第一个第二模块单 元(B)中所述开关器件Sb1的第一接线端(a)与并联连接的所述输出直流电容Cb和所述负载 电阻Rb的第一接线端(e)及所述开关器件S1的第二接线端(n)相连,所述开关器件S1的第一 接线端(m)与所述快恢复二极管D1的阳极相连，所述快恢复二极管D1的阴极与并联连接的所 述输出直流电容C1和所述负载电阻R1的一端相连，并联连接的所述输出直流电容C1和所述 负载电阻R1的另一端与级联的第一个所述第二模块单元(B)中并联连接的所述输出直流电 容Cb和所述负载电阻Rb的第一接线端(e)相连，所述开关器件S1的第一接线端(m)与所述升 压电感L的一端相连，所述升压电感L的另一端与所述单相二极管整流桥的整流输出正端相 连，所述开关器件S2的第一接线端(m)与级联的第N个所述第二模块单元(B)中所述开关器 件Sb1的第二接线端(b)相连，级联的第N个所述第二模块单元(B)中并联连接的所述输出直 流电容Cb和所述负载电阻Rb的第二接线端(f)与并联连接的所述输出直流电容C2和所述负 载电阻R2的一端相连，并联连接的所述输出直流电容C2和所述负载电阻R2的另一端与所述 快恢复二极管D2的阳极相连，所述开关器件S2的第二接线端(n)与所述快恢复二极管D2的阴 极及所述单相二极管整流桥的整流输出负端相连，每相所述第三模块单元(C)剩余2个交流 输入端，三相所述第三模块单元(C)的第一交流输入端构成一组接线端，三相所述第三模块 单元(C)的第二交流输入端构成另一组接线端，其中一组接线端连接到一个公共中性点，另 CN 111786579 A 说 明 书 一组接线端分别与三个所述桥臂电感的一端相连，而在每相桥臂上的两个所述桥臂电感的 另一端各自相连,并分别经三个所述高频滤波器之一接至三相电网输入端，同时，第一组星 形连接中的公共中性点和第二组星形连接中的公共中性点分别与所述直流电容的两端相 连，构成双星形连接。 [0009]为达到上述目的，本发明提供的一种具有公共高压直流母线的级联多电平整流器 的控制策略，其特征在于，具有公共高压直流母线的级联多电平整流器的控制策略步骤如 下： [0010] (1)对具有公共高压直流母线的级联多电平整流器的输出侧直流电压进行采样， 得到N+2个输出侧直流电压信号Uol、U02和UoBl、U°B2…UoBN ； [0011] (2)利用下式计算步骤⑴中的N+2个输出侧直流电压信号U01、U°2和U°B1、 UoB2. . .UoBN的平均值Uo： N 「00121 ίΛ&gt;=----(U + Σ U ,+U ) LUU」 n + 公 ol oBj o2 [0013] (3)将步骤(2)中的U。与直流电压给定信号U。*比较后送入PI电压调节器，得到PI电 压调节器输出直流电流信号幅值Id； [0014] (4)将步骤⑴中的N+2个输出侧直流电压信号U0i、U°2和U°Bi、U°B2...U°BN分别与直 流电压给定信号U。*比较后送入ΡΙ电压调节器，得到ΡΙ电压调节器输出直流电流信号幅值 Idl&gt;Id2iBIdBl&gt;IdB2. . .IdBN； [0015] ⑸将步骤(4)中直流电流信号幅值Idl、Id2和IdBl、IdB2. .」dBN分别与步骤⑵中的 直流电流信号幅值Id相加，相加后得到直流电流给定信号幅值Idl*、Id2¥HdBl*、IdB2* • . JdBN*,将直流电流给定信号幅值Idl*、Id2*和IdBl*、IdB2*..」dBN*与利用锁相环PLL (PhaseLockedloop)得到的和电网电压相位相同的正弦信号相乘，产生交流电流给定信号idi*、id2* 和idBl*、idB2*. . . idBN*； [0016] (6)检测当前tk时刻的电网电压e (tk)和交流电流i (tk),利用下式预测tk+i时刻交 流电流idl (tk+l)、id2 (tk+1)和idBl (tk+1)、idB2 (tk+1) . . . idBN (tk+1)的值： [0017] idi(tk+j)=(l - )i(tk)+ 广[(e(tk)-iidi(tk))] [0018] id2(tk&gt;i)=(l-')i(tk)+4 KMtk)』d2(tk))] Li RT T [0019] /dBi (tk+i )=(1 - [(e(tk)-i/(irn(tk))] L Li [0020] [0021]: » [0022] ?)£(tk)+ y- K^(tk)-ildBN(tk))] [0023] 式中，Li为升压也感；R为升压也感Li内阻；Ts为采样周期；Udi (tk)、Ud2 (tk)和UdBi (tk)、UdE2(tk) . ·・UdEN(tk)分别为整流器在第k个采样周期内应用开关状态所对应交流侧也 压； [0024] ⑺利用下式计算步骤⑹中的Udl (tk)、Ud2 (tk)和UdBl (tk)、UdB2 (tk) . . . UdBN (tk)： [0025] Udl (tk) = Sdi (tk) *Uoi (tk) [0026] Ud2 (tk) = Sd2 (tk) *Uo2 (tk) [0027] UdBl (tk) = SdBl (tk) *UoBl (tk) [0028] UdB2 (tk) = SdB2 (tk) *UoB2 (tk) [0029]: « [0030] UdBN (tk) = SdBN (tk) *UoBN (tk) [0031] 式中,Uol (tk) &gt;Uo2 (tk)和U°B1 (tk)、U0B2 (tk) . . .UoBN(tk)是tk时刻整流器输出侧N+2个 直流电压信号，Sdl (tk)、Sd2 (tk)和SdBl (tk)、SdB2 (tk) . . . SdBN (tk)是tk时刻整流器对应的开关 1 且开关状态为关断 状态：Sdl (tk)、Sd2(tk)和 SdBl (tk)、SdB2 (tk)„,S dBX (tk) 10 i(tk) &gt; 0 或者 且开关状态为导通 -1 且开关状态为关断 [0032] (8)构造价值函数gdl、gd2、和gdBl、gdB2. . . gdBN： [0033] gdi= I idi*-idi (tk+i) [0034] gd2= I id2*-id2 (tk+i) [0035] gdBi= I idBi*-idBi (tk+i) [0036] gdB2= I idB2*-idB2 (tk+1) [0037]: a [0038] gdBN= I idBN*-idBN (tk+1) [0039] 式中，1(11*E2*和1(^*、1(«2*..(^*为步骤(5)中的交流电流给定信号，idi (tk+1)、 id2 (tk+1)和idBl (tk+1)、idB2 (tk+1) ... idBN (tk+1)为步骤(6)中 tk+1 时刻交流电流预测值； [0040] ⑼通过价值函数gdl、gd2、和gdBl、gdB2. . . gdBN对整流器的每一个开关状态进行评 估,选出使得价值函数最小的预测电流值所对应的开关状态，生成开关器件的驱动信号Q1、 Q2和Q1B1、Q1B2. . .Q1BN；将驱动信号Q2和Q1B2、Q1B3. . .Q1BN取反后得到驱动信号Q2B1、Q2B2. . .Q2BN； [0041] (10)将步骤(9)中的驱动信号Qi、Q2和Qibi、Qib2...Qibn以及步骤(9)中的驱动信号 Q2B1 «2Β2 . · . Q2BN送给对应的开关器件，实现有源功率因数校正，使输入电流正弦化，同时实 现对级联的N+2个输出直流电容电压的均衡控制。 [0042]本发明具有公共高压直流母线的级联多电平整流器的优点和积极效果在于：与传 统中高压变频器整流级比较,本发明提供的新型级联整流器无需在输入端使用工频移相变 压器,可以使用低耐压的功率开关管完成高电压下的大功率单位功率因数整流变换。与无 工频变压器级联式多电平变换器比较，本发明提供的新型级联整流器可在直流侧构成一对 公共的高压直流母线，并可灵活的实现对各级联整流模块输出侧电容电压的平衡控制。本 发明提供的新型级联整流器主功率电路的拓扑结构简单，系统的工作效率高，体积小，重量 轻,成本低，在高压直流输电(HVDC)、大功率电力电子变压器，大功率中高压交-直-交变频 器等领域具有重要的应用价值。 [0043]下面将结合实施例参照附图进行详细说明。 附图说明 [0044]图1是本发明具有公共高压直流母线的级联多电平整流器及控制策略中第二模块 单元(B)的电路图； [0045]图2是本发明具有公共高压直流母线的级联多电平整流器及控制策略中第一模块 单元(A)电路图； [0046]图3是本发明具有公共高压直流母线的级联多电平整流器及控制策略中第三模块 单元(C)电路图； [0047]图4是本发明具有公共高压直流母线的级联多电平整流器及控制策略的三相星接 整流器的电路图； [0048]图5是本发明具有公共高压直流母线的级联多电平整流器及控制策略的三相角接 整流器的电路图； [0049]图6是本发明具有公共高压直流母线的级联多电平整流器及控制策略的三相双星 接整流器的电路图； [0050]图7是本发明具有公共高压直流母线的级联多电平整流器及控制策略的控制策略 图； [0051]图8是本发明具有公共高压直流母线的级联多电平整流器及控制策略的流程图； [0052]图9是本发明具有公共高压直流母线的级联多电平整流器及控制策略的整体框 图； 具体实施方式 [0053]下面结合附图对本发明的实施方式和工作原理做进一步的描述： [0054] 参照图1和图2,一种具有公共高压直流母线的级联多电平整流器，包括主功率电 路，主功率电路包括高频滤波器、单相二极管整流桥、升压电感L和第一模块单元(A)，第一 模块单元(A)包括两个开关器件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两 个负载电阻R1、R2和N个级联的第二模块单元(B)，N为正整数，第二模块单元(B)包括两个开 关器件Sb1、Sb2,一个输出直流电容Cb，一个滤波电感Lb和一个负载电阻Rb，开关器件Sb1的第 二接线端(b)与开关器件SB2的第一接线端(C)相连，开关器件SB2的第二接线端(d)与滤波电 感Lb的一端相连，滤波电感Lb的另一端与并联连接的输出直流电容Cb和负载电阻Rb的第二 接线端(f)相连,N个级联的第二模块单元(B),其中各个第二模块单元(B)中开关器件Sb1的 第二接线端(b)与下一个第二模块单元(B)中开关器件Sb1的第一接线端(a)相连，各个第二 模块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)与下一个第二模 块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第一接线端(e)相连，级联的第一 个第二模块单元(B)中开关器件Sb1的第一接线端(a)与并联连接的输出直流电容Cb和负载 电阻Rb的第一接线端(e)及开关器件S1的第二接线端(n)相连，开关器件S1的第一接线端(m) 与快恢复二极管D1的阳极相连,快恢复二极管D1的阴极与并联连接的输出直流电容C1和负 载电阻R1的一端相连，并联连接的输出直流电容C1和负载电阻R1的另一端与级联的第一个 第二模块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第一接线端(e)相连，开关 器件S1的第一接线端(m)与升压电感L的一端相连，升压电感L的另一端与单相二极管整流 桥的整流输出正端相连，开关器件S2的第一接线端(m)与级联的第N个第二模块单元(B)中 开关器件Sbi的第二接线端(b)相连，级联的第N个第二模块单元(B)中并联连接的输出直流 电容Cb和负载电阻Rb的第二接线端(f)与并联连接的输出直流电容C2和负载电阻R2的一端 相连，并联连接的输出直流电容C2和负载电阻R2的另一端与快恢复二极管D2的阳极相连，开 关器件S2的第二接线端(n)与快恢复二极管D2的阴极及单相二极管整流桥的整流输出负端 相连，单相二极管整流桥的交流输入端经高频滤波器串联接入交流电网。 [0055] 参照图1、图2、图3和图4,一种采用具有公共高压直流母线的级联多电平整流器构 成的具有公共高压直流母线的级联多电平三相星接整流器，包括三相主功率电路，三相主 功率电路包括三个高频滤波器和三个第三模块单元(C)，第三模块单元(C)包括单相二极管 整流桥、升压电感L和第一模块单元(A)，第一模块单元(A)包括两个开关器件S1、S2,两个快 恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的第二模块单元 (B)，N为正整数，第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直流电容Cb，一个滤 波电感Lb和一个负载电阻Rb，开关器件Sb1的第二接线端(b)与开关器件Sb2的第一接线端(c) 相连，开关器件Sb2的第二接线端(d)与滤波电感Lb的一端相连，滤波电感Lb的另一端与并联 连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)相连,N个级联的第二模块单元(B), 其中各个第二模块单元(B)中开关器件Sb1的第二接线端⑹与下一个第二模块单元(B)中开 关器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的输出直流电容Cb和负 载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的输出直流电容Cb和负载 电阻Rb的第一接线端(e)相连,级联的第一个第二模块单元(B)中开关器件Sb1的第一接线端 (a)与并联连接的输出直流电容Cb和负载电阻Rb的第一接线端(e)及开关器件S1的第二接线 端(n)相连，开关器件S1的第一接线端(m)与快恢复二极管D1的阳极相连,快恢复二极管D1的 阴极与并联连接的输出直流电容C1和负载电阻R1的一端相连，并联连接的输出直流电容C1 和负载电阻R1的另一端与级联的第一个第二模块单元(B)中并联连接的输出直流电容Cb和 负载电阻Rb的第一接线端(e)相连，开关器件S1的第一接线端(m)与升压电感L的一端相连, 升压电感L的另一端与单相二极管整流桥的整流输出正端相连，开关器件S2的第一接线端 (m)与级联的第N个第二模块单元(B)中开关器件Sb1的第二接线端(b)相连，级联的第N个第 二模块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)与并联连接的 输出直流电容C2和负载电阻R2的一端相连，并联连接的输出直流电容C2和负载电阻R2的另 一端与快恢复二极管D2的阳极相连，开关器件S2的第二接线端(n)与快恢复二极管D2的阴极 及单相二极管整流桥的整流输出负端相连，每相第三模块单元(C)剩余2个交流输入端，三 相第三模块单元(C)的第一交流输入端构成一组接线端，三相第三模块单元(C)的第二交流 输入端构成另一组接线端，其中一组接线端连接到一个公共的中性点上，另外一组接线端 分别与三个高频滤波器串联,接入三相电网，构成星形连接。 [0056] 参照图1、图2、图3和图5,一种采用具有公共高压直流母线的级联多电平整流器构 成的具有公共高压直流母线的级联多电平三相角接整流器，包括三相主功率电路,三相主 功率电路包括三个高频滤波器和三个第三模块单元(C),第三模块单元(C)包括单相二极管 整流桥、升压电感L和第一模块单元(A),第一模块单元(A)包括两个开关器件S1、S2,两个快 恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的第二模块单元 (B),N为正整数,第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直流电容Cb,一个滤 波电感Lb和一个负载电阻Rb,开关器件Sb1的第二接线端(b)与开关器件Sb2的第一接线端(c) 相连，开关器件Sb2的第二接线端(d)与滤波电感Lb的一端相连，滤波电感Lb的另一端与并联 连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)相连，N个级联的第二模块单元(B)， 其中各个第二模块单元(B)中开关器件Sb1的第二接线端⑹与下一个第二模块单元(B)中开 关器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的输出直流电容Cb和负 载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的输出直流电容Cb和负载 电阻Rb的第一接线端(e)相连，级联的第一个第二模块单元(B)中开关器件Sb1的第一接线端 (a)与并联连接的输出直流电容Cb和负载电阻Rb的第一接线端(e)及开关器件S1的第二接线 端(n)相连，开关器件S1的第一接线端(m)与快恢复二极管D1的阳极相连，快恢复二极管D1的 阴极与并联连接的输出直流电容C1和负载电阻R1的一端相连，并联连接的输出直流电容C1 和负载电阻R1的另一端与级联的第一个第二模块单元(B)中并联连接的输出直流电容Cb和 负载电阻Rb的第一接线端(e)相连，开关器件S1的第一接线端(m)与升压电感L的一端相连， 升压电感L的另一端与单相二极管整流桥的整流输出正端相连，开关器件S2的第一接线端 (m)与级联的第N个第二模块单元(B)中开关器件Sb1的第二接线端(b)相连，级联的第N个第 二模块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)与并联连接的 输出直流电容C2和负载电阻R2的一端相连，并联连接的输出直流电容C2和负载电阻R2的另 一端与快恢复二极管D2的阳极相连，开关器件S2的第二接线端(n)与快恢复二极管D2的阴极 及单相二极管整流桥的整流输出负端相连，每相第三模块单元(C)剩余2个交流输入端，三 相第三模块单元(C)的第一交流输入端构成一组接线端，三相第三模块单元(C)的第二交流 输入端构成另一组接线端，其中一组接线端分别经三个高频滤波器接至三相电网输入端， 另一组接线端依次连接至三相电网中的下一相输入端，构成角形连接。 [0057] 参照图1、图2、图3和图6,一种采用具有公共高压直流母线的级联多电平整流器构 成的具有公共高压直流母线的级联多电平三相双星接整流器，包括三相主功率电路，三相 主功率电路包括三个高频滤波器、六个桥臂电感、一个直流电容和六个第三模块单元(C)， 六个第三模块单元(C)构成对接的两组星形连接，即在每组星形连接中，第三模块单元(C) 包括单相二极管整流桥、升压电感L和第一模块单元(A)，第一模块单元(A)包括两个开关器 件S1、S2,两个快恢复二极管D1、D2,两个输出直流电容C1、C2,两个负载电阻R1、R2和N个级联的 第二模块单元(B)，N为正整数，第二模块单元(B)包括两个开关器件Sb1、Sb2,一个输出直流 电容Cb，一个滤波电感Lb和一个负载电阻Rb，开关器件Sb1的第二接线端(b)与开关器件Sb2的 第一接线端(c)相连，开关器件Sb2的第二接线端(d)与滤波电感Lb的一端相连，滤波电感Lb 的另一端与并联连接的输出直流电容Cb和负载电阻Rb的第二接线端(f)相连,N个级联的第 二模块单元(B)，其中各个第二模块单元(B)中开关器件Sb1的第二接线端(b)与下一个第二 模块单元(B)中开关器件Sb1的第一接线端(a)相连，各个第二模块单元(B)中并联连接的输 出直流电容Cb和负载电阻Rb的第二接线端(f)与下一个第二模块单元(B)中并联连接的输出 直流电容Cb和负载电阻Rb的第一接线端(e)相连,级联的第一个第二模块单元(B)中开关器 件Sb1的第一接线端(a)与并联连接的输出直流电容Cb和负载电阻Rb的第一接线端(e)及开 关器件S1的第二接线端(n)相连，开关器件S1的第一接线端(m)与快恢复二极管D1的阳极相 连,快恢复二极管D1的阴极与并联连接的输出直流电容C1和负载电阻R1的一端相连,并联连 接的输出直流电容C1和负载电阻R1的另一端与级联的第一个第二模块单元(B)中并联连接 的输出直流电容Cb和负载电阻Rb的第一接线端(e)相连，开关器件S1的第一接线端(m)与升 压电感L的一端相连，升压电感L的另一端与单相二极管整流桥的整流输出正端相连，开关 器件S2的第一接线端(m)与级联的第N个第二模块单元(B)中开关器件Sbi的第二接线端(b) 相连，级联的第N个第二模块单元(B)中并联连接的输出直流电容Cb和负载电阻Rb的第二接 线端⑹与并联连接的输出直流电容C2和负载电阻R2的一端相连，并联连接的输出直流电容 C2和负载电阻R2的另一端与快恢复二极管D2的阳极相连，开关器件S2的第二接线端(η)与快 恢复二极管D2的阴极及单相二极管整流桥的整流输出负端相连，每相第三模块单元(C)剩 余2个交流输入端，三相第三模块单元(C)的第一交流输入端构成一组接线端，三相第三模 块单元(C)的第二交流输入端构成另一组接线端,其中一组接线端连接到一个公共中性点， 另一组接线端分别与三个桥臂电感的一端相连,而在每相桥臂上的两个桥臂电感的另一端 各自相连,并分别经三个高频滤波器之一接至三相电网输入端，同时,第一组星形连接中的 公共中性点和第二组星形连接中的公共中性点分别与直流电容的两端相连,构成双星形连 接。 [0058] 4、参照图7、图8和图9, 一种具有公共高压直流母线的级联多电平整流器的控制策 略,控制策略步骤如下： [0059] (1)对具有公共高压直流母线的级联多电平整流器的输出侧直流电压进行采样， 得到Ν+2个输出侧直流电压信号Uol、U02和UoBl、U°B2…UoBN ； [0060] (2)利用下式计算步骤⑴中的N+2个输出侧直流电压信号U°i、U°2和U°bi、 UoB2. . .UoBN的平均值Uo： ί N [0061] ^o=——(t/ + R.+U J TV+ 2 01 j=[ oBj 02 [0062] (3)将步骤(2)中的U。与直流电压给定信号U。*比较后送入PI电压调节器，得到PI电 压调节器输出直流电流信号幅值Id； [0063] (4)将步骤⑴中的N+2个输出侧直流电压信号U0i、U°2和U°Bi、U°B2...U°BN分别与直 流电压给定信号U。*比较后送入ΡΙ电压调节器，得到ΡΙ电压调节器输出直流电流信号幅值 Idl&gt;Id2iBIdBl&gt;IdB2. . .IdBN； [0064] ⑸将步骤(4)中直流电流信号幅值Idl、Id2和IdBl、IdB2. .」dBN分别与步骤⑵中的 直流电流信号幅值Id相加，相加后得到直流电流给定信号幅值Idl*、Id2¥HdBl*、IdB2* • . JdBN*,将直流电流给定信号幅值Idl*、Id2*和IdBl*、IdB2*..」dBN*与利用锁相环PLL (PhaseLockedloop)得到的和电网电压相位相同的正弦信号相乘，产生交流电流给定信号idi*、id2* 和idBl*、idB2*. . . idBN*； [0065] (6)检测当前tk时刻的电网电压e (tk)和交流电流i (tk),利用下式预测tk+i时刻交 流电流idl (tk+l)、id2 (tk+1)和idBl (tk+1)、idB2 (tk+1) . . . idBN (tk+1)的值： [0066] RT /dl(tk+l)=(l - L 工 如 &amp;))]A [0067] RT /d2(tk+l)=(l-^ Mtk吓[(e(tk)』d2(tk))] A [0068] RT L ί RTT [0069] idB2(tki 1)=(1--- )?(tk)^~~- [(^(tk)-^dB2(tk))] L]L [0070]: . RTT [0071 ] idBN(tk+l)=(l--- )z(tk)+—— [(e(tk)-Wd[3N(tk))] L[L] [0072] 式中，Li为升压电感；R为升压电感Li内阻；Ts为采样周期；Udi (tk)、Ud2 (tk)和UdBi (tk)、UdB2 (tk) . . .UdBN (tk)分别为整流器在第k个采样周期内应用开关状态所对应交流侧电 压； [0073] ⑺利用下式计算步骤⑹中的Udl (tk)、Ud2 (tk)和UdBl (tk)、UdB2 (tk) . . . UdBN (tk)： [0074] Udl (tk) = Sdi (tk) *Uoi (tk) [0075] Ud2 (tk) = Sd2 (tk) *Uo2 (tk) [0076] UdBl (tk) = SdBl (tk) *UoBl (tk) [0077] UdB2 (tk) = SdB2 (tk) *UoB2 (tk) [0078]: . [0079] UdBN (tk) = SdBN (tk) *UoBN (tk) [0080] 式中,Uol (tk) &gt;Uo2 (tk)和U°B1 (tk)、U0B2 (tk) . . .UoBN(tk)是tk时刻整流器输出侧N+2个 直流电压信号，Sdl (tk)、Sd2 (tk)和SdBl (tk)、SdB2 (tk) . . . SdBN (tk)是tk时刻整流器对应的开关 i(tk)〉orui：关状态为关断 状态：Sdl (tk)、Sd2(tk)和 SdBl (tk)、SdB2(tk)...S dBN (tk) = - 0 f(tk)&gt;0或者 &lt; Oil开关状态为导通 -1 关状态为关断 [0081] (8)构造价值函数gdl、gd2、和gdBl、gdB2. . . gdBN： [0082] gdi= I idi*-idi (tk+i) [0083] gd2= ¦ id2*-id2 (tk+i) [0084] gdBi= ¦ idBi*-idBi (tk+i) [0085] gdB2= ¦ idB2*-idB2 (tk+1) [0086]: . [0087] gdBN= I idBN*-idBN (tk+1) [0088] 式中，1(11*E2*和1(^*、1(«2*..(^*为步骤(5)中的交流电流给定信号，idi (tk+1)、 id2 (tk+1)和idBl (tk+1)、idB2 (tk+1) ... idBN (tk+1)为步骤(6)中 tk+1 时刻交流电流预测值； [0089] ⑼通过价值函数gdl、gd2、和gdBl、gdB2. . . gdBN对整流器的每一个开关状态进行评 估,选出使得价值函数最小的预测电流值所对应的开关状态，生成开关器件的驱动信号Q1、 Q2和Q1B1、Q1B2. . .Q1BN；将驱动信号Q2和Q1B2、Q1B3. . .Q1BN取反后得到驱动信号Q2B1、Q2B2. . .Q2BN； [0090] (10)将步骤(9)中的驱动信号Qi、Q2和Qibi、Qib2...Qibn以及步骤(9)中的驱动信号 Q2B1 «2Β2 . · . Q2BN送给对应的开关器件，实现有源功率因数校正，使输入电流正弦化，同时实 现对级联的N+2个输出直流电容电压的均衡控制。 [0091]在本发明具有公共高压直流母线的级联单位功率因数整流器应用的其他实施例 中，所描述的三相星接、角接和三相双星接整流器，除了采用第三模块单元(C)外，也可以是 由第三模块单元(C)衍生出来的不同电路的组合。 [0092]所描述的具有公共高压直流母线的级联单位功率因数整流应用电路，可以简化应 用于大功率场合的电力电子整流器的电路拓扑结构，通过适当的控制策略可以提高系统的 工作效率，稳定且能平衡直流侧的电容电压，为后级的电能变换提供有利条件，在高压直流 传输、大功率电力电子变压器，大功率中高压交-直-交变频器等应用领域具有重要的应用 价值。 [0093]上面所述的实施例仅仅是对本发明的优选实施方式进行描述，并非对本发明的构 思和范围进行限定，在不脱离本发明设计方案前提下，本领域中普通工程技术人员对本发 明的技术方案做出的各种变型和改进，均应落入本发明的保护范围，本发明请求保护的技 术内容，已经全部记载在权利要求书中。 [EN CN111786579A]: Cascaded multi-level rectifier with a public high-voltage DC bus and control strategy Technical field [0001] The present invention belongs to the technical field of high-power high-voltage rectification and conversion, and in particular relates to a cascaded multi-level rectifier circuit with a high-voltage public DC bus System implementation plan. BACKGROUND OF THE INVENTION [0002] In recent years, "Multilevel Converter (MultilevelConverter) has been increasingly used in the fields of medium and high voltage and high power variable frequency speed regulation, active power filtering, high voltage direct current (HVDC) transmission and power system reactive power compensation. Many successful applications. The basic circuit topology of multilevel converters can be roughly divided into two categories: clamp type and unit cascade type. At present, diode clamps produced by Siemens or ABB are widely used in industry. Type three-level medium and high voltage inverters, as well as the cascaded H-bridge medium and high voltage inverters produced by Robincon Company or Lead Huafu Company, are typical representatives of these two types of products. In these two types of medium and high voltage inverters, Regardless of the type, in order to use low withstand voltage power electronic devices to complete high-voltage power conversion, it is necessary to use bulky, complicated wiring, and expensive power frequency phase-shifting transformers on the rectifier input side to achieve electrical isolation. The application of many industrial occasions is restricted [1]. [0003] Non-power frequency transformer cascaded multilevel converter [2], has received extensive attention in the field of power electronics in recent years, and is considered to be a smart grid suitable for new energy power generation systems to access and meet the needs of distributed power generation Interface or the ideal realization of a new generation of medium and high voltage inverters. This type of converter uses a high-frequency transformer to replace the power frequency phase-shifting transformer in the traditional cascaded converter to achieve electrical isolation. When used for bidirectional power transmission, the rectifier side adopts a cascaded fully-controlled H-bridge multilevel power converter structure. When used for unidirectional power transmission, the rectifier side adopts a unidirectional cascaded multilevel power converter structure (including: cascaded diode + Boost rectifier circuit, cascaded bridgeless rectifier circuit, cascaded VIENNA rectifier circuit, etc.). Compared with the rectification stage of the traditional medium and high voltage inverter, the realization of the rectification stage of this type of converter eliminates the bulky, complicated wiring, and expensive power frequency phase shifting transformer, thereby effectively reducing the system volume, weight and manufacturing cost. However, this type of converter also has obvious shortcomings, mainly in the following: N cascaded rectifier modules for each phase will generate N groups of DC output terminals, and because the input terminals are not isolated, the DC output terminals of these N groups of rectifier modules cannot be directly The series connection forms a pair of common high-voltage DC output buses, so it cannot be directly used for high-voltage DC transmission, nor can it be directly connected with a multi-level inverter circuit for medium and high voltage frequency conversion speed regulation. In order to realize a common high-voltage DC output bus or realize flexible control of N groups of rectified output DC voltage, N The group cascaded rectifier module must be followed by N high-frequency isolation DC-DC conversion modules, which leads to an increase in the complexity of the overall system topology and control mode, and a decrease in work efficiency. SUMMARY OF THE INVENTION [0004] The purpose of the present invention is to overcome the above-mentioned shortcomings and provide a new high-voltage high-power cascaded multi-level unity power factor rectifier implementation scheme. Compared with the rectifier stage of the traditional medium and high voltage inverter, the new cascade provided by the present invention The rectifier does not need to use a power frequency phase-shifting transformer at the input end, and can use a low withstand voltage power switch tube to complete the high-power unit power factor rectification conversion under high voltage. Compared with cascaded multilevel converters without power frequency transformers, the novel cascaded rectifier provided by the present invention can form a pair of common high-voltage DC buses on the DC side, and can flexibly realize the capacitance of the output side of the rectifier module Voltage balance control. The main power circuit of the novel cascaded rectifier provided by the present invention has a simple topological structure, high working efficiency, small size, light weight, and low cost. It is used in high-voltage direct current (HVDC) and high-power power electronic transformers. Power medium and high voltage AC-DC-AC inverters and other fields have important application value. [0005] In order to achieve the above objective, the cascaded multilevel rectifier with a common high-voltage DC bus provided by the present invention includes a main power circuit including a high-frequency filter, a single-phase diode rectifier bridge, and a boost inductor L and the first module unit (A), characterized in that: the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, Two load resistors R1, R2 and N cascaded second module units (B), N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, and an output DC capacitor Cb, A filter inductor Lb and a load resistor Rb, the second terminal (b) of the switching device SB1 is connected to the first terminal (c) of the switching device SB2, and the second terminal (c) of the switching device Sb2 d) Connected to one end of the filter inductance Lb, and the other end of the filter inductance Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel, N cascades The second module unit (B), wherein the second terminal (b) of the switching device Sb1 in each of the second module units (B) and the switching device Sb1 in the next second module unit (B) Connected to the first terminal (a), each second module The second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel in element (B) is connected to the output DC capacitor Cb and the load resistor in parallel in the next second module unit (B) The first terminal (e) of the load resistor Rb is connected, and the first terminal (a) of the switching device Sb1 in the first second module unit (B) of the cascade is connected to the output DC capacitor connected in parallel Cb is connected to the first terminal (e) of the load resistor Rb and the second terminal (n) of the switching device S1, and the first terminal (m) of the switching device S1 is connected to the fast recovery diode The anode of D1 is connected, the cathode of the fast recovery diode D1 is connected to one end of the output DC capacitor C1 and the load resistor R1 connected in parallel, and the other of the output DC capacitor C1 and the load resistor R1 connected in parallel One end is connected to the first terminal (e) of the output DC capacitor Cb and the load resistor Rb connected in parallel in the first cascaded second module unit (B), and the first terminal (e) of the switching device S1 A terminal (m) is connected to one end of the boost inductor L, and the other end of the boost inductor L is connected to the positive terminal of the rectified output of the single-phase diode rectifier bridge. The first connection of the switching device S2 The terminal (m) is connected to the second terminal (b) of the switching device Sb1 in the Nth second module unit (B) of the cascade, and the Nth second module unit (B) of the cascade ) The second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel is connected to one end of the output DC capacitor C2 and the load resistor R2 connected in parallel, and the output The other end of the DC capacitor C2 and the load resistor R2 is connected to the anode of the fast recovery diode D2, and the second terminal (n) of the switching device S2 is connected to the cathode of the fast recovery diode D2 and the single phase The negative end of the rectification output of the diode rectifier bridge is connected, and the AC input end of the single-phase diode rectifier bridge is connected to the AC power grid in series through the high frequency filter. [0006] In order to achieve the above objective, the present invention provides a cascaded multi-level three-phase star-connected rectifier with a common high-voltage DC bus composed of a cascaded multi-level rectifier with a common high-voltage DC bus, including a three-phase main power circuit , Characterized in that: the three-phase main power circuit includes three high-frequency filters and three third module units (C), the third module unit (C) includes a single-phase diode rectifier bridge, a boost inductor L And the first module unit (A), the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, and two load resistors R1 , R2 and N cascaded second module units (B), N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and A load resistor Rb, the second terminal (b) of the switching device Sb1 is connected to the first terminal (c) of the switching device SB2, and the second terminal (d) of the switching device SB2 is connected to the One end of the filter inductor Lb is connected, and the other end of the filter inductor Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel. The module unit (B), wherein the second terminal (b) of the switching device Sb1 in each of the second module units (B) and the switching device in the next second module unit (B) The first terminal (a) of Sb1 is connected, and the output DC capacitor Cb and the output DC capacitor Cb connected in parallel in each second module unit (B) The second terminal (f) of the load resistor Rb is connected to the first terminal (e) of the output DC capacitor Cb and the load resistor Rb connected in parallel in the next second module unit (B), which is cascaded The first terminal (a) of the switching device Sb1 in the first second module unit (B) is connected in parallel with the first terminal (e) of the output DC capacitor Cb and the load resistance Rb and the The second terminal (n) of the switching device S1 is connected, the first terminal (m) of the switching device S1 is connected with the anode of the fast recovery diode D1, and the cathode of the fast recovery diode D1 is connected in parallel with The output DC capacitor C1 is connected to one end of the load resistor R1, and the other end of the output DC capacitor C1 and the load resistor R1 connected in parallel is connected to the first second module unit (B) connected in parallel The output DC capacitor Cb connected in parallel is connected to the first terminal (e) of the load resistor Rb, and the first terminal (m) of the switching device S1 is connected to one end of the boost inductor L, The other end of the boost inductor L is connected to the positive end of the rectified output of the single-phase diode rectifier bridge, and the first terminal (m) of the switching device S2 is connected to the Nth second module unit in cascade connection. The second terminal (b) of the switching device Sb1 in (B) is connected, and the output DC capacitor Cb and the negative terminal connected in parallel in the Nth second module unit (B) in the cascade The second terminal (f) of the load resistor Rb is connected to one end of the output DC capacitor C2 and the load resistor R2 connected in parallel, and the other end of the output DC capacitor C2 and the load resistor R2 connected in parallel is connected to The anode of the fast recovery diode D2 is connected, and the second terminal (n) of the switching device S2 is connected to the cathode of the fast recovery diode D2 and the negative terminal of the rectification output of the single-phase diode rectifier bridge. The third module unit (C) has two remaining AC input terminals, the first AC input terminal of the three-phase third module unit (C) constitutes a set of terminals, and the three-phase third module unit (C) The second AC input terminal constitutes another set of terminals, one of which is connected to a common neutral point, and the other set of terminals are connected in series with the three high-frequency filters to connect to the three-phase power grid. Form a star connection. [0007] In order to achieve the above object, the present invention provides a cascaded multi-level three-phase corner rectifier with a common high-voltage DC bus composed of a cascaded multi-level rectifier with a common high-voltage DC bus, including a three-phase main power circuit , Characterized in that: the three-phase main power circuit includes three high-frequency filters and three third module units (C), and the third module unit (C) includes a single-phase diode rectifier bridge, a boost inductor L And the first module unit (A), the first module unit (A) includes two switching devices S1, S2, two fast recovery diodes D1, D2, two output DC capacitors C1, C2, and two load resistors R1 , R2 and N cascaded second module units (B), N is a positive integer, the second module unit (B) includes two switching devices Sb1, Sb2, an output DC capacitor Cb, a filter inductor Lb and A load resistor Rb, the second terminal (b) of the switching device Sb1 is connected to the first terminal (C) of the switching device SB2, and the second terminal (d) of the switching device SB2 is connected to the One end of the filter inductor Lb is connected, and the other end of the filter inductor Lb is connected to the second terminal (f) of the output DC capacitor Cb and the load resistor Rb connected in parallel. The module unit (B), wherein the second terminal (b) of the switching device Sb1 in each of the second module units (B) and the switching device in the next second module unit (B) The first terminal (a) of Sb1 is connected, and the second terminal (f) of the output DC capacitor Cb and
[ZH CN112436534A]: 一种级联H桥储能系统直流侧滤波电路 [EN CN112436534A]: Cascaded H-bridge energy storage system DC side filter circuit | [ZH CN112436534A]: 本发明的级联H桥储能系统直流侧滤波电路，H桥变流器的直流侧经直流侧滤波电路与电池组相连接；直流侧滤波电路由电容C1、电感L1、电容C2和电感L2组成，电容C1与电感L1串联构成LC串联谐振电路，电容C2与LC串联谐振电路相并联后的两端接于H桥变流器的直流侧，电池组的一端经电感L2接于LC串联谐振电路中电感L1所在一端，电池组的另一端接于LC串联谐振电路中电容C1所在一端。本发明的级联H桥储能系统直流侧滤波电路，通过将LC串联谐振电路的谐振频率设计为二倍工频，使得整个直流侧滤波电路能平滑储能电池电流，从而提高储能电池的循环寿命，降低电池剩余电量估算复杂度。 [EN CN112436534A]: The invention relates to a cascaded H-bridge energy storage system DC side filter circuit. A direct current side of an H-bridge converter is connected with a battery pack through A direct current sidefilter circuit; the direct current side filter circuit is composed of a capacitor C1, an inductor L1, a capacitor C2 and an inductor L2; the capacitor C1 and the inductor L1 are connected in series to form an LC series resonance circuit; the two ends, connected in parallel, of the capacitor C2 and the LC series resonance circuit are connected to the direct current side of the H-bridge converter;one end of the battery pack is connected with one end of the inductor L1 in the LC series resonance circuit through the inductor L2; and the other end of the battery pack is connected with one end ofthe capacitor C1 in the LC series resonance circuit. According to the cascaded H-bridge energy storage system DC side filter circuit, the resonant frequency of the LC series resonance circuit is designed to be double of the power frequency, so that the whole direct-current side filter circuit can smooth the current of the energy storage battery, the cycle life of the energy storage battery is prolonged, and the estimation complexity of the residual electric quantity of the battery is reduced. | CN112436534A | 2021-03-02 | CN202011294651A | 2020-11-18 | CN202011294651A, 2020-11-18 | CN112436534A: 2021-03-02 | SHANDONG WINDSUN ELECTRONICS SCIENCE & TECH CO LTD | REN QIGUANG XU CHUNHONG LI QIANG CHEN ZAOJUN LU XINZHONG SONG LINLIN RU XULI | H02J3/32: I H02J1/02: I H02M1/14: I H02M7/72: I H02M7/797: I | H02J1/02: I H02J3/32: I H02M1/14: I H02M7/72: I H02M7/797: I Y02B70/10: A |  |  | [ZH CN112436534A]: 1 .一种级联H桥储能系统直流侧滤波电路，级联H桥储能系统由若干H桥储能单元（3）级 联组成,H桥储能单元由H桥变流器（1）和电池组（2）组成,H桥变流器具有整流和逆变作用， 电池组用于存储电能，H桥变流器的交流侧接于交流电网上，H桥变流器的直流侧经直流侧 滤波电路与电池组相连接；其特征在于:所述直流侧滤波电路由电容C1、电感L1、电容C2和 电感L2组成，电容C1与电感L1串联构成LC串联谐振电路，LC串联谐振电路的谐振频率为交 流电网频率的二倍;电容C2与LC串联谐振电路相并联后的两端接于H桥变流器的直流侧，电 容C2用于吸收H桥变流器开关频率附近的高频谐波；电池组的一端经电感L2接于LC串联谐 振电路中电感L1所在一端，电池组的另一端接于LC串联谐振电路中电容C1所在一端，电感 L2用于进一步衰减由H桥变流器流向电池组的高频谐波电流。 2 .根据权利要求1所述的级联H桥储能系统直流侧滤波电路，其特征在于，储能状态时： 电能由交流电网流向电池组（2），H桥变流器（1）通过整流将交流电转化为直流电存储在电 池组中；放电状态时：电能由电池组流向交流电网，H桥变流器通过逆变将电池组存储的直 流电转化为交流电并输出至交流电网上。 3 .根据权利要求1或2所述的级联H桥储能系统直流侧滤波电路，其特征在于:设交流电 网的频率为f，则电容C1和电感L1的数值满足如下关系式： L1*C1=1/（4^f）2 （1） 式中，L1、C1分别为电感L1、电容C1的数值大小，f为交流电网频率。 4 .根据权利要求1或2所述的级联H桥储能系统直流侧滤波电路，其特征在于:所述交流 电网的频率为50Hz，每相中所级联的H桥储能单元⑶的个数为3个，电感L1、电容C1、电感L2 和电容C2 的数值分别为0.9mH、2800uF、0.8mH、1000uF。 [EN CN112436534A]: 1 .A cascaded H-bridge energy storage system DC side filter circuit, the cascaded H-bridge energy storage system is composed of a number of H-bridge energy storage units (3) cascaded, and the H-bridge energy storage unit is composed of an H-bridge converter (1) It is composed of battery pack (2). The H-bridge converter has rectification and inverter functions. The battery pack is used to store electric energy. The AC side of the H-bridge converter is connected to the AC power grid. The DC side of the H-bridge converter is connected to the AC power grid. The side filter circuit is connected to the battery pack; it is characterized in that: the DC side filter circuit is composed of a capacitor C1, an inductor L1, a capacitor C2, and an inductor L2. The capacitor C1 and the inductor L1 are connected in series to form an LC series resonant circuit. The resonant frequency is twice the frequency of the AC grid; the two ends of the capacitor C2 and the LC series resonant circuit are connected in parallel to the DC side of the H-bridge converter, and the capacitor C2 is used to absorb the high frequency near the switching frequency of the H-bridge converter Harmonic: One end of the battery pack is connected to the end of the LC series resonant circuit where the inductor L1 is located through the inductor L2, and the other end of the battery pack is connected to the end of the capacitor C1 in the LC series resonant circuit. The inductor L2 is used to further attenuate the H-bridge conversion The high-frequency harmonic current flowing from the device to the battery pack. 2 The DC side filter circuit of the cascaded H-bridge energy storage system according to claim 1, characterized in that, in the energy storage state: electric energy flows from the AC grid to the battery pack (2), and the H-bridge converter (1) is rectified Convert AC power to DC power and store it in the battery pack; in the discharging state: electric energy flows from the battery pack to the AC power grid, and the H-bridge converter converts the DC power stored in the battery pack into AC power and outputs it to the AC power grid through inverter. 3 The DC side filter circuit of the cascaded H-bridge energy storage system according to claim 1 or 2, characterized in that: assuming that the frequency of the AC power grid is f, the values of the capacitor C1 and the inductance L1 satisfy the following relationship: L1*C1=1/(4^f)2 (1) In the formula, L1 and C1 are the numerical values of the inductance L1 and the capacitor C1 respectively, and f is the frequency of the AC power grid. 4 The DC side filter circuit of the cascaded H-bridge energy storage system according to claim 1 or 2, characterized in that: the frequency of the AC power grid is 50 Hz, and the number of cascaded H-bridge energy storage units (3) in each phase The number is three, and the values of inductor L1, capacitor C1, inductor L2, and capacitor C2 are 0.9mH, 2800uF, 0.8mH, and 1000uF, respectively. | [ZH CN112436534A]: 一种级联H桥储能系统直流侧滤波电路 技术领域 [0001]本发明涉及高压储能电力电子设备领域，更具体的说，尤其涉及一种的级联H桥储 能系统直流侧滤波电路。 背景技术 [0002]高压级联H桥储能系统是一种新型的储能变流器。这种变流器通过H桥的级联拓扑 达到较高的交流侧输出电压，可与10kV、35kV高压等级电网直接相连省略了升压变压器，从 而提高了变流器的效率。与常规低压380V储能变流器相比，级联H桥结构每个功率单元直流 侧相互隔离，没有公共直流母线。因此从原理上分析可知，在交流侧功率稳定时，H桥单元直 流侧电流必然包含以电网电压频率二倍为主的高频谐波成分。二倍频及高频分量会使储能 电池寿命大打折扣，并且二倍频分量会对电池剩余电量估算带来挑战。为提高电池寿命和 电池剩余电量估算精度，需要在功率单元直流侧与储能电池之间增加滤波电路。 [0003]现有用于级联H桥直流侧滤波电路多为LC低通滤波电路或LC谐振电路。若采用LC 低通滤波电路，则截止频率需要低于二倍频分量，会造成滤波器体积增大，且不能很好滤除 二倍频分量。LC串联谐振电路虽然理论上可全部吸收特定频率谐波成分，但在实际应用中 当电网频率发生偏移，或谐振电感电容参数与标称参数存在误差时，LC串联谐振不能较好 的吸收为电网电压二倍频率的谐波成分。 发明内容 [0004]本发明为了克服上述技术问题的缺点，提供了一种级联H桥储能系统直流侧滤波 电路。 [0005]本发明的级联H桥储能系统直流侧滤波电路，级联H桥储能系统由若干H桥储能单 元级联组成，H桥储能单元由H桥变流器和电池组组成，H桥变流器具有整流和逆变作用，电 池组用于存储电能，H桥变流器的交流侧接于交流电网上，H桥变流器的直流侧经直流侧滤 波电路与电池组相连接;其特征在于:所述直流侧滤波电路由电容C1、电感L1、电容C2和电 感L2组成，电容C1与电感L1串联构成LC串联谐振电路，LC串联谐振电路的谐振频率为交流 电网频率的二倍；电容C2与LC串联谐振电路相并联后的两端接于H桥变流器的直流侧，电容 C2用于吸收H桥变流器开关频率附近的高频谐波；电池组的一端经电感L2接于LC串联谐振 电路中电感L1所在一端，电池组的另一端接于LC串联谐振电路中电容C1所在一端，电感L2 用于进一步衰减由H桥变流器流向电池组的高频谐波电流。 [0006]本发明的级联H桥储能系统直流侧滤波电路，储能状态时：电能由交流电网流向电 池组（2），H桥变流器（1）通过整流将交流电转化为直流电存储在电池组中；放电状态时：电 能由电池组流向交流电网，H桥变流器通过逆变将电池组存储的直流电转化为交流电并输 出至交流电网上。 [0007]本发明的级联H桥储能系统直流侧滤波电路，设交流电网的频率为f，则电容C1和 电感L1的数值满足如下关系式： L1*C1=1/（4nf）2 （1） 式中，L1、C1分别为电感L1、电容C1的数值大小，f为交流电网频率。 [0008]本发明的级联H桥储能系统直流侧滤波电路，所述交流电网的频率为50Hz，每相中 所级联的H桥储能单元（3）的个数为3个，电感L1、电容C1、电感L2和电容C2的数值分别为 0.9mH、2800uF、0.8mH、1000uF。 [0009]本发明的有益效果是：本发明的级联H桥储能系统直流侧滤波电路，由两个电容 （C1、C2）和两个电感（L1、L2）串并联组合而成，其中的电容C1与电感L1串联构成LC串联谐振 电路，电容C2与LC串联谐振电路并联后再与电感L2串联的两端接于电池组上，H桥变流器直 流侧的两端分别接于LC串联谐振电路的两端;通过将LC串联谐振电路的谐振频率设计为交 流电网的二倍（二倍工频），使其具有良好的滤除二倍工频谐波的作用，加之电容C2对H桥变 流器开关频率附近高频谐波的吸收、电感L2对高频谐波电流的进一步衰减，使得整个直流 侧滤波电路能平滑储能电池电流，从而提高储能电池的循环寿命，降低电池剩余电量估算 复杂度。 附图说明 [0010]图1为本发明的级联H桥储能系统直流侧滤波电路的电路图； 图2为本发明中一种级联H桥储能系统的结构原理图； 图3为图2所提供的级联H桥储能系统中编号为模块A1的H桥储能单元的直流侧电流波 形图。 [0011]图中：1 H桥变流器，2电池组，3 H桥储能单元。 具体实施方式 [0012]下面结合附图与实施例对本发明作进一步说明。 [0013]级联H桥储能系统用于将交流电网上电能存储起来，并且在需要的时候将存储的 电能输送至电网上，如现有的轨道交通的吸能装置，当列车制动时将电网上富余的电能收 集起来存储在电池组中，当列车启动时再将存储在电池组中的电能释放出来，既实现了电 能的充分利用，避免电能浪费，又可避免交流电网上的电压过度波动。级联H桥储能系统由 三相组成，每相又由多个H桥储能单元3串联而成，如图2所示，给出了本发明中一种级联H桥 储能系统的结构原理图，所示的每相由3个H桥储能单元3串联而成。 [0014] H桥储能单元3由H桥变流器1、直流侧滤波电路、电池组2组成，H桥变流器1由开关 器件构成，H桥变流器1具有整流和逆变功能，H桥变流器的交流侧接于交流电网上，直流侧 经直流侧滤波电路与电池组2相连接，电池组2实现对电能的存储。储能状态时：电能由交流 电网流向电池组2，H桥变流器1通过整流将交流电转化为直流电存储在电池组中；放电状态 时：电能由电池组2流向交流电网，H桥变流器1通过逆变将电池组存储的直流电转化为交流 电并输出至交流电网上。 [0015]如图1所示，给出了本发明的级联H桥储能系统直流侧滤波电路的电路图，所示的 直流侧滤波电路由2个电容和2个电感串并联构成，2个电容和2个电感的标号分别为C1、C2 和L1、L2,电容C1与电感L1串联构成LC串联谐振电路，LC串联谐振电路的谐振频率为交流电 网频率的二倍（即二倍工频）。电容C2与LC串联谐振电路相并联后的两端接于H桥变流器的 直流侧，电容C2用于吸收H桥变流器开关频率附近的高频谐波；电池组2的一端经电感L2接 于LC串联谐振电路中电感L1所在一端，电池组的另一端接于LC串联谐振电路中电容C1所在 一端，电感L2用于进一步衰减由Η桥变流器流向电池组的高频谐波电流。 [0016]直流侧滤波电路的形成步骤如下： 第一,一个电容C1和一个电感L1串联组成LC串联谐振电路，谐振频率为电网电压频率 的二倍,LC谐振电路主要用于吸收Η桥单元直流侧二倍频电流。 [0017]第二，在LC串联谐振电路上并联滤波电容C2,滤波电容C2的作用是吸收Η桥单元直 流侧开关频率次谐波。 [0018]第三,将LC串联谐振电路和滤波电容C2并联在Η桥单元直流侧。 [0019]第四，将滤波电感L2和储能电池串联在第三步所述并联结构上，滤波电感L2在高 频呈现高阻特性进一步衰减流向电池侧高频电流。 [0020]将图1所示滤波结构放在如图2所示级联Η桥储能系统中应用，电路中的参数如表1 所示： 表1 亘港电压 招多7 电忌羲毒 5ϋΗζ 交淹递波至善 2mH 变涕襄每指缓蒙个教 3 受渣遂齐关线率 ikHz 整能与漫至法 120 V 直威滤疫至感U 直海湿浅至容C1 直淹递波至善建 然以击 有涕超我空客C2 ίΟΟΟμΤ 根据电感电容串联谐振原理可计算LC串联谐振频率为： fr=l/ [2n* (Ll*Cl)1/2]=100.26Hz (2) 式中，行为LC串联谐振频率,L1、C1参数如表1所示。 [0021] 电网采用380V工频电网，因此Η桥单元直流侧二倍频电流频率为100Hz,故选用如 表1所示直流滤波参数。由式⑵可知,L1和C1组成串联谐振电路谐振频率为100Hz。 [0022]图3为级联储能变流器恒功率放电时模块Al直流侧电流波形，从上到下依次为Η桥 直流侧电流i dc_all，电池电流i dc_bat, LC谐振电路电流i d jLC和滤波电容电流1 dc_C ο根据电路原 理可知idjall为其他三个电流代数和，电流参考方向如图1所示。由图3可知Η桥直流侧电流 idjall为PWM电流,主要成分为直流电流、二倍频成分以及变流器开关引起的谐波成分，如果 不加滤波电路将缩短储能电池循环寿命;LC谐振电路电流ide-C为吸收idjall中的二倍频成 分;滤波电容电流ide-C为吸收ide.all中的开关引起的谐波成分；电池电流ide-bat呈现直流波 形，直流电流在-28A左右，而电流纹波仅有2A,且另外两个支路有电容的存在,idjaii中全部 直流成分会全部流向电池侧，几乎无额外功率损失。所发明滤波电路从如idjall所示的电流 波形中提取直流成分流向电池侧，大大提高储能电池循环使用寿命，也降低了储能电池剩 余电量估算复杂度。 [0023]可见，本发明的用于级联H桥储能系统直流侧滤波电路，其特点是滤波电路由两个 电容和两个电感组成，通过电感电容的特定串并联组合，可有效吸收功率单元直流侧流向 电池侧的二倍频电流及其他高频成分，大大提高储能电池循环使用寿命，降低储能电池剩 余电量估算复杂度，是一种值得推广的级联储能系统直流侧滤波电路。 [EN CN112436534A]: A cascaded H-bridge energy storage system DC side filter circuit technical field [0001] The present invention relates to the field of high-voltage energy storage power electronic equipment, and more specifically, to a DC side filter circuit of a cascaded H-bridge energy storage system. Background technique [0002] The high-voltage cascaded H-bridge energy storage system is a new type of energy storage converter. This kind of converter achieves a higher AC side output voltage through the cascading topology of the H bridge, and can be directly connected to the 10kV and 35kV high-voltage power grids, omitting the step-up transformer, thereby improving the efficiency of the converter. Compared with the conventional low-voltage 380V energy storage converter, the DC side of each power unit of the cascaded H-bridge structure is isolated from each other, and there is no common DC bus. Therefore, from a theoretical analysis, it can be known that when the AC side power is stable, the DC side current of the H-bridge unit must contain high-frequency harmonic components dominated by twice the frequency of the grid voltage. The double frequency and high frequency components will greatly reduce the life of the energy storage battery, and the double frequency component will bring challenges to the estimation of the remaining battery power. In order to improve the accuracy of battery life and battery remaining power estimation, a filter circuit needs to be added between the DC side of the power unit and the energy storage battery. [0003] The existing DC side filter circuits used for cascaded H-bridges are mostly LC low-pass filter circuits or LC resonance circuits. If the LC low-pass filter circuit is used, the cut-off frequency needs to be lower than the double frequency component, which will increase the size of the filter and cannot filter the double frequency component well. Although the LC series resonance circuit can absorb all the harmonic components of a specific frequency in theory, in practical applications, when the grid frequency is shifted, or there is an error between the resonance inductance and capacitance parameters and the nominal parameters, the LC series resonance cannot be better absorbed as Harmonic components at twice the frequency of the grid voltage. Summary of the invention [0004] In order to overcome the shortcomings of the above technical problems, the present invention provides a cascaded H-bridge energy storage system DC side filter circuit. [0005] The DC side filter circuit of the cascaded H-bridge energy storage system of the present invention. The cascaded H-bridge energy storage system is composed of a cascade of several H-bridge energy storage units, and the H-bridge energy storage unit is composed of an H-bridge converter and a battery pack. The H-bridge converter has rectification and inverter functions. The battery pack is used to store electric energy. The AC side of the H-bridge converter is connected to the AC power grid. The DC side of the H-bridge converter is connected to the battery pack through the DC side filter circuit. Phase connection; characterized in that: the DC side filter circuit is composed of capacitor C1, inductor L1, capacitor C2, and inductor L2, capacitor C1 and inductor L1 are connected in series to form an LC series resonant circuit, and the resonance frequency of the LC series resonant circuit is the AC grid frequency The two ends of the capacitor C2 and the LC series resonant circuit in parallel are connected to the DC side of the H-bridge converter. The capacitor C2 is used to absorb high-frequency harmonics near the switching frequency of the H-bridge converter; One end is connected to the end of the LC series resonant circuit where the inductor L1 is located through the inductor L2, and the other end of the battery pack is connected to the end where the capacitor C1 is located in the LC series resonant circuit. The inductor L2 is used to further attenuate the high flow from the H-bridge converter to the battery pack. Frequency harmonic current. [0006] The DC side filter circuit of the cascaded H-bridge energy storage system of the present invention, in the energy storage state: electric energy flows from the AC grid to the battery pack (2), and the H-bridge converter (1) converts AC power into DC power through rectification and storage In the battery pack; in the discharging state: electric energy flows from the battery pack to the AC power grid, and the H-bridge converter converts the DC power stored in the battery pack into AC power through inverter and outputs it to the AC power grid. [0007] In the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention, assuming that the frequency of the AC power grid is f, the values of the capacitor C1 and the inductance L1 satisfy the following relationship: L1*C1=1/(4nf)2 (1) In the formula, L1 and C1 are the numerical values of the inductance L1 and the capacitor C1 respectively, and f is the frequency of the AC power grid. [0008] In the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention, the frequency of the AC power grid is 50 Hz, the number of cascaded H-bridge energy storage units (3) in each phase is 3, and the inductor The values of L1, capacitor C1, inductance L2, and capacitor C2 are 0.9mH, 2800uF, 0.8mH, and 1000uF, respectively. [0009] The beneficial effect of the present invention is: the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention is composed of two capacitors (C1, C2) and two inductors (L1, L2) in series and parallel, wherein The capacitor C1 and the inductor L1 are connected in series to form an LC series resonant circuit. The capacitor C2 is connected in parallel with the LC series resonant circuit and then connected in series with the inductor L2 to the battery pack. The two ends of the DC side of the H-bridge converter are respectively connected to the LC Both ends of the series resonant circuit; by designing the resonant frequency of the LC series resonant circuit to be twice that of the AC grid (twice the power frequency), it has a good effect of filtering out the double power frequency harmonics, and the capacitor C2 is added to The absorption of high-frequency harmonics near the switching frequency of the H-bridge converter and the further attenuation of high-frequency harmonic currents by the inductor L2 enable the entire DC-side filter circuit to smooth the current of the energy storage battery, thereby improving the cycle life of the energy storage battery and reducing The remaining battery power estimation complexity. Description of the drawings [0010] Figure 1 is a circuit diagram of the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention; Figure 2 is a schematic structural diagram of a cascaded H-bridge energy storage system of the present invention; Figure 3 is provided in Figure 2 The DC side current waveform diagram of the H-bridge energy storage unit numbered as module A1 in the cascaded H-bridge energy storage system. [0011] In the figure: 1 H bridge converter, 2 battery packs, 3 H bridge energy storage unit. detailed description [0012] The present invention will be further described below with reference to the accompanying drawings and embodiments. [0013] The cascaded H-bridge energy storage system is used to store electrical energy on the AC power grid and transmit the stored electrical energy to the power grid when needed, such as the existing energy absorbing device for rail transit, which will be used when the train is braking. The surplus electric energy on the power grid is collected and stored in the battery pack. When the train starts, the electric energy stored in the battery pack is released. This not only realizes the full use of electric energy, avoids power waste, but also avoids excessive voltage fluctuations on the AC grid. . The cascaded H-bridge energy storage system is composed of three phases, and each phase is formed by a plurality of H-bridge energy storage units 3 connected in series. As shown in Figure 2, the cascaded H-bridge energy storage system in the present invention is shown The structural principle diagram shows that each phase is composed of three H-bridge energy storage units 3 connected in series. [0014] The H-bridge energy storage unit 3 is composed of an H-bridge converter 1, a DC side filter circuit, and a battery pack 2. The H-bridge converter 1 is composed of switching devices, and the H-bridge converter 1 has rectification and inverter functions. , The AC side of the H-bridge converter is connected to the AC power grid, and the DC side is connected to the battery pack 2 through the DC side filter circuit, and the battery pack 2 realizes the storage of electric energy. In the state of energy storage: electric energy flows from the AC grid to the battery pack 2, and the H-bridge converter 1 converts the AC power into DC power through rectification and is stored in the battery pack; in the state of discharging: electric energy flows from the battery pack 2 to the AC grid, and the H-bridge converts the current The converter 1 converts the direct current stored in the battery pack into alternating current through inverter and outputs it to the alternating current grid. [0015] As shown in FIG. 1, a circuit diagram of the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention is given. The DC side filter circuit shown is composed of two capacitors and two inductors in series and parallel, and two The labels of the capacitor and the two inductors are C1, C2 and L1, L2, respectively. The capacitor C1 and the inductor L1 are connected in series to form an LC series resonant circuit. The resonance frequency of the LC series resonant circuit is twice the frequency of the AC power grid (that is, twice the power frequency) . After the capacitor C2 is connected in parallel with the LC series resonant circuit, the two ends are connected to the H-bridge converter On the DC side, capacitor C2 is used to absorb high-frequency harmonics near the switching frequency of the H-bridge converter; one end of the battery pack 2 is connected to the end of the inductor L1 in the LC series resonance circuit through the inductor L2, and the other end of the battery pack is connected to the LC In the series resonance circuit, the capacitor C1 is located at one end, and the inductor L2 is used to further attenuate the high-frequency harmonic current flowing from the H-bridge converter to the battery pack. [0016] The steps of forming the DC side filter circuit are as follows: First, a capacitor C1 and an inductor L1 are connected in series to form an LC series resonant circuit. The resonant frequency is twice the frequency of the grid voltage. The LC resonant circuit is mainly used to absorb the DC of the H bridge unit. Double frequency current on the side. [0017] Second, the filter capacitor C2 is connected in parallel on the LC series resonant circuit, and the filter capacitor C2 functions to absorb the sub-harmonics of the switching frequency of the DC side of the H bridge unit. [0018] Third, connect the LC series resonant circuit and the filter capacitor C2 in parallel on the DC side of the H bridge unit. [0019] Fourth, the filter inductor L2 and the energy storage battery are connected in series to the parallel structure described in the third step, and the filter inductor L2 exhibits high resistance characteristics at high frequencies to further attenuate the high frequency current flowing to the battery side. [0020] The filter structure shown in FIG. 1 is applied in the cascaded H-bridge energy storage system shown in FIG. 2, and the parameters in the circuit are shown in Table 1: Table 1 Port voltage More than 7 Electricity avoid poison 5ϋΗζ Cross flooding 2mH Change your tears, and every finger slowly teaches you 3 Rate of scumming ikHz Shaping and Dangzhi 120 V Zhiwei filters the epidemic to the sense U Straight sea wet and shallow to full C1 Directly flooding the wave to build goodness Then hit Airbus C2 ίΟΟΟμΤ According to the principle of inductance and capacitance series resonance, the LC series resonance frequency can be calculated as: fr=l/ [2n* (Ll*Cl)1/2]=100.26Hz (2) where, the behavior is the LC series resonance frequency, and the parameters of L1 and C1 are shown in Table 1. [0021] The power grid uses a 380V power frequency power grid, so the frequency of the double-frequency current on the DC side of the H bridge unit is 100 Hz, so the DC filter parameters shown in Table 1 are selected. It can be seen from formula (2) that the resonant frequency of the series resonant circuit composed of L1 and C1 is 100Hz. [0022] FIG. 3 is the current waveform of the DC side of the module A1 during constant power discharge of the cascaded energy storage converter. From top to bottom, the DC side current of the H bridge is i dc_all, the battery current i dc_bat, the LC resonance circuit current id jLC and the filter The capacitance current 1 dc_C ο According to the circuit principle, it can be known that idjall is the algebraic sum of the other three currents, and the current reference direction is shown in Figure 1. It can be seen from Figure 3 that the DC side current idjall of the H bridge is a PWM current, and the main components are DC current, double frequency components and harmonic components caused by converter switching. If no filter circuit is added, the cycle life of the energy storage battery will be shortened; LC resonance The circuit current ide-C absorbs the double frequency component in idjall; the filter capacitor current ide-C absorbs the harmonic component caused by the switch in ide.all; the battery current ide-bat presents a DC waveform, and the DC current is about -28A , And the current ripple is only 2A, and the other two branches have capacitors, all the DC components in idjaii will all flow to the battery side, and there is almost no additional power loss. The invented filter circuit extracts the DC component from the current waveform shown by idjall and flows to the battery side, which greatly improves the cycle life of the energy storage battery and reduces the remaining energy storage battery. The remaining power estimation complexity. [0023] It can be seen that the DC side filter circuit of the cascaded H-bridge energy storage system of the present invention is characterized in that the filter circuit is composed of two capacitors and two inductors. The specific series-parallel combination of inductors and capacitors can effectively absorb power. The double-frequency current and other high-frequency components flowing from the DC side of the unit to the battery side greatly improve the cycle life of the energy storage battery and reduce the complexity of estimating the remaining power of the energy storage battery. It is a DC side filter circuit of the cascade energy storage system worthy of promotion. .
[JA WO2021070323A1]: 電力変換装置 [EN WO2021070323A1]: POWER CONVERSION DEVICE [FR WO2021070323A1]: DISPOSITIF DE CONVERSION DE PUISSANCE | [JA WO2021070323A1]: 電力変換装置は、それぞれ第１および第２の制御信号を出力する第１および第２の制御部（１０，２０）と、第１および第２の制御信号のうちの選択された制御信号を通過させるゲート回路（７１，７２，７３，７４）と、ゲート回路を通過した制御信号に基づいて主回路（５０）を駆動させる駆動回路（６２）とを備える。ゲート回路は、第１の制御信号を通過させている場合に第２の制御信号が選択されたときには、交流電流（Ｉｕｖ）の瞬時値の絶対値がしきい値電流（ＩＴＨ）よりも減少したことに応じて、第１の制御信号を遮断するとともに第２の制御信号を通過させる。 [EN WO2021070323A1]: This power conversion device is provided with: first and second control units (10, 20) that output first and second control signals, respectively; gate circuits (71, 72, 73, 74) that allow control signals selected from the first and second control signals to pass through; and a drive circuit (62) that drives a main circuit (50) on the basis of the control signals that have passed through the gate circuits. If the second control signal is selected while the first control signal has been allowed to pass through, the gate circuits block the first control signal and allow the second control signal to pass through in response to the absolute value of the instantaneous value of an alternating current (Iuv) falling below a threshold current (ITH). [FR WO2021070323A1]: La présente invention concerne un dispositif de conversion de puissance qui comporte: des première et deuxième unités de commande (10, 20) qui émettent des premier et deuxième signaux de commande, respectivement; des circuits de grille (71, 72, 73, 74) qui autorisent les signaux de commande sélectionnés parmi les premier et deuxième signaux de commande à les traverser; et un circuit d'attaque (62) qui attaque un circuit principal (50) sur la base des signaux de commande qui ont traversé les circuits de grille. Si le deuxième signal de commande est sélectionné tandis que le premier signal de commande a été autorisé à passer, les circuits de grille bloquent le premier signal de commande et autorisent le deuxième signal de commande à passer en réponse au fait que la valeur absolue de la valeur instantanée d'un courant alternatif (Iuv) passe en dessous d'un courant de seuil (ITH). | WO2021070323A1 | 2021-04-15 | JP2019040007W | 2019-10-10 | JP2019040007W, 2019-10-10 | JP6792097B1: 2020-11-25 WO2021070323A1: 2021-04-15 | 東芝三菱電機産業システム株式会社 TOSHIBA MITSUBISHI ELEC IND | OKUYAMA RYOTA ISHITOBI HIROKI SUGIYAMA TAKASHI | H02M7/48: I H02M7/483: I | H02M7/48: I H02M7/483: I | WO2019069394A1 JP2014124068A WO2018211624A1 WO2016203516A1 |  | [JA WO2021070323A1]: コンデンサと、 前記コンデンサと交流電源との間で電力を授受する電力変換器と、 前記交流電源と前記電力変換器との間に流れる交流電流の瞬時値を検出する電流検出器と、 それぞれ第1および第2の制御信号を出力する第1および第2の制御部と、 前記第1および第2の制御信号のうちの選択された制御信号を通過させるゲート回路と、 前記ゲート回路を通過した制御信号に基づいて前記電力変換器を駆動させる駆動回路とを備え、 前記ゲート回路は、 前記第1の制御信号を通過させている場合に前記第2の制御信号が選択されたときには、前記電流検出器によって検出される前記交流電流の瞬時値の絶対値が予め定められた値よりも減少したことに応じて、前記第1の制御信号を遮断するとともに前記第2の制御信号を通過させる、電力変換装置。 前記ゲート回路は、 前記第2の制御信号を通過させている場合に前記第1の制御信号が選択されたときには、前記電流検出器によって検出される前記交流電流の瞬時値の絶対値が前記予め定められた値よりも減少したことに応じて、前記第2の制御信号を遮断するとともに前記第1の制御信号を通過させる、請求項1に記載の電力変換装置。 前記ゲート回路は、 前記第1の制御信号を遮断するとともに前記第2の制御信号を通過させる場合には、前記第1の制御信号を遮断してから予め定められた時間が経過した後に前記第2の制御信号を通過させ、 前記第2の制御信号を遮断するとともに前記第1の制御信号を通過させる場合には、前記第2の制御信号を遮断してから前記予め定められた時間が経過した後に前記第1の制御信号を通過させる、請求項2に記載の電力変換装置。 前記第1および第2の制御信号のうちの所望の制御信号を選択する選択部をさらに備える、請求項2に記載の電力変換装置。 各々が前記コンデンサ、前記電力変換器、および前記駆動回路を含む複数の単位変換器を備え、 前記複数の単位変換器に含まれる複数の前記電力変換器はカスケード接続され、 前記電流検出器は、前記交流電源とカスケード接続された複数の前記電力変換器との間に流れる交流電流の瞬時値を検出する、請求項1に記載の電力変換装置。 各々が前記複数の単位変換器を含む3個のアームを備え、 前記3個のアームはデルタ接続されており、 前記交流電源は電力系統であり、 前記電力変換装置は、前記電力系統の無効電力を補償する無効電力補償装置として使用される、請求項5に記載の電力変換装置。 [EN WO2021070323A1]: The first is a capacitor, a power converter that transfers power between the capacitor and the AC power supply, and a current detector that detects the instantaneous value of the AC current flowing between the AC power supply and the power converter. The first and second control units that output the second control signal, the gate circuit that passes the selected control signal from the first and second control signals, and the control that passes through the gate circuit. The gate circuit includes a drive circuit for driving the power converter based on the signal, and the gate circuit detects the current when the second control signal is selected when the first control signal is passed. A power source that shuts off the first control signal and passes the second control signal in response to the absolute value of the instantaneous value of the alternating current detected by the capacitor being less than a predetermined value. Conversion device. In the gate circuit, when the first control signal is selected when the second control signal is passed, the absolute value of the instantaneous value of the alternating current detected by the current detector is the advance. The power conversion device according to claim 1, wherein the second control signal is cut off and the first control signal is passed in response to a decrease from a predetermined value. When the gate circuit cuts off the first control signal and passes the second control signal, the gate circuit cuts off the first control signal and waits for a predetermined time after the first control signal is cut off. When the second control signal is passed, the second control signal is blocked, and the first control signal is passed, the predetermined time has elapsed since the second control signal was blocked. The power conversion device according to claim 2, wherein the first control signal is passed therethrough. The power conversion device according to claim 2, further comprising a selection unit for selecting a desired control signal from the first and second control signals. Each includes the capacitor, the power converter, and a plurality of unit converters including the drive circuit, the plurality of the power converters included in the plurality of unit converters are cascaded, and the current detector is a current detector. The power conversion device according to claim 1, wherein an instantaneous value of an AC current flowing between the AC power supply and the plurality of power converters connected in cascade is detected. Each includes three arms, each containing the plurality of unit converters, the three arms being delta-connected, the AC power supply being a power system, and the power converter being the reactive power of the power system. The power conversion device according to claim 5, which is used as an ineffective power compensation device for compensating for the power supply. | [JA WO2021070323A1]: 電力変換装置 この発明は、電力変換装置に関し、より特定的には、コンデンサと交流電源との間で電力を授受する電力変換器を備えた電力変換装置に関する。 近年、STATCOM(Static Synchronous Compensator)などの自励式無効電力補償装置、BTB(Back to Back)システムなどの直流送電システム、および、モータドライブインバータなどにおいては、モジュラー・マルチレベル変換器(MMC:Modular Multilevel Converter)の適用が検討されている(たとえば、国際公開第2016/203516号(特許文献1)参照)。 MMCは、複数の単位変換器を直列に接続して構成されている。単位変換器は、コンデンサと、そのコンデンサと交流電源との間で電力を授受する電力変換器と、MMC全体を制御する上位の制御装置から供給される制御信号に基づいて電力変換器を駆動させる駆動回路とを備える。 国際公開第2016/203516号 1台の制御装置だけでMMCを制御する場合、その制御装置のメンテナンスを行なう場合にはMMCの運転を停止する必要がある。この対策として、2台の制御装置を設け、一方の制御装置のメンテナンスを行なう場合に、他方の制御装置によってMMCを制御する方法が考えられる。しかし、この方法では、制御信号の切換時に、交流電源と電力変換器との間に流れる交流電流の波形が歪む恐れがある。 それゆえに、本発明の目的は、制御信号の切換時に交流電流に発生する波形歪を小さく抑制することが可能な電力変換装置を提供することである。 本発明の電力変換装置は、コンデンサと、コンデンサと交流電源との間で電力を授受する電力変換器と、交流電源と電力変換器との間に流れる交流電流の瞬時値を検出する電流検出器と、それぞれ第1および第2の制御信号を出力する第1および第2の制御部と、第1および第2の制御信号のうちの選択された制御信号を通過させるゲート回路と、ゲート回路を通過した制御信号に基づいて電力変換器を駆動させる駆動回路とを備えたものである。ゲート回路は、第1の制御信号を通過させている場合に第2の制御信号が選択されたときには、電流検出器によって検出される交流電流の瞬時値の絶対値が予め定められた値よりも減少したことに応じて、第1の制御信号を遮断するとともに第2の制御信号を通過させる。 本発明によれば、交流電流の瞬時値の絶対値が予め定められた値よりも減少したときに制御信号を切り換えるので、制御信号の切換時に交流電流に発生する波形歪を小さく抑制することができる。 実施の形態の電力変換装置の構成を示す回路ブロック図である。 図1に示す制御装置7,8の要部を示すブロック図である。 図2に示す選択指令部11,21の構成を示す回路ブロック図である。 図2に示す選択指令部11~13,21~23の動作を例示するタイムチャートである。 図1に示す単位変換器5の構成を示す回路ブロック図である。 図5に示すI/F回路61の要部を示す回路ブロック図である。 図6に示すゲート回路71の構成を示す回路ブロック図である。 図6に示すゲート回路71~74の効果および問題点を説明するためのタイムチャートである。 実施の形態の比較例を示す回路ブロック図である。 図9に示す比較例の問題点を説明するためのタイムチャートである。 以下、実施の形態について、図面を参照しながら詳細に説明する。なお、図中の同一または相当部分には同一符号を付してその説明は繰返さない。 図1は、実施の形態の電力変換装置の構成を示す回路ブロック図である。この電力変換装置100は、電力系統1(交流電源)の無効電力を補償する無効電力補償装置として使用される。図1を参照して、電力変換装置100は、少なくとも1つの主回路給電方式の単位変換器5を直列接続して構成されたアームA1~A3と、各々が全単位変換器5を制御するように構成された2台の制御装置7,8とを備える。より詳細には、電力変換装置100は、スイッチS1~S6、変圧器2,3、限流抵抗器R1~R3、交流ラインUL,VL,WL、変流器C1~C3、リアクトルL1~L3、アームA1~A3、操作部6、および制御装置7,8を備える。 スイッチS1,S2,S3の各々の一方端子はそれぞれ電力系統1の三相の送電線1u,1v,1wに接続され、他方端子はそれぞれ変圧器2の3つの一次巻線に接続される。スイッチS1,S2,S3は、通常は導通状態であり、たとえば電力変換装置100のメンテナンス時に非導通状態にされる。変圧器2は、3つの一次巻線と3つの二次巻線とを含み、三相交流電力を授受する。 限流抵抗器R1~R3の各々の一方端子はそれぞれ変圧器2の3つの二次巻線に接続され、他方端子はそれぞれ交流ラインUL,VL,WLに接続される。限流抵抗器R1~R3は、電力変換装置100の起動時に電力系統1からアームA1~A3にそれぞれ流れる電流を制限する。 スイッチS4,S5,S6は、それぞれ限流抵抗器R1~R3に並列接続される。スイッチS4,S5,S6は、電力変換装置100の起動時においてアームA1~A3に流れる電流が安定した後に導通状態にされる。変圧器3は、交流ラインUL,VL,WLの交流電圧に応じた値の三相交流電圧Vu,Vv,Vwを制御装置7,8の各々に出力する。 リアクトルL1およびアームA1は、交流ラインULと交流ラインVLとの間に直列接続される。リアクトルL2およびアームA2は、交流ラインVLと交流ラインWLとの間に直列接続される。リアクトルL3およびアームA3は、交流ラインWLと交流ラインULとの間に直列接続される。すなわち、アームA1~A3はデルタ接続されている。アームA1~A3は、制御装置7,8のうちの選択された制御装置によって制御され、三相交流電力を発生する。 アームA1~A3の各々は、カスケード接続された複数の単位変換器5を含む。複数の単位変換器5の各々は、制御装置7,8のうちの選択された制御装置によって制御され、交流電力を発生する。 アームA1の初段の単位変換器5の第1端子5aは、リアクトルL1の一方端子に接続されている。アームA1において、最終段以外の単位変換器5の第2端子5bは、後段の単位変換器5の第1端子5aに接続されている。アームA1の最終段の単位変換器5の第2端子5bは、リアクトルL2の一方端子に接続されている。 アームA2の初段の単位変換器5の第1端子5aは、リアクトルL2の一方端子に接続されている。アームA2において、最終段以外の単位変換器5の第2端子5bは、後段の単位変換器5の第1端子5aに接続されている。アームA2の最終段の単位変換器5の第2端子5bは、リアクトルL3の一方端子に接続されている。 アームA3の初段の単位変換器5の第1端子5aは、リアクトルL3の一方端子に接続されている。アームA3において、最終段以外の単位変換器5の第2端子5bは、後段の単位変換器5の第1端子5aに接続されている。アームA3の最終段の単位変換器5の第2端子5bは、リアクトルL1の一方端子に接続されている。 リアクトルL1~L3は、アームA1~A3に流れる循環電流をそれぞれ抑制する。リアクトルL1~L3は、アームA1~A3とは別に設けられていてもよいし、アームA1~A3のインダクタンス成分であっても構わない。変流器C1~C3(電流検出器)は、アームA1~A3に流れる交流電流Iuv,Ivw,Iwuの瞬時値をそれぞれ検出して、制御装置7,8の各々に出力する。 操作部6(選択部)は、複数のボタン、複数のスイッチ、画像表示装置などを含み、電力変換装置100の使用者によって操作される。電力変換装置100の使用者は、操作部6を操作することにより、制御装置7,8のうちの所望の制御装置を選択したり、電力変換装置100の運転を開始したり、停止することができる。 操作部6は、制御装置7が選択された場合には選択信号SEをLレベルにし、制御装置8が選択された場合には選択信号SEをHレベルにする。たとえば、通常時には、選択信号SEがLレベルにされ、制御装置7によってアームA1~A3が制御される。制御装置7のメンテナンス時には、選択信号SEがHレベルにされ、制御装置8によってアームA1~A3が制御される。制御装置7のメンテナンスが終了した場合には、選択信号SEがLレベルにされ、制御装置7によってアームA1~A3が制御される。 制御装置7は、選択信号SE、無効電力指令値Qr、三相交流電圧Vu,Vv,Vw、三相交流電流Iuv,Ivw,Iwu、複数の直流電圧Vdcに基づいて、制御信号CNT1A~CNT3Aおよび選択指令信号SE1A~SE3Aを生成する。ここで、無効電力指令値Qrは、たとえば電力系統1の中央指令室(図示せず)から与えられる。電力変換装置100は、無効電力指令値Qrに応じた値の無効電力を電力系統1に供給する。複数の直流電圧Vdcは、それぞれ複数の単位変換器5から与えられる。直流電圧Vdcについては後述する。 制御信号CNT1Aおよび選択指令信号SE1Aは、アームA1の各単位変換器5に与えられる。制御信号CNT2Aおよび選択指令信号SE2Aは、アームA2の各単位変換器5に与えられる。制御信号CNT3Aおよび選択指令信号SE3Aは、アームA3の各単位変換器5に与えられる。 制御装置8は、選択信号SE、無効電力指令値Qr、三相交流電圧Vu,Vv,Vw、三相交流電流Iuv,Ivw,Iwu、後述する複数の直流電圧Vdcに基づいて、制御信号CNT1B~CNT3Bおよび選択指令信号SE1B~SE3Bを生成する。制御信号CNT1Bおよび選択指令信号SE1Bは、アームA1の各単位変換器5に与えられる。制御信号CNT2Bおよび選択指令信号SE2Bは、アームA2の各単位変換器5に与えられる。制御信号CNT3Bおよび選択指令信号SE3Bは、アームA3の各単位変換器5に与えられる。 制御装置7が選択された場合には、選択指令信号SE1A~SE3AがともにHレベルにされるとともに選択指令信号SE1B~SE3BがともにLレベルにされ、アームA1~A3は、制御装置7から出力される制御信号CNT1A~CNT3Aに従って三相交流電力を生成する。 制御装置8が選択された場合には、選択指令信号SE1A~SE3AがともにLレベルにされるとともに選択指令信号SE1B~SE3BがともにHレベルにされ、アームA1~A3は、制御装置8から出力される制御信号CNT1B~CNT3Bに従って三相交流電力を生成する。 図2は、制御装置7,8の構成を示すブロック図である。図2において、制御装置7は制御部10および選択指令部11~13を含み、制御装置8は制御部20および選択指令部21~23を含む。 制御部10は、無効電力指令値Qr、三相交流電圧Vu,Vv,Vw、三相交流電流Iuv,Ivw,Iwu、および複数の直流電圧Vdcに基づいて、制御信号CNT1A~CNT3Aを生成する。 具体的には、制御部10は、変流器C1~C3からの交流電流Iuv,Ivw,Iwuに基づいて、交流ラインUL,VL,WLに流れる交流電流に応じたレベルの三相交流電流Iu,Iv,Iwを求める。ただし、Iu=Iuv-Iwu、Iv=Ivw-Iuv、Iw=Iwu-Ivwである。 制御部10は、変圧器3からの三相交流電圧Vu,Vv,Vwと上記三相交流電流Iu,Iv,Iwとに基づいて無効電力Q0を求める。制御装置7は、無効電力指令値Qrと無効電力Q0との偏差ΔQ=Qr-Q0を求める。 制御部10は、変流器C1~C3からの交流電流Iuv,Ivw,Iwu、変圧器3からの三相交流電圧Vu,Vv,Vwなどに基づいて、それぞれ複数個の単位変換器5に対応する複数の電圧指令値Vdcrを生成する。 制御部10は、電圧指令値Vdcrと直流電圧Vdcとの偏差ΔVdcを求める。制御部10は、電圧偏差ΔVdcを0とし、かつ無効電力偏差ΔQを0とするための制御演算を実行することにより、三相交流電圧指令値Vuvr,Vvwr,Vwurを生成する。 換言すると、制御部10は、アームA1~A3に制御信号CNT1A~CNT3Aを与えることにより、電圧偏差ΔVdcが0になるように各単位変換器5の有効電流制御を行なうとともに、無効電力偏差ΔQが0になるように各単位変換器5の無効電流制御を行なう。 三相交流電圧指令値Vuvr,Vvwr,Vwurを基に、アームA1~A3の各単位変換器5が運転され、直流電圧Vdcが電圧指令値Vdcrに一致するとともに、無効電力Q0が無効電力指令値Qrに一致する。 制御部20は、制御部10と同様の構成であり、無効電力指令値Qr、三相交流電圧Vu,Vv,Vw、三相交流電流Iuv,Ivw,Iwu、および複数の直流電圧Vdcに基づいて、制御信号CNT1B~CNT3Bを生成する。 選択指令部11は、選択信号SEがHレベルにされている場合(すなわち、制御装置8が選択されている場合)には、選択指令信号SE1AをLレベルにする。選択指令部11は、選択信号SEがLレベルにされた場合(すなわち、制御装置7が選択された場合)には、アームA1に流れる交流電流Iuvの絶対値が所定のしきい値電流ITH(予め定められた値)よりも小さくなったとき(すなわち、交流電流Iuvがゼロクロス点を通るとき)、選択指令信号SE1AをHレベルに立ち上げる。ただし、しきい値電流ITHは、交流電流Iuvのピーク値よりも十分に小さな値であり、略0Aに設定されている。 選択指令部21は、選択信号SEがLレベルにされている場合(すなわち、制御装置7が選択されている場合)には、選択指令信号SE1BをLレベルにする。選択指令部21は、選択信号SEがHレベルにされた場合(すなわち、制御装置8が選択された場合)には、アームA1に流れる交流電流Iuvの絶対値が所定のしきい値電流ITHよりも小さくなったとき(すなわち、交流電流Iuvがゼロクロス点を通るとき)、選択指令信号SE1BをHレベルに立ち上げる。図2で点線で示すように、選択指令部11,21間で信号が授受され、選択指令信号SE1Bは選択指令信号SE1Aの反転信号とされる。 選択指令部12は、選択信号SEがHレベルにされている場合(すなわち、制御装置8が選択されている場合)には、選択指令信号SE2AをLレベルにする。選択指令部12は、選択信号SEがLレベルにされた場合(すなわち、制御装置7が選択された場合)には、アームA2に流れる交流電流Ivwの絶対値が所定のしきい値電流ITHよりも小さくなったとき(すなわち、交流電流Ivwがゼロクロス点を通るとき)、選択指令信号SE2AをHレベルに立ち上げる。 選択指令部22は、選択信号SEがLレベルにされている場合(すなわち、制御装置7が選択されている場合)には、選択指令信号SE2BをLレベルにする。選択指令部22は、選択信号SEがHレベルにされた場合(すなわち、制御装置8が選択された場合)には、アームA2に流れる交流電流Ivwの絶対値が所定のしきい値電流ITHよりも小さくなったとき(すなわち、交流電流Ivwがゼロクロス点を通るとき)、選択指令信号SE2BをHレベルに立ち上げる。図2で点線で示すように、選択指令部12,22間で信号が授受され、選択指令信号SE2Bは選択指令信号SE2Aの反転信号とされる。 選択指令部13は、選択信号SEがHレベルにされている場合(すなわち、制御装置8が選択されている場合)には、選択指令信号SE3AをLレベルにする。選択指令部13は、選択信号SEがLレベルにされた場合(すなわち、制御装置7が選択された場合)には、アームA3に流れる交流電流Iwuの絶対値が所定のしきい値電流ITHよりも小さくなったとき(すなわち、交流電流Iwuがゼロクロス点を通るとき)、選択指令信号SE3AをHレベルに立ち上げる。 選択指令部23は、選択信号SEがLレベルにされている場合(すなわち、制御装置7が選択されている場合)には、選択指令信号SE3BをLレベルにする。選択指令部23は、選択信号SEがHレベルにされた場合(すなわち、制御装置8が選択された場合)には、アームA3に流れる交流電流Iwuの絶対値が所定のしきい値電流ITHよりも小さくなったとき(すなわち、交流電流Iwuがゼロクロス点を通るとき)、選択指令信号SE3BをHレベルに立ち上げる。図2で点線で示すように、選択指令部13,23間で信号が授受され、選択指令信号SE3Bは選択指令信号SE3Aの反転信号とされる。 図3は、図2に示した選択指令部11,21の構成を示す回路ブロック図である。図3において、選択指令部11は、絶対値検出器31、比較器32、インバータ33、ANDゲート34、およびフリップフロップ35を含む。選択指令部21は、絶対値検出器41、比較器42、ANDゲート43、およびフリップフロップ44を含む。 絶対値検出器31は、対応するアームA1に流れる交流電流Iuvの絶対値¦Iuv¦を検出する。比較器32の非反転入力端子(+端子)にはしきい値電流ITHが与えられ、その反転入力端子(-端子)には、交流電流Iuvの絶対値¦Iuv¦が与えられる。比較器32は、しきい値電流ITHと交流電流Iuvの絶対値¦Iuv¦との大小を比較し、比較結果を示す信号φ32を出力する。 ¦Iuv¦&gt;ITHである場合には、信号φ32はLレベルにされる。¦Iuv¦&lt;ITHである場合には、信号φ32はHレベルにされる。ITH≒0Aであるので、交流電流Iuvがゼロクロス点を通るときに信号φ32はHレベルにされる。 絶対値検出器41は、対応するアームA1に流れる交流電流Iuvの絶対値¦Iuv¦を検出する。比較器42の非反転入力端子(+端子)にはしきい値電流ITHが与えられ、その反転入力端子(-端子)には、交流電流Iuvの絶対値¦Iuv¦が与えられる。比較器42は、しきい値電流ITHと交流電流Iuvの絶対値¦Iuv¦との大小を比較し、比較結果を示す信号φ42を出力する。 ¦Iuv¦&gt;ITHである場合には、信号φ42はLレベルにされる。¦Iuv¦&lt;ITHである場合には、信号φ42はHレベルにされる。ITH≒0Aであるので、交流電流Iuvがゼロクロス点を通るときに信号φ42はHレベルにされる。 インバータ33は、選択信号SEの反転信号を出力する。ANDゲート34は、比較器32の出力信号φ32とインバータ33の出力信号との論理積信号φ34を出力する。ANDゲート43は、比較器42の出力信号φ42と選択信号SEとの論理積信号φ43を出力する。 ANDゲート34の出力信号φ34は、フリップフロップ35のセット端子(S)に与えられるとともに、フリップフロップ44のリセット端子(R)に与えられる。ANDゲート43の出力信号φ43は、フリップフロップ44のセット端子(S)に与えられるとともに、フリップフロップ35のリセット端子(R)に与えられる。フリップフロップ35,44の出力端子(Q)に現れる信号は、それぞれ選択指令信号SE1A,SE1Bとなる。 選択信号SEがLレベルにされている場合(すなわち、制御装置7が選択されている場合)には、ANDゲート43の出力信号φ43がLレベルに固定されるとともに、インバータ33の出力信号がHレベルにされ、比較器32の出力信号φ32がANDゲート34を通過してフリップフロップ35のセット端子およびフリップフロップ44のリセット端子に与えられる。交流電流Iuvがゼロクロス点を通るとき、比較器32の出力信号φ32がHレベルにされ、フリップフロップ35がセットされるとともにフリップフロップ44がリセットされ、選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされる。 選択信号SEがHレベルにされている場合(すなわち、制御装置8が選択されている場合)には、ANDゲート34の出力信号φ34がLレベルに固定されるとともに、比較器42の出力信号φ42がANDゲート43を通過してフリップフロップ35のリセット端子およびフリップフロップ44のセット端子に与えられる。交流電流Iuvがゼロクロス点を通るとき、比較器42の出力信号φ42がHレベルにされ、フリップフロップ35がリセットされるとともにフリップフロップ44がセットされ、選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされる。 すなわち、選択指令部11,21間で信号φ34,φ43が授受され、選択指令信号SE1Bは選択指令信号SE1Aの反転信号とされる。選択指令部12,22および選択指令部13,23の各々は、選択指令部11,21と同様の構成であるので、その説明は繰り返さない。 図4は、図2および図3に示した選択指令部11~13,21~23の動作を例示するタイムチャートである。図4において、(A)は三相交流電流Iuv,Ivw,Iwuの波形を示し、(B)は選択信号SEの波形を示し、(C)~(E)はそれぞれ選択指令信号SE1A~SE3Aの波形を示し、(F)~(H)はそれぞれ選択指令信号SE1B~SE3Bの波形を示している。 ある時刻t0において、選択信号SEがLレベルにされているものとする。選択信号SEがLレベルにされている場合には、交流電流Iuv,Ivw,Iwuがゼロクロス点を通るときに、選択指令部11~13,21~23の各々のフリップフロップ35がセットされるとともにフリップフロップ44がリセットされ、選択指令信号SE1A~SE3AがHレベルにされるとともに選択指令信号SE1B~SE3BがLレベルにされる。 ある時刻t1において、選択信号SEがLレベルからHレベルに立ち上げられると、選択指令部11~13,21~23の各々において、ANDゲート34の出力信号φ34がLレベルに固定され、比較器42の出力信号φ42がANDゲート43を通過してフリップフロップ35のリセット端子(R)およびフリップフロップ44のセット端子(S)に与えられる。 時刻t2において交流電流Iuvがゼロクロス点を通るとき、選択指令部21において、比較器42の出力信号φ42がHレベルになり、フリップフロップ35がリセットされるとともにフリップフロップ44がセットされ、選択指令信号SE1AがLレベルにされるとともに選択指令信号SE1BがHレベルにされる。 次に、時刻t3において交流電流Iwuがゼロクロス点を通るとき、選択指令部23において、比較器42の出力信号φ42がHレベルになり、フリップフロップ35がリセットされるとともにフリップフロップ44がセットされ、選択指令信号SE3AがLレベルにされるとともに選択指令信号SE3BがHレベルにされる。 次いで、時刻t4において交流電流Ivwがゼロクロス点を通るとき、選択指令部22において、比較器42の出力信号φ42がHレベルになり、フリップフロップ35がリセットされるとともにフリップフロップ44がセットされ、選択指令信号SE2AがLレベルにされるとともに選択指令信号SE2BがHレベルにされる。 図5は、図1に示した単位変換器5の構成を示す回路ブロック図である。図5を参照して、単位変換器5は、主回路50と、制御回路60と、限流抵抗回路64と、電源65とを含む。図5では、アームA1に含まれる単位変換器5が示されており、この単位変換器5は制御装置7,8から制御信号CNT1A,CNT1Bおよび選択指令信号SE1A,SE1Bを受ける。 主回路50は、コンデンサを備えたフルブリッジ回路により構成される。具体的には、主回路50は、第1端子5aおよび第2端子5bを有する。主回路50は、スイッチング素子51~54と、ダイオードD1~D4と、コンデンサ55とを含む。主回路50は、スイッチング素子51~54の導通/非導通を制御することによりコンデンサ55の電圧に応じた振幅の電圧パルスを第1端子5aおよび第2端子5b間に出力することで、電力変換を行なう。 スイッチング素子51~54は、自己消弧型電力用半導体素子であり、たとえばIGBT(Insulated Gate Bipolar Transistor)で構成されている。スイッチング素子51,53は第1の直流ラインPLおよび第2の直流ラインNLの間に直列に接続されている。スイッチング素子52,54は第1の直流ラインPLおよび第2の直流ラインNLの間に直列に接続されている。スイッチング素子51,52のコレクタはともに第1の直流ラインPLに接続され、スイッチング素子53,54のエミッタはともに第2の直流ラインNLに接続されている。スイッチング素子51のエミッタとスイッチング素子53のコレクタとの接続点は第1端子5aに接続されている。スイッチング素子52のエミッタとスイッチング素子54のコレクタとの接続点は第2端子5bに接続されている。 ダイオードD1~D4は、スイッチング素子51~54にそれぞれ逆並列に接続されている。コンデンサ55は、第1の直流ラインPLと第2の直流ラインNLとの間に電気的に接続され、直流電力を蓄える。 単位変換器5において、スイッチング素子51~54の各々の導通/非導通は制御回路60によって制御される。スイッチング素子51,53はそれぞれ相補的に導通状態とされる。スイッチング素子52,54はそれぞれ相補的に導通状態とされる。図5に示されるように、第2端子5bを基準とした第1端子5aまでの電圧をセル電圧Vcellと定義すると、セル電圧Vcellは、スイッチング素子51~54の導通/非導通によって制御される。 具体的には、スイッチング素子51,54が共に導通状態であり、スイッチング素子52,53が共に非導通状態である場合、セル電圧Vcellはコンデンサ55の直流電圧Vdcと略等しい。スイッチング素子51,52が共に導通状態であり、スイッチング素子53,54が共に非導通状態である場合、セル電圧Vcellは略零である。スイッチング素子51,52が共に非導通状態であり、スイッチング素子53,54が共に導通状態である場合、セル電圧Vcellは略零である。スイッチング素子51,54が共に非導通状態であり、スイッチング素子52,53が共に導通状態である場合、セル電圧Vcellはコンデンサ55の直流電圧Vdcの極性を反転させた電圧に略等しい。 アームA1~A3各々の全体の電圧は、対応するアームA1~A3に含まれる各単位変換器5のセル電圧Vcellの和で表される。したがって、アームA1~A3各々の全体の電圧は、各単位変換器5を構成するスイッチング素子51~54の導通/非導通によって制御することができる。 主回路50は、スイッチS7をさらに含む。スイッチS7は、第1端子5aと第2端子5bとの間に接続されている。スイッチS7は、制御回路60からの導通指令信号Sonに応じて閉成することにより、第1端子5aおよび第2端子5bを短絡することが可能に構成されている。 制御回路60は、I/F(インターフェイス)回路61と、駆動回路62と、スイッチ操作回路63とを含む。制御回路60は、制御装置7,8から受信した制御信号CNT1A,CNT1Bおよび選択指令信号SE1A,SE1Bに従ってスイッチング素子51~54の導通/非導通を制御するように構成される。 I/F回路61は、図示しない有線または無線で制御装置7,8と通信する。I/F回路61は、制御装置7,8から制御信号CNT1A,CNT1Bを受ける。制御信号CNT1Aは、主回路50のフルブリッジ回路を制御するためのゲート信号GC1a~GC4aと、フルブリッジ回路を構成するスイッチング素子51~54を全て非導通に固定するためのゲートブロック信号GBaと、フルブリッジ回路を構成するスイッチング素子51~54の非導通固定を解除するためのゲートデブロック信号DEBaと、対応する単位変換器5が故障した場合にスイッチS7を導通状態にするための導通指令信号SONaとを含む。制御信号CNT1Bは、制御信号CNT1Aと同様に、ゲート信号GC1b~GC4bと、ゲートブロック信号GBbと、ゲートデブロック信号DEBbと、導通指令信号SONbとを含む。 より具体的には、スイッチング素子51~54を全て非導通に固定するときには、ゲートブロック信号GBa,GBbは、Hレベルに活性化される。ゲートブロック信号GBa,GBbのHレベルの活性化に応じて、ゲートデブロック信号DEBa,DEBbは、Lレベルに非活性化される。 スイッチング素子51~54の非導通固定を解除するときには、ゲートデブロック信号DEBa,DEBbは、Hレベルに活性化される。ゲートデブロック信号DEBa,DEBbのHレベルの活性化に応じて、ゲートブロック信号GBa,GBbは、Lレベルに非活性化される。 対応する単位変換器5が故障したときには、導通指令信号SONa,SONbは、Hレベルに活性化される。対応する単位変換器5が正常であるときには、導通指令信号SONa,SONbは、Lレベルに非活性化される。 また、IF回路61は、制御装置7,8から、制御信号CNT1A,CNT1Bのうちのいずれかの制御信号を選択するための選択指令信号SE1A,SE1Bを受ける。制御信号CNT1Aが選択された場合には、選択指令信号SE1A,SE1BはそれぞれHレベルおよびLレベルにされる。制御信号CNT1Bが選択された場合には、選択指令信号SE1A,SE1BはそれぞれLレベルおよびHレベルにされる。 選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされた場合には、I/F回路61は、制御装置7から受信した信号GC1a~GC4a、信号GBa、および信号DEBaを、それぞれゲート信号GC1~GC4、ゲートブロック信号GB、およびゲートデブロック信号DEBとして駆動回路62に与えるとともに、制御装置7から受信した信号SONaを導通指令信号SONとしてスイッチ操作回路63に与える。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされた場合には、I/F回路61は、制御装置8から受信した信号GC1b~GC4b、信号GBb、および信号DEBbを、それぞれゲート信号GC1~GC4、ゲートブロック信号GB、およびゲートデブロック信号DEBとして駆動回路62に与えるとともに、制御装置8から受信した信号SONbを導通指令信号SONとしてスイッチ操作回路63に与える。 駆動回路62は、ゲート信号GC1~GC4に応答してスイッチング素子51~54の導通/非導通を制御する。駆動回路62は、ゲートブロック信号GBに応答して、スイッチング素子51~54を非導通状態に固定された状態(停止状態、またはゲートブロック状態)とする。駆動回路62は、ゲートデブロック信号DEBに応答して、スイッチング素子51~54の非導通固定状態が解除された状態(ゲートブロック状態ではない状態、またはゲートデブロック状態)とする。 言い換えると、ゲートブロック信号GBがHレベル、およびゲートデブロック信号DEBがLレベルのときに、スイッチング素子51~54は、ゲートブロック状態となる。ゲートブロック信号GBがLレベル、およびゲートデブロック信号DEBがHレベルのときに、スイッチング素子51~54は、ゲートブロック状態ではない状態となる。 制御装置7,8は、アームA1内のすべての単位変換器5へのゲートブロック信号GBa,GBbのレベルおよびゲートデブロック信号DEBa,DEBbのレベルを同時に制御する。これによって、アームA1内のすべての単位変換器5のスイッチング素子51~54は、同時に非導通となるとともに、同時に非導通固定が解除される。アームA2、およびアームA3についても同様である。 スイッチ操作回路63は、スイッチS7を操作するための回路である。スイッチ操作回路63は、励磁コイル56への通電を導通指令信号SONに応じて制御する。通常動作時、励磁コイル56への電流供給が停止されているため、スイッチS7は非導通状態とされる。一方、制御装置7,8は、複数の単位変換器5のうちのいずれかの単位変換器5において、スイッチング素子の短絡故障等の異常を検知した場合には、この故障した単位変換器5に対応する導通指令信号SONa,SONbをHレベルにする。 故障した単位変換器5では、I/F回路61が信号SONaまたはSONbを導通指令信号SONとしてスイッチ操作回路63へ出力する。導通指令信号SONがHレベルにされたことに応じてスイッチ操作回路63が励磁コイル56に電流を供給することにより、スイッチS7が導通状態にされる。これにより、故障した単位変換器5の出力が短絡される。 限流抵抗回路64は、主回路50と電源65との間の第1の直流ラインPLに介挿される。限流抵抗回路64は、コンデンサ55の直流電圧Vdcを降圧する。電源65は、入力端子65a,65bを含む。入力端子65aは第1の直流ラインPLに接続される。入力端子65bは第2の直流ラインNLに接続される。電源65は、コンデンサ55に電気的に並列に接続される。電源65は、コンデンサ55の電圧を降圧して電源電圧を生成し、電源電圧を制御回路60へ供給する。これにより、単位変換器5は、主回路50から制御回路60に電力を供給することができる自給式のセルを形成する。 図6は、図5に示したI/F回路61の要部を示す回路ブロック図である。図6において、I/F回路61は、ゲート回路71~74、およびORゲート75~77を含む。選択指令信号SE1A,SE1Bは、ゲート回路71~74の各々に与えられる。ゲート信号GC1a~GC4aは、それぞれゲート回路71~74に与えられる。ゲート信号GC1b~GC4bは、それぞれゲート回路71~74に与えられる。ゲート回路71~74は、それぞれゲート信号GC1~GC4を駆動回路62に出力する。 選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされている場合には、ゲート信号GC1a~GC4aがそれぞれゲート回路71~74を通過してゲート信号GC1~GC4となる。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされている場合には、ゲート信号GC1b~GC4bがそれぞれゲート回路71~74を通過してゲート信号GC1~GC4となる。 選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされている場合に、選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされたときには、所定時間Tcだけゲート信号GC1a~GC4a,GC1b~GC4bがゲート回路71~74によって一旦遮断された後に、ゲート信号GC1b~GC4bがそれぞれゲート回路71~74を通過してゲート信号GC1~GC4となる。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされている場合に、選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされたときには、所定時間Tcだけゲート信号GC1a~GC4a,GC1b~GC4bがゲート回路71~74によって一旦遮断された後に、ゲート信号GC1a~GC4aがそれぞれゲート回路71~74を通過してゲート信号GC1~GC4となる。 図7は、ゲート回路71の構成を示す回路ブロック図である。図7において、ゲート回路71は、ワンショットパルス発生回路81,82、ゲート回路83,84、およびORゲート85を含む。 ワンショットパルス発生回路81は、選択指令信号SE1Aに応答して信号φ81を出力する。選択指令信号SE1AがLレベルにされている場合には、信号φ81はLレベルにされている。選択指令信号SE1AがLレベルからHレベルに立ち上げられた場合には、信号φ81は所定時間TcだけHレベルにされた後にLレベルにされる。選択指令信号SE1AがHレベルからLレベルに立ち下げられた場合には、信号φ81は直ぐにLレベルにされる。 ワンショットパルス発生回路82は、選択指令信号SE1Bに応答して信号φ82を出力する。選択指令信号SE1BがLレベルにされている場合には、信号φ82はLレベルにされている。選択指令信号SE1BがLレベルからHレベルに立ち上げられた場合には、信号φ82は所定時間TcだけHレベルにされた後にLレベルにされる。選択指令信号SE1BがHレベルからLレベルに立ち下げられた場合には、信号φ82は直ぐにLレベルにされる。 ゲート回路83は、ゲート信号GC1a、選択指令信号SE1A、および信号φ81を受けて信号φ83を出力する。選択指令信号SE1AがHレベルにされ、かつ信号φ81がLレベルである場合には、ゲート信号GC1aがゲート回路83を通過して信号φ83となる。選択指令信号SE1AがLレベルにされている場合には、ゲート信号GC1aはゲート回路83によって遮断され、信号φ83はLレベルに固定される。また、信号φ81がHレベルである場合には、ゲート信号GC1aはゲート回路83によって遮断され、信号φ83はLレベルに固定される。 ゲート回路84は、ゲート信号GC1b、選択指令信号SE1B、および信号φ82を受けて信号φ84を出力する。選択指令信号SE1BがHレベルにされ、かつ信号φ82がLレベルである場合には、ゲート信号GC1bがゲート回路84を通過して信号φ84となる。選択指令信号SE1BがLレベルにされている場合には、ゲート信号GC1bはゲート回路84によって遮断され、信号φ84はLレベルに固定される。また、信号φ82がHレベルである場合には、ゲート信号GC1bはゲート回路84によって遮断され、信号φ84はLレベルに固定される。ORゲート85は、信号φ83,φ84の論理和信号をゲート信号GC1として出力する。 選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされている場合には、ゲート信号GC1bがゲート回路84によって遮断され、ゲート信号GC1aがゲート回路83およびORゲート85を通過してゲート信号GC1となる。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされている場合には、ゲート信号GC1aがゲート回路83によって遮断され、ゲート信号GC1bがゲート回路84およびORゲート85を通過してゲート信号GC1となる。 選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされている場合に、選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされたときには、ゲート信号GC1aがゲート回路83によって遮断される。また、ワンショットパルス発生回路82によって信号φ82が所定時間TcだけHレベルに立ち上げられ、所定時間Tcだけゲート信号GC1bがゲート回路84によって一旦遮断された後に、ゲート信号GC1bがゲート回路84およびORゲート85を通過してゲート信号GC1となる。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされている場合に、選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされたときには、ゲート信号GC1bがゲート回路84によって遮断される。また、ワンショットパルス発生回路81によって信号φ81が所定時間TcだけHレベルに立ち上げられ、所定時間Tcだけゲート信号GC1aがゲート回路83によって一旦遮断された後に、ゲート信号GC1aがゲート回路83およびORゲート85を通過してゲート信号GC1となる。 図8は、図6に示したゲート回路71,73の効果および問題点を説明するためのタイムチャートである。図8において、(A)~(D)はそれぞれゲート信号GC1a,GC3a,GC1b,GC3bの波形を示し、(E),(F)はそれぞれ選択指令信号SE1A,SE1Bの波形を示し、(G),(H)はそれぞれワンショットパルス信号φ81,φ82の波形を示している。ゲート信号GC1a,GC3a,GC1b,GC3bの各々は、PWM(Pulse Width Modulation)信号である。 ゲート信号GC1aとゲート信号GC3aは、互いに相補な信号である。ゲート信号GC1a,GC3aがゲート信号GC1,GC3として駆動回路62(図5)に与えられている場合、ゲート信号GC1a,GC3aがそれぞれHレベルおよびLレベルであるときには、スイッチング素子51(図5)が導通状態にされるとともにスイッチング素子53(図5)が非導通状態にされる。また、ゲート信号GC1a,GC3aがそれぞれLレベルおよびHレベルであるときには、スイッチング素子51が非導通状態にされるとともにスイッチング素子53が導通状態にされる。 同様に、ゲート信号GC1bとゲート信号GC3bは、互いに相補な信号である。ゲート信号GC1b,GC3bがゲート信号GC1,GC3として駆動回路62に与えられている場合、ゲート信号GC1b,GC3bがそれぞれHレベルおよびLレベルであるときには、スイッチング素子51が導通状態にされるとともにスイッチング素子53が非導通状態にされる。また、ゲート信号GC1b,GC3bがそれぞれLレベルおよびHレベルであるときには、スイッチング素子51が非導通状態にされるとともにスイッチング素子53が導通状態にされる。 制御装置7によって生成されるゲート信号GC1a,GC3aの位相と、制御装置8によって生成されるゲート信号GC1b,GC3bの位相とは、理想的には一致しているが、実際には若干ずれる。図8では、ゲート信号GC1a,GC3aの位相がゲート信号GC1b,GC3bの位相よりも若干遅れている場合が示されている。このため、ゲート信号GC1aとゲート信号GC3bの両方がHレベルになる期間(時刻t1~t3)が存在する。 初期状態(時刻t0)では、選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされており、ゲート信号GC1a,GC3aがゲート信号GC1,GC3として駆動回路62(図5)に与えられているものとする。また、時刻t1と時刻t3の間の時刻t2において、選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルに切り換えられたものとする。 このような場合において、選択指令信号SE1A,SE1Bの切換に応答して、直ぐにゲート信号GC1,GC2をゲート信号GC1a,GC3aからゲート信号GC1b,GC3bに切り換えると、スイッチング素子51がまだ導通状態であるのにスイッチング素子53が導通状態になる恐れがある。スイッチング素子51,53が同時に導通状態になると、コンデンサ55の端子間がスイッチング素子51,53によって短絡され、過電流が流れてスイッチング素子51,53などが破損する恐れがある。 これに対してゲート回路71では、選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルに切り換えられると、ワンショットパルス発生回路82の出力信号φ82が所定時間TcだけHレベルになり、所定時間Tcだけゲート信号GC1,GC3がともにLレベルにされ、スイッチング素子51,53が非導通状態にされる。したがって、スイッチング素子51,53が同時に導通状態になることが防止される。ゲート回路72,73,74の各々は、ゲート回路71と同様の構成であるので、その説明は繰り返さない。 なお、本実施の形態では、ゲート回路71~74により、選択指令信号SE1A,SE1Bのレベルを切り換える時に所定時間Tcだけ全てのゲート信号GC1~GC4をLレベルに固定する。したがって、スイッチング素子51,53(またはスイッチング素子52,54)が同時に導通状態になることを防止することができる反面、所定時間Tcだけスイッチング素子51~54のPWM制御が停止されることとなる。 このため、選択指令信号SE1A,SE1Bのレベルの切換を任意のタイミングで行なうと、所定時間Tcだけスイッチング素子51~54のPWM制御が停止され、交流電流Iuvの波形が歪む恐れがある。しかし、本実施の形態では、交流電流Iuvがゼロクロス点を通るときに選択指令信号SE1A,SE1Bのレベルを切り換えるので、交流電流Iuvの波形歪を十分に小さく抑制することができる。 図6に戻って、ORゲート75は、制御装置7,8からのゲートブロック信号GBa,GBbの論理和信号をゲートブロック信号GBとして駆動回路62に出力する。ORゲート76は、制御装置7,8からのゲートデブロック信号DEBa,DEBbの論理和信号をゲートデブロック信号DEBとして駆動回路62に出力する。ORゲート77は、導通指令信号SONa,SONbの論理和信号を導通指令信号SONとして駆動回路62に出力する。 なお、制御装置7,8からのゲート信号GC1a,GC1bの論理和信号をゲート信号GC1とすることはできない。図8で示したように、ゲート信号GC1aの位相とゲート信号GC1bの位相とがずれている場合には、ゲート信号GC1のパルス幅が拡がってしまい、正確にPWM制御をすることができないからである。 次に、図1~図8に示した電力変換装置100の動作について説明する。ここでは、説明の簡単化を図るために、アームA1に関連する動作のみについて説明する。今、操作部6(図1)を用いて制御装置7が選択され、選択信号SEがLレベルにされているものとする。選択信号SEがLレベルにされているので、選択指令部11,21(図2)によって選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされる。 制御部10(図2)は、選択信号SEのレベルに関係なく、アームA1を制御するための制御信号CNT1Aを生成する。制御部20(図2)は、選択信号SEのレベルに関係なく、アームA1を制御するための制御信号CNT1Bを生成する。制御信号CNT1A,CNT1Bおよび選択指令信号SE1A,SE1Bは、アームA1の各単位変換器5に含まれるI/F回路61(図5)に与えられる。 I/F回路61は、選択指令信号SE1A,SE1BがそれぞれHレベルおよびLレベルにされているので、制御信号CNT1Aを通過させる。制御信号CNT1Aに含まれるゲート信号GC1a~GC4aがI/F回路61を通過してゲート信号GC1~GC4となる。駆動回路62は、ゲート信号GC1~GC4に従ってスイッチング素子51~54を駆動させる。 次に、操作部6(図1)を用いて制御装置8が選択され、選択信号SEがLレベルからHレベルに立ち上げられたものとする。選択信号SEがLレベルからHレベルに立ち上げられると、選択指令部11,21により、アームA1に流れる交流電流Iuvがゼロクロス点を通るときに、選択指令信号SE1AがHレベルからLレベルに立ち下げられるとともに、選択指令信号SE1BがLレベルからHレベルに立ち上げられる(図4の時刻t2)。 選択指令信号SE1A,SE1BがそれぞれLレベルおよびHレベルにされると、ゲート回路71~74(図6)は、所定時間Tc(図8)だけゲート信号GC1a~GC4a,GC1b~GC4bの通過を遮断した後に、ゲート信号GC1b~GC4bを通過させる。ゲート回路71~74を通過したゲート信号GC1b~GC4bは、駆動回路62に与えられる。駆動回路62は、ゲート信号GC1~GC4に従ってスイッチング素子51~54を駆動させる。 以上のように、本実施の形態では、選択信号SEのレベルが切換えられた場合には、交流電流Iuvの絶対値がしきい値電流ITHよりも小さくなったときに、選択指令信号SE1A,SE1Bのレベルを切り換えてゲート信号GC1~GC4を切り換える。したがって、ゲート信号GC1~GC4の切換時における交流電流Iuvの波形歪を小さく抑制することができる。 図9は、実施の形態の比較例の要部を示す回路ブロック図であって、図2と対比される図である。図9を参照して、この比較例は、電力変換装置100の制御装置7,8を制御装置7A,8Aで置換したものである。制御装置7Aは、制御装置7の選択指令部11~13をインバータ91~93で置換したものである。制御装置8Aは、制御装置8の選択指令部21~23をバッファ94~96で置換したものである。 選択信号SEは、インバータ91~93およびバッファ94~96の各々に与えられる。インバータ91~93の出力信号は選択指令信号SE1A~SE3Aとなり、バッファ94~96の出力信号は選択指令信号SE1B~SE3Bとなる。 図10は、図9で示した比較例の問題点を説明するためのタイムチャートであって、図4と対比される図である。図10において、(A)は三相交流電流Iuv,Ivw,Iwuの波形を示し、(B)は選択信号SEの波形を示し、(C)~(E)はそれぞれ選択指令信号SE1A~SE3Aの波形を示し、(F)~(H)はそれぞれ選択指令信号SE1B~SE3Bの波形を示している。 ある時刻t0において、選択信号SEがLレベルにされているものとする。選択信号SEがLレベルにされている場合には、インバータ91~93によって選択指令信号SE1A~SE3AがHレベルにされるとともに、バッファ94~96によって選択指令信号SE1B~SE3BがLレベルにされる。この場合、制御装置7からのゲート信号GC1a~GC4aがゲート回路71~74(図6)を通過して駆動回路62に与えられ、駆動回路62によってスイッチング素子51~54が駆動される。 ある時刻t1において、選択信号SEがLレベルからHレベルに立ち上げられると、インバータ91~93によって選択指令信号SE1A~SE3AがLレベルにされるとともに、バッファ94~96によって選択指令信号SE1B~SE3BがHレベルにされる。選択指令信号SE1A~SE3A,SE1B~SE3Bのレベルが切換えられると、ゲート回路71~74(図6)によって所定時間Tcだけゲート信号GC1a~GC4a,GC1b~GC4bが一旦遮断された後、ゲート信号GC1b~GC4bがゲート回路71~74を通過して駆動回路62に与えられ、駆動回路62によってスイッチング素子51~54が駆動される。 この比較例では、選択信号SEのレベルが切換えられた場合には、直ぐに選択指令信号SE1A,SE1B,...のレベルを切り換えてゲート信号GC1~GC4を切り換える。したがって、交流電流Iuv,Ivw,Iwuがゼロクロス点を通るときにゲート信号GC1~GC4を切り換える実施の形態に比べ、図10(A)に示すように、交流電流Iuv,Ivw,Iwuの波形歪が大きくなる。 今回開示された実施の形態はすべての点で例示であって制限的なものではないと考えられるべきである。本発明は上記した説明ではなくて請求の範囲によって示され、請求の範囲と均等の意味および範囲内でのすべての変更が含まれることが意図される。 1 電力系統、S1~S7 スイッチ、2,3 変圧器、R1~R3 限流抵抗器、UL,VL,WL 交流ライン、C1~C3 変流器、L1~L3 リアクトル、A1~A3 アーム、6 操作部、7,8 制御装置、10,20 制御部、11~13,21~23 選択指令部、31,41 絶対値検出器、32,42 比較器、33,91~93 インバータ、34,43,83,84 ANDゲート、35,44 フリップフロップ、50 主回路、51~54 スイッチング素子、D1~D4 ダイオード、55 コンデンサ、60 制御回路、61 I/F回路、62 駆動回路、63 スイッチ操作回路、64 限流抵抗回路、65 電源、71~74 ゲート回路、75~77,85 ORゲート、81,82 ワンショットパルス発生回路、94~96 バッファ、100 電力変換装置。 [EN WO2021070323A1]: Power converter The present invention relates to a power converter, and more specifically to a power converter comprising a power converter that transfers power between a capacitor and an AC power source. In recent years, in static magneto compensators such as STATCOM (Static Synchronous Compensator), DC power transmission systems such as BTB (Back to Back) systems, and motor drive inverters, modular multilevel converters (MMCs) have been used. The application of Converter) is being considered (see, for example, International Publication No. 2016/203516 (Patent Document 1)). The MMC is configured by connecting a plurality of unit converters in series. The unit converter drives a power converter based on a capacitor, a power converter that transfers power between the capacitor and an AC power supply, and a control signal supplied from a higher-level control device that controls the entire MMC. It is equipped with a drive circuit. International Publication No. 2016/203516 When controlling MMC with only one control device, it is necessary to stop the operation of MMC when performing maintenance on that control device. As a countermeasure against this, a method in which two control devices are provided and one control device is maintained and the MMC is controlled by the other control device can be considered. However, in this method, the waveform of the AC current flowing between the AC power supply and the power converter may be distorted when the control signal is switched. Therefore, an object of the present invention is to provide a power conversion device capable of suppressing the waveform distortion generated in an alternating current when switching a control signal to a small extent. The power converter of the present invention includes a capacitor, a power converter that transfers power between the capacitor and an AC power supply, and a current detector that detects an instantaneous value of an AC current flowing between the AC power supply and the power converter. And the first and second control units that output the first and second control signals, the gate circuit that passes the selected control signal from the first and second control signals, and the gate circuit. It is provided with a drive circuit that drives a power converter based on a passed control signal. When the second control signal is selected when the gate circuit is passing the first control signal, the absolute value of the instantaneous value of the alternating current detected by the current detector is larger than the predetermined value. According to the decrease, the first control signal is blocked and the second control signal is passed. According to the present invention, the control signal is switched when the absolute value of the instantaneous value of the alternating current is smaller than a predetermined value, so that the waveform distortion generated in the alternating current when the control signal is switched can be suppressed to a small value. it can. It is a circuit block diagram which shows the structure of the power conversion apparatus of embodiment. It is a block diagram which shows the main part of the control devices 7 and 8 shown in FIG. It is a circuit block diagram which shows the structure of the selection command part 11, 21 shown in FIG. It is a time chart which illustrates the operation of the selection command part 11 ~ 13, 21 ~ 23 shown in FIG. It is a circuit block diagram which shows the structure of the unit converter 5 shown in FIG. It is a circuit block diagram which shows the main part of the I / F circuit 61 shown in FIG. It is a circuit block diagram which shows the structure of the gate circuit 71 shown in FIG. It is a time chart for demonstrating the effect and problem of the gate circuits 71 to 74 shown in FIG. It is a circuit block diagram which shows the comparative example of embodiment. It is a time chart for demonstrating the problem of the comparative example shown in FIG. Hereinafter, embodiments will be described in detail with reference to the drawings. The same or corresponding parts in the drawings are designated by the same reference numerals, and the description thereof will not be repeated. FIG. 1 is a circuit block diagram showing a configuration of a power conversion device according to an embodiment. The power conversion device 100 is used as a static power compensator that compensates for the static power of the power system 1 (AC power supply). With reference to FIG. 1, the power converter 100 controls arms A1 to A3 configured by connecting at least one main circuit power supply type unit converter 5 in series, and each controls all unit converters 5. It is equipped with two control devices 7 and 8 configured in. More specifically, the power converter 100 includes switches S1 to S6, transformers 2,3, current limiting resistors R1 to R3, AC lines UL, VL, WL, current transformers C1 to C3, reactors L1 to L3, It is equipped with arms A1 to A3, an operation unit 6, and control devices 7 and 8. One terminal of each of the switches S1, S2, S3 is connected to the three-phase transmission lines 1u, 1v, 1w of the power system 1, and the other terminal is connected to the three primary windings of the transformer 2, respectively. The switches S1, S2, and S3 are normally in a conductive state, and are brought into a non-conducting state during maintenance of, for example, the power converter 100. Transformer 2 includes three primary windings and three secondary windings to transfer three-phase AC power. One terminal of each of the current limiting resistors R1 to R3 is connected to each of the three secondary windings of the transformer 2, and the other terminal is connected to the AC lines UL, VL, and WL, respectively. The current limiting resistors R1 to R3 limit the current flowing from the power system 1 to the arms A1 to A3 when the power converter 100 is started. The switches S4, S5, and S6 are connected in parallel to the current limiting resistors R1 to R3, respectively. The switches S4, S5, and S6 are put into a conductive state after the currents flowing through the arms A1 to A3 are stabilized when the power converter 100 is started. The transformer 3 outputs three-phase AC voltages Vu, Vv, and Vw corresponding to the AC voltages of the AC lines UL, VL, and WL to each of the control devices 7 and 8. The reactor L1 and the arm A1 are connected in series between the AC line UL and the AC line VL. The reactor L2 and arm A2 are connected in series between the AC line VL and the AC line WL. The reactor L3 and arm A3 are connected in series between the AC line WL and the AC line UL. That is, the arms A1 to A3 are delta-connected. The arms A1 to A3 are controlled by the control device selected from the control devices 7 and 8, and generate three-phase AC power. Each of the arms A1 to A3 includes a plurality of cascaded unit converters 5. Each of the plurality of unit converters 5 is controlled by a selected control device among the control devices 7 and 8, and generates AC power. The first terminal 5a of the unit converter 5 in the first stage of the arm A1 is connected to one terminal of the reactor L1. In the arm A1, the second terminal 5b of the unit converter 5 other than the final stage is connected to the first terminal 5a of the unit converter 5 in the subsequent stage. The second terminal 5b of the unit converter 5 in the final stage of the arm A1 is connected to one terminal of the reactor L2. The first terminal 5a of the unit converter 5 in the first stage of the arm A2 is connected to one terminal of the reactor L2. In the arm A2, the second terminal 5b of the unit converter 5 other than the final stage is connected to the first terminal 5a of the unit converter 5 in the subsequent stage. The second terminal 5b of the unit converter 5 in the final stage of the arm A2 is connected to one terminal of the reactor L3. The first terminal 5a of the unit converter 5 in the first stage of the arm A3 is connected to one terminal of the reactor L3. In the arm A3, the second terminal 5b of the unit converter 5 other than the final stage is connected to the first terminal 5a of the unit converter 5 in the subsequent stage. The second terminal 5b of the unit converter 5 in the final stage of the arm A3 is connected to one terminal of the reactor L1. The reactors L1 to L3 suppress the circulating current flowing through the arms A1 to A3, respectively. The reactors L1 to L3 may be provided separately from the arms A1 to A3, or may be an inductance component of the arms A1 to A3. The current transformers C1 to C3 (current detectors) detect the instantaneous values of the alternating currents Iuv, Ivw, and Iwu flowing through the arms A1 to A3, and output them to the control devices 7 and 8, respectively. The operation unit 6 (selection unit) includes a plurality of buttons, a plurality of switches, an image display device, and the like, and is operated by a user of the power conversion device 100. By operating the operation unit 6, the user of the power conversion device 100 can select a desired control device from the control devices 7 and 8 and start or stop the operation of the power conversion device 100. it can. The operation unit 6 sets the selection signal SE to the L level when the control device 7 is selected, and sets the selection signal SE to the H level when the control device 8 is selected. For example, normally, the selection signal SE is s
[KO KR20200124459A]: HILS를 이용한 MMC의 구성요소 테스트 장치 [EN KR20200124459A]: HILS MMC APPARATUS FOR TESTING COMPONENTS OF MMC USING HILS | [KO KR20200124459A]: 본 발명은 HILS를 이용한 MMC의 구성요소 테스트 장치에 관한 것으로, MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 종속 전압원에 대응하여 상기 타겟 SM의 커패시터(Cmmc)의 충방전을 테스트하기 위한 전류를 인가하는 전압원 모사회로; 및 상기 MMC 전력 변환기의 타겟 SM의 동작에 대응하여 상기 전압원 모사회로의 전류원 및 스위칭 소자를 제어하고, 상기 전압원 모사회로에 의해 타겟 SM에 인가된 전류에 의해 충방전되는 상기 커패시터(Cmmc)의 전압(JPEGpat00034.jpg713)을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함한다. [EN KR20200124459A]: The present invention relates to a modular multi-level converter (MMC) component test device using a hardware-in-the-loop system (HILS), comprising: an HILS for generating a simulation model by replacing a target sub-module (SM) to be tested in an MMC with a dependent voltage source, and verifying the simulation model; a voltage source simulated circuit for applying current for testing the charging/discharging of a capacitor (Cmmc) of the target SM to correspond to the dependent voltage source; and an HILS control unit for controlling a current source of the voltage source simulated circuit and a switching element to correspond to an operation of the target SM of the MMC, and verifying the simulation model using voltage (U_cmmc) of the capacitor (Cmmc) charged and discharged by the current applied to the target SM by the voltage source simulated circuit. According to the present invention, the operation for SM can be tested. | KR20200124459A | 2020-11-03 | KR20190047800A | 2019-04-24 | KR20190047800A, 2019-04-24 | KR20200124459A: 2020-11-03 | KOREA ELECTRIC POWER CORP HONGIK UNIV INDUSTRY ACADEMIA COOPERATION FOUNDATION | LEE DONG MYUNG | G01R31/3185: I G01R31/3183: I G01R31/40: I H02M7/483: I | G01R31/318314: I G01R31/318364: I G01R31/318513: I G01R31/40: I H02M7/483: I |  |  | [KO KR20200124459A]: MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 종속 전압원에 대응하여 상기 타겟 SM의 커패시터(Cmmc)의 충방전을 테스트하기 위한 전류를 인가하는 전압원 모사회로; 및 상기 MMC 전력 변환기의 타겟 SM의 동작에 대응하여 상기 전압원 모사회로의 전류원 및 스위칭 소자를 제어하고, 상기 전압원 모사회로에 의해 타겟 SM에 인가된 전류에 의해 충방전되는 상기 커패시터(Cmmc)의 전압()을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 1항에 있어서, 상기 전압원 모사회로는, 상기 HILS 제어부로부터 전류의 방향과 크기가 제어되는 전류원(isource); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1); 상기 제1 스위칭 소자(SH1)의 드레인 측에 애노드 측이 연결되는 제1 다이오드(DH1); 상기 제1 다이오드(DH1)의 캐소드 측에 소오스 측이 연결되는 제2 스위칭 소자(SH2); 상기 제2 스위칭 소자(SH2)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제2 다이오드(DH2); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제3 스위칭 소자(SH3); 상기 제3 스위칭 소자(SH3)의 드레인 측에 애노드 측이 연결되는 제3 다이오드(DH3); 상기 제3 다이오드(DH3)의 캐소드 측에 소오스 측이 연결되는 제4 스위칭 소자(SH4); 및 상기 제4 스위칭 소자(SH4)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제4 다이오드(DH4)가 연결되어 구현되는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 2항에 있어서, 상기 제1 다이오드(DH1)와 상기 제1 스위칭 소자(SH2)의 접속점(A)에 타겟 SM의 커패시터(Cmmc)의 양극(+)이 접속되고, 상기 제3 다이오드(DH3)와 상기 제4 스위칭 소자(SH4)의 접속점(B)에 커패시터(Cmmc)의 음극(-)이 접속되는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 2항에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 스위칭 소자의 온오프 및 전류(immc)의 방향과 크기에 대응하여 상기 전압원 모사회로의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 2항에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 하단 스위치(S2)가 ON인 SF(Switch Function)=0인 경우, 전류(immc)의 방향에 관계없이 커패시터 전압()의 변화는 없으므로, 전류원(isource)의 흐름 및 커패시터(Cmmc)의 충방전에 관여하지 않으며, 상기 타겟 SM의 상단 스위치(S1)가 ON인 SF=1이고 전류(immc)가 음인 경우, 커패시터 전압()이 충전되는 상황을 모사하기 위하여 제1 및 제4 스위칭 소자(SH1 and SH4)의 온(ON) 스위칭 제어를 수행하며, 또한 상기 타겟 SM의 SF=1이고, 전류(immc)가 양인 경우, 커패시터 전압()이 방전되는 상황을 모사하기 위하여 제2 및 제3 스위칭 소자(SH2 and SH3)의 온(ON) 스위칭 제어를 수행하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 2항에 있어서, 상기 HILS 제어부는, MMC 시뮬레이션 모델링 결과를 바탕으로, 상기 전류원에 의해 인가되는 전류(immc)의 크기를 제어하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 2항에 있어서, 상기 다이오드(DH1 ~ DH4)는, 커패시터(Cmmc)의 쇼트(short) 방지 및 회생 방지용 다이오드인 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 타겟 SM의 커패시터(Cmmc)를 테스트하기 위한 전류를 상기 타겟 SM의 지정된 접속점(A, B)에 직접 인가하는 전류 공급부; 및 상기 전류 공급부의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어하며, 또한 상기 타겟 SM의 스위칭 소자(S1, S2)를 온오프를 제어하여 측정되는 커패시터(Cmmc)의 전압(Vcmmc) 값을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 8항에 있어서, 상기 전류 공급부는, HILS 제어부로부터 전류의 방향과 크기가 제어되는 전류원(isource); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1) 및 제3 스위칭 소자(SH3); 상기 제1 스위칭 소자(SH1) 및 상기 제3 스위칭 소자(SH3)의 드레인 측에 소오스 측이 각기 연결되는 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4); 상기 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4)의 드레인 측이 상기 전류원(isource)의 타 측에 연결되어 구현된 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 9항에 있어서, 상기 제1 스위칭 소자(SH1)와 제2 스위칭 소자(SH2)의 접속점(A)에 상기 타겟 SM의 제1 스위칭 소자(S1)와 제2 스위칭 소자(S2)의 접속점(A)이 연결되고, 상기 제3 스위칭 소자(SH3)와 제4 스위칭 소자(SH4)의 접속점(B)에 상기 타겟 SM의 제2 스위칭 소자(S2)의 접속점(B)이 연결되어 구현된 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 종속 전압원에 대응하여 상기 타겟 SM의 커패시터(Cmmc)의 충반전을 테스트하기 위한 전류를 인가하는 충전부와 방전부; 및 상기 MMC 전력 변환기의 타겟 SM의 동작에 대응하여 상기 충전부와 방전부를 각기 제어하고, 상기 충전부와 방전부에 의해 충방전되는 상기 커패시터(Cmmc)의 전압()을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 11항에 있어서, 상기 충전부와 방전부는, 상기 타겟 SM의 기 지정된 점속점(A, B)으로서, 상기 커패시터(Cmmc)가 연결되는 양극(+) 및 음극(-)에 각기 공통으로 연결되는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. 제 11항에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 하단 스위치(S2)가 ON인 SF(Switch Function)=0인 경우, 전류(immc)의 방향에 관계없이 커패시터 전압()의 변화는 없으므로, 상기 충전부와 방전부의 제어에 관여하지 않으며, 상기 타겟 SM의 상단 스위치(S1)가 ON인 SF=1이고 전류(immc)가 음인 경우, 커패시터 전압()이 충전되는 상황을 모사하기 위하여 상기 충전부에서 상기 커패시터(Cmmc)에 충전 전류가 흐르도록 제어하며, 또한 상기 타겟 SM의 SF=1이고, 전류(immc)가 양인 경우, 커패시터 전압()이 방전되는 상황을 모사하기 위하여 상기 커패시터(Cmmc)에 충전된 전류를 방전시키기 위하여 상기 방전부를 제어하는 것을 특징으로 하는 HILS를 이용한 MMC의 구성요소 테스트 장치. [EN KR20200124459A]: A Hardware In the Loop System (HILS) for generating a simulation model by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source and verifying the simulation model; A voltage source matrix furnace for applying a current for testing the charging/discharging of the capacitor Cmmc of the target SM in response to the dependent voltage source; And a voltage of the capacitor Cmmc, which controls a current source and a switching element to the voltage source matrix in response to the operation of the target SM of the MMC power converter, and charges and discharges by the current applied to the target SM by the voltage source matrix. () Using the HILS control unit for performing verification of the simulation model; component testing device for MMC using HILS, characterized in that it comprises a. The method of claim 1, wherein the voltage source matrix comprises: a current source whose direction and magnitude of current is controlled by the HILS controller; A first switching element (SH) having a source side connected to one side of the current source (isource)1); The first switching element (SH1), the anode side is connected to the drain side of the first diode DH1); The first diode (DH1The second switching element (SH) to which the source side is connected to the cathode side of2); The second switching element (SH2), the anode side is connected to the drain side, and the other side of the current source is connected to the cathode side.2); The third switching element (SH) to which the source side is connected to one side of the current source (isource)3); The third switching element (SH3) To the drain side of the third diode (DH3); The third diode (DH3) To the cathode side of the fourth switching element (SH4); And the fourth switching element SH4), the anode side is connected to the drain side, and the other side of the current source is connected to the cathode side.4) The component test device of the MMC using HILS, characterized in that the connection is implemented. The method of claim 2, wherein the first diode (DH1) And the first switching element SH2), the anode (+) of the capacitor (Cmmc) of the target SM is connected to the connection point (A), and the third diode (DH3) And the fourth switching element (SH4) The component test device of the MMC using HILS, characterized in that the cathode (-) of the capacitor (Cmmc) is connected to the connection point (B) of. The method of claim 2, wherein the HILS controller comprises: a current source and a switching element (SH1 ~ SH4) MMC component testing device using HILS, characterized in that to control. The method of claim 2, wherein the HILS control unit, the lower switch of the target SM (S2When SF (Switch Function) = 0, where) is ON, the capacitor voltage () Because there is no change, it is not involved in the flow of the current source and the charging and discharging of the capacitor Cmmc, and the upper switch S of the target SM1) Is ON and SF=1 and current (immc) is negative, capacitor voltage () To simulate the charging situation, the first and fourth switching elements (SH1 and SH4) To perform ON switching control, and if SF=1 of the target SM and current immc is positive, the capacitor voltage () In order to simulate a discharge situation, the second and third switching elements (SH2 and SH3) On (ON) component testing device of the MMC using HILS, characterized in that performing the switching control. The apparatus of claim 2, wherein the HILS control unit controls the magnitude of the current immc applied by the current source based on the MMC simulation modeling result. The method of claim 2, wherein the diode (DH1 ~ DH4) Is a component testing device of MMC using HILS, characterized in that the capacitor (Cmmc) is a diode for preventing short and regenerative prevention. A Hardware In the Loop System (HILS) for generating a simulation model by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source and verifying the simulation model; A current supply unit for directly applying a current for testing the capacitor (Cmmc) of the target SM to a designated connection point (A, B) of the target SM; And a current source and a switching element SH of the current supply unit.1 ~ SH4) And the switching element (S) of the target SM1, S2), a HILS control unit that performs verification of the simulation model using a voltage (Vcmmc) value of a capacitor (Cmmc) measured by controlling on/off. The method of claim 8, wherein the current supply unit comprises: a current source in which the direction and magnitude of the current is controlled from the HILS controller; A first switching element (SH) having a source side connected to one side of the current source (isource)1) And a third switching element (SH3); The first switching element (SH1) And the third switching element (SH3), the source side is connected to the drain side of the second switching element (SH2) And the fourth switching element (SH4); The second switching element (SH2) And the fourth switching element (SH4) Of the drain side is connected to the other side of the current source (isource). 10. The method of claim 9, wherein the first switching element (SH1) And the second switching element (SH2The first switching element (S) of the target SM at the connection point (A) of1) And the second switching element (S2) Of the connection point (A) is connected, the third switching element (SH3) And the fourth switching element (SH4) The second switching element (S) of the target SM at the connection point (B)2) The component test device of the MMC using HILS, characterized in that the connection point (B) is connected and implemented. A Hardware In the Loop System (HILS) for generating a simulation model by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source and verifying the simulation model; A charging unit and a discharging unit for applying a current for testing the charging and recharging of the capacitor Cmmc of the target SM in response to the dependent voltage source; And a voltage of the capacitor Cmmc charged and discharged by the charging unit and the discharging unit, respectively controlling the charging unit and the discharging unit in response to the operation of the target SM of the MMC power converter () Using the HILS control unit for performing verification of the simulation model; component testing device for MMC using HILS, characterized in that it comprises a. The method of claim 11, wherein the charging unit and the discharging unit are pre-designated dot points (A, B) of the target SM and are connected in common to an anode (+) and a cathode (-) to which the capacitor Cmmc is connected. Component testing device for MMC using HILS, characterized in that. The method of claim 11, wherein the HILS control unit, the lower switch of the target SM (S2When SF (Switch Function) = 0, where) is ON, the capacitor voltage () Because there is no change, it is not involved in the control of the charging part and the discharging part,1) Is ON and SF=1 and current (immc) is negative, capacitor voltage (In order to simulate a situation in which) is charged, the charging unit controls a charging current to flow through the capacitor Cmmc, and when SF=1 of the target SM and the current immc is positive, the capacitor voltage () The component testing device of the MMC using HILS, characterized in that controlling the discharge unit to discharge the current charged in the capacitor (Cmmc) in order to simulate a discharged situation. | [KO KR20200124459A]: HILS를 이용한 MMC의 구성요소 테스트 장치{APPARATUS FOR TESTING COMPONENTS OF MMC USING HILS} 본 발명은 HILS를 이용한 MMC의 구성요소 테스트 장치에 관한 것으로, 보다 상세하게는 MMC(Modular Multi-Level Converter) 전력 변환기를 구성하는 단위인 SM(Sub Module)에 대한 동작을 테스트할 수 있도록 하는, HILS(Hardware In the Loop System)를 이용한 MMC의 구성요소 테스트 장치에 관한 것이다. 일반적으로 모듈러 멀티 레벨 컨버터(MMC : Modular Multi-Level Converter)는 멀티 레벨 컨버터의 한 종류로서 전압형 초고압직류송전(HVDC, High Voltage Direct Current) 시스템에 적합한 회로 구조로 알려져 있다. 상기 모듈러 멀티 레벨 컨버터(MMC)는 스위칭 소자로서 절연 게이트 양극성 트랜지스터(IGBT, Insulated gate bipolar transistor)를 사용하여 서브 모듈(SM : Sub Module)이라고 불리는 단위 구조를 캐스케이드로 연결하는 형태를 가지므로, 기존의 멀티 레벨 컨버터의 응용분야였던 중간 전압 구동(Medium Voltage Drive)용 전력 변환 장치(또는 전력 변환기)보다 훨씬 많은 레벨을 가지게 된다. 도 1은 일반적인 MMC의 기본 구성을 보인 예시도이고, 도 2는 하프 브리지 타입(Half Bridge Type) SM으로 구성된 일반적인 MMC의 구성을 보인 예시도이다. 또한 도 3의 (a)는 일반적인 하프 브리지 타입 SM의 형태를 보인 예시도이고, 도 3의 (b)는 일반적인 풀 브리지 타입 SM의 형태를 보인 예시도이다. 참고로 도 3의 (b)는 3상의 DC/AC 전력변환에 MMC를 적용한 예이며, 3개의 위상(phase)을 갖는다. 한편, 1개의 위상(phase)은 어퍼암(upper arm)과 로어암(lower arm)으로 구성되어 있다. 여기서 서브 모듈(이하 SM)은 MMC의 스위칭 블록의 한 단위(unit)를 의미하며, 도 3의 (a)와 같은 하프 브리지 타입의 SM과 도 3의 (b)와 같은 풀 브리지 타입의 SM이 있다. 최근 상기와 같은 MMC는 전압형 HVDC 등의 멜티 레벨 전력 변환기에 널리 적용되고 있다. 상기 HVDC(High Voltage Direct Current)의 경우 높은 전압을 블록킹 하면서 전력 변환기의 출력 전압의 고조파 성분 저감을 위하여 다수개의 SM을 직렬로 연결하여 사용한다. 예컨대 상기 HVDC의 경우, 가령 하나의 암(arm)(예 : 어퍼암, 로어암)당 200개의 SM을 갖는다고 가정할 때, 3상의 경우 6*200=1,200개의 SM이 연결되고, MMC가 연이어(back to back) 연결되므로 2,400개의 SM이 시스템(즉, MMC 전력 변환기)에 존재한다. 한편, 도 3의 (a)와 같이 SM이 하프 브리지 형태로 구성되는 경우 4,800개의 전력용 스위칭 소자가 한 시스템에 필요하며, 도 3의 (b)와 같이 SM이 풀 브리지 형태로 구성되는 경우 9,600개의 전력용 스위칭 소자가 한 시스템에 필요하다. 이처럼 MMC로 구성된 전력 변환기는 다수의 전력용 스위칭 소자를 필요로 하는 시스템이므로, 전체 시스템을 제작하여 동작이나 알고리즘을 검증하기에는 그 복잡성이나 경제적 부담, 및 제작과 검증에 많은 시간이 소요되는 문제점이 있다. 본 발명의 배경기술은 대한민국 공개특허 10-2015-0051676호(2015.05.13. 공개, 모듈라 멀티 레벨 컨버터의 변조 방법)에 개시되어 있다. 본 발명의 일 측면에 따르면, 본 발명은 상기와 같은 문제점을 해결하기 위해 창작된 것으로서, MMC(Modular Multi-Level Converter) 전력 변환기를 구성하는 단위인 SM(Sub Module)에 대한 동작을 테스트할 수 있도록 하는, HILS(Hardware In the Loop System)를 이용한 MMC의 구성요소 테스트 장치를 제공하는 데 그 목적이 있다. 본 발명의 일 측면에 따른 HILS를 이용한 MMC의 구성요소 테스트 장치는, MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 종속 전압원에 대응하여 상기 타겟 SM의 커패시터(Cmmc)의 충방전을 테스트하기 위한 전류를 인가하는 전압원 모사회로; 및 상기 MMC 전력 변환기의 타겟 SM의 동작에 대응하여 상기 전압원 모사회로의 전류원 및 스위칭 소자를 제어하고, 상기 전압원 모사회로에 의해 타겟 SM에 인가된 전류에 의해 충방전되는 상기 커패시터(Cmmc)의 전압()을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 한다. 본 발명에 있어서, 상기 전압원 모사회로는, 상기 HILS 제어부로부터 전류의 방향과 크기가 제어되는 전류원(isource); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1); 상기 제1 스위칭 소자(SH1)의 드레인 측에 애노드 측이 연결되는 제1 다이오드(DH1); 상기 제1 다이오드(DH1)의 캐소드 측에 소오스 측이 연결되는 제2 스위칭 소자(SH2); 상기 제2 스위칭 소자(SH2)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제2 다이오드(DH2); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제3 스위칭 소자(SH3); 상기 제3 스위칭 소자(SH3)의 드레인 측에 애노드 측이 연결되는 제3 다이오드(DH3); 상기 제3 다이오드(DH3)의 캐소드 측에 소오스 측이 연결되는 제4 스위칭 소자(SH4); 및 상기 제4 스위칭 소자(SH4)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제4 다이오드(DH4)가 연결되어 구현되는 것을 특징으로 한다. 본 발명에 있어서, 상기 제1 다이오드(DH1)와 상기 제1 스위칭 소자(SH2)의 접속점(A)에 타겟 SM의 커패시터(Cmmc)의 양극(+)이 접속되고, 상기 제3 다이오드(DH3)와 상기 제4 스위칭 소자(SH4)의 접속점(B)에 커패시터(Cmmc)의 음극(-)이 접속되는 것을 특징으로 한다. 본 발명에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 스위칭 소자의 온오프 및 전류(immc)의 방향과 크기에 대응하여 상기 전압원 모사회로의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어하는 것을 특징으로 한다. 본 발명에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 하단 스위치(S2)가 ON인 SF(Switch Function)=0인 경우, 전류(immc)의 방향에 관계없이 커패시터 전압()의 변화는 없으므로, 전류원(isource)의 흐름 및 커패시터(Cmmc)의 충방전에 관여하지 않으며, 상기 타겟 SM의 상단 스위치(S1)가 ON인 SF=1이고 전류(immc)가 음인 경우, 커패시터 전압()이 충전되는 상황을 모사하기 위하여 제1 및 제4 스위칭 소자(SH1 and SH4)의 온(ON) 스위칭 제어를 수행하며, 또한 상기 타겟 SM의 SF=1이고, 전류(immc)가 양인 경우, 커패시터 전압()이 방전되는 상황을 모사하기 위하여 제2 및 제3 스위칭 소자(SH2 and SH3)의 온(ON) 스위칭 제어를 수행하는 것을 특징으로 한다. 본 발명에 있어서, 상기 HILS 제어부는, MMC 시뮬레이션 모델링 결과를 바탕으로, 상기 전류원에 의해 인가되는 전류(immc)의 크기를 제어하는 것을 특징으로 한다. 본 발명에 있어서, 상기 다이오드(DH1 ~ DH4)는, 커패시터(Cmmc)의 쇼트(short) 방지 및 회생 방지용 다이오드인 것을 특징으로 한다. 본 발명의 다른 측면에 따른 HILS를 이용한 MMC의 구성요소 테스트 장치는, MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 타겟 SM의 커패시터(Cmmc)를 테스트하기 위한 전류를 상기 타겟 SM의 지정된 접속점(A, B)에 직접 인가하는 전류 공급부; 및 상기 전류 공급부의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어하며, 또한 상기 타겟 SM의 스위칭 소자(S1, S2)를 온오프를 제어하여 측정되는 커패시터(Cmmc)의 전압(Vcmmc) 값을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 한다. 본 발명에 있어서, 상기 전류 공급부는, HILS 제어부로부터 전류의 방향과 크기가 제어되는 전류원(isource); 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1) 및 제3 스위칭 소자(SH3); 상기 제1 스위칭 소자(SH1) 및 상기 제3 스위칭 소자(SH3)의 드레인 측에 소오스 측이 각기 연결되는 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4); 상기 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4)의 드레인 측이 상기 전류원(isource)의 타 측에 연결되어 구현된 것을 특징으로 한다. 본 발명에 있어서, 상기 제1 스위칭 소자(SH1)와 제2 스위칭 소자(SH2)의 접속점(A)에 상기 타겟 SM의 제1 스위칭 소자(S1)와 제2 스위칭 소자(S2)의 접속점(A)이 연결되고, 상기 제3 스위칭 소자(SH3)와 제4 스위칭 소자(SH4)의 접속점(B)에 상기 타겟 SM의 제2 스위칭 소자(S2)의 접속점(B)이 연결되어 구현된 것을 특징으로 한다. 본 발명의 또 다른 측면에 따른 HILS를 이용한 MMC의 구성요소 테스트 장치는, MMC(Modular Multi-Level Converter) 전력 변환기에서 테스트할 타겟 SM(Sub Module)을 종속 전압원으로 대체하여 시뮬레이션 모델을 생성하고 상기 시뮬레이션 모델의 검증을 수행하는 HILS(Hardware In the Loop System); 상기 종속 전압원에 대응하여 상기 타겟 SM의 커패시터(Cmmc)의 충반전을 테스트하기 위한 전류를 인가하는 충전부와 방전부; 및 상기 MMC 전력 변환기의 타겟 SM의 동작에 대응하여 상기 충전부와 방전부를 각기 제어하고, 상기 충전부와 방전부에 의해 충방전되는 상기 커패시터(Cmmc)의 전압()을 이용하여 상기 시뮬레이션 모델의 검증을 수행하는 HILS 제어부;를 포함하는 것을 특징으로 한다. 본 발명에 있어서, 상기 충전부와 방전부는, 상기 타겟 SM의 기 지정된 점속점(A, B)으로서, 상기 커패시터(Cmmc)가 연결되는 양극(+) 및 음극(-)에 각기 공통으로 연결되는 것을 특징으로 한다. 본 발명에 있어서, 상기 HILS 제어부는, 상기 타겟 SM의 하단 스위치(S2)가 ON인 SF(Switch Function)=0인 경우, 전류(immc)의 방향에 관계없이 커패시터 전압()의 변화는 없으므로, 상기 충전부와 방전부의 제어에 관여하지 않으며, 상기 타겟 SM의 상단 스위치(S1)가 ON인 SF=1이고 전류(immc)가 음인 경우, 커패시터 전압()이 충전되는 상황을 모사하기 위하여 상기 충전부에서 상기 커패시터(Cmmc)에 충전 전류가 흐르도록 제어하며, 또한 상기 타겟 SM의 SF=1이고, 전류(immc)가 양인 경우, 커패시터 전압()이 방전되는 상황을 모사하기 위하여 상기 커패시터(Cmmc)에 충전된 전류를 방전시키기 위하여 상기 방전부를 제어하는 것을 특징으로 한다. 본 발명의 일 측면에 따르면, 본 발명은 MMC 전력 변환기를 구성하는 단위인 SM(Sub Module)에 대한 동작을 테스트할 수 있도록 한다. 이에 따라 전체 시스템을 제작하지 않더라도 시스템을 검증할 수 있도록 하여 전체 시스템을 제작하여 동작을 검증하는 경우에 비하여 경제적 부담 및 제작과 검증에 많은 소요되는 시간을 절감할 수 있도록 한다. 도 1은 일반적인 MMC의 기본 구성을 보인 예시도. 도 2는 하프 브리지 타입(Half Bridge Type) SM으로 구성된 일반적인 MMC의 구성을 보인 예시도. 도 3의 (a)는 일반적인 하프 브리지 타입 SM의 형태를 보인 예시도. 도 3의 (b)는 일반적인 풀 브리지 타입 SM의 형태를 보인 예시도. 도 4는 본 발명의 일 실시예에 따른 HILS를 이용하여 SM의 테스트를 수행하기 위한 HILS의 시뮬레이션 모델과 전압원 모사회로의 구성을 보인 예시도. 도 5는 상기 도 4에 있어서, 전압원 모사회로의 동작 원리를 설명하기 위하여 보인 예시도. 도 6은 상기 도 4에 있어서, SM 블록의 하드웨어인 커패시터(Cmmc)의 전압 특성을 검증하기 위한 장치의 구성을 보인 예시도. 도 7은 본 발명의 HILS를 이용한 MMC의 구성요소 테스트 장치의 또 다른 실시예를 보인 예시도. 도 8은 본 발명의 HILS를 이용한 MMC의 구성요소 테스트 장치의 또 다른 실시예를 보인 예시도. 이하, 첨부된 도면을 참조하여 본 발명에 따른 HILS를 이용한 MMC의 구성요소 테스트 장치의 일 실시예를 설명한다. 이 과정에서 도면에 도시된 선들의 두께나 구성요소의 크기 등은 설명의 명료성과 편의상 과장되게 도시되어 있을 수 있다. 또한, 후술되는 용어들은 본 발명에서의 기능을 고려하여 정의된 용어들로서 이는 사용자, 운용자의 의도 또는 관례에 따라 달라질 수 있다. 그러므로 이러한 용어들에 대한 정의는 본 명세서 전반에 걸친 내용을 토대로 내려져야 할 것이다. 상술한 바와 같이 MMC 전력 변환기의 하드웨어 전체를 대상으로 검증을 수행하기 위해서는 전체 시스템(즉, MMC 전력 변환기)의 제작과 검증에 많은 시간과 비용이 소요되는 문제점이 있다. 또한 MMC는 동일한 SM이 직렬 연결된 구조이므로, 하나의 SM에 대한 설계상의 오류는 전체 SM을 새로 바꾸어야 하는 작업이 필요하기 때문에 전체 시스템을 제작하기 전에 SM에 대한 하드웨어의 검증이 필요하다. 따라서 본 실시예에서는 전체 시스템(즉, MMC 전력 변환기)의 검증에 앞서, 하나의 SM에서의 커패시터(capacitor)의 동작, 하나의 SM 블록, 혹은 지정된 임의의 개수에 대한 SM 블록의 동작을 테스트할 수 있도록 하는 장치 및 방법을 제공하는 것이다. 도 4는 본 발명의 일 실시예에 따른 HILS를 이용하여 SM의 테스트를 수행하기 위한 HILS의 시뮬레이션 모델과 전압원 모사회로의 구성을 보인 예시도이고, 도 5는 상기 도 4에 있어서, 전압원 모사회로의 동작 원리를 설명하기 위하여 보인 예시도이다. 도 4의 (a)는 상기 도 2에 도시된 일반적인 MMC에서 하나의 레그를 보인 예시도이고, 도 4의 (b)는 하나의 레그에 포함된 SM의 커패시터(Cmmc)를 테스트(예 : 충방전 테스트)하기 위한 전압원 모사회로를 보인 예시도이고, 도 4의 (c)는 본 실시예에 따른 HILS에서 구현되는 MMC 레그의 시뮬레이션 모델을 보인 예시도이다. 도 4의 (c)를 참조하면, 본 실시예에 따른 HILS에서는 1개의 SM 블록이 종속 전압원(110a)으로 대체되어 시뮬레이션 모델(소프트웨어로 구현되는 시뮬레이션 모델)로 구현된다. 그리고 상기 시뮬레이션 모델에서 종속 전압원(110a)으로 대체된 1개의 SM의 커패시터(Cmmc)는 도 4의 (b)에 도시된 바와 같은 전압원 모사회로(110)를 통해 테스트하고, 상기 전압원 모사회로(110)를 이용한 테스트를 통해 검출된 상기 커패시터(Cmmc)의 충방전 값(즉, 커패시터 전압)을 HILS에 입력하여 HILS 제어부(도 6의 100)가 기 지정된 알고리즘에 따라 상기 시뮬레이션 모델의 동작을 검증하게 한다. 이때 상기 HILS 제어부(100)는 상기 전압원 모사회로(110)를 제어한다. 이하 도 5를 참조하여 MMC에 적용된 하프 브리지 타입 SM의 테스트 방법에 대해 설명한다. 즉, 상기 SM의 동작(즉, 스위칭 소자의 온/오프)에 대응하여 상기 HILS 제어부(도 6의 100)가 상기 전압원 모사회로(110)를 제어하여 상기 SM의 커패시터(Cmmc)를 충방전시킨다. 도 4의 (c)에 도시된 1개의 SM 블록(즉, 종속 전압원(110a)으로 대체된 1개의 SM 블록)의 출력전압에 해당하는 SM의 출력전압()은 아래의 수학식 1과 같다. 여기서 Switching function(이하 SF)은, 0 혹은 1의 값을 가지며, 상단 스위치가 온인 경우 1, 하단 스위치가 온인 경우 0이다. 다시 말해, SF=1인 경우는 SM에서의 상단 스위치(S1)가 온(on)(도 5의 (a), S1 on, S2 off), SF=0인 경우는 SM에서의 하단 스위치(S2)가 온(on)(도 5의 (a), S1 off, S2 on)을 의미한다. 한편, 상단 스위치(S1)가 온인 경우(즉 SF=1), 전류(immc)의 방향에 관계없이 출력전압()은 커패시터 전압()이 되고, 상단 스위치(S1)가 오프인 경우(즉 SF=0), 전류(immc)의 방향에 관계없이 출력전압()은 0이 된다. 이때 커패시터 전압()은 도 4의 (c)에서 전압원 모사회로(100)를 통해 테스트하여 검출(측정)한 커패시터의 전압 정보(즉, 커패시터의 충방전에 따라 출력되는 값)를 입력으로 받아 상기 수학식 1에 적용한다. 도 4의 (c)에서 커패시터(Cmmc, 120)의 전압인 는 아래 도 5를 참조하여 설명하는 동작에 대응하여 결정된다. 도 5의 (a)에서 전류 방향이 양인 경우(즉, 교류에서 양인 경우), 즉 SF=1인 경우(즉, 상단 스위치 S1이 온인 경우), 커패시터 전압()에 의한 전류가 부하단으로 전달되어 커패시터(Cmmc)는 방전되므로 커패시터 전압()은 감소하게 된다. 반대로 도면에 도시하지는 않았으나 전류(immc)가 음인 경우(즉, 교류에서 음인 경우) 커패시터(Cmmc)는 충전되므로 커패시터 전압()은 상승하게 된다. 한편 도 5의 (b)와 같이 SF=0인 경우, 하단 스위치(S2)가 온 이므로, 양의 전류(immc)는 하단 스위치(S2)의 환류 다이오드(D2)(free wheeling diode)를 통해 흘러가고, 음의 전류(immc)는 하단 스위치(S2)를 통해 흘러가므로 커패시터(Cmmc)가 전력 전달에 관여하지 않으므로 커패시터 전압()의 변화는 없다. 한편 상기 전류(immc)가 음이고 상단 스위치(S1)가 온인 경우에는 커패시터(Cmmc)가 충전되지만, 상기 전류(immc)가 음이고 하단 스위치(S2)가 온인 경우에는 하단 스위치(S2)를 통해 전류가 흐르므로 커패시터 전압()의 변동은 없다. 따라서 상기와 같은 커패시터(Cmmc)의 전압 변동을 모사하기 위하여, 도 6의 (c)에 도시된 바와 같은 전압원 모사회로(110)를 제어한다. 도 6은 상기 도 4에 있어서, SM 블록의 하드웨어인 커패시터(Cmmc, 120)의 전압 특성을 검증하기 위한 장치의 구성을 보인 예시도이며, 특히 MMC 구조에서는 다수의 커패시터가 존재함으로 인해 개별 커패시터의 전압()을 균일하게 하고자 하는 알고리즘(예 : 전압 밸런싱 알고리즘)이 중요하다. 따라서 이러한 알고리즘(예 : 전압 밸런싱 알고리즘)의 검증이 필요하며, 도 6은 상기 알고리즘(예 : 전압 밸런싱 알고리즘)을 검증하기 위한 시뮬레이션 모델에서 종속 전압원(110a)에 대응하는 전압원 모사장치(100)의 구성을 보인 예시도이며, 커패시터(Cmmc, 120) 자체의 하드웨어 검증을 위해 사용된다. 도 6을 참조하여, 본 실시예에 따른 HILS를 통해 SM 블록의 커패시터(Cmmc, 120)를 테스트하기 위한 전압원 모사장치(100)의 동작을 설명한다. 도 6의 (a)는 테스트할 1개의 SM을 보인 예시도이고, 도 6의 (b)는 상기 테스트할 1개의 SM(즉, 타겟 SM)을 대체한 종속 전압원(110a)을 보인 예시도이며, 도 6의 (c)는 상기 종속 전압원(110a)에 대응하는 전압원 모사회로(110)를 보인 예시도이다. 상기 전압원 모사회로(110)는, HILS 제어부(100)로부터 전류의 방향과 크기가 제어되는 전류원(isource), 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1), 상기 제1 스위칭 소자(SH1)의 드레인 측에 애노드 측이 연결되는 제1 다이오드(DH1), 상기 제1 다이오드(DH1)의 캐소드 측에 소오스 측이 연결되는 제2 스위칭 소자(SH2), 상기 제2 스위칭 소자(SH2)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제2 다이오드(DH2), 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제3 스위칭 소자(SH3), 상기 제3 스위칭 소자(SH3)의 드레인 측에 애노드 측이 연결되는 제3 다이오드(DH3), 상기 제3 다이오드(DH3)의 캐소드 측에 소오스 측이 연결되는 제4 스위칭 소자(SH4), 상기 제4 스위칭 소자(SH4)의 드레인 측에 애노드 측이 연결되고 상기 전류원(isource)의 타 측이 캐소드 측에 연결되는 제4 다이오드(DH4)가 연결된다. 여기서 상기 제1 다이오드(DH1)와 상기 제1 스위칭 소자(SH2)의 접속점(A)에 커패시터(Cmmc)의 양극(+)이 접속되고, 상기 제3 다이오드(DH3)와 상기 제4 스위칭 소자(SH4)의 접속점(B)에 커패시터(Cmmc)의 음극(-)이 접속된다. 상기 HILS 제어부(100)는, 상기 도 5를 참조하여 설명한 바와 같이, SM 블록의 스위칭 소자(S1, S2)의 온오프 및 전류(immc)의 방향과 크기에 대응하여 상기 전압원 모사회로(110)의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어한다. 이에 따라 검출(측정)되는 커패시터(Cmmc)의 전압(Vcmmc) 값을 상기 HILS 제어부(100)에 전달함으로써 HILS의 시뮬레이션 모델에 적용할 수 있도록 한다. 즉, 도 6에 도시된 바와 같이, SF(Switch Function)에 따른 커패시터(Cmmc)의 충방전을 모사하기 위하여 구성된, 즉, 전류원(isource), 스위칭 소자(SH1 ~ SH4), 및 다이오드(DH1 ~ DH4)를 포함하여 구성된 전압원 모사회로의 동작은 아래와 같다. 참고로 도 6에서 A, B의 위치는 도 4에 도시된 A, B와 동일한 위치이다. 먼저 SF=0인 경우(즉, 도 5에서 하단 스위치 S2가 온인 경우), 전류(immc)의 방향에 관계없이 커패시터 전압()의 전압 변화는 없다. 여기서 준비(ready) 상태인 경우(즉, SH1 and SH2 on, 또는 SH3 and SH4 on)에 전류원(isource)의 흐름 및 커패시터(Cmmc)의 충방전에 관여하지 않는다. 반대로 SF=1이고(즉, 도 5에서 상단 스위치 S1이 온이고), 전류(immc)가 음인 경우, 상단 스위치(S1) on시에 가 즉시 충전되는 상황을 모사하기 위하여 스위칭 제어동작(SH1 and SH4 on)을 수행한다. 그리고 SF=1이고(즉, 도 5에서 상단 스위치 S1이 온이고), 전류(immc)가 양인 경우, 방전되는 상황을 모사하기 위하여 스위칭 제어동작(SH2 and SH3 on)을 수행한다. 이때 전류(immc)의 크기(즉, 전류원의 크기)는 MMC 시뮬레이션 모델링 결과를 바탕으로 HILS 제어부(100)로부터 지령치를 전달받을 수 있다. 여기서 다이오드(DH1 ~ DH4)는 커패시터(Cmmc)의 쇼트(short) 방지 및 회생 방지용 다이오드이다. 예컨대 만약 제2, 제3 다이오드(DH2, DH4)없이 제2 스위칭 소자(SH2)가 on될 경우 제4 스위칭 소자(SH4)에 연결되어 있는 환류 다이오드(freewheeling diode)를 통해 쇼트 경로(short path)가 생성되므로, 이 쇼트 경로를 제거하기 위해 쇼트 및 회생 방지용 다이오드(DH4)를 삽입한다. 도 7은 본 발명의 HILS를 이용한 MMC의 구성요소 테스트 장치의 다른 실시예를 보인 예시도이다. 도 7은 상기 도 6에 있어서, 전압원 모사회로(110)의 두 접속점(A, B)을 테스트 할 타겟 SM의 대응하는 접속점(A, B)에 곧바로 접속하고, 상기 HILS 제어부(100)에 의해 상기 전류 공급부(120)의 전류원(isource) 및 스위칭 소자(SH1 ~ SH4)를 제어한다. 또한 상기 타겟 SM의 스위칭 소자(S1, S2)를 온오프를 제어하여 검출(측정)되는 커패시터(Cmmc)의 전압(Vcmmc) 값을 상기 HILS 제어부(100)에 전달함으로써 HILS의 시뮬레이션 모델에 적용할 수 있도록 한다. 이때 상기 전류 공급부(120)는 상기 전압원 모사회로(110)에서 환류 다이오드(freewheeling diode)를 포함하지 않는다. 왜냐하면 상기 타겟 SM의 스위칭 소자(S1, S2)에 의해 쇼트 경로가 생성되지 않기 때문이다. 상기 전류 공급부(120)는, HILS 제어부(100)로부터 전류의 방향과 크기가 제어되는 전류원(isource), 상기 전류원(isource)의 일 측에 소오스 측이 연결되는 제1 스위칭 소자(SH1) 및 제3 스위칭 소자(SH3), 상기 제1 스위칭 소자(SH1) 및 상기 제3 스위칭 소자(SH3)의 드레인 측에 소오스 측이 각기 연결되는 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4)가 연결되고, 상기 제2 스위칭 소자(SH2) 및 제4 스위칭 소자(SH4)의 드레인 측이 상기 전류원(isource)의 타 측에 연결된다. 여기서 상기 제1 스위칭 소자(SH1)와 제2 스위칭 소자(SH2)의 접속점(A)에 상기 타겟 SM의 제1 스위칭 소자(S1)와 제2 스위칭 소자(S2)의 접속점(A)이 연결되고, 상기 제3 스위칭 소자(SH3)와 제4 스위칭 소자(SH4)의 접속점(B)에 상기 타겟 SM의 제2 스위칭 소자(S2)의 접속점(B)이 연결된다. 도 8은 본 발명의 HILS를 이용한 MMC의 구성요소 테스트 장치의 또 다른 실시예를 보인 예시도로서, 상기 도 6에서 A, B지점에 충전부(111)와 방전부(112)가 공통으로 연결된다. 도 8을 참조하면, SF=0인 경우(즉, 도 5에서 하단 스위치 S2가 온인 경우) 커패시터 전압()의 변화는 없다. 여기서 준비(ready) 상태인 경우에 충전기 및 방전기의 동작은 없다. 즉, 상기 HILS 제어부(100)는 상기 충전부(111)와 방전부(112)를 제어하지 않는다. 한편 SF=1이고(즉, 도 5에서 상단 스위치 S1가 온이고), 전류(immc)가 음인 경우에는 충전 동작이므로, 상기 HILS 제어부(100)는 상기 전류(immc)의 크기와 방향(음 방향)에 해당하는 전류가 상기 충전부(111)에서 커패시터(Cmmc)로 흘러 충전을 수행하도록 제어한다. 그리고 SF=1이고, 전류(immc)가 양인 경우에는 방전 동작이므로, 상기 HILS 제어부(100)는 상기 전류(immc)의 크기와 방향(양 방향)에 해당하는 전류가 상기 방전부(112)에서 커패시터(Cmmc)를 방전하도록 제어한다. 이때 상기 충방전에 따른 커패시터 전압(vcmmc)의 크기는 HILS 제어부(100)로 전송되어 도 4의 (c)에서 SM의 출력 전압()의 크기 결정에 사용된다. 상기와 같이 본 실시예는 MMC 전력 변환기를 구성하는 단위인 SM(Sub Module)에 대한 동작을 테스트할 수 있도록 함으로써, 전체 시스템을 제작하지 않더라도 시스템을 검증할 수 있도록 하여 전체 시스템을 제작하여 동작을 검증하는 경우에 비하여 경제적 부담 및 제작과 검증에 많은 소요되는 시간을 절감할 수 있도록 하는 효과가 있다. 이상으로 본 발명은 도면에 도시된 실시예를 참고로 하여 설명되었으나, 이는 예시적인 것에 불과하며, 당해 기술이 속하는 분야에서 통상의 지식을 가진 자라면 이로부터 다양한 변형 및 균등한 타 실시예가 가능하다는 점을 이해할 것이다. 따라서 본 발명의 기술적 보호범위는 아래의 특허청구범위에 의해서 정하여져야 할 것이다. 또한 본 명세서에서 설명된 구현은, 예컨대, 방법 또는 프로세스, 장치, 소프트웨어 프로그램, 데이터 스트림 또는 신호로 구현될 수 있다. 단일 형태의 구현의 맥락에서만 논의(예컨대, 방법으로서만 논의)되었더라도, 논의된 특징의 구현은 또한 다른 형태(예컨대, 장치 또는 프로그램)로도 구현될 수 있다. 장치는 적절한 하드웨어, 소프트웨어 및 펌웨어 등으로 구현될 수 있다. 방법은, 예컨대, 컴퓨터, 마이크로프로세서, 집적 회로 또는 프로그래밍 가능한 로직 디바이스 등을 포함하는 프로세싱 디바이스를 일반적으로 지칭하는 프로세서 등과 같은 장치에서 구현될 수 있다. 프로세서는 또한 최종-사용자 사이에 정보의 통신을 용이하게 하는 컴퓨터, 셀 폰, 휴대용/개인용 정보 단말기(personal digital assistant: "PDA") 및 다른 디바이스 등과 같은 통신 디바이스를 포함한다. 100 : HILS 제어부 110 : 전압원 모사회로 110a : 종속 전압원 111 : 충전부 112 : 방전부 120 : 전류 공급부 [EN KR20200124459A]: Component testing device of MMC using HILS{APPARATUS FOR TESTING COMPONENTS OF MMC USING HILS} The present invention relates to an MMC component testing apparatus using HILS, and more particularly, to test the operation of a sub module (SM), which is a unit constituting a Modular Multi-Level Converter (MMC) power converter, It relates to a component test device of MMC using HILS (Hardware In the Loop System). In general, a modular multi-level converter (MMC) is a type of multi-level converter and is known as a circuit structure suitable for a voltage-type ultra-high voltage direct current (HVDC) system. The modular multi-level converter (MMC) has a type of cascade connection of a unit structure called a sub module (SM) using an insulated gate bipolar transistor (IGBT) as a switching element. It has a much higher level than the power conversion device (or power converter) for medium voltage drive, which was the application field of the multi-level converter of 1 is an exemplary diagram showing a basic configuration of a general MMC, and FIG. 2 is an exemplary diagram illustrating a configuration of a general MMC composed of a half bridge type SM. In addition, (a) of FIG. 3 is an exemplary view showing the form of a general half-bridge type SM, and (b) of FIG. 3 is an exemplary view showing the form of a general full-bridge type SM. For reference, (b) of FIG. 3 is an example of applying MMC to DC/AC power conversion of three phases, and has three phases. On the other hand, one phase is composed of an upper arm and a lower arm. Here, the sub-module (hereinafter, SM) means one unit of the switching block of the MMC, and the half-bridge type SM as shown in Fig. 3(a) and the full bridge type SM as shown in Fig. 3(b) are have. Recently, the MMC as described above has been widely applied to a melty level power converter such as a voltage type HVDC. In the case of the HVDC (High Voltage Direct Current), a plurality of SMs are connected in series to reduce the harmonic component of the output voltage of the power converter while blocking the high voltage. For example, in the case of the HVDC, for example, assuming that each arm (eg, upper arm, lower arm) has 200 SMs, in the case of 3 phases, 6*200=1,200 SMs are connected, and MMCs are consecutively Since it is connected (back to back), there are 2,400 SMs in the system (ie, MMC power converter). On the other hand, when the SM is configured in a half-bridge form as shown in FIG. 3A, 4,800 power switching elements are required in one system, and 9,600 when the SM is configured in a full-bridge form as shown in FIG. 3B. Two switching elements for power are required in one system. As such a power converter composed of MMC is a system that requires a number of switching elements for power, there is a problem that it takes a lot of time to manufacture and verify the complexity, economic burden, and manufacturing and verification of the entire system to verify the operation or algorithm. . The background technology of the present invention is disclosed in Korean Patent Laid-Open No. 10-2015-0051676 (published on May 13, 2015, modulation method of a modular multi-level converter). According to an aspect of the present invention, the present invention was created to solve the above problems, and it is possible to test the operation of the SM (Sub Module), which is a unit constituting the Modular Multi-Level Converter (MMC) power converter. The purpose of this is to provide a component testing device of MMC using HILS (Hardware In the Loop System). The component testing apparatus of MMC using HILS according to an aspect of the present invention generates a simulation model by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source, and the simulation HILS (Hardware In the Loop System) that performs model verification; A voltage source matrix furnace for applying a current for testing the charging/discharging of the capacitor Cmmc of the target SM in response to the dependent voltage source; And a voltage of the capacitor Cmmc, which controls a current source and a switching element to the voltage source matrix in response to the operation of the target SM of the MMC power converter, and is charged and discharged by the current applied to the target SM by the voltage source matrix. (It characterized in that it comprises a;) HILS control unit for performing verification of the simulation model. In the present invention, the voltage source matrix includes: a current source whose direction and magnitude of current is controlled from the HILS controller; A first switching element (SH) having a source side connected to one side of the current source (isource)1); The first switching element (SH1), the anode side is connected to the drain side of the first diode DH1); The first diode (DH1The second switching element (SH) to which the source side is connected to the cathode side of2); The second switching element (SH2), the anode side is connected to the drain side, and the other side of the current source is connected to the cathode side.2); The third switching element (SH) to which the source side is connected to one side of the current source (isource)3); The third switching element (SH3) To the drain side of the third diode (DH3); The third diode (DH3) To the cathode side of the fourth switching element (SH4); And the fourth switching element SH4), the anode side is connected to the drain side, and the other side of the current source is connected to the cathode side.4) Is connected and implemented. In the present invention, the first diode (DH1) And the first switching element SH2), the anode (+) of the capacitor (Cmmc) of the target SM is connected to the connection point (A), and the third diode (DH3) And the fourth switching element (SH4), the cathode (-) of the capacitor Cmmc is connected to the connection point B. In the present invention, the HILS control unit, the current source (isource) and the switching element (SH1 ~ SH4) To control. In the present invention, the HILS control unit, the lower switch of the target SM (S2When SF (Switch Function) = 0, where) is ON, the capacitor voltage () Because there is no change, it is not involved in the flow of the current source and the charging and discharging of the capacitor Cmmc, and the upper switch S of the target SM1) Is ON and SF=1 and current (immc) is negative, capacitor voltage () To simulate the charging situation, the first and fourth switching elements (SH1 and SH4) To perform ON switching control, and if SF=1 of the target SM and current immc is positive, the capacitor voltage () In order to simulate a discharge situation, the second and third switching elements (SH2 and SH3) To perform ON switching control. In the present invention, the HILS control unit is characterized in that it controls the magnitude of the current immc applied by the current source based on the MMC simulation modeling result. In the present invention, the diode (DH1 ~ DH4) Is a diode for preventing short and regeneration of the capacitor Cmmc. In the component testing apparatus of MMC using HILS according to another aspect of the present invention, a simulation model is generated by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source, and the simulation HILS (Hardware In the Loop System) that performs model verification; A current supply unit for directly applying a current for testing the capacitor (Cmmc) of the target SM to the designated connection points (A, B) of the target SM; And a current source of the current supply and a switching element SH1 ~ SH4) And the switching element (S) of the target SM1, S2It characterized in that it comprises a; and a HILS control unit for performing verification of the simulation model using the voltage (Vcmmc) value of the capacitor (Cmmc) measured by controlling the on-off). In the present invention, the current supply unit, a current source (isource) for controlling the direction and magnitude of the current from the HILS control unit; A first switching element (SH) having a source side connected to one side of the current source (isource)1) And a third switching element (SH3); The first switching element (SH1) And the third switching element (SH3), the source side is connected to the drain side of the second switching element (SH2) And the fourth switching element (SH4); The second switching element (SH2) And the fourth switching element (SH4), the drain side is connected to the other side of the current source (isource). In the present invention, the first switching element (SH1) And the second switching element (SH2The first switching element (S) of the target SM at the connection point (A) of1) And the second switching element (S2) Of the connection point (A) is connected, the third switching element (SH3) And the fourth switching element (SH4) The second switching element (S) of the target SM at the connection point (B)2) Of the connection point (B) is connected and implemented. The component testing apparatus of MMC using HILS according to another aspect of the present invention generates a simulation model by replacing a target SM (Sub Module) to be tested in a Modular Multi-Level Converter (MMC) power converter with a dependent voltage source, and the HILS (Hardware In the Loop System) to verify the simulation model; A charging unit and a discharging unit for applying a current for testing the charging and recharging of the capacitor Cmmc of the target SM in response to the dependent voltage source; And a voltage of the capacitor Cmmc charged and discharged by the charging unit and the discharging unit, respectively controlling the charging unit and the discharging unit in response to the operation of the target SM of the MMC power converter (It characterized in that it comprises a;) HILS control unit for performing verification of the simulation model. In the present invention, the charging unit and the discharging unit are pre-designated dot points (A, B) of the target SM, respectively, which are connected in common to the positive (+) and negative (-) to which the capacitor (Cmmc) is connected. It is characterized. In the present invention, the HILS control unit, the lower switch of the target SM (S2When SF (Switch Function) = 0, where) is ON, the capacitor voltage () Because there is no change, it is not involved in the control of the charging part and the discharging part,1) Is ON and SF=1 and current (immc) is negative, capacitor voltage (In order to simulate a situation in which) is charged, the charging unit controls a charging current to flow through the capacitor Cmmc, and when SF=1 of the target SM and the current immc is positive, the capacitor voltage () Is characterized in that the discharging unit is controlled to discharge the current charged in the capacitor Cmmc in order to simulate a discharge situation. According to an aspect of the present invention, the present invention enables testing of an operation of a sub module (SM), which is a unit constituting an MMC power converter. Accordingly, it is possible to verify the system even if the entire system is not manufactured, thereby reducing the economic burden and time required for manufacturing and verification compared to the case of verifying the operation by manufacturing the entire system. 1 is an exemplary view showing a basic configuration of a general MMC. 2 is an exemplary view showing the configuration of a general MMC composed of a half-bridge type SM. Figure 3 (a) is an exemplary view showing the form of a general half-bridge type SM. 3(b) is an exemplary view showing a general full bridge type SM. 4 is an exemplary view showing the configuration of a simulation model of HILS and a voltage source matrix for performing a test of SM using HILS according to an embodiment of the present invention. 5 is an exemplary view shown to explain the principle of operation of a voltage source matrix in FIG. 4. 6 is an exemplary view showing the configuration of a device for verifying voltage characteristics of a capacitor Cmmc, which is hardware of an SM block, in FIG. 4. Figure 7 is an exemplary view showing another embodiment of the component test device of the MMC using the HILS of the present invention. Figure 8 is an exemplary view showing another embodiment of the component test device of the MMC using the HILS of the present invention. Hereinafter, an embodiment of an MMC component testing apparatus using HILS according to the present invention will be described with reference to the accompanying drawings. In this process, the thickness of the lines or the size of components shown in the drawings may be exaggerated for clarity and convenience of description. In addition, terms to be described later are terms defined in consideration of functions in the present invention and may vary according to the intention or custom of users or operators. Therefore, definitions for these terms should be made based on the contents throughout the present specification. As described above, in order to perform verification for the entire hardware of the MMC power converter, there is a problem that a lot of time and cost are required to manufacture and verify the entire system (ie, MMC power converter). In addition, since the MMC has a structure in which the same SM is connected in series, a design error for one SM requires the work of replacing the entire SM, and therefore hardware verification for the SM is required before manufacturing the entire system. Therefore, in this embodiment, before verifying the entire system (i.e., MMC power converter), the operation of the capacitor in one SM, one SM block, or the operation of the SM blocks for a specified number is tested. It is to provide an apparatus and a method to enable it. FIG. 4 is an exemplary diagram showing the configuration of a simulation model of HILS and a voltage source matrix for performing a SM test using HILS according to an embodiment of the present invention, and FIG. 5 is a diagram illustrating the configuration of a voltage source matrix It is an exemplary diagram shown to explain the operation principle of. 4(a) is an exemplary view showing one leg in the general MMC shown in FIG. 2, and FIG. 4(b) is a test for a capacitor (Cmmc) of SM included in one leg (e.g., charging). Discharge test) is an exemplary diagram showing a voltage source matrix path, and FIG. 4C is an exemplary diagram showing a simulation model of an MMC leg implemented in HILS according to the present embodiment. Referring to (c) of FIG. 4, in the HILS according to the present embodiment, one SM block is replaced with a dependent voltage source 110a and implemented as a simulation model (a simulation model implemented by software). And one SM capacitor (Cmmc) replaced by the dependent voltage source 110a in the simulation model is tested through the voltage source matrix furnace 110 as shown in FIG. 4B, and the voltage source matrix is used as the voltage source matrix. By inputting the charge/discharge value (i.e., capacitor voltage) of the capacitor (Cmmc) detected through the test using (110) into HILS, the HILS control unit (100 in FIG. 6) performs the operation of the simulation model according to a predetermined algorithm. Let them verify. At this time, the HILS control unit 100 controls the voltage source parent society furnace 110. Hereinafter, a test method of the half-bridge type SM applied to the MMC will be described with reference to FIG. 5. That is, in response to the operation of the SM (that is, on/off of the switching element), the HILS controller (100 in FIG. 6) controls the voltage source matrix furnace 110 to charge/discharge the capacitor Cmmc of the SM. Let it. The output voltage of the SM corresponding to the output voltage of one SM block (that is, one SM block replaced by the dependent voltage source 110a) shown in FIG. 4C () Is as shown in Equation 1 below. Here, the switching function (hereinafter, SF) has a value of 0 or 1, and is 1 when the upper switch is on, and 0 when the lower switch is on. In other words, in the case of SF = 1, the upper switch S1 in the SM is on (Fig. 5 (a), S1 on, S2 off), when SF = 0, the lower switch (S2) of the SM is on (Fig. 5 (a), S1 off, S2 on). Meanwhile, the upper switch (S1) Is on (i.e. SF=1), regardless of the direction of the current (immc), the output voltage () Is the capacitor voltage (), and the upper switch (S1) Is off (i.e. SF=0), regardless of the direction of the current (immc), the output voltage () Becomes 0. At this time, the capacitor voltage () Is the voltage information of the capacitor detected (measured) by testing through the voltage source matrix furnace 100 in (c) of FIG. 4 (ie, the value output according to the charging and discharging of the capacitor) as an input, and the equation 1 Apply to In Figure 4 (c), the voltage of the capacitor (Cmmc, 120) Is determined corresponding to the operation described with reference to FIG. 5 below. In Figure 5 (a), when the current direction is positive (that is, when it is positive in alternating current), that is, when SF = 1 (ie, upper switch S1Is on), capacitor voltage () Is transferred to the load